## Contents
SEPD Network Headroom Report 2022 Summary
Our Network Headroom Report (NHR) is published to enable customers, developers, generators, local authorities and other interested third parties to view the possible headroom capacity at our Primary Substations and Bulk Supply Points (BSP) up to 2050. SSEN have used the latest Distribution Future Energy Scenarios (DFES) data to inform four scenarios of demand and generation forecasts. SSEN best view of the future demand and generation needs on our network is aligned to the Customer Transformation scenario. Although the NHR provides a view of the future in terms of our potential available capacity and constraints on our network, we would encourage any party using this information in their decision-making process to engage with us ahead of making an application to connect or offer flexible services.
Network Headroom Report Contents
Tab | Description
Key Information | This tab provides some additional detail to assist users with how to read the data presented within this report.
Primary Headroom Dem | This tab provides the demand headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
Primary Headroom Gen | This tab provides the generation headroom capacity at each of our Primary substations, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Dem | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
BSP Headroom Gen | This tab provides the demand headroom capacity at each of our BSP, grid references, connectivity upto the Grid Supply Point and upstream constraints.
LEP Reference | This tab provides information on the LEPs, local authorities and the connected GSPs, BSPs and Primaries that support those areas
May 2022 Version 1.1

## Key Information
SEPD Network Headroom Report 2022 Key Information
Our Network Headroom Report (NHR) has been developed to be used in conjunction with our others documents that combine to make the full Network Development Plan; the other documents to reference are the Network Development Plan Methodology & Assumptions and Network Development Report. The capacity that demand and generation growth is measured against is the firm capacity of the primary substation or BSP as per out Load Indices submission to Ofgem and as indicated by our Long Term Development Statement. Firm capacity means the available capacity on the network with a single feed on outage; for instance a twin transformer sites firm capacity would be the lowest capacity available on a single transformer. Alternatively, for single transformer sites the firm capacity is based on the backfeed supply available to restore supplies; this may be limited by the backfeed circuit capacity rather than the transformer providing the backfeed. When reviewing the headroom reports for demand and generation the following applies: GREEN and POSTIVE VALUES = Capacity is forecast to be available RED and NEGATIVE VALUES = There are constraints forecast It must be noted that forecasts in RED do not mean that connections cannot be made; there are opportunities through flexible services that can enable connections without triggering network reinforcement. We would encourage any developer, generator or customer to contact us to discuss their connection and available opportuinites to connect. The data shown within this NHR is used by us to identify long term investment opportunities where there are constraints highlighted. As the forecast is scenario based, these constraints are subject to change and will be reviewed and published annually by SEPD.
May 2022
Version 1.1

## Primary Headroom Dem
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Demand Headroom Winter MVA | [13 empty] | Demand Headroom Summer MVA | [13 empty] | Demand Headroom Spring/Autumn MVA
[6 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH | ALDERNEY | MINIMUM HEADROOM | SZ 04270 95141 | YES | 8.2208 | 8.0122 | 7.7583 | 7.4567 | 7.081 | 6.6435 | 6.132 | 5.5696 | 4.8276 | 3.9697 | 1.0686 | -2.3676 | -3.1133 | -3.5866 | 14.0474 | 13.9402 | 13.8155 | 13.66 | 13.5044 | 13.3232 | 13.067 | 12.6558 | 12.1191 | 11.4914 | 9.3756 | 6.8872 | 6.3786 | 4.3829 | 11.5937 | 11.4663 | 11.3052 | 11.1128 | 10.903 | 10.6623 | 10.1624 | 9.5769 | 8.8278 | 7.9792 | 5.5423 | 2.4971 | 0.61746 | -0.6047
|  | ALDERNEY | CT |  |  | 8.2208 | 8.0237 | 7.7944 | 7.5139 | 7.2091 | 6.8677 | 6.4906 | 6.0753 | 5.5467 | 4.8917 | 2.5938 | -1.2616 | -2.7692 | -3.5395 | 14.0474 | 13.9402 | 13.8155 | 13.66 | 13.5044 | 13.3316 | 13.1412 | 12.9318 | 12.6577 | 12.1659 | 10.5175 | 7.7625 | 6.6943 | 4.6453 | 11.5937 | 11.4663 | 11.3178 | 11.1312 | 10.9391 | 10.7245 | 10.4742 | 10.1592 | 9.7479 | 9.0392 | 6.6733 | 2.9331 | 0.61746 | -0.6047
|  | ALDERNEY | LW |  |  | 8.2362 | 8.0122 | 7.7583 | 7.4567 | 7.081 | 6.6435 | 6.132 | 5.5696 | 4.8276 | 3.9697 | 1.0686 | -2.3676 | -3.1133 | -3.5866 | 14.0642 | 13.9534 | 13.8214 | 13.6688 | 13.5074 | 13.3232 | 13.067 | 12.6558 | 12.1191 | 11.4914 | 9.3756 | 6.8872 | 6.3786 | 6.0515 | 11.609 | 11.4695 | 11.3052 | 11.1128 | 10.903 | 10.6623 | 10.1624 | 9.5769 | 8.8278 | 7.9792 | 5.5423 | 2.4971 | 1.371 | 0.66645
|  | ALDERNEY | ST |  |  | 8.3781 | 8.2803 | 8.1732 | 8.0508 | 7.8993 | 7.7222 | 7.5144 | 7.2736 | 6.9297 | 6.5095 | 4.7742 | 0.27281 | -1.9228 | -2.4567 | 14.1177 | 14.0552 | 13.9851 | 13.909 | 13.8222 | 13.7236 | 13.6105 | 13.481 | 13.2999 | 13.0891 | 12.1379 | 8.7008 | 6.9902 | 6.5328 | 11.6868 | 11.6185 | 11.5424 | 11.4578 | 11.3565 | 11.2398 | 11.1046 | 10.9487 | 10.7253 | 10.4469 | 9.0531 | 4.7164 | 2.6153 | 2.1174
|  | ALDERNEY | SP |  |  | 8.3926 | 8.3043 | 8.2045 | 8.0977 | 7.98 | 7.8511 | 7.7088 | 7.5441 | 7.3295 | 7.0789 | 6.1568 | 3.1359 | 0.19016 | -0.66151 | 14.1249 | 14.0644 | 13.995 | 13.9233 | 13.8544 | 13.7804 | 13.6999 | 13.6075 | 13.4883 | 13.3468 | 12.8125 | 10.8723 | 8.0908 | 4.3829 | 11.6976 | 11.6337 | 11.5612 | 11.4856 | 11.4077 | 11.324 | 11.2326 | 11.1269 | 10.9874 | 10.8312 | 10.1878 | 7.4839 | 4.657 | 3.8519
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT | MINIMUM HEADROOM | SU 85976 48834 | YES | 5.8286 | 5.3798 | 4.8822 | 4.3357 | 3.546 | 2.6851 | 1.7442 | 0.73054 | -0.65209 | -2.011 | -5.1018 | -9.2102 | -12.0748 | -14.109 | 10.2853 | 9.9994 | 9.6729 | 9.2956 | 8.8238 | 8.3001 | 7.7099 | 7.0665 | 6.1237 | 5.2062 | 3.2792 | 0.7184 | -1.4775 | -3.4271 | 7.1744 | 6.7612 | 6.2963 | 5.7786 | 5.0441 | 4.2414 | 3.3585 | 2.4042 | 1.0828 | -0.21347 | -3.1024 | -6.8348 | -9.2413 | -10.9548
|  | ALDERSHOT | CT |  |  | 5.9264 | 5.5664 | 5.1632 | 4.6792 | 4.1166 | 3.4965 | 2.8382 | 2.1201 | 1.1901 | -0.17457 | -3.3573 | -8.5096 | -12.0748 | -14.109 | 10.2853 | 10.0192 | 9.7153 | 9.3325 | 8.9414 | 8.5068 | 8.0364 | 7.5189 | 6.8283 | 5.8869 | 3.8029 | 0.7184 | -1.4775 | -3.4271 | 7.2455 | 6.911 | 6.5303 | 6.0655 | 5.5443 | 4.9587 | 4.3343 | 3.6512 | 2.7578 | 1.4587 | -1.5142 | -6.1527 | -9.2413 | -10.9548
|  | ALDERSHOT | LW |  |  | 5.8286 | 5.3798 | 4.8822 | 4.3357 | 3.546 | 2.6851 | 1.7442 | 0.73054 | -0.65209 | -2.011 | -5.1018 | -9.2102 | -11.1109 | -12.4014 | 10.2857 | 9.9994 | 9.6729 | 9.2956 | 8.8238 | 8.3001 | 7.7099 | 7.0665 | 6.1237 | 5.2062 | 3.2792 | 0.92934 | 0.032263 | -0.59858 | 7.1744 | 6.7612 | 6.2963 | 5.7786 | 5.0441 | 4.2414 | 3.3585 | 2.4042 | 1.0828 | -0.21347 | -3.1024 | -6.8348 | -8.4489 | -9.5222
|  | ALDERSHOT | ST |  |  | 6.2476 | 6.0833 | 5.9006 | 5.6717 | 5.4074 | 5.1117 | 4.781 | 4.4223 | 3.9745 | 3.5037 | 1.2295 | -3.2987 | -5.8109 | -7.305 | 10.5172 | 10.3895 | 10.2423 | 10.0471 | 9.8347 | 9.5974 | 9.3288 | 9.0355 | 8.6668 | 8.2936 | 6.4709 | 2.9561 | 0.89475 | -0.85195 | 7.5556 | 7.4076 | 7.2367 | 7.0201 | 6.7682 | 6.4867 | 6.1698 | 5.8246 | 5.3928 | 4.9509 | 2.7542 | -1.499 | -3.7245 | -4.975
|  | ALDERSHOT | SP |  |  | 6.2819 | 6.1244 | 5.9647 | 5.7769 | 5.5681 | 5.3378 | 5.1082 | 4.8294 | 4.5094 | 4.1451 | 2.6617 | -1.7189 | -4.3177 | -5.5415 | 10.5324 | 10.4028 | 10.2644 | 10.0914 | 9.927 | 9.7426 | 9.5529 | 9.3216 | 9.0518 | 8.739 | 7.4473 | 3.6282 | 0.64175 | -2.4061 | 7.5841 | 7.4388 | 7.2878 | 7.1098 | 6.9171 | 6.7029 | 6.4885 | 6.2225 | 5.9169 | 5.5761 | 4.1594 | -0.04303 | -2.3913 | -3.4352
MELKSHAM GSP | CHIPPENHAM | ALDERTON | MINIMUM HEADROOM | ST 84609 84059 | YES | 0.15877 | -0.045382 | -0.25615 | 3.8164 | 3.5239 | 3.2255 | 2.9097 | 2.549 | 2.1472 | 1.8177 | 1.1175 | 0.37396 | 0.23694 | 0.17654 | 0.92148 | 0.82536 | 0.72184 | 5.8034 | 5.6604 | 5.5139 | 5.3541 | 5.1645 | 4.9407 | 4.7543 | 4.4188 | 4.0609 | 3.9994 | 3.9728 | -0.29084 | -0.47649 | -0.66863 | 4.3226 | 4.0563 | 3.7844 | 3.4949 | 3.1613 | 2.7858 | 2.4795 | 1.846 | 1.1732 | 1.0517 | 0.99892
|  | ALDERTON | CT |  |  | 0.34307 | 0.23643 | 0.11887 | 4.2868 | 4.1146 | 3.9373 | 3.7407 | 3.5283 | 3.2879 | 2.982 | 2.4188 | 1.5636 | 1.0794 | 0.92915 | 0.97136 | 0.90395 | 0.82755 | 5.9367 | 5.8406 | 5.7408 | 5.6239 | 5.4951 | 5.3415 | 5.1489 | 4.8554 | 4.4304 | 4.167 | 3.9923 | -0.131 | -0.23126 | -0.34229 | 4.7321 | 4.5728 | 4.4086 | 4.2251 | 4.0262 | 3.7994 | 3.5103 | 2.9948 | 2.2271 | 1.7997 | 1.6681
|  | ALDERTON | LW |  |  | 0.15877 | -0.045382 | -0.25615 | 3.8164 | 3.5239 | 3.2255 | 2.9097 | 2.549 | 2.1472 | 1.8177 | 1.1175 | 0.37396 | 0.23694 | 0.17654 | 0.92148 | 0.82536 | 0.72184 | 5.8034 | 5.6604 | 5.5139 | 5.3541 | 5.1645 | 4.9407 | 4.7543 | 4.4188 | 4.0609 | 3.9994 | 3.9728 | -0.29084 | -0.47649 | -0.66863 | 4.3226 | 4.0563 | 3.7844 | 3.4949 | 3.1613 | 2.7858 | 2.4795 | 1.846 | 1.1732 | 1.0517 | 0.99892
|  | ALDERTON | ST |  |  | 0.43559 | 0.3871 | 0.32959 | 4.5552 | 4.4554 | 4.3507 | 4.2421 | 4.1244 | 3.994 | 3.8579 | 3.2492 | 2.4954 | 2.1277 | 1.9358 | 1.0316 | 1.0019 | 0.96433 | 6.1105 | 6.0533 | 5.9921 | 5.9263 | 5.8532 | 5.768 | 5.6879 | 5.2815 | 4.8034 | 4.5775 | 4.3875 | -0.042817 | -0.087674 | -0.14153 | 4.9877 | 4.8955 | 4.7984 | 4.6973 | 4.5874 | 4.4646 | 4.3379 | 3.7591 | 3.0555 | 2.7254 | 2.5571
|  | ALDERTON | SP |  |  | 0.468 | 0.43157 | 0.39275 | 4.642 | 4.5427 | 4.4446 | 4.3441 | 4.2324 | 4.1186 | 3.9534 | 3.3955 | 2.0958 | 1.3822 | 0.94011 | 1.0411 | 1.0146 | 0.98541 | 6.1437 | 6.0911 | 6.0398 | 5.9852 | 5.921 | 5.854 | 5.768 | 5.4494 | 4.657 | 4.2783 | 4.0352 | -0.014486 | -0.048822 | -0.085531 | 5.0658 | 4.975 | 4.8855 | 4.7936 | 4.6905 | 4.5853 | 4.434 | 3.9169 | 2.7025 | 2.0579 | 1.6661
BRAMLEY (FLEE) | ALTON | ALRESFORD | MINIMUM HEADROOM | SU 59684 32511 | YES | -0.075136 | -0.8311 | -1.6195 | 10.5314 | 9.364 | 8.1657 | 6.8941 | 5.516 | 3.9099 | 2.5443 | -0.54592 | -4.1321 | -5.0549 | -5.4918 | 1.9515 | 1.5365 | 1.1173 | 16.6648 | 16.0767 | 15.4713 | 14.8063 | 14.0649 | 13.1279 | 12.3694 | 10.895 | 9.2443 | 8.282 | 7.0829 | -1.1023 | -1.7478 | -2.4241 | 12.8344 | 11.7803 | 10.6963 | 9.5362 | 8.2723 | 6.7858 | 5.5272 | 2.7406 | -0.48061 | -1.2965 | -1.6985
|  | ALRESFORD | CT |  |  | 0.50779 | 0.062737 | -0.42095 | 12.0203 | 11.2791 | 10.5051 | 9.6806 | 8.7431 | 7.7307 | 6.4257 | 3.7038 | -0.93466 | -3.7757 | -4.6031 | 2.1512 | 1.8427 | 1.5233 | 17.159 | 16.7267 | 16.2654 | 15.7607 | 15.1686 | 14.5154 | 13.7149 | 12.2396 | 9.9273 | 8.282 | 7.0829 | -0.6619 | -1.0652 | -1.5054 | 13.9854 | 13.3413 | 12.665 | 11.9371 | 11.0979 | 10.1843 | 8.9704 | 6.4956 | 2.3617 | -0.14168 | -0.86964
|  | ALRESFORD | LW |  |  | -0.075136 | -0.8311 | -1.6195 | 10.5314 | 9.364 | 8.1657 | 6.8941 | 5.516 | 3.9099 | 2.5443 | -0.54592 | -4.1321 | -5.0549 | -5.4918 | 1.9515 | 1.5365 | 1.1173 | 16.6648 | 16.0767 | 15.4713 | 14.8063 | 14.0649 | 13.1279 | 12.3694 | 10.895 | 9.2443 | 8.842 | 8.653 | -1.1023 | -1.7478 | -2.4241 | 12.8344 | 11.7803 | 10.6963 | 9.5362 | 8.2723 | 6.7858 | 5.5272 | 2.7406 | -0.48061 | -1.2965 | -1.6985
|  | ALRESFORD | ST |  |  | 0.75799 | 0.47973 | 0.18533 | 12.8531 | 12.4027 | 11.9382 | 11.4565 | 10.9349 | 10.3543 | 9.7931 | 7.4945 | 4.3721 | 2.6807 | 1.553 | 2.3148 | 2.1137 | 1.9149 | 17.6939 | 17.4221 | 17.1406 | 16.8414 | 16.5133 | 16.141 | 15.7898 | 14.2036 | 12.0877 | 10.8335 | 9.574 | -0.41816 | -0.65989 | -0.91824 | 14.7894 | 14.3993 | 13.9948 | 13.571 | 13.1098 | 12.5912 | 12.0947 | 9.9598 | 7.0677 | 5.5543 | 4.5625
|  | ALRESFORD | SP |  |  | 0.83216 | 0.59003 | 0.35897 | 13.1092 | 12.5714 | 12.0305 | 11.484 | 10.885 | 10.2655 | 9.5543 | 7.1846 | 2.0887 | -0.55034 | -2.0887 | 2.3402 | 2.149 | 1.9761 | 17.7934 | 17.5012 | 17.2042 | 16.898 | 16.5514 | 16.1848 | 15.7869 | 14.3963 | 11.0734 | 9.1013 | 7.1713 | -0.36076 | -0.57618 | -0.78038 | 15.0006 | 14.5561 | 14.1074 | 13.6521 | 13.1442 | 12.6171 | 11.9893 | 9.8113 | 5.0715 | 2.6834 | 1.3188
BRAMLEY (FLEE) | ALTON | ALTON LOCAL | MINIMUM HEADROOM | SU 72434 39606 | YES | 19.2653 | 17.7863 | 16.3581 | 14.9499 | 13.1209 | 11.3697 | 9.4838 | 7.3714 | 4.88 | 2.5797 | -2.6218 | -9.068 | -11.9643 | -14.6332 | 29.8459 | 28.8798 | 27.9939 | 27.1184 | 26.1123 | 25.1359 | 24.0316 | 22.7528 | 21.1682 | 19.7432 | 16.8596 | 13.4777 | 10.2739 | 7.3821 | 22.8189 | 21.4749 | 20.1695 | 18.8669 | 17.2072 | 15.5933 | 13.8273 | 11.8346 | 9.4791 | 7.3122 | 2.5098 | -3.3419 | -5.5969 | -7.8021
|  | ALTON LOCAL | CT |  |  | 19.7993 | 18.643 | 17.5205 | 16.3653 | 15.1206 | 13.956 | 12.7174 | 11.3041 | 9.7218 | 7.3865 | 2.3015 | -6.0388 | -11.9643 | -14.6332 | 29.9691 | 29.0999 | 28.2996 | 27.4728 | 26.6734 | 25.9069 | 25.0646 | 24.087 | 22.9664 | 21.436 | 18.3687 | 13.6951 | 10.2739 | 7.3821 | 23.2532 | 22.1848 | 21.1563 | 20.084 | 18.9337 | 17.8383 | 16.6678 | 15.3276 | 13.8191 | 11.611 | 6.9046 | -0.63416 | -5.5969 | -7.8021
|  | ALTON LOCAL | LW |  |  | 19.2653 | 17.7863 | 16.3581 | 14.9499 | 13.1209 | 11.3697 | 9.4838 | 7.3714 | 4.88 | 2.5797 | -2.6218 | -9.068 | -11.3136 | -12.4879 | 29.8459 | 28.8798 | 27.9939 | 27.1184 | 26.1123 | 25.1359 | 24.0316 | 22.7528 | 21.1682 | 19.7432 | 16.8596 | 13.4777 | 12.5159 | 12.036 | 22.8189 | 21.4749 | 20.1695 | 18.8669 | 17.2072 | 15.5933 | 13.8273 | 11.8346 | 9.4791 | 7.3122 | 2.5098 | -3.3419 | -5.2435 | -6.2221
|  | ALTON LOCAL | ST |  |  | 20.3607 | 19.5884 | 18.9319 | 18.2939 | 17.6485 | 17.0767 | 16.4454 | 15.7368 | 14.9293 | 14.1062 | 10.3963 | 4.2731 | 1.0428 | -1.0326 | 30.3479 | 29.7205 | 29.2223 | 28.7493 | 28.2951 | 27.869 | 27.3899 | 26.8471 | 26.2175 | 25.6135 | 22.7719 | 18.1258 | 15.372 | 12.6241 | 23.794 | 23.0984 | 22.508 | 21.9302 | 21.3349 | 20.7917 | 20.1911 | 19.5159 | 18.7423 | 17.9604 | 14.3816 | 8.5784 | 5.6385 | 3.7956
|  | ALTON LOCAL | SP |  |  | 20.4468 | 19.7171 | 19.1347 | 18.6069 | 18.003 | 17.4918 | 16.9425 | 16.3211 | 15.6497 | 14.8407 | 11.9361 | 4.6222 | 0.86841 | -0.93833 | 30.3797 | 29.762 | 29.2985 | 28.8793 | 28.4673 | 28.1087 | 27.7117 | 27.2453 | 26.7305 | 26.1387 | 23.9067 | 17.9473 | 13.6465 | 8.8545 | 23.8701 | 23.2057 | 22.6901 | 22.2159 | 21.6679 | 21.1901 | 20.6781 | 20.0945 | 19.4617 | 18.7035 | 15.9541 | 8.9651 | 5.4563 | 3.8149
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER | MINIMUM HEADROOM | SU 35240 46643 | YES | 21.1716 | 20.9139 | 20.6223 | 20.3066 | 19.7724 | 19.2113 | 18.6092 | 17.9649 | 17.1747 | 16.3658 | 14.3406 | 11.925 | 10.6026 | 9.6809 | 24.0323 | 23.893 | 23.7309 | 23.5517 | 23.2779 | 22.9862 | 22.6639 | 22.3143 | 21.8563 | 21.3861 | 20.2552 | 18.9888 | 17.8524 | 16.9626 | 21.8901 | 21.6589 | 21.3988 | 21.1177 | 20.6367 | 20.1317 | 19.5908 | 18.987 | 18.2037 | 17.4044 | 15.4882 | 13.298 | 12.2697 | 11.5104
|  | ANDOVER | CT |  |  | 21.3189 | 21.1533 | 20.9635 | 20.718 | 20.3696 | 19.997 | 19.6199 | 19.2027 | 18.7044 | 17.92 | 15.869 | 12.6842 | 10.6026 | 9.6809 | 24.0748 | 23.9644 | 23.8367 | 23.6694 | 23.4631 | 23.2397 | 23.0066 | 22.7458 | 22.4261 | 21.9618 | 20.7704 | 19.0318 | 17.8524 | 16.9626 | 22.0262 | 21.8792 | 21.7114 | 21.496 | 21.1803 | 20.8166 | 20.4431 | 20.0263 | 19.5194 | 18.7457 | 16.789 | 13.9956 | 12.2697 | 11.5104
|  | ANDOVER | LW |  |  | 21.1716 | 20.9139 | 20.6223 | 20.3066 | 19.7724 | 19.2113 | 18.6092 | 17.9649 | 17.1747 | 16.3658 | 14.3406 | 11.925 | 11.0411 | 10.6726 | 24.0323 | 23.893 | 23.7309 | 23.5517 | 23.2779 | 22.9862 | 22.6639 | 22.3143 | 21.8563 | 21.3861 | 20.2552 | 18.9888 | 18.5932 | 18.4189 | 21.8901 | 21.6589 | 21.3988 | 21.1177 | 20.6367 | 20.1317 | 19.5908 | 18.987 | 18.2037 | 17.4044 | 15.4882 | 13.298 | 12.5589 | 12.2556
|  | ANDOVER | ST |  |  | 21.471 | 21.4031 | 21.3223 | 21.2228 | 21.0797 | 20.9277 | 20.7518 | 20.559 | 20.3263 | 20.0708 | 18.9232 | 16.4137 | 15.0766 | 14.2598 | 24.168 | 24.1176 | 24.0575 | 23.9833 | 23.8852 | 23.7797 | 23.6554 | 23.5177 | 23.3483 | 23.1706 | 22.3598 | 20.583 | 19.5692 | 18.72 | 22.162 | 22.1022 | 22.0315 | 21.9447 | 21.8185 | 21.684 | 21.5288 | 21.3559 | 21.1142 | 20.8596 | 19.6728 | 17.1939 | 16.0236 | 15.3558
|  | ANDOVER | SP |  |  | 21.497 | 21.4352 | 21.3677 | 21.292 | 21.1673 | 21.0414 | 20.9078 | 20.7542 | 20.5762 | 20.3498 | 19.5165 | 17.1734 | 15.7179 | 15.1089 | 24.1781 | 24.1278 | 24.0713 | 24.0076 | 23.9247 | 23.8396 | 23.7466 | 23.6373 | 23.5084 | 23.3474 | 22.7356 | 20.9507 | 19.4631 | 18.1198 | 22.1853 | 22.132 | 22.0738 | 22.0083 | 21.8979 | 21.7859 | 21.667 | 21.5309 | 21.3726 | 21.1587 | 20.3162 | 17.9171 | 16.5185 | 15.978
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST | MINIMUM HEADROOM | SU 37953 46433 | YES | 10.6342 | 9.8273 | 9.1999 | 8.5944 | 7.6619 | 6.6692 | 5.6236 | 4.5498 | 3.3396 | 2.0958 | -1.378 | -5.1398 | -7.5989 | -9.0465 | 15.6037 | 15.0988 | 14.7057 | 14.3415 | 13.9104 | 13.4599 | 12.9434 | 12.3312 | 11.6466 | 10.8279 | 8.6334 | 6.5375 | 4.6489 | 3.0576 | 12.2967 | 11.5857 | 11.0064 | 10.442 | 9.591 | 8.6859 | 7.7269 | 6.7366 | 5.6079 | 4.4479 | 1.2239 | -2.2116 | -4.3377 | -5.6132
|  | ANDOVER EAST | CT |  |  | 10.8717 | 10.2009 | 9.7419 | 9.2479 | 8.5737 | 7.8498 | 7.0953 | 6.2881 | 5.4632 | 4.225 | 0.79855 | -4.2768 | -7.5989 | -9.0465 | 15.6428 | 15.1625 | 14.8 | 14.4545 | 14.0746 | 13.6808 | 13.2635 | 12.8182 | 12.3572 | 11.576 | 9.3274 | 6.5375 | 4.6489 | 3.0576 | 12.5027 | 11.912 | 11.4852 | 11.0166 | 10.3943 | 9.7282 | 9.0306 | 8.2775 | 7.5024 | 6.3504 | 3.1777 | -1.4022 | -4.3377 | -5.6132
|  | ANDOVER EAST | LW |  |  | 10.6342 | 9.8273 | 9.1999 | 8.5944 | 7.6619 | 6.6692 | 5.6236 | 4.5498 | 3.3396 | 2.0958 | -1.378 | -5.1398 | -6.4607 | -6.9873 | 15.6037 | 15.0988 | 14.7057 | 14.3415 | 13.9104 | 13.4599 | 12.9434 | 12.3312 | 11.6466 | 10.8279 | 8.6334 | 6.5956 | 6.034 | 5.8018 | 12.2967 | 11.5857 | 11.0064 | 10.442 | 9.591 | 8.6859 | 7.7269 | 6.7366 | 5.6079 | 4.4479 | 1.2239 | -2.2116 | -3.3831 | -3.8471
|  | ANDOVER EAST | ST |  |  | 11.1501 | 10.6432 | 10.2997 | 9.9874 | 9.5899 | 9.1621 | 8.7101 | 8.2376 | 7.7419 | 7.2044 | 5.3347 | 2.1116 | 0.22098 | -1.0595 | 15.7264 | 15.2952 | 14.9739 | 14.6881 | 14.3852 | 14.0733 | 13.741 | 13.389 | 13.0161 | 12.6073 | 11.3695 | 9.333 | 7.7733 | 6.2346 | 12.7705 | 12.3343 | 12.0176 | 11.7256 | 11.3582 | 10.965 | 10.5468 | 10.1058 | 9.6383 | 9.134 | 7.3603 | 4.3242 | 2.6093 | 1.4785
|  | ANDOVER EAST | SP |  |  | 11.1905 | 10.692 | 10.3665 | 10.074 | 9.6565 | 9.2166 | 8.7642 | 8.2878 | 7.8043 | 7.2582 | 5.5536 | 2.6289 | 0.84614 | 0.042411 | 15.7348 | 15.3051 | 14.988 | 14.7067 | 14.4048 | 14.0971 | 13.7734 | 13.4312 | 13.0755 | 12.6746 | 11.5226 | 9.4907 | 6.9581 | 3.8797 | 12.807 | 12.3766 | 12.0756 | 11.8011 | 11.4206 | 11.0223 | 10.61 | 10.1715 | 9.7226 | 9.2157 | 7.6232 | 4.8653 | 3.1966 | 2.4721
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER TOWN | MINIMUM HEADROOM | SU 36207 45078 | YES | 4.1713 | 3.9142 | 3.6061 | 3.2764 | 2.7229 | 2.1357 | 1.5071 | 0.84332 | 0.058478 | -0.79705 | -2.8117 | -5.3737 | -7.0307 | -8.2098 | 3.4912 | 3.3455 | 3.1525 | 2.9399 | 2.6453 | 2.3225 | 1.9573 | 1.5593 | 1.0377 | 0.45803 | -0.73983 | -2.4988 | -4.162 | -6.0976 | 1.1475 | 0.90679 | 0.60829 | 0.286 | -0.22454 | -0.77144 | -1.3665 | -1.9984 | -2.7751 | -3.6276 | -5.5308 | -7.8432 | -9.1259 | -10.0828
|  | ANDOVER TOWN | CT |  |  | 4.3319 | 4.1694 | 3.9802 | 3.7251 | 3.363 | 2.976 | 2.5844 | 2.1624 | 1.6801 | 0.8292 | -1.2729 | -4.6269 | -7.0307 | -8.2098 | 3.5142 | 3.3833 | 3.2268 | 3.0047 | 2.7555 | 2.4821 | 2.1896 | 1.8689 | 1.4866 | 0.87899 | -0.50682 | -2.4988 | -4.162 | -5.8533 | 1.2723 | 1.1099 | 0.91776 | 0.6506 | 0.29962 | -0.078185 | -0.46702 | -0.88818 | -1.3784 | -2.225 | -4.2288 | -7.1457 | -9.1259 | -10.0828
|  | ANDOVER TOWN | LW |  |  | 4.1713 | 3.9142 | 3.6061 | 3.2764 | 2.7229 | 2.1357 | 1.5071 | 0.84332 | 0.058478 | -0.79705 | -2.8117 | -5.3737 | -6.4718 | -7.0278 | 3.4912 | 3.3455 | 3.1525 | 2.9399 | 2.6453 | 2.3225 | 1.9573 | 1.5593 | 1.0377 | 0.45803 | -0.73983 | -2.1041 | -2.5766 | -2.8302 | 1.1475 | 0.90679 | 0.60829 | 0.286 | -0.22454 | -0.77144 | -1.3665 | -1.9984 | -2.7751 | -3.6276 | -5.5308 | -7.8432 | -8.7514 | -9.203
|  | ANDOVER TOWN | ST |  |  | 4.4854 | 4.4184 | 4.3358 | 4.2375 | 4.0926 | 3.9323 | 3.7559 | 3.5645 | 3.3442 | 3.0993 | 2.019 | -0.41553 | -1.7347 | -2.6625 | 3.6238 | 3.5607 | 3.4812 | 3.3847 | 3.256 | 3.1116 | 2.9476 | 2.767 | 2.5548 | 2.342 | 1.3556 | -0.7289 | -2.0895 | -3.6968 | 1.4282 | 1.3625 | 1.279 | 1.1777 | 1.0308 | 0.86691 | 0.68438 | 0.48555 | 0.25397 | 0.0069486 | -1.1218 | -3.4841 | -4.6526 | -5.4228
|  | ANDOVER TOWN | SP |  |  | 4.5102 | 4.4458 | 4.3697 | 4.2884 | 4.16 | 4.0266 | 3.8838 | 3.7271 | 3.5496 | 3.3251 | 2.4953 | 0.11494 | -1.3174 | -1.9773 | 3.6309 | 3.5603 | 3.4743 | 3.3807 | 3.2691 | 3.1481 | 3.0115 | 2.8556 | 2.6747 | 2.4609 | 1.621 | -0.83229 | -3.1229 | -6.0976 | 1.4497 | 1.383 | 1.3028 | 1.2169 | 1.0925 | 0.96237 | 0.82072 | 0.66272 | 0.48205 | 0.25945 | -0.58278 | -2.9812 | -4.3067 | -4.8795
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD | MINIMUM HEADROOM | SU 75949 65766 | YES | 13.2083 | 12.8591 | 12.5258 | 12.1812 | 11.6611 | 11.1142 | 10.527 | 9.8675 | 9.0638 | 8.2969 | 6.548 | 4.2083 | 3.4507 | 2.9014 | 17.5112 | 17.3226 | 17.1419 | 16.9509 | 16.6792 | 16.3899 | 16.0698 | 15.7002 | 15.2277 | 14.7826 | 13.8367 | 12.6001 | 11.5898 | 10.7498 | 14.7552 | 14.4514 | 14.1581 | 13.8427 | 13.3643 | 12.8605 | 12.3162 | 11.7006 | 10.941 | 10.2201 | 8.6136 | 6.5145 | 5.8616 | 5.4244
|  | ARBORFIELD | CT |  |  | 13.4137 | 13.183 | 12.9497 | 12.7093 | 12.3748 | 12.0163 | 11.6422 | 11.2112 | 10.7181 | 9.9722 | 8.3408 | 5.4232 | 3.5792 | 2.9014 | 17.5731 | 17.4203 | 17.2608 | 17.0927 | 16.8885 | 16.6672 | 16.4294 | 16.1507 | 15.8253 | 15.3672 | 14.3946 | 12.7189 | 11.5898 | 10.7498 | 14.9082 | 14.6977 | 14.4789 | 14.251 | 13.951 | 13.6288 | 13.2887 | 12.8918 | 12.4217 | 11.7164 | 10.2094 | 7.5658 | 6 | 5.4244
|  | ARBORFIELD | LW |  |  | 13.2083 | 12.8591 | 12.5258 | 12.1812 | 11.6611 | 11.1142 | 10.527 | 9.8675 | 9.0638 | 8.2969 | 6.548 | 4.2083 | 3.4507 | 3.1074 | 17.5112 | 17.3226 | 17.1419 | 16.9509 | 16.6792 | 16.3899 | 16.0698 | 15.7002 | 15.2277 | 14.7826 | 13.8367 | 12.6001 | 12.2291 | 12.0532 | 14.7552 | 14.4514 | 14.1581 | 13.8427 | 13.3643 | 12.8605 | 12.3162 | 11.7006 | 10.941 | 10.2201 | 8.6136 | 6.5145 | 5.8616 | 5.5664
|  | ARBORFIELD | ST |  |  | 13.5994 | 13.4815 | 13.3647 | 13.2336 | 13.0614 | 12.8735 | 12.6765 | 12.4568 | 12.2027 | 11.928 | 10.7113 | 8.622 | 7.4635 | 6.6898 | 17.6953 | 17.6151 | 17.5322 | 17.4365 | 17.3218 | 17.1951 | 17.0586 | 16.9039 | 16.7219 | 16.5364 | 15.6927 | 14.164 | 13.2348 | 12.3353 | 15.0894 | 14.9874 | 14.881 | 14.7587 | 14.6022 | 14.4309 | 14.2503 | 14.0469 | 13.8089 | 13.5567 | 12.4004 | 10.4298 | 9.3731 | 8.6814
|  | ARBORFIELD | SP |  |  | 13.6226 | 13.523 | 13.4339 | 13.3451 | 13.144 | 12.9411 | 12.7363 | 12.4998 | 12.2551 | 11.958 | 10.9259 | 8.222 | 6.7814 | 6.0032 | 17.7016 | 17.628 | 17.5563 | 17.4814 | 17.3636 | 17.2427 | 17.1163 | 16.9669 | 16.8074 | 16.6224 | 15.9524 | 14.044 | 12.8103 | 11.6786 | 15.107 | 15.0197 | 14.9379 | 14.8548 | 14.6813 | 14.5072 | 14.3298 | 14.1214 | 13.9043 | 13.6323 | 12.6674 | 10.1061 | 8.7712 | 8.0678
LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD | MINIMUM HEADROOM | SZ 93193 99152 | NO | 14.2776 | 13.9347 | 13.5127 | 13.0529 | 12.3007 | 11.5018 | 10.6645 | 9.7743 | 8.6552 | 7.5139 | 4.2726 | -0.12992 | -4.0474 | -6.8093 | 13.1525 | 12.9773 | 12.74 | 12.4782 | 12.0915 | 11.6776 | 11.2283 | 10.7463 | 10.1303 | 9.4526 | 7.0875 | 2.5881 | -4.0013 | -17.6639 | 9.3055 | 9.0036 | 8.6332 | 8.2346 | 7.5584 | 6.8465 | 6.101 | 5.3117 | 4.3299 | 3.3218 | 0.36639 | -3.5878 | -6.8835 | -9.2193
|  | ARGYLE ROAD | CT |  |  | 14.5028 | 14.2875 | 14.0584 | 13.6872 | 13.1767 | 12.6345 | 12.0329 | 11.3894 | 10.6829 | 9.5507 | 6.2734 | 0.60139 | -4.0474 | -6.8093 | 13.186 | 13.0052 | 12.8097 | 12.5087 | 12.1331 | 11.7296 | 11.2793 | 10.7893 | 10.2382 | 9.4526 | 7.0875 | 2.5881 | -2.6573 | -9.5236 | 9.5242 | 9.3435 | 9.1504 | 8.8518 | 8.4117 | 7.9459 | 7.4273 | 6.874 | 6.2588 | 5.2305 | 2.2483 | -2.8947 | -6.8835 | -9.2193
|  | ARGYLE ROAD | LW |  |  | 14.2776 | 13.9347 | 13.5127 | 13.0529 | 12.3007 | 11.5018 | 10.6645 | 9.7743 | 8.6552 | 7.5139 | 4.2726 | -0.12992 | -2.6942 | -4.4636 | 13.1525 | 12.9773 | 12.74 | 12.4782 | 12.0915 | 11.6776 | 11.2283 | 10.7463 | 10.1303 | 9.4912 | 7.7 | 5.4236 | 4.2643 | 3.4168 | 9.3055 | 9.0036 | 8.6332 | 8.2346 | 7.5584 | 6.8465 | 6.101 | 5.3117 | 4.3299 | 3.3218 | 0.36639 | -3.5878 | -5.7446 | -7.2029
|  | ARGYLE ROAD | ST |  |  | 14.7232 | 14.6375 | 14.5434 | 14.4392 | 14.2321 | 14.0079 | 13.7638 | 13.5004 | 13.191 | 12.8564 | 11.4509 | 7.746 | 5.1101 | 3.1498 | 13.3132 | 13.2062 | 13.0877 | 12.955 | 12.7393 | 12.5043 | 12.2405 | 11.9496 | 11.611 | 11.2489 | 9.7724 | 5.7517 | 1.1138 | -5.4542 | 9.7166 | 9.6505 | 9.577 | 9.4955 | 9.3284 | 9.1477 | 8.9511 | 8.7387 | 8.4876 | 8.2011 | 7.0001 | 3.7178 | 1.4256 | -0.25344
|  | ARGYLE ROAD | SP |  |  | 14.7642 | 14.6707 | 14.5765 | 14.4711 | 14.3453 | 14.2089 | 14.0649 | 13.8997 | 13.7155 | 13.4529 | 12.434 | 9.3618 | 6.8742 | 5.3492 | 13.3218 | 13.1968 | 13.0577 | 12.9006 | 12.6927 | 12.459 | 12.1972 | 11.8992 | 11.5555 | 11.0993 | 9.3127 | 4.157 | -4.0013 | -17.6639 | 9.7548 | 9.6877 | 9.6192 | 9.5423 | 9.4453 | 9.3398 | 9.228 | 9.0993 | 8.9551 | 8.7329 | 7.8966 | 5.2157 | 3.0287 | 1.7707
COWLEY GSP | HEADINGTON BSP | ARNCOTT | MINIMUM HEADROOM | SP 60730 18095 | NO | 6.4267 | 5.8387 | 5.2238 | 4.2711 | 3.2522 | 2.1521 | 1.2979 | 0.35988 | -0.56349 | -1.416 | -3.1859 | -4.9387 | -5.3469 | -5.5879 | 10.1498 | 9.8553 | 9.495 | 8.9209 | 8.3667 | 7.73 | 7.2407 | 6.6674 | 6.1422 | 5.6379 | 4.6248 | 3.7227 | 3.5329 | 3.1519 | 7.7603 | 7.2341 | 6.6931 | 5.8716 | 4.9933 | 4.0369 | 3.278 | 2.4318 | 1.5942 | 0.82398 | -0.75233 | -2.2792 | -2.6245 | -2.8247
|  | ARNCOTT | CT |  |  | 6.6888 | 6.245 | 5.7537 | 4.9274 | 4.0868 | 3.1588 | 2.5059 | 1.7741 | 1.0856 | 0.28365 | -1.2899 | -3.3388 | -4.4689 | -4.8732 | 10.1498 | 9.8553 | 9.6041 | 9.1703 | 8.6871 | 8.1186 | 7.7121 | 7.2231 | 6.7909 | 6.2977 | 5.3286 | 4.2001 | 3.5707 | 3.1519 | 7.9844 | 7.5888 | 7.1547 | 6.4431 | 5.7236 | 4.9197 | 4.3417 | 3.6808 | 3.0604 | 2.333 | 0.90862 | -0.92569 | -1.88 | -2.2154
|  | ARNCOTT | LW |  |  | 6.4267 | 5.8387 | 5.2238 | 4.2711 | 3.2522 | 2.1521 | 1.2979 | 0.35988 | -0.56349 | -1.416 | -3.1859 | -4.9387 | -5.3469 | -5.5879 | 10.1557 | 9.8577 | 9.495 | 8.9209 | 8.3667 | 7.73 | 7.2407 | 6.6674 | 6.1422 | 5.6379 | 4.6248 | 3.7227 | 3.5329 | 3.43 | 7.7603 | 7.2341 | 6.6931 | 5.8716 | 4.9933 | 4.0369 | 3.278 | 2.4318 | 1.5942 | 0.82398 | -0.75233 | -2.2792 | -2.6245 | -2.8247
|  | ARNCOTT | ST |  |  | 6.8474 | 6.5042 | 6.1493 | 5.558 | 4.9581 | 4.2843 | 3.8083 | 3.2743 | 2.8119 | 2.3682 | 1.0312 | -0.56883 | -1.3502 | -1.7863 | 10.1905 | 9.9213 | 9.7001 | 9.3495 | 9.0794 | 8.6516 | 8.3286 | 7.9343 | 7.625 | 7.3408 | 6.486 | 5.4099 | 4.8542 | 4.4108 | 8.1355 | 7.8373 | 7.5316 | 7.0367 | 6.534 | 5.9602 | 5.5443 | 5.0677 | 4.6573 | 4.2653 | 3.0257 | 1.5399 | 0.83617 | 0.45005
|  | ARNCOTT | SP |  |  | 6.8895 | 6.5704 | 6.2594 | 5.7341 | 5.1633 | 4.5168 | 4.0378 | 3.4953 | 3.0295 | 2.541 | 1.2113 | -1.1171 | -2.3672 | -3.031 | 10.1917 | 9.9248 | 9.7076 | 9.3649 | 9.1079 | 8.7592 | 8.4389 | 8.0444 | 7.7389 | 7.4407 | 6.6266 | 5.2445 | 4.3945 | 3.7519 | 8.1691 | 7.8961 | 7.6315 | 7.1985 | 6.7279 | 6.1838 | 5.7688 | 5.2874 | 4.8783 | 4.4493 | 3.2434 | 1.0854 | -0.052809 | -0.64632
BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT | MINIMUM HEADROOM | SU 91615 68855 | YES | 13.7116 | 13.1705 | 12.5859 | 11.9587 | 11.0747 | 10.2012 | 9.272 | 8.2362 | 7 | 5.7465 | 2.7896 | -1.0835 | -2.913 | -4.4095 | 18.4323 | 18.1027 | 17.7502 | 17.3661 | 16.8769 | 16.3828 | 15.8364 | 15.2111 | 14.4063 | 13.5989 | 11.8274 | 9.6062 | 7.6479 | 5.9273 | 15.3145 | 14.8351 | 14.3211 | 13.7555 | 12.9556 | 12.155 | 11.2945 | 10.33 | 9.1616 | 7.9787 | 5.2289 | 1.673 | 0.1623 | -1.1188
|  | ASCOT | CT |  |  | 13.878 | 13.4492 | 12.9365 | 12.4047 | 11.7671 | 11.1474 | 10.5333 | 9.8437 | 9.0508 | 7.8013 | 4.8887 | 0.16825 | -2.913 | -4.4095 | 18.4564 | 18.1511 | 17.7884 | 17.4106 | 17.0054 | 16.5986 | 16.173 | 15.6886 | 15.1197 | 14.2836 | 12.426 | 9.6062 | 7.6479 | 5.9273 | 15.4328 | 15.0421 | 14.5752 | 14.09 | 13.5256 | 12.9669 | 12.4011 | 11.7587 | 11.0082 | 9.8298 | 7.1257 | 2.8551 | 0.1623 | -1.1188
|  | ASCOT | LW |  |  | 13.7116 | 13.1705 | 12.5859 | 11.9587 | 11.0747 | 10.2012 | 9.272 | 8.2362 | 7 | 5.7465 | 2.7896 | -1.0835 | -2.5063 | -3.2679 | 18.4323 | 18.1027 | 17.7502 | 17.3661 | 16.8769 | 16.3828 | 15.8364 | 15.2111 | 14.4063 | 13.5989 | 11.8274 | 9.6207 | 8.9713 | 8.6172 | 15.3145 | 14.8351 | 14.3211 | 13.7555 | 12.9556 | 12.155 | 11.2945 | 10.33 | 9.1616 | 7.9787 | 5.2289 | 1.673 | 0.44611 | -0.19116
|  | ASCOT | ST |  |  | 14.1832 | 13.9566 | 13.6803 | 13.3791 | 13.0643 | 12.7678 | 12.4613 | 12.1162 | 11.7128 | 11.2766 | 9.3485 | 5.71 | 3.7744 | 2.6107 | 18.6761 | 18.5104 | 18.3088 | 18.0837 | 17.8559 | 17.6322 | 17.3933 | 17.1217 | 16.7991 | 16.4655 | 14.9377 | 12.0693 | 10.3653 | 8.7747 | 15.7298 | 15.5324 | 15.2905 | 15.0218 | 14.7402 | 14.4679 | 14.1818 | 13.8575 | 13.4748 | 13.0662 | 11.2047 | 7.784 | 6.0964 | 5.1082
|  | ASCOT | SP |  |  | 14.2171 | 14.0089 | 13.7745 | 13.5286 | 13.2337 | 12.9544 | 12.6745 | 12.3503 | 11.9896 | 11.5795 | 10.1141 | 6.2374 | 3.9548 | 2.9358 | 18.6902 | 18.5296 | 18.3492 | 18.1548 | 17.9567 | 17.7602 | 17.5559 | 17.3141 | 17.0362 | 16.7149 | 15.5114 | 12.1624 | 9.4543 | 6.6381 | 15.7595 | 15.577 | 15.3743 | 15.1581 | 14.9041 | 14.6571 | 14.4056 | 14.1101 | 13.7772 | 13.4015 | 12.0308 | 8.3263 | 6.2185 | 5.3203
LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD | MINIMUM HEADROOM | SU 84085 06737 | YES | 1.726 | 0.70348 | -0.6682 | -2.1596 | 7.5263 | 5.1868 | 2.8563 | 0.35245 | -2.6431 | -5.7357 | -14.2587 | -22.5366 | -25.5577 | -27.8817 | 4.6676 | 4.0796 | 3.2679 | 2.3801 | 19.1286 | 17.8455 | 16.5192 | 15.0683 | 13.2146 | 11.2858 | 6.4606 | 1.5698 | -2.1126 | -5.6432 | -3.6857 | -4.6021 | -5.8345 | -7.1818 | 8.7861 | 6.7124 | 4.606 | 2.3241 | -0.47743 | -3.3761 | -10.9861 | -18.2619 | -20.5912 | -22.4915
|  | ASHLING ROAD | CT |  |  | 2.1919 | 1.4514 | 0.41095 | -0.83135 | 9.3955 | 7.6126 | 5.8813 | 3.9731 | 1.7647 | -1.3426 | -9.8772 | -20.0581 | -25.5577 | -27.8817 | 4.7521 | 4.2241 | 3.5144 | 2.6458 | 19.5594 | 18.4506 | 17.3416 | 16.1216 | 14.6806 | 12.7098 | 7.5466 | 1.5698 | -2.1126 | -5.6432 | -3.3292 | -4.0157 | -4.9603 | -6.1159 | 10.3089 | 8.7096 | 7.1384 | 5.4209 | 3.4196 | 0.5773 | -7.0636 | -16.0402 | -20.5912 | -22.4915
|  | ASHLING ROAD | LW |  |  | 1.726 | 0.70348 | -0.6682 | -2.1596 | 7.5263 | 5.1868 | 2.8563 | 0.35245 | -2.6431 | -5.7357 | -14.2587 | -22.5366 | -24.5597 | -25.5084 | 4.6676 | 4.0796 | 3.2679 | 2.3801 | 19.1286 | 17.8455 | 16.5192 | 15.0683 | 13.2146 | 11.2858 | 6.4606 | 2.0772 | 1.2652 | 0.90922 | -3.6857 | -4.6021 | -5.8345 | -7.1818 | 8.7861 | 6.7124 | 4.606 | 2.3241 | -0.47743 | -3.3761 | -10.9861 | -18.2619 | -19.9483 | -20.7274
|  | ASHLING ROAD | ST |  |  | 2.7033 | 2.3196 | 1.7539 | 1.1348 | 12.1553 | 11.1712 | 10.2332 | 9.2326 | 8.0058 | 6.7076 | 1.2751 | -7.2021 | -10.6029 | -12.3698 | 5.1287 | 4.8493 | 4.4483 | 3.9983 | 21.314 | 20.6141 | 19.9209 | 19.1747 | 18.2884 | 17.3869 | 13.4839 | 6.9122 | 3.4938 | 0.1095 | -2.8056 | -3.1341 | -3.6149 | -4.1529 | 12.9849 | 12.1055 | 11.2472 | 10.3274 | 9.2381 | 8.0909 | 3.1993 | -4.6785 | -7.7874 | -9.3449
|  | ASHLING ROAD | SP |  |  | 2.786 | 2.4265 | 1.9297 | 1.4036 | 12.5854 | 11.7844 | 10.9964 | 10.1372 | 9.1945 | 8.0651 | 3.8447 | -4.4218 | -8.5897 | -10.1458 | 5.1564 | 4.8679 | 4.4898 | 4.0805 | 21.5254 | 20.9644 | 20.3783 | 19.723 | 18.9856 | 18.1468 | 14.9333 | 7.8118 | 2.2753 | -3.9073 | -2.7349 | -3.0512 | -3.4704 | -3.9212 | 13.3947 | 12.7143 | 12.0173 | 11.2448 | 10.3913 | 9.3966 | 5.6873 | -2.0387 | -5.9704 | -7.3886
MELKSHAM GSP | NORRINGTON | ASHTON PARK | MINIMUM HEADROOM | ST 87141 57741 | NO | 7.705 | 6.4663 | 4.917 | 12.0713 | 10.3948 | 8.6814 | 6.9526 | 5.1719 | 3.0584 | 0.84159 | -4.1535 | -9.5997 | -13.4145 | -15.7192 | 15.4505 | 14.7335 | 13.7763 | 19.5572 | 18.5945 | 17.5575 | 16.4783 | 15.3644 | 13.9343 | 12.4628 | 9.4649 | 5.8936 | 2.5961 | -0.53917 | 9.255 | 8.2027 | 6.8553 | 12.2199 | 10.7096 | 9.1419 | 7.5469 | 5.8994 | 3.9183 | 1.8851 | -2.7095 | -7.7268 | -11.032 | -13.0566
|  | ASHTON PARK | CT |  |  | 8.0299 | 7.0077 | 5.7372 | 13.0519 | 11.8349 | 10.5951 | 9.3945 | 8.1419 | 6.6558 | 4.4014 | -0.9595 | -8.2682 | -13.4145 | -15.7192 | 15.4945 | 14.8287 | 13.9857 | 19.7742 | 18.9641 | 18.0822 | 17.1991 | 16.2976 | 15.2214 | 13.6935 | 10.1851 | 5.8936 | 2.5961 | -0.53917 | 9.5342 | 8.6742 | 7.581 | 13.0818 | 11.9799 | 10.8348 | 9.7161 | 8.5717 | 7.2426 | 5.2119 | 0.29592 | -6.4947 | -11.032 | -13.0566
|  | ASHTON PARK | LW |  |  | 7.705 | 6.4663 | 4.917 | 12.0713 | 10.3948 | 8.6814 | 6.9526 | 5.1719 | 3.0584 | 0.84159 | -4.1535 | -9.5997 | -11.6158 | -12.5629 | 15.4505 | 14.7335 | 13.7763 | 19.5572 | 18.5945 | 17.5575 | 16.4783 | 15.3644 | 13.9343 | 12.4628 | 9.4649 | 6.6056 | 5.7819 | 5.4016 | 9.255 | 8.2027 | 6.8553 | 12.2199 | 10.7096 | 9.1419 | 7.5469 | 5.8994 | 3.9183 | 1.8851 | -2.7095 | -7.7268 | -9.5047 | -10.3352
|  | ASHTON PARK | ST |  |  | 8.522 | 7.8908 | 7.0988 | 15.0921 | 14.4527 | 13.769 | 13.1152 | 12.4753 | 11.7658 | 11.045 | 7.82 | 1.7638 | -1.009 | -2.7604 | 15.8598 | 15.4481 | 14.8996 | 21.1332 | 20.6412 | 20.0874 | 19.5339 | 18.988 | 18.3725 | 17.7788 | 15.1465 | 10.2519 | 7.496 | 4.507 | 10.0043 | 9.5136 | 8.8676 | 15.0075 | 14.4372 | 13.8064 | 13.1964 | 12.597 | 11.9281 | 11.2514 | 8.3527 | 2.6899 | 0.17774 | -1.3891
|  | ASHTON PARK | SP |  |  | 8.583 | 7.9737 | 7.2493 | 15.325 | 14.7818 | 14.2124 | 13.6626 | 13.1328 | 12.5587 | 11.9185 | 9.6166 | 3.5312 | 0.54485 | -0.57466 | 15.8751 | 15.4566 | 14.9356 | 21.2061 | 20.8041 | 20.3432 | 19.882 | 19.4253 | 18.9197 | 18.3501 | 16.2034 | 10.5428 | 5.8753 | 0.094306 | 10.0595 | 9.5849 | 9.0011 | 15.2171 | 14.7436 | 14.2257 | 13.721 | 13.2316 | 12.6983 | 12.1023 | 9.9547 | 4.3681 | 1.5456 | 0.5309
BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT | MINIMUM HEADROOM | SU 91122 63523 | YES | 8.9689 | 8.5448 | 8.0852 | 7.578 | 6.7575 | 5.8895 | 4.9241 | 3.8116 | 2.4376 | 1.2244 | -1.3265 | -4.8063 | -7.0253 | -8.5105 | 14.1686 | 13.9056 | 13.591 | 13.2354 | 12.7881 | 12.2756 | 11.6819 | 10.9746 | 10.0431 | 9.2523 | 7.7687 | 5.5549 | 3.577 | 1.797 | 10.9262 | 10.5239 | 10.0868 | 9.6025 | 8.8378 | 8.0265 | 7.1175 | 6.0633 | 4.7454 | 3.5908 | 1.2182 | -1.9722 | -3.8447 | -5.1276
|  | BAGSHOT | CT |  |  | 9.0878 | 8.7661 | 8.3759 | 7.9424 | 7.3899 | 6.7974 | 6.1517 | 5.4026 | 4.5439 | 3.215 | 0.57006 | -3.9311 | -7.0253 | -8.5105 | 14.1686 | 13.9086 | 13.591 | 13.2354 | 12.851 | 12.4366 | 11.9618 | 11.3988 | 10.7392 | 9.8291 | 8.2068 | 5.5549 | 3.577 | 1.797 | 11.017 | 10.7021 | 10.3175 | 9.8891 | 9.3776 | 8.824 | 8.2056 | 7.4852 | 6.656 | 5.3895 | 2.9331 | -1.1315 | -3.8447 | -5.1276
|  | BAGSHOT | LW |  |  | 8.9689 | 8.5448 | 8.0852 | 7.578 | 6.7575 | 5.8895 | 4.9241 | 3.8116 | 2.4376 | 1.2244 | -1.3265 | -4.8063 | -6.1545 | -6.8774 | 14.1801 | 13.9056 | 13.6043 | 13.2649 | 12.7881 | 12.2756 | 11.6819 | 10.9746 | 10.0431 | 9.2523 | 7.7687 | 5.8518 | 5.2575 | 4.936 | 10.9262 | 10.5239 | 10.0868 | 9.6025 | 8.8378 | 8.0265 | 7.1175 | 6.0633 | 4.7454 | 3.5908 | 1.2182 | -1.9722 | -3.1443 | -3.7586
|  | BAGSHOT | ST |  |  | 9.4102 | 9.2845 | 9.1125 | 8.9088 | 8.6646 | 8.4009 | 8.1021 | 7.761 | 7.3537 | 6.9414 | 4.764 | 1.4507 | -0.37983 | -1.5275 | 14.4126 | 14.3001 | 14.146 | 13.9636 | 13.7573 | 13.533 | 13.2753 | 12.9794 | 12.6241 | 12.2899 | 10.4887 | 7.8546 | 6.2148 | 4.5641 | 11.3365 | 11.215 | 11.0445 | 10.8424 | 10.6037 | 10.3456 | 10.0515 | 9.7147 | 9.311 | 8.9109 | 6.752 | 3.6299 | 2.0345 | 1.0479
|  | BAGSHOT | SP |  |  | 9.4365 | 9.3179 | 9.1854 | 9.0323 | 8.832 | 8.6098 | 8.3865 | 8.0981 | 7.7825 | 7.4042 | 5.9239 | 1.9586 | 0.10753 | -0.71298 | 14.4208 | 14.3055 | 14.1741 | 14.0217 | 13.8579 | 13.6742 | 13.4836 | 13.2362 | 12.9564 | 12.6382 | 11.3522 | 7.7993 | 5.4465 | 2.8521 | 11.3583 | 11.2413 | 11.1102 | 10.958 | 10.7681 | 10.5589 | 10.349 | 10.072 | 9.7653 | 9.4055 | 7.9654 | 4.0696 | 2.3892 | 1.6839
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL | MINIMUM HEADROOM | SU 42417 63142 | YES | 2.1427 | 1.5842 | 1.0258 | 0.46807 | -0.28523 | -1.0523 | -1.8059 | -2.4995 | -3.0561 | -3.3542 | -3.661 | -6.578 | -8.8596 | -10.4539 | 2.897 | 2.6569 | 2.418 | 2.1751 | 1.8558 | 1.5264 | 1.1916 | 0.8382 | 0.48961 | 0.28865 | 0.099162 | -1.2115 | -2.2443 | -3.1296 | 1.1442 | 0.64469 | 0.14539 | -0.35411 | -1.0271 | -1.7132 | -2.3858 | -3.0204 | -3.5417 | -3.8233 | -4.1097 | -6.6014 | -8.5412 | -9.8811
|  | BALL HILL | CT |  |  | 2.7768 | 2.5324 | 2.2599 | 2.0066 | 1.5966 | 1.1725 | 0.75184 | 0.29434 | -0.037131 | -0.36346 | -0.62617 | -0.96828 | -1.1055 | -1.175 | 3.0925 | 2.9523 | 2.7873 | 2.6371 | 2.4357 | 2.2235 | 2.0027 | 1.7369 | 1.5118 | 1.2572 | 1.0376 | 0.71151 | 0.46285 | 0.13223 | 1.6967 | 1.4716 | 1.2159 | 0.98145 | 0.61903 | 0.23571 | -0.14632 | -0.56694 | -0.88229 | -1.2133 | -1.4646 | -1.782 | -1.9034 | -1.9627
|  | BALL HILL | LW |  |  | 2.1427 | 1.5842 | 1.0258 | 0.46807 | -0.28523 | -1.0523 | -1.8059 | -2.4995 | -3.0561 | -3.3542 | -3.661 | -4.0117 | -4.0741 | -4.0958 | 2.897 | 2.6569 | 2.418 | 2.1751 | 1.8558 | 1.5264 | 1.1916 | 0.8382 | 0.48961 | 0.28865 | 0.099162 | -0.1189 | -0.15367 | -0.16772 | 1.1442 | 0.64469 | 0.14539 | -0.35411 | -1.0271 | -1.7132 | -2.3858 | -3.0204 | -3.5417 | -3.8233 | -4.1097 | -4.4354 | -4.4895 | -4.5067
|  | BALL HILL | ST |  |  | 2.8657 | 2.6866 | 2.4957 | 2.2919 | 2.0048 | 1.7148 | 1.423 | 1.113 | 0.79341 | 0.44902 | -0.88119 | -2.7479 | -3.2744 | -3.3628 | 3.1744 | 3.0872 | 2.9884 | 2.8759 | 2.7367 | 2.5955 | 2.4473 | 2.284 | 2.1071 | 1.932 | 1.1372 | 0.15318 | -0.24951 | -0.58462 | 1.7858 | 1.6253 | 1.4531 | 1.268 | 1.01 | 0.74947 | 0.48623 | 0.20562 | -0.085185 | -0.39656 | -1.6237 | -3.3045 | -3.7717 | -3.8474
|  | BALL HILL | SP |  |  | 2.9273 | 2.7966 | 2.6613 | 2.5263 | 2.0279 | 1.526 | 1.034 | 0.51945 | -0.0052564 | -0.62238 | -2.6441 | -6.578 | -8.8596 | -10.4539 | 3.1916 | 3.1228 | 3.0471 | 2.9698 | 2.7685 | 2.5632 | 2.361 | 2.1386 | 1.9088 | 1.6449 | 0.73211 | -1.2115 | -2.2443 | -3.1296 | 1.8394 | 1.722 | 1.5998 | 1.478 | 1.0367 | 0.59206 | 0.15629 | -0.30142 | -0.7684 | -1.3163 | -3.0932 | -6.6014 | -8.5412 | -9.8811
BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY | MINIMUM HEADROOM | SU 42075 42720 | YES | 1.089 | 0.81006 | 0.5162 | 0.21451 | -0.17489 | -0.57815 | -0.9955 | -1.4609 | -2.0036 | -2.5019 | -3.6277 | -4.8793 | -5.0883 | -5.1648 | 2.0528 | 1.9295 | 1.7938 | 1.6512 | 1.4775 | 1.2928 | 1.0906 | 0.85075 | 0.55455 | 0.28916 | -0.17167 | -0.67016 | -0.74533 | -0.81544 | 0.12833 | -0.13189 | -0.40446 | -0.68376 | -1.0454 | -1.4193 | -1.8048 | -2.2326 | -2.7289 | -3.1866 | -4.2438 | -5.3893 | -5.5728 | -5.6386
|  | BARTON STACEY | CT |  |  | 1.3458 | 1.2001 | 1.0443 | 0.87274 | 0.63836 | 0.39359 | 0.13416 | -0.16613 | -0.48473 | -0.93447 | -1.8316 | -3.2646 | -3.9493 | -4.0999 | 2.1152 | 2.0261 | 1.9285 | 1.8164 | 1.6908 | 1.5565 | 1.4101 | 1.2304 | 1.0342 | 0.75842 | 0.3278 | -0.26037 | -0.56057 | -0.7429 | 0.35311 | 0.21727 | 0.071113 | -0.090914 | -0.30718 | -0.53371 | -0.77462 | -1.0557 | -1.355 | -1.7786 | -2.5966 | -3.8919 | -4.5367 | -4.6771
|  | BARTON STACEY | LW |  |  | 1.089 | 0.81006 | 0.5162 | 0.21451 | -0.17489 | -0.57815 | -0.9955 | -1.4609 | -2.0036 | -2.5019 | -3.6277 | -4.8793 | -5.0883 | -5.1648 | 2.0528 | 1.9295 | 1.7938 | 1.6512 | 1.4775 | 1.2928 | 1.0906 | 0.85075 | 0.55455 | 0.28916 | -0.17167 | -0.67016 | -0.74533 | -0.77176 | 0.12833 | -0.13189 | -0.40446 | -0.68376 | -1.0454 | -1.4193 | -1.8048 | -2.2326 | -2.7289 | -3.1866 | -4.2438 | -5.3893 | -5.5728 | -5.6386
|  | BARTON STACEY | ST |  |  | 1.4511 | 1.3663 | 1.2821 | 1.1893 | 1.0484 | 0.9029 | 0.75088 | 0.58774 | 0.40557 | 0.20895 | -0.59458 | -1.6815 | -2.2167 | -2.5402 | 2.184 | 2.1334 | 2.0829 | 2.0241 | 1.9472 | 1.8667 | 1.7785 | 1.6814 | 1.5695 | 1.4598 | 0.94486 | 0.2863 | 0.0017491 | -0.22626 | 0.45345 | 0.37542 | 0.29762 | 0.21105 | 0.081257 | -0.053014 | -0.19406 | -0.34593 | -0.51623 | -0.69854 | -1.4581 | -2.471 | -2.9487 | -3.231
|  | BARTON STACEY | SP |  |  | 1.4884 | 1.4193 | 1.3563 | 1.2937 | 1.1341 | 0.97479 | 0.81181 | 0.6373 | 0.45218 | 0.20719 | -0.62552 | -2.5448 | -3.6005 | -4.2327 | 2.1942 | 2.146 | 2.1022 | 2.0578 | 1.9835 | 1.9084 | 1.831 | 1.7414 | 1.6439 | 1.5284 | 1.0977 | 0.0064639 | -0.49394 | -0.81544 | 0.48616 | 0.42158 | 0.3627 | 0.30402 | 0.15949 | 0.015182 | -0.13249 | -0.29197 | -0.46153 | -0.68426 | -1.45 | -3.2296 | -4.1987 | -4.793
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE | MINIMUM HEADROOM | SU 65155 52705 | YES | 21.14 | 20.8783 | 20.5346 | 20.1329 | 19.6756 | 19.1559 | 18.5351 | 17.8515 | 17.0259 | 16.0683 | 12.8649 | 9.2441 | 8.5595 | 8.2496 | 14.2798 | 14.131 | 13.8821 | 13.5864 | 13.2263 | 12.8376 | 12.4734 | 12.0964 | 11.6458 | 11.1721 | 9.9088 | 7.7992 | 6.8399 | 5.3261 | 11.8559 | 11.6571 | 11.3781 | 11.0523 | 10.6911 | 10.278 | 9.8421 | 9.3658 | 8.7708 | 8.0787 | 5.3797 | 1.9604 | 1.3352 | 1.0497
|  | BASINGSTOKE | CT |  |  | 21.14 | 20.9029 | 20.577 | 20.2096 | 19.8123 | 19.3731 | 18.9441 | 18.4866 | 17.9706 | 17.2753 | 15.0211 | 10.909 | 9.3201 | 8.5943 | 14.2798 | 14.131 | 13.8821 | 13.6001 | 13.3334 | 13.0089 | 12.7155 | 12.4096 | 12.0738 | 11.6114 | 10.349 | 8.3152 | 6.8399 | 5.4299 | 11.8559 | 11.6583 | 11.3869 | 11.0813 | 10.7576 | 10.3986 | 10.0519 | 9.6815 | 9.2629 | 8.7336 | 7.1656 | 3.5535 | 2.1117 | 1.4536
|  | BASINGSTOKE | LW |  |  | 21.1517 | 20.8783 | 20.5346 | 20.1329 | 19.6756 | 19.1559 | 18.5351 | 17.8515 | 17.0259 | 16.0683 | 12.8649 | 9.2441 | 8.5595 | 8.2496 | 14.2884 | 14.1329 | 13.8853 | 13.5864 | 13.2263 | 12.8376 | 12.4734 | 12.0964 | 11.6458 | 11.1721 | 9.9088 | 7.7992 | 7.4604 | 7.2716 | 11.8775 | 11.6571 | 11.3781 | 11.0523 | 10.6911 | 10.278 | 9.8421 | 9.3658 | 8.7708 | 8.0787 | 5.3797 | 1.9604 | 1.3352 | 1.0497
|  | BASINGSTOKE | ST |  |  | 21.3378 | 21.2179 | 21.0343 | 20.824 | 20.5826 | 20.3043 | 20.0366 | 19.7424 | 19.3633 | 18.8956 | 17.0744 | 12.2607 | 10.3977 | 9.7682 | 14.3665 | 14.2666 | 14.0775 | 13.8616 | 13.6618 | 13.4402 | 13.2601 | 13.0777 | 12.8671 | 12.6371 | 11.7086 | 8.8278 | 7.4902 | 6.8286 | 12.014 | 11.91 | 11.7527 | 11.5735 | 11.368 | 11.1313 | 10.9085 | 10.6644 | 10.3529 | 9.9741 | 8.4895 | 4.4938 | 2.882 | 2.3587
|  | BASINGSTOKE | SP |  |  | 21.338 | 21.2352 | 21.0659 | 20.8774 | 20.6656 | 20.4294 | 20.2197 | 19.995 | 19.7314 | 19.414 | 18.3381 | 14.8323 | 12.1051 | 11.3895 | 14.3677 | 14.2721 | 14.0866 | 13.8781 | 13.6893 | 13.4831 | 13.324 | 13.1651 | 12.9934 | 12.7973 | 12.0327 | 10.0379 | 7.9838 | 5.3261 | 12.0133 | 11.9224 | 11.7766 | 11.6153 | 11.4347 | 11.2333 | 11.0591 | 10.8724 | 10.6557 | 10.3996 | 9.5275 | 6.7446 | 4.3659 | 3.7237
NURSLING GSP | VELMORE BSP | BASSETT | MINIMUM HEADROOM | SU 42193 15958 | YES | 14.5694 | 14.2792 | 13.951 | 13.6 | 12.9831 | 12.3388 | 11.6599 | 10.9425 | 10.0831 | 9.1734 | 6.3598 | 2.4937 | -0.52368 | -2.685 | 12.9527 | 12.7648 | 12.5363 | 12.2714 | 11.9294 | 11.5501 | 11.1219 | 10.6402 | 10.0114 | 9.3308 | 7.1995 | 3.5385 | -0.81722 | -10.4453 | 8.3558 | 8.0536 | 7.6913 | 7.2976 | 6.6851 | 6.0371 | 5.3321 | 4.5775 | 3.6287 | 2.6131 | -0.17659 | -3.6631 | -6.1571 | -7.9043
|  | BASSETT | CT |  |  | 14.739 | 14.5481 | 14.3369 | 14.0703 | 13.674 | 13.2572 | 12.815 | 12.3406 | 11.8155 | 10.9119 | 7.9643 | 3.101 | -0.52368 | -2.685 | 12.9658 | 12.7705 | 12.5535 | 12.2714 | 11.9417 | 11.5887 | 11.1885 | 10.7373 | 10.213 | 9.4501 | 7.1995 | 3.5385 | -0.27413 | -5.2278 | 8.4737 | 8.2509 | 7.9976 | 7.6588 | 7.2276 | 6.7703 | 6.275 | 5.7374 | 5.1226 | 4.1312 | 1.2767 | -3.0655 | -6.1571 | -7.9043
|  | BASSETT | LW |  |  | 14.5694 | 14.2792 | 13.951 | 13.6 | 12.9831 | 12.3388 | 11.6599 | 10.9425 | 10.0831 | 9.1734 | 6.3598 | 2.4937 | 0.49438 | -0.77013 | 12.9527 | 12.7648 | 12.5363 | 12.2853 | 11.9294 | 11.5501 | 11.1219 | 10.6402 | 10.0114 | 9.3308 | 7.519 | 5.4099 | 4.4772 | 3.8524 | 8.3558 | 8.0536 | 7.6913 | 7.2976 | 6.6851 | 6.0371 | 5.3321 | 4.5775 | 3.6287 | 2.6131 | -0.17659 | -3.6631 | -5.3519 | -6.3917
|  | BASSETT | ST |  |  | 14.9001 | 14.8111 | 14.7176 | 14.6156 | 14.4658 | 14.3028 | 14.129 | 13.936 | 13.7085 | 13.4436 | 12.3557 | 8.8053 | 6.5471 | 4.9842 | 13.0811 | 12.9658 | 12.8447 | 12.7039 | 12.5164 | 12.3106 | 12.0824 | 11.8248 | 11.5227 | 11.1999 | 9.7803 | 6.0399 | 2.561 | -2.0511 | 8.6665 | 8.5643 | 8.4525 | 8.3277 | 8.1436 | 7.9418 | 7.7224 | 7.475 | 7.1805 | 6.8686 | 5.5102 | 2.0433 | 0.077843 | -1.2195
|  | BASSETT | SP |  |  | 14.9277 | 14.8398 | 14.7541 | 14.6631 | 14.5466 | 14.4142 | 14.2714 | 14.1215 | 13.952 | 13.7316 | 12.9172 | 10.1399 | 7.824 | 6.6323 | 13.0862 | 12.9587 | 12.8225 | 12.6703 | 12.4991 | 12.3013 | 12.0838 | 11.8387 | 11.5533 | 11.1722 | 9.6873 | 5.2646 | -0.81722 | -10.4453 | 8.6913 | 8.58 | 8.47 | 8.352 | 8.2173 | 8.061 | 7.8948 | 7.7114 | 7.4989 | 7.242 | 6.2489 | 3.3087 | 1.2142 | 0.21932
NORTH HYDE GSP | NORTH HYDE (D) | BATH ROAD EAST | MINIMUM HEADROOM | TQ 09097 76885 | YES | 5.6109 | 5.481 | 5.3114 | 5.1235 | 4.8518 | 4.545 | 4.2107 | 3.8506 | 3.4007 | 2.9208 | 1.3801 | -1.1126 | -3.4319 | -5.2782 | 5.8789 | 5.8066 | 5.7236 | 5.6307 | 5.494 | 5.3456 | 5.1818 | 5.0051 | 4.7725 | 4.5259 | 3.1893 | 1.3229 | -0.23076 | -3.87 | 4.8088 | 4.6913 | 4.535 | 4.3611 | 4.1118 | 3.843 | 3.5472 | 3.2269 | 2.8242 | 2.3755 | 0.85104 | -1.6707 | -3.1045 | -4.5938
|  | BATH ROAD EAST | CT |  |  | 5.645 | 5.5436 | 5.4249 | 5.2494 | 5.0366 | 4.8061 | 4.5558 | 4.2763 | 3.9524 | 3.4988 | 2.0146 | -0.91897 | -3.4319 | -5.2782 | 5.8853 | 5.821 | 5.7481 | 5.6562 | 5.5375 | 5.4086 | 5.2682 | 5.1169 | 4.9318 | 4.689 | 3.7339 | 1.7365 | -0.23076 | -2.4658 | 4.838 | 4.7461 | 4.638 | 4.4738 | 4.2769 | 4.0633 | 3.8303 | 3.5791 | 3.286 | 2.8804 | 1.5334 | -1.0438 | -3.1045 | -4.5938
|  | BATH ROAD EAST | LW |  |  | 5.6109 | 5.481 | 5.3114 | 5.1235 | 4.8518 | 4.545 | 4.2107 | 3.8506 | 3.4007 | 2.9208 | 1.3801 | -1.1126 | -2.9065 | -4.3673 | 5.8789 | 5.8066 | 5.7236 | 5.6307 | 5.494 | 5.3456 | 5.1818 | 5.0051 | 4.7725 | 4.5259 | 3.1893 | 1.3229 | 0.7809 | 0.32676 | 4.8088 | 4.6913 | 4.535 | 4.3611 | 4.1118 | 3.843 | 3.5472 | 3.2269 | 2.8242 | 2.3755 | 0.85104 | -1.6707 | -2.7268 | -3.9142
|  | BATH ROAD EAST | ST |  |  | 5.7242 | 5.6735 | 5.6168 | 5.5518 | 5.4502 | 5.3377 | 5.2173 | 5.0823 | 4.9148 | 4.7366 | 3.9869 | -0.13307 | -1.7454 | -2.3467 | 5.933 | 5.8995 | 5.8632 | 5.8224 | 5.7588 | 5.6871 | 5.6071 | 5.5162 | 5.3924 | 5.2462 | 4.4769 | 1.4143 | 0.22651 | -0.98845 | 4.914 | 4.8705 | 4.8214 | 4.7641 | 4.6713 | 4.5681 | 4.4568 | 4.3312 | 4.1741 | 4.0074 | 3.144 | -0.96631 | -2.4548 | -2.976
|  | BATH ROAD EAST | SP |  |  | 5.7318 | 5.6776 | 5.6193 | 5.5559 | 5.4763 | 5.3909 | 5.2946 | 5.192 | 5.0707 | 4.9347 | 4.4146 | 1.7103 | -0.6629 | -1.4639 | 5.9354 | 5.9042 | 5.8696 | 5.8312 | 5.7734 | 5.7092 | 5.6365 | 5.5567 | 5.4543 | 5.3205 | 4.8364 | 2.6506 | -0.029052 | -3.87 | 4.9209 | 4.8734 | 4.8222 | 4.766 | 4.6947 | 4.6181 | 4.5304 | 4.4366 | 4.3244 | 4.1981 | 3.7168 | 0.79227 | -1.4427 | -2.1661
IVER 132KV | LONGFORD | BATH ROAD WEST | MINIMUM HEADROOM | TQ 05814 76820 | YES | 18.9822 | 18.8301 | 18.69 | 18.5408 | 18.3406 | 17.9594 | 17.4788 | 16.9386 | 16.255 | 15.428 | 12.6942 | 9.6508 | 9.4072 | 9.2855 | 17.1115 | 16.9859 | 16.8733 | 16.7514 | 16.6185 | 16.4702 | 16.2939 | 16.0952 | 15.7302 | 15.1137 | 13.0663 | 10.8085 | 10.6588 | 10.5305 | 18.209 | 18.0487 | 17.8785 | 17.6848 | 17.3637 | 16.9761 | 16.5167 | 15.9999 | 15.3454 | 14.5246 | 11.8093 | 8.8665 | 8.6436 | 8.5316
|  | BATH ROAD WEST | CT |  |  | 18.9864 | 18.852 | 18.7263 | 18.5872 | 18.4394 | 18.1679 | 17.8023 | 17.404 | 16.9398 | 16.3437 | 14.404 | 11.3079 | 10.6077 | 10.355 | 17.1115 | 16.9859 | 16.8772 | 16.7614 | 16.6416 | 16.5138 | 16.3732 | 16.2196 | 16.0342 | 15.7482 | 14.3053 | 12.0617 | 11.6903 | 11.5492 | 18.209 | 18.0487 | 17.8884 | 17.7084 | 17.4883 | 17.1721 | 16.8225 | 16.4415 | 15.9968 | 15.4258 | 13.5561 | 10.4607 | 9.8138 | 9.5841
|  | BATH ROAD WEST | LW |  |  | 18.9822 | 18.8301 | 18.69 | 18.5408 | 18.3406 | 17.9594 | 17.4788 | 16.9386 | 16.255 | 15.428 | 12.6942 | 9.6508 | 9.4072 | 9.2855 | 17.1223 | 16.9876 | 16.8733 | 16.7514 | 16.6185 | 16.4702 | 16.2939 | 16.0952 | 15.7302 | 15.1137 | 13.0663 | 10.8085 | 10.6665 | 10.5882 | 18.2265 | 18.0488 | 17.8785 | 17.6848 | 17.3637 | 16.9761 | 16.5167 | 15.9999 | 15.3454 | 14.5246 | 11.8093 | 8.8665 | 8.6436 | 8.5316
|  | BATH ROAD WEST | ST |  |  | 19.0681 | 18.9856 | 18.9227 | 18.8616 | 18.7848 | 18.6986 | 18.5974 | 18.4789 | 18.3067 | 17.8813 | 16.2242 | 11.7283 | 9.7304 | 9.5369 | 17.1752 | 17.0901 | 17.0305 | 16.9757 | 16.9112 | 16.8411 | 16.7592 | 16.6637 | 16.532 | 16.3703 | 15.6031 | 12.1668 | 10.6588 | 10.5305 | 18.3222 | 18.2341 | 18.1608 | 18.086 | 17.987 | 17.8733 | 17.7387 | 17.5807 | 17.3073 | 16.8987 | 15.3049 | 10.9818 | 9.0356 | 8.8307
|  | BATH ROAD WEST | SP |  |  | 19.0712 | 18.9936 | 18.9341 | 18.8787 | 18.8161 | 18.7511 | 18.6783 | 18.5941 | 18.4866 | 18.36 | 17.4723 | 14.3104 | 11.1992 | 10.5359 | 17.1775 | 17.0961 | 17.0389 | 16.9883 | 16.935 | 16.8814 | 16.8216 | 16.7529 | 16.6659 | 16.5652 | 16.2213 | 14.1608 | 11.7928 | 11.286 | 18.3259 | 18.245 | 18.1769 | 18.1102 | 18.0303 | 17.9445 | 17.8482 | 17.7363 | 17.593 | 17.373 | 16.5063 | 13.467 | 10.452 | 9.8014
IVER 132KV | UPTON BSP | BEACONSFIELD (END BB) | MINIMUM HEADROOM | SU 93668 91219 | YES | 1.4669 | 1.3339 | 1.2079 | 1.0668 | 0.84055 | 0.60177 | 0.31968 | -0.0051209 | -0.38472 | -0.7235 | -1.5097 | -2.531 | -3.0492 | -3.4365 | 1.2998 | 1.2578 | 1.2154 | 1.1657 | 1.0979 | 1.0219 | 0.92975 | 0.82491 | 0.70148 | 0.5656 | 0.12987 | -0.383 | -0.73806 | -1.3044 | 0.62858 | 0.49907 | 0.37614 | 0.23866 | 0.017683 | -0.2155 | -0.48844 | -0.80262 | -1.1695 | -1.4971 | -2.2478 | -3.1703 | -3.6093 | -3.9531
|  | BEACONSFIELD (END BB) | CT |  |  | 1.5021 | 1.4015 | 1.2776 | 1.1687 | 1.0217 | 0.86488 | 0.67826 | 0.46682 | 0.23709 | -0.12721 | -0.91493 | -2.2005 | -3.0492 | -3.4365 | 1.3021 | 1.2673 | 1.2262 | 1.1832 | 1.1307 | 1.0737 | 1.0069 | 0.933 | 0.85337 | 0.7384 | 0.41943 | -0.16853 | -0.73806 | -1.3044 | 0.66376 | 0.56614 | 0.44594 | 0.34013 | 0.19665 | 0.043553 | -0.13598 | -0.33943 | -0.56048 | -0.91273 | -1.6741 | -2.8635 | -3.6093 | -3.9531
|  | BEACONSFIELD (END BB) | LW |  |  | 1.4669 | 1.3339 | 1.2079 | 1.0668 | 0.84055 | 0.60177 | 0.31968 | -0.0051209 | -0.38472 | -0.7235 | -1.5097 | -2.531 | -2.8633 | -3.0401 | 1.2998 | 1.2578 | 1.2154 | 1.1657 | 1.0979 | 1.0219 | 0.92975 | 0.82491 | 0.70148 | 0.5656 | 0.12987 | -0.383 | -0.46924 | -0.51801 | 0.62858 | 0.49907 | 0.37614 | 0.23866 | 0.017683 | -0.2155 | -0.48844 | -0.80262 | -1.1695 | -1.4971 | -2.2478 | -3.1703 | -3.4611 | -3.6134
|  | BEACONSFIELD (END BB) | ST |  |  | 1.6106 | 1.5719 | 1.5199 | 1.4591 | 1.3944 | 1.3223 | 1.2299 | 1.1242 | 1.0019 | 0.87541 | 0.24096 | -0.72149 | -1.1733 | -1.4565 | 1.3372 | 1.3233 | 1.3069 | 1.2882 | 1.2648 | 1.237 | 1.2008 | 1.1594 | 1.1076 | 1.0427 | 0.77472 | 0.17803 | -0.079362 | -0.54874 | 0.76916 | 0.73173 | 0.68146 | 0.62263 | 0.55992 | 0.4899 | 0.40258 | 0.30247 | 0.18631 | 0.066084 | -0.53936 | -1.4585 | -1.8869 | -2.1485
|  | BEACONSFIELD (END BB) | SP |  |  | 1.6146 | 1.5832 | 1.549 | 1.5088 | 1.4468 | 1.3831 | 1.3079 | 1.2131 | 1.1099 | 0.98811 | 0.51633 | -0.6147 | -1.1224 | -1.3303 | 1.3376 | 1.3259 | 1.3128 | 1.2977 | 1.2766 | 1.254 | 1.2252 | 1.1914 | 1.1532 | 1.1047 | 0.93121 | 0.38161 | -0.3369 | -1.1721 | 0.77312 | 0.74272 | 0.70967 | 0.6708 | 0.61048 | 0.54856 | 0.47777 | 0.38827 | 0.29067 | 0.17469 | -0.27405 | -1.3611 | -1.8561 | -2.0555
IVER 132KV | DENHAM | BEACONSFIELD (MIDDLE BB) | MINIMUM HEADROOM | SU 93668 91219 | YES | 1.7463 | 1.244 | 0.75862 | 2.2934 | 1.3376 | 0.33185 | -0.84805 | -2.1964 | -3.749 | -5.1481 | -8.4311 | -12.5165 | -14.6552 | -16.3144 | 1.3609 | 1.0208 | 0.64904 | 4.0982 | 3.6037 | 3.0393 | 2.3544 | 1.5419 | 0.53469 | -0.33532 | -2.1757 | -4.7823 | -7.1232 | -9.3887 | 0.17261 | -0.34545 | -0.83718 | 2.4129 | 1.529 | 0.59626 | -0.49548 | -1.7522 | -3.2197 | -4.5301 | -7.5329 | -11.2228 | -12.9791 | -14.3267
|  | BEACONSFIELD (MIDDLE BB) | CT |  |  | 1.9793 | 1.6149 | 1.1202 | 2.7831 | 2.1725 | 1.5226 | 0.75664 | -0.10787 | -1.0445 | -2.5435 | -5.873 | -11.1946 | -14.6552 | -16.3144 | 1.3609 | 1.0424 | 0.64904 | 4.0982 | 3.6874 | 3.2434 | 2.7037 | 2.0855 | 1.4047 | 0.40738 | -1.6466 | -4.7823 | -7.1232 | -9.3887 | 0.31333 | -0.077168 | -0.55798 | 2.8188 | 2.2449 | 1.6325 | 0.91434 | 0.10054 | -0.78366 | -2.1927 | -5.238 | -9.9956 | -12.9791 | -14.3267
|  | BEACONSFIELD (MIDDLE BB) | LW |  |  | 1.7463 | 1.244 | 0.75862 | 2.2934 | 1.3376 | 0.33185 | -0.84805 | -2.1964 | -3.749 | -5.1481 | -8.4311 | -12.5165 | -13.8457 | -14.5527 | 1.3652 | 1.0208 | 0.69948 | 4.1309 | 3.6037 | 3.0393 | 2.3544 | 1.5419 | 0.53469 | -0.33532 | -2.1757 | -4.3204 | -4.8808 | -5.1743 | 0.17261 | -0.34545 | -0.83718 | 2.4129 | 1.529 | 0.59626 | -0.49548 | -1.7522 | -3.2197 | -4.5301 | -7.5329 | -11.2228 | -12.3863 | -12.9952
|  | BEACONSFIELD (MIDDLE BB) | ST |  |  | 2.3344 | 2.1988 | 2.0252 | 3.9255 | 3.682 | 3.3906 | 3.0174 | 2.5915 | 2.1001 | 1.5863 | -0.95087 | -4.8756 | -6.7789 | -7.9843 | 1.6782 | 1.5399 | 1.3573 | 4.9432 | 4.7261 | 4.4821 | 4.1785 | 3.8289 | 3.4201 | 3.0225 | 1.0046 | -2.1555 | -4.0968 | -6.2304 | 0.73491 | 0.58518 | 0.3841 | 3.9488 | 3.698 | 3.4179 | 3.0686 | 2.6682 | 2.2035 | 1.7226 | -0.69918 | -4.3757 | -6.0894 | -7.1356
|  | BEACONSFIELD (MIDDLE BB) | SP |  |  | 2.3599 | 2.2544 | 2.14 | 4.1084 | 3.8646 | 3.6186 | 3.3149 | 2.9285 | 2.5086 | 2.0088 | 0.093686 | -4.4718 | -6.5828 | -7.4725 | 1.6755 | 1.5496 | 1.4086 | 5.0429 | 4.8461 | 4.6355 | 4.3878 | 4.0726 | 3.7208 | 3.318 | 1.7136 | -2.3682 | -5.3257 | -8.7905 | 0.75074 | 0.62915 | 0.49697 | 4.1415 | 3.9002 | 3.6525 | 3.3694 | 3.0114 | 2.6209 | 2.157 | 0.36209 | -3.9861 | -5.9662 | -6.7636
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM | MINIMUM HEADROOM | SU 58204 69025 | YES | 5.5897 | 5.2679 | 4.934 | 4.5937 | 4.1385 | 3.6687 | 3.1697 | 2.5967 | 1.9479 | 1.3746 | -0.06487 | -1.6543 | -1.8612 | -1.9059 | 5.8328 | 5.7865 | 5.734 | 5.6732 | 5.5021 | 5.265 | 5.0026 | 4.684 | 4.3055 | 3.9833 | 3.2586 | 2.4459 | 2.3446 | 2.3169 | 2.2989 | 2.0063 | 1.702 | 1.3908 | 0.97628 | 0.54777 | 0.089816 | -0.44089 | -1.0463 | -1.5776 | -2.8864 | -4.3338 | -4.5191 | -4.5588
|  | BEENHAM | CT |  |  | 5.8796 | 5.7086 | 5.5247 | 5.3276 | 5.0531 | 4.7671 | 4.465 | 4.0947 | 3.7113 | 3.1849 | 2.0878 | 0.22649 | -0.37102 | -0.46845 | 5.8328 | 5.7865 | 5.734 | 5.6732 | 5.6069 | 5.5347 | 5.4547 | 5.2219 | 4.9763 | 4.6463 | 4.0507 | 3.0839 | 2.7211 | 2.5121 | 2.5503 | 2.3898 | 2.2165 | 2.03 | 1.776 | 1.511 | 1.2297 | 0.88136 | 0.52034 | 0.024536 | -0.97893 | -2.6609 | -3.1938 | -3.2807
|  | BEENHAM | LW |  |  | 5.5897 | 5.2679 | 4.934 | 4.5937 | 4.1385 | 3.6687 | 3.1697 | 2.5967 | 1.9479 | 1.3746 | -0.06487 | -1.6543 | -1.8612 | -1.9059 | 5.8405 | 5.7922 | 5.7387 | 5.6775 | 5.5021 | 5.265 | 5.0026 | 4.684 | 4.3055 | 3.9833 | 3.2586 | 2.4459 | 2.3446 | 2.3169 | 2.2989 | 2.0063 | 1.702 | 1.3908 | 0.97628 | 0.54777 | 0.089816 | -0.44089 | -1.0463 | -1.5776 | -2.8864 | -4.3338 | -4.5191 | -4.5588
|  | BEENHAM | ST |  |  | 6.0043 | 5.9165 | 5.8198 | 5.7049 | 5.5417 | 5.3687 | 5.1883 | 4.9916 | 4.763 | 4.5237 | 3.4842 | 1.979 | 1.1828 | 0.77859 | 5.8747 | 5.8554 | 5.8334 | 5.8063 | 5.7731 | 5.734 | 5.6874 | 5.634 | 5.5579 | 5.468 | 4.7966 | 3.8026 | 3.2889 | 2.9657 | 2.6698 | 2.5889 | 2.4992 | 2.3913 | 2.2409 | 2.081 | 1.9136 | 1.7302 | 1.5152 | 1.292 | 0.30496 | -1.1056 | -1.8309 | -2.1871
|  | BEENHAM | SP |  |  | 6.0455 | 5.9792 | 5.911 | 5.8384 | 5.6479 | 5.4641 | 5.2775 | 5.065 | 4.8458 | 4.5574 | 3.5619 | 1.2711 | -0.091215 | -0.86271 | 5.8774 | 5.8603 | 5.842 | 5.82 | 5.7933 | 5.7653 | 5.734 | 5.6958 | 5.6482 | 5.5864 | 5.0224 | 3.6298 | 2.8569 | 2.4154 | 2.7063 | 2.6443 | 2.5803 | 2.5121 | 2.3392 | 2.1726 | 2.0031 | 1.8084 | 1.6072 | 1.344 | 0.42624 | -1.7055 | -2.9476 | -3.635
MANNINGTON GSP | SALISBURY | BEMERTON | MINIMUM HEADROOM | SU 11583 31233 | YES | 18.1264 | 17.631 | 17.1006 | 16.5425 | 15.9472 | 15.3535 | 14.7171 | 14.0413 | 13.2003 | 12.3055 | 10.0638 | 7.6978 | 6.1688 | 5.181 | 21.5574 | 21.2406 | 20.9278 | 20.5998 | 20.2956 | 19.9771 | 19.6065 | 19.2048 | 18.6939 | 18.137 | 16.8107 | 15.4004 | 14.0494 | 12.8297 | 19.4942 | 19.0601 | 18.5954 | 18.099 | 17.5584 | 17.0139 | 16.4274 | 15.7941 | 15.0071 | 14.1651 | 12.071 | 9.9062 | 8.6303 | 7.7609
|  | BEMERTON | CT |  |  | 18.3255 | 17.9322 | 17.552 | 17.062 | 16.6444 | 16.2371 | 15.7858 | 15.2984 | 14.7427 | 13.8709 | 11.5396 | 8.343 | 6.1688 | 5.181 | 21.6211 | 21.3375 | 21.0878 | 20.776 | 20.5316 | 20.267 | 19.9688 | 19.6444 | 19.2629 | 18.7053 | 17.2337 | 15.4004 | 14.0494 | 12.8297 | 19.6718 | 19.3279 | 18.9967 | 18.5635 | 18.1773 | 17.7955 | 17.3725 | 16.9155 | 16.3902 | 15.5726 | 13.3945 | 10.505 | 8.6303 | 7.7609
|  | BEMERTON | LW |  |  | 18.1264 | 17.631 | 17.1006 | 16.5425 | 15.9472 | 15.3535 | 14.7171 | 14.0413 | 13.2003 | 12.3055 | 10.0638 | 7.6978 | 6.8389 | 6.5261 | 21.5574 | 21.2406 | 20.9278 | 20.5998 | 20.2956 | 19.9771 | 19.6065 | 19.2048 | 18.6939 | 18.137 | 16.8107 | 15.5565 | 15.1776 | 15.0394 | 19.4942 | 19.0601 | 18.5954 | 18.099 | 17.5584 | 17.0139 | 16.4274 | 15.7941 | 15.0071 | 14.1651 | 12.071 | 9.9062 | 9.1445 | 8.8807
|  | BEMERTON | ST |  |  | 18.4841 | 18.2082 | 17.968 | 17.7214 | 17.5242 | 17.3356 | 17.1201 | 16.8845 | 16.6174 | 16.3383 | 15.2441 | 12.7168 | 11.443 | 10.6177 | 21.7176 | 21.4975 | 21.3222 | 21.1431 | 21.0112 | 20.8819 | 20.7393 | 20.583 | 20.3966 | 20.1887 | 19.3372 | 17.3738 | 16.2436 | 15.0581 | 19.8175 | 19.5825 | 19.3868 | 19.1811 | 19.0011 | 18.8246 | 18.6301 | 18.4077 | 18.1541 | 17.8912 | 16.842 | 14.4363 | 13.283 | 12.5548
|  | BEMERTON | SP |  |  | 18.5236 | 18.2523 | 18.0242 | 17.7921 | 17.6065 | 17.4334 | 17.2482 | 17.0399 | 16.8148 | 16.5485 | 15.6281 | 13.2913 | 11.9321 | 11.3591 | 21.7318 | 21.5077 | 21.3348 | 21.1571 | 21.0395 | 20.9271 | 20.8038 | 20.6668 | 20.5166 | 20.3236 | 19.5896 | 17.5242 | 15.6033 | 13.2606 | 19.8525 | 19.6212 | 19.4368 | 19.241 | 19.0751 | 18.9168 | 18.7471 | 18.5601 | 18.3539 | 18.107 | 17.24 | 15.01 | 13.7309 | 13.2144
COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD | MINIMUM HEADROOM | SU 58382 95467 | NO | 10.2785 | 9.4524 | 8.8187 | 7.886 | 6.3503 | 4.3333 | 2.1674 | -0.235 | -2.9876 | -5.7484 | -14.1055 | -23.79 | -26.2872 | -27.4788 | 15.167 | 14.6379 | 14.2447 | 13.6936 | 12.8699 | 11.8007 | 10.6419 | 9.3542 | 7.8304 | 6.323 | 2.1104 | -2.7344 | -4.3563 | -5.3379 | 12.2984 | 11.552 | 10.9823 | 10.1717 | 8.8681 | 7.173 | 5.343 | 3.3002 | 0.91514 | -1.4616 | -8.3746 | -16.4198 | -18.5457 | -19.5983
|  | BERINSFIELD | CT |  |  | 10.55 | 9.8374 | 9.3657 | 8.5411 | 7.2389 | 5.4618 | 3.5472 | 1.4061 | -0.96602 | -3.7394 | -12.1232 | -23.009 | -26.2872 | -27.4788 | 15.2263 | 14.7348 | 14.4004 | 13.871 | 13.133 | 12.1513 | 11.0956 | 9.9172 | 8.6022 | 7.0645 | 2.6966 | -2.7089 | -4.3563 | -5.3379 | 12.511 | 11.882 | 11.4492 | 10.7269 | 9.6257 | 8.1369 | 6.5261 | 4.719 | 2.7043 | 0.31949 | -6.7068 | -15.6993 | -18.5457 | -19.5983
|  | BERINSFIELD | LW |  |  | 10.2785 | 9.4524 | 8.8187 | 7.886 | 6.3503 | 4.3333 | 2.1674 | -0.235 | -2.9876 | -5.7484 | -14.1055 | -23.79 | -25.3676 | -25.9363 | 15.167 | 14.6379 | 14.2447 | 13.6936 | 12.8699 | 11.8007 | 10.6419 | 9.3542 | 7.8304 | 6.323 | 2.1104 | -2.7344 | -3.4601 | -3.6907 | 12.2984 | 11.552 | 10.9823 | 10.1717 | 8.8681 | 7.173 | 5.343 | 3.3002 | 0.91514 | -1.4616 | -8.3746 | -16.4198 | -17.7691 | -18.2721
|  | BERINSFIELD | ST |  |  | 10.6982 | 10.2138 | 9.9339 | 9.4478 | 8.6323 | 7.481 | 6.2623 | 4.9143 | 3.4461 | 1.9442 | -3.7242 | -11.0825 | -12.7841 | -13.6834 | 15.3434 | 14.9455 | 14.7375 | 14.4759 | 13.9555 | 13.2561 | 12.516 | 11.6991 | 10.8081 | 9.9178 | 6.4814 | 1.9754 | 0.8048 | -0.10324 | 12.7216 | 12.2788 | 12.0037 | 11.6017 | 10.9307 | 10.0043 | 9.0194 | 7.9262 | 6.7285 | 5.507 | 0.833 | -5.2769 | -6.7544 | -7.5525
|  | BERINSFIELD | SP |  |  | 10.7356 | 10.2737 | 10.018 | 9.5893 | 8.8591 | 7.8885 | 6.7716 | 5.5593 | 4.2794 | 2.9129 | -1.9015 | -9.3091 | -11.2006 | -11.9991 | 15.3443 | 14.9471 | 14.7433 | 14.5055 | 14.098 | 13.5243 | 12.8481 | 12.107 | 11.32 | 10.488 | 7.5154 | 2.6774 | 1.139 | -0.099495 | 12.7536 | 12.3241 | 12.0779 | 11.7292 | 11.157 | 10.3966 | 9.5082 | 8.5411 | 7.518 | 6.4193 | 2.5422 | -3.6788 | -5.3614 | -6.0786
NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY | MINIMUM HEADROOM | SU 42648 13187 | YES | 15.4827 | 15.3299 | 15.1403 | 14.9053 | 14.5054 | 14.1132 | 13.4307 | 12.5471 | 11.5104 | 10.4494 | 6.8733 | 2.0713 | -0.77135 | -3.0017 | 13.489 | 13.2925 | 13.0698 | 12.7993 | 12.2772 | 11.7148 | 11.1172 | 10.4363 | 9.6668 | 8.7447 | 5.7321 | -0.73027 | -14.0714 | -36.8984 | 10.6211 | 10.391 | 10.1331 | 9.8467 | 9.0981 | 8.4102 | 7.694 | 6.9018 | 5.9678 | 5.0076 | 2.0577 | -2.2957 | -4.6485 | -6.5057
|  | BEVOIS VALLEY | CT |  |  | 15.4827 | 15.3299 | 15.1403 | 14.9114 | 14.5343 | 14.1786 | 13.7996 | 13.3622 | 12.8396 | 11.965 | 8.638 | 2.9459 | -0.77135 | -3.0017 | 13.489 | 13.2925 | 13.0698 | 12.7993 | 12.2772 | 11.7148 | 11.1172 | 10.4363 | 9.6668 | 8.7447 | 5.7321 | -0.62429 | -8.3158 | -19.5759 | 10.7529 | 10.6031 | 10.4291 | 10.2187 | 9.6282 | 9.105 | 8.5807 | 7.9891 | 7.3279 | 6.4253 | 3.6788 | -1.4358 | -4.6485 | -6.5057
|  | BEVOIS VALLEY | LW |  |  | 15.5073 | 15.3398 | 15.1417 | 14.9053 | 14.5054 | 14.1132 | 13.4307 | 12.5471 | 11.5104 | 10.4494 | 6.8733 | 2.0713 | -0.10847 | -1.5299 | 13.5182 | 13.3776 | 13.2138 | 13.0292 | 12.5924 | 12.1942 | 11.7586 | 11.2231 | 10.5768 | 9.9085 | 7.8007 | 5.02 | 3.9458 | 3.2139 | 10.6211 | 10.391 | 10.1331 | 9.8467 | 9.0981 | 8.4102 | 7.694 | 6.9018 | 5.9678 | 5.0076 | 2.0577 | -2.2957 | -4.1441 | -5.3206
|  | BEVOIS VALLEY | ST |  |  | 15.6308 | 15.5627 | 15.4789 | 15.3803 | 15.1293 | 14.9053 | 14.662 | 14.3624 | 13.9846 | 13.5466 | 11.9218 | 7.5311 | 5.1588 | 4.4272 | 13.6066 | 13.472 | 13.3197 | 13.1469 | 12.8085 | 12.4776 | 12.0589 | 11.5693 | 11.0058 | 10.4144 | 8.2553 | 2.2463 | -5.3197 | -16.3456 | 10.9292 | 10.8753 | 10.8103 | 10.7359 | 10.4991 | 10.2928 | 10.0719 | 9.8031 | 9.4781 | 9.0993 | 7.8246 | 4.0774 | 1.6501 | 0.28012
|  | BEVOIS VALLEY | SP |  |  | 15.6466 | 15.589 | 15.5109 | 15.427 | 15.2142 | 15.0337 | 14.8442 | 14.6128 | 14.3439 | 14.0514 | 13.1156 | 10.3113 | 7.2187 | 6.1645 | 13.6046 | 13.4605 | 13.2843 | 13.089 | 12.7163 | 12.2966 | 11.7909 | 11.2063 | 10.5377 | 9.7922 | 7.0015 | -0.73027 | -14.0714 | -36.8984 | 10.9557 | 10.9128 | 10.8558 | 10.7967 | 10.6083 | 10.4535 | 10.2837 | 10.079 | 9.8525 | 9.5808 | 8.7252 | 6.122 | 3.6032 | 2.3999
EAST CLAYDON GSP | BICESTER NORTH | BICESTER | MINIMUM HEADROOM | SP 58381 21988 | NO | 39.4691 | 38.1007 | 36.2639 | 34.3868 | 31.293 | 28.1086 | 24.718 | 21.0557 | 16.7813 | 12.2649 | 4.0629 | -4.5784 | -8.4845 | -11.5358 | 45.9898 | 45.2094 | 44.1529 | 43.0628 | 41.4051 | 39.6833 | 37.8126 | 35.7693 | 33.2492 | 30.585 | 25.8028 | 21.0447 | 17.0614 | 13.7301 | 40.9339 | 39.7517 | 38.1857 | 36.5664 | 33.8746 | 31.0924 | 28.1248 | 24.9152 | 21.1739 | 17.2194 | 9.7777 | 1.8108 | -1.7958 | -4.4755
|  | BICESTER | CT |  |  | 39.978 | 38.934 | 37.4583 | 35.8251 | 33.3473 | 30.8014 | 28.1785 | 25.3042 | 22.013 | 17.5699 | 9.3555 | -1.6685 | -8.4845 | -11.5358 | 46.12 | 45.4405 | 44.5099 | 43.4466 | 42.0076 | 40.5179 | 38.9551 | 37.2269 | 35.2124 | 32.5388 | 27.4852 | 21.1693 | 17.0614 | 13.7301 | 41.4195 | 40.5431 | 39.3135 | 37.9304 | 35.8179 | 33.6356 | 31.3861 | 28.9138 | 26.0749 | 22.1385 | 14.6126 | 4.532 | -1.7958 | -4.4755
|  | BICESTER | LW |  |  | 39.4691 | 38.1007 | 36.2639 | 34.3868 | 31.293 | 28.1086 | 24.718 | 21.0557 | 16.7813 | 12.2649 | 4.0629 | -4.5784 | -7.2977 | -8.63 | 45.9898 | 45.2094 | 44.1529 | 43.0628 | 41.4051 | 39.6833 | 37.8126 | 35.7693 | 33.2492 | 30.585 | 25.8028 | 21.0447 | 19.8223 | 19.2452 | 40.9339 | 39.7517 | 38.1857 | 36.5664 | 33.8746 | 31.0924 | 28.1248 | 24.9152 | 21.1739 | 17.2194 | 9.7777 | 1.8108 | -0.70497 | -1.9425
|  | BICESTER | ST |  |  | 40.5819 | 39.9966 | 39.1432 | 38.2963 | 36.8786 | 35.4371 | 33.9079 | 32.2523 | 30.3761 | 28.3331 | 23.2493 | 14.1025 | 9.6953 | 7.267 | 46.537 | 46.156 | 45.6063 | 45.0433 | 44.1354 | 43.2055 | 42.2082 | 41.121 | 39.8736 | 38.5475 | 34.7797 | 27.8187 | 24.1315 | 20.9518 | 41.9643 | 41.5038 | 40.8422 | 40.1721 | 39.0448 | 37.8876 | 36.6512 | 35.3044 | 33.7662 | 32.0775 | 27.3725 | 18.7157 | 14.7008 | 12.5638
|  | BICESTER | SP |  |  | 40.6782 | 40.1266 | 39.3818 | 38.6583 | 37.4417 | 36.1872 | 34.832 | 33.3649 | 31.7437 | 29.9138 | 25.9197 | 16.7761 | 11.4962 | 9.4106 | 46.5785 | 46.2006 | 45.7035 | 45.2022 | 44.4633 | 43.688 | 42.8214 | 41.8622 | 40.7897 | 39.5654 | 36.5601 | 29.0469 | 23.1057 | 17.2303 | 42.0535 | 41.6269 | 41.065 | 40.508 | 39.5543 | 38.5593 | 37.4773 | 36.3008 | 34.9942 | 33.5054 | 29.9976 | 21.2985 | 16.3263 | 14.4289
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST | MINIMUM HEADROOM | TQ 08305 26315 | YES | 15.7634 | 15.4873 | 15.1881 | 14.8625 | 14.3385 | 13.7898 | 13.2031 | 12.5683 | 11.8252 | 11.0854 | 9.3108 | 7.2034 | 6.4919 | 5.8069 | 18.8725 | 18.7145 | 18.539 | 18.3467 | 18.0743 | 17.7839 | 17.4607 | 17.1023 | 16.6438 | 16.1917 | 15.2044 | 14.1045 | 13.3706 | 12.5967 | 16.9882 | 16.7193 | 16.4306 | 16.1238 | 15.6408 | 15.1357 | 14.5975 | 14.0168 | 13.3442 | 12.6724 | 11.0382 | 9.093 | 8.4415 | 7.8212
|  | BILLINGSHURST | CT |  |  | 15.9458 | 15.7763 | 15.5739 | 15.3493 | 15.0394 | 14.7054 | 14.3597 | 13.9849 | 13.5459 | 12.829 | 11.1318 | 8.4582 | 6.6504 | 5.8069 | 18.9328 | 18.8126 | 18.6664 | 18.5017 | 18.3033 | 18.0862 | 17.8536 | 17.5985 | 17.2922 | 16.8303 | 15.8081 | 14.3723 | 13.3706 | 12.5967 | 17.1879 | 17.032 | 16.8481 | 16.6451 | 16.3499 | 16.0337 | 15.7102 | 15.3609 | 14.9581 | 14.3093 | 12.7316 | 10.2687 | 8.5803 | 7.8212
|  | BILLINGSHURST | LW |  |  | 15.7634 | 15.4873 | 15.1881 | 14.8625 | 14.3385 | 13.7898 | 13.2031 | 12.5683 | 11.8252 | 11.0854 | 9.3108 | 7.2034 | 6.4919 | 6.125 | 18.8725 | 18.7145 | 18.539 | 18.3467 | 18.0743 | 17.7839 | 17.4607 | 17.1023 | 16.6438 | 16.1917 | 15.2044 | 14.1045 | 13.7887 | 13.6259 | 16.9882 | 16.7193 | 16.4306 | 16.1238 | 15.6408 | 15.1357 | 14.5975 | 14.0168 | 13.3442 | 12.6724 | 11.0382 | 9.093 | 8.4415 | 8.1121
|  | BILLINGSHURST | ST |  |  | 16.0854 | 16.0034 | 15.9061 | 15.7933 | 15.6374 | 15.4767 | 15.2979 | 15.1011 | 14.8785 | 14.6396 | 13.55 | 11.5252 | 10.4721 | 9.7978 | 19.0311 | 18.9719 | 18.9003 | 18.8155 | 18.7075 | 18.5953 | 18.4666 | 18.3231 | 18.156 | 17.9861 | 17.1764 | 15.6903 | 14.9018 | 14.1825 | 17.3136 | 17.2367 | 17.147 | 17.0443 | 16.8984 | 16.7481 | 16.5826 | 16.4015 | 16.1985 | 15.9758 | 14.9913 | 13.0626 | 12.1186 | 11.5341
|  | BILLINGSHURST | SP |  |  | 16.1199 | 16.0522 | 15.9762 | 15.8932 | 15.7305 | 15.5649 | 15.3968 | 15.2042 | 14.9972 | 14.7449 | 13.7931 | 11.3567 | 9.967 | 9.2751 | 19.0462 | 18.9918 | 18.9296 | 18.8601 | 18.7583 | 18.6526 | 18.542 | 18.4115 | 18.2672 | 18.0936 | 17.4225 | 15.5985 | 14.3124 | 13.1088 | 17.3487 | 17.2873 | 17.2185 | 17.1441 | 16.9859 | 16.8251 | 16.6628 | 16.4794 | 16.2835 | 16.0411 | 15.1683 | 12.9407 | 11.6541 | 11.0399
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM | MINIMUM HEADROOM | SU 97366 01594 | NO | 12.5033 | 11.2898 | 10.0121 | 8.5198 | 6.5756 | 4.455 | 2.3423 | 0.1158 | -2.3751 | -4.7593 | -10.9437 | -15.8191 | -18.2072 | -19.8575 | 18.0633 | 17.393 | 16.6754 | 15.845 | 14.8143 | 13.6848 | 12.5415 | 11.3308 | 9.9205 | 8.5407 | 5.198 | 2.3922 | 0.071642 | -1.9134 | 15.3901 | 14.3984 | 13.3149 | 12.0468 | 10.3862 | 8.5709 | 6.7445 | 4.8115 | 2.6139 | 0.4883 | -4.912 | -9.2626 | -11.3367 | -12.7478
|  | BILSHAM | CT |  |  | 12.788 | 11.742 | 10.6949 | 9.3344 | 7.6966 | 5.8996 | 4.1218 | 2.2457 | 0.23749 | -2.1029 | -8.4206 | -14.57 | -18.2072 | -19.8575 | 18.1382 | 17.5137 | 16.8897 | 16.0707 | 15.139 | 14.1203 | 13.1015 | 12.0223 | 10.8364 | 9.4464 | 5.8442 | 2.3922 | 0.071642 | -1.9134 | 15.605 | 14.7474 | 13.8798 | 12.7326 | 11.3741 | 9.8483 | 8.3246 | 6.7093 | 4.9586 | 2.8748 | -2.6603 | -8.1175 | -11.3367 | -12.7478
|  | BILSHAM | LW |  |  | 12.5033 | 11.2898 | 10.0121 | 8.5198 | 6.5756 | 4.455 | 2.3423 | 0.1158 | -2.3751 | -4.7593 | -10.9437 | -15.8191 | -17.3268 | -18.0474 | 18.0633 | 17.393 | 16.6754 | 15.845 | 14.8143 | 13.6848 | 12.5415 | 11.3308 | 9.9205 | 8.5407 | 5.198 | 2.6373 | 1.9275 | 1.5999 | 15.3901 | 14.3984 | 13.3149 | 12.0468 | 10.3862 | 8.5709 | 6.7445 | 4.8115 | 2.6139 | 0.4883 | -4.912 | -9.2626 | -10.6012 | -11.2429
|  | BILSHAM | ST |  |  | 13.233 | 12.5664 | 11.929 | 11.186 | 10.1737 | 9.0676 | 7.9942 | 6.8671 | 5.7015 | 4.6221 | 0.72073 | -3.899 | -5.96 | -7.2913 | 18.439 | 18.0433 | 17.6546 | 17.1982 | 16.5648 | 15.8745 | 15.1955 | 14.4781 | 13.7254 | 13.0376 | 10.4337 | 6.9911 | 5.1549 | 3.256 | 16.0275 | 15.5146 | 15.0122 | 14.421 | 13.5859 | 12.6727 | 11.7786 | 10.8348 | 9.8498 | 8.9372 | 5.5405 | 1.328 | -0.44589 | -1.6325
|  | BILSHAM | SP |  |  | 13.2904 | 12.6531 | 12.0783 | 11.4112 | 10.5634 | 9.6418 | 8.6863 | 7.7027 | 6.716 | 5.7418 | 2.5128 | -2.2624 | -4.6507 | -5.7185 | 18.4617 | 18.071 | 17.7097 | 17.2867 | 16.7745 | 16.2112 | 15.6006 | 14.9611 | 14.306 | 13.6584 | 11.4195 | 7.5237 | 4.6093 | 1.3128 | 16.0754 | 15.5835 | 15.1352 | 14.6097 | 13.9402 | 13.2088 | 12.4253 | 11.6128 | 10.7913 | 9.9756 | 7.2249 | 2.8302 | 0.69893 | -0.23844
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD | MINIMUM HEADROOM | SZ 56409 91399 | NO | 8.7739 | 8.5821 | 8.3201 | 8.0305 | 7.5845 | 7.112 | 6.5925 | 6.0443 | 5.3547 | 4.6025 | 2.7158 | 0.86094 | -0.30122 | -1.0433 | 10.4629 | 10.3574 | 10.2105 | 10.0466 | 9.806 | 9.5398 | 9.2381 | 8.916 | 8.4939 | 8.0279 | 6.8872 | 5.8178 | 4.8967 | 4.1704 | 8.9719 | 8.9108 | 8.831 | 8.7292 | 8.3509 | 7.9173 | 7.4422 | 6.9413 | 6.3049 | 5.5875 | 3.8092 | 2.1078 | 1.0653 | 0.41844
|  | BINSTEAD | CT |  |  | 8.8698 | 8.743 | 8.5901 | 8.3458 | 8.0412 | 7.714 | 7.3593 | 6.9683 | 6.5083 | 5.7848 | 3.7996 | 1.2604 | -0.30122 | -1.0433 | 10.4918 | 10.41 | 10.3113 | 10.1569 | 9.9672 | 9.7575 | 9.5285 | 9.2732 | 8.966 | 8.5142 | 7.2793 | 5.8178 | 4.8967 | 4.1704 | 8.9719 | 8.9108 | 8.8368 | 8.7342 | 8.6254 | 8.4831 | 8.161 | 7.7891 | 7.3472 | 6.6597 | 4.7861 | 2.4817 | 1.0653 | 0.41844
|  | BINSTEAD | LW |  |  | 8.7739 | 8.5821 | 8.3201 | 8.0305 | 7.5845 | 7.112 | 6.5925 | 6.0443 | 5.3547 | 4.6025 | 2.7158 | 0.86094 | 0.26391 | -0.011447 | 10.4629 | 10.3574 | 10.2105 | 10.0466 | 9.806 | 9.5398 | 9.2381 | 8.916 | 8.4939 | 8.0279 | 6.8872 | 5.8647 | 5.6094 | 5.4894 | 8.9839 | 8.9171 | 8.831 | 8.7292 | 8.3509 | 7.9173 | 7.4422 | 6.9413 | 6.3049 | 5.5875 | 3.8092 | 2.1078 | 1.5858 | 1.3341
|  | BINSTEAD | ST |  |  | 8.9914 | 8.9393 | 8.8777 | 8.8006 | 8.6611 | 8.5092 | 8.3361 | 8.1458 | 7.9095 | 7.6607 | 6.5466 | 3.9709 | 2.8808 | 2.3243 | 10.5636 | 10.526 | 10.4822 | 10.428 | 10.3382 | 10.2396 | 10.1262 | 9.9886 | 9.8139 | 9.6348 | 8.8242 | 6.9537 | 6.0792 | 5.4072 | 9.0282 | 9.0016 | 8.972 | 8.9352 | 8.8781 | 8.8123 | 8.7349 | 8.6463 | 8.5144 | 8.3697 | 7.358 | 4.8846 | 3.8887 | 3.4043
|  | BINSTEAD | SP |  |  | 9.0125 | 8.9536 | 8.8932 | 8.8212 | 8.7263 | 8.6255 | 8.5208 | 8.3925 | 8.241 | 8.0537 | 7.31 | 5.1691 | 3.8566 | 3.4803 | 10.5726 | 10.5295 | 10.4836 | 10.4296 | 10.3659 | 10.2972 | 10.2242 | 10.1345 | 10.0183 | 9.8739 | 9.2914 | 7.5883 | 6.1809 | 4.948 | 9.0329 | 9.0066 | 8.9776 | 8.9444 | 8.9034 | 8.8581 | 8.8083 | 8.7485 | 8.6651 | 8.5749 | 8.0987 | 6.0251 | 4.7756 | 4.4355
LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM | MINIMUM HEADROOM | SZ 81965 99422 | NO | 1.1026 | 0.73324 | 13.2945 | 12.8187 | 12.0816 | 11.3139 | 10.4792 | 9.5298 | 8.3591 | 7.1574 | 4.218 | 1.105 | -0.36636 | -1.6132 | 1.5507 | 1.3614 | 17.1182 | 16.8475 | 16.478 | 16.0882 | 15.6447 | 15.1162 | 14.446 | 13.7189 | 12.1386 | 10.6153 | 9.5906 | 8.7353 | -0.87154 | -1.2141 | -1.6255 | 13.9266 | 13.2453 | 12.5342 | 11.7559 | 10.8648 | 9.7703 | 8.6487 | 5.9724 | 3.1757 | 1.9304 | 0.90559
|  | BIRDHAM | CT |  |  | 1.3396 | 1.1163 | 13.86 | 13.4991 | 13.027 | 12.5293 | 11.9934 | 11.3623 | 10.5865 | 9.3739 | 6.3726 | 2.2554 | -0.36636 | -1.6132 | 1.6082 | 1.4647 | 17.2962 | 17.044 | 16.7661 | 16.47 | 16.1443 | 15.7465 | 15.2686 | 14.5323 | 12.8263 | 10.87 | 9.5906 | 8.7353 | -0.68796 | -0.89726 | -1.1396 | 14.5107 | 14.0786 | 13.6083 | 13.1002 | 12.4983 | 11.7702 | 10.6353 | 7.8899 | 4.215 | 1.9304 | 0.90559
|  | BIRDHAM | LW |  |  | 1.1026 | 0.73324 | 13.2945 | 12.8187 | 12.0816 | 11.3139 | 10.4792 | 9.5298 | 8.3591 | 7.1574 | 4.218 | 1.105 | 0.14396 | -0.37818 | 1.5507 | 1.3614 | 17.1182 | 16.8475 | 16.478 | 16.0882 | 15.6447 | 15.1162 | 14.446 | 13.7189 | 12.1386 | 10.6153 | 10.2004 | 9.9807 | -0.87154 | -1.2141 | -1.6255 | 13.9266 | 13.2453 | 12.5342 | 11.7559 | 10.8648 | 9.7703 | 8.6487 | 5.9724 | 3.1757 | 2.3236 | 1.8684
|  | BIRDHAM | ST |  |  | 1.5234 | 1.425 | 14.2995 | 14.1558 | 13.9284 | 13.6876 | 13.4196 | 13.1226 | 12.72 | 12.2897 | 10.3419 | 7.0158 | 5.5318 | 4.578 | 1.7254 | 1.6634 | 17.5785 | 17.479 | 17.3329 | 17.1772 | 16.9993 | 16.7995 | 16.5327 | 16.2716 | 14.9682 | 12.6739 | 11.7467 | 11.0039 | -0.51378 | -0.60381 | -0.72203 | 15.1413 | 14.9287 | 14.7032 | 14.4499 | 14.1678 | 13.7925 | 13.396 | 11.5686 | 8.4461 | 7.1024 | 6.2603
|  | BIRDHAM | SP |  |  | 1.564 | 1.4686 | 14.3675 | 14.2566 | 14.0521 | 13.8504 | 13.638 | 13.3886 | 13.0655 | 12.6633 | 11.1507 | 7.6303 | 5.8664 | 5.0963 | 1.7406 | 1.6702 | 17.5936 | 17.5087 | 17.3893 | 17.2712 | 17.1466 | 16.9883 | 16.7872 | 16.5478 | 15.5924 | 13.0503 | 11.6362 | 10.5999 | -0.47894 | -0.57122 | -0.66937 | 15.2227 | 15.038 | 14.8562 | 14.6651 | 14.4328 | 14.1365 | 13.7696 | 12.379 | 9.0479 | 7.3968 | 6.704
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM | MINIMUM HEADROOM | SU 56691 16683 | YES | 5.682 | 4.6687 | 3.6038 | 2.5973 | 1.1666 | -0.3073 | -1.8786 | -3.5919 | -5.6043 | -7.3312 | -11.3242 | -16.2304 | -17.566 | -18.5574 | 13.4742 | 13.2299 | 12.9326 | 12.687 | 12.3673 | 11.7331 | 10.9014 | 9.9046 | 8.6404 | 7.6142 | 5.5092 | 3.0018 | 1.8823 | 0.52847 | 8.8827 | 8.3889 | 7.8449 | 7.3564 | 6.6543 | 5.9269 | 5.1627 | 3.6305 | 1.7312 | 0.11764 | -3.5347 | -8.0019 | -9.1883 | -9.8999
|  | BISHOPS WALTHAM | CT |  |  | 6.2348 | 5.5599 | 4.7815 | 4.0777 | 3.1544 | 2.1893 | 1.1859 | 0.071055 | -1.1626 | -2.8899 | -6.4993 | -12.7757 | -16.8025 | -18.5574 | 13.5065 | 13.2936 | 13.0144 | 12.7913 | 12.5397 | 12.2744 | 11.9314 | 11.1861 | 10.3392 | 9.2379 | 7.1928 | 3.9372 | 1.8823 | 0.52847 | 9.1738 | 8.8498 | 8.46 | 8.1318 | 7.6782 | 7.206 | 6.7272 | 6.2171 | 5.3779 | 3.8317 | 0.7559 | -4.8995 | -8.4602 | -9.8999
|  | BISHOPS WALTHAM | LW |  |  | 5.682 | 4.6687 | 3.6038 | 2.5973 | 1.1666 | -0.3073 | -1.8786 | -3.5919 | -5.6043 | -7.3312 | -11.3242 | -16.2304 | -17.566 | -18.2348 | 13.4742 | 13.2299 | 12.9326 | 12.687 | 12.3673 | 11.7331 | 10.9014 | 9.9046 | 8.6404 | 7.6142 | 5.5092 | 3.0018 | 2.4301 | 2.1636 | 8.8827 | 8.3889 | 7.8449 | 7.3564 | 6.6543 | 5.9269 | 5.1627 | 3.6305 | 1.7312 | 0.11764 | -3.5347 | -8.0019 | -9.1883 | -9.7542
|  | BISHOPS WALTHAM | ST |  |  | 6.7101 | 6.3298 | 5.88 | 5.474 | 4.9581 | 4.4244 | 3.8612 | 3.2652 | 2.6047 | 1.9165 | -1.2548 | -5.869 | -8.3415 | -9.7711 | 13.6377 | 13.5037 | 13.3151 | 13.1818 | 13.0279 | 12.8652 | 12.6955 | 12.5118 | 12.2854 | 12.0432 | 10.0175 | 6.8211 | 5.1247 | 3.842 | 9.3689 | 9.1702 | 8.9237 | 8.7318 | 8.4806 | 8.2179 | 7.9476 | 7.6631 | 7.3351 | 6.9589 | 5.2191 | 1.1615 | -1.0047 | -2.2669
|  | BISHOPS WALTHAM | SP |  |  | 6.8168 | 6.4925 | 6.1387 | 5.8456 | 5.273 | 4.7127 | 4.1384 | 3.5193 | 2.8707 | 2.0923 | -0.68174 | -7.0801 | -10.3458 | -12.0039 | 13.6508 | 13.5262 | 13.3531 | 13.2407 | 13.095 | 12.9519 | 12.8052 | 12.6485 | 12.4695 | 12.2699 | 10.8861 | 6.5295 | 4.2412 | 2.6572 | 9.4246 | 9.2564 | 9.0504 | 8.9059 | 8.6178 | 8.3349 | 8.0483 | 7.75 | 7.4294 | 7.0435 | 5.7305 | 0.23616 | -2.7775 | -4.2679
NURSLING GSP | VELMORE BSP | BISHOPSTOKE | MINIMUM HEADROOM | SU 46463 18472 | YES | 6.4226 | 5.9298 | 5.5263 | 5.2681 | 5.0469 | 4.8455 | 4.6347 | 4.4096 | 4.1219 | 3.8389 | 2.9235 | 1.9023 | 1.7492 | 1.6471 | 6.7865 | 6.2245 | 5.7458 | 5.4776 | 5.2656 | 5.0871 | 4.9149 | 4.7338 | 4.506 | 4.3061 | 3.3708 | 2.2519 | 1.9839 | 1.8424 | 4.266 | 3.9447 | 3.7027 | 3.5722 | 3.4804 | 3.4143 | 3.3568 | 3.169 | 2.8212 | 2.4787 | 1.2354 | -0.16786 | -0.50078 | -0.67781
|  | BISHOPSTOKE | CT |  |  | 6.4226 | 5.9386 | 5.5402 | 5.2909 | 5.0839 | 4.8998 | 4.7205 | 4.5307 | 4.3004 | 4.0817 | 3.3891 | 2.3103 | 2.0086 | 1.8608 | 6.7865 | 6.2245 | 5.7458 | 5.4777 | 5.2701 | 5.0979 | 4.9408 | 4.7767 | 4.5805 | 4.4184 | 3.8285 | 2.6566 | 2.3726 | 2.2456 | 4.2661 | 3.9453 | 3.7037 | 3.5736 | 3.4826 | 3.4174 | 3.3615 | 3.2614 | 2.9773 | 2.7112 | 1.8082 | 0.33718 | -0.022646 | -0.18326
|  | BISHOPSTOKE | LW |  |  | 6.4239 | 5.9298 | 5.5263 | 5.2681 | 5.0469 | 4.8455 | 4.6347 | 4.4096 | 4.1219 | 3.8389 | 2.9235 | 1.9023 | 1.7492 | 1.6471 | 6.7925 | 6.2271 | 5.7479 | 5.4776 | 5.2656 | 5.0871 | 4.9149 | 4.7338 | 4.506 | 4.3061 | 3.3708 | 2.2519 | 2.1132 | 2.0257 | 4.266 | 3.9447 | 3.7027 | 3.5722 | 3.4804 | 3.4143 | 3.3568 | 3.169 | 2.8212 | 2.4787 | 1.2354 | -0.16786 | -0.34448 | -0.45615
|  | BISHOPSTOKE | ST |  |  | 6.4735 | 6.02 | 5.6617 | 5.4602 | 5.2975 | 5.1639 | 5.0336 | 4.8938 | 4.7191 | 4.553 | 3.9717 | 2.5382 | 1.8389 | 1.6768 | 6.8176 | 6.2742 | 5.8199 | 5.5815 | 5.3996 | 5.2577 | 5.1294 | 4.9948 | 4.8342 | 4.702 | 4.2845 | 2.7823 | 1.9839 | 1.8424 | 4.2687 | 3.9496 | 3.71 | 3.5825 | 3.4939 | 3.4314 | 3.3782 | 3.3245 | 3.2687 | 3.2382 | 2.5134 | 0.49993 | -0.50078 | -0.67781
|  | BISHOPSTOKE | SP |  |  | 6.4775 | 6.0293 | 5.6754 | 5.4786 | 5.3285 | 5.2104 | 5.102 | 4.987 | 4.8533 | 4.7445 | 4.4324 | 3.5104 | 2.5813 | 2.3334 | 6.8201 | 6.2805 | 5.8292 | 5.594 | 5.4205 | 5.2883 | 5.1745 | 5.0564 | 4.9238 | 4.8305 | 4.5974 | 3.9178 | 2.8643 | 2.5865 | 4.269 | 3.9502 | 3.7109 | 3.5837 | 3.4959 | 3.4342 | 3.3823 | 3.33 | 3.2765 | 3.2491 | 3.1215 | 1.9254 | 0.60912 | 0.26574
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE | MINIMUM HEADROOM | SU 45116 13082 | YES | 1.9478 | 1.7386 | 1.4548 | 1.1455 | 0.64248 | 0.1093 | -0.45305 | -1.0535 | -1.7616 | -2.5574 | -4.7658 | -8.5837 | -13.1726 | -16.5532 | 2.5713 | 2.4533 | 2.2801 | 2.0901 | 1.8224 | 1.514 | 1.1569 | 0.76749 | 0.30563 | -0.22502 | -1.5868 | -4.3467 | -7.4098 | -12.1424 | 0.6593 | 0.47737 | 0.22299 | -0.055571 | -0.50559 | -0.98389 | -1.4927 | -2.0616 | -2.7257 | -3.4668 | -5.5069 | -8.7247 | -12.5628 | -15.3447
|  | BITTERNE | CT |  |  | 2.0371 | 1.8826 | 1.6991 | 1.4256 | 1.0746 | 0.69933 | 0.29685 | -0.13871 | -0.63959 | -1.45 | -3.882 | -8.5837 | -13.1726 | -16.5532 | 2.59 | 2.4813 | 2.3525 | 2.1537 | 1.9282 | 1.657 | 1.3521 | 1.0213 | 0.64979 | 0.079183 | -1.5868 | -4.3467 | -7.4098 | -10.7492 | 0.73669 | 0.60323 | 0.44262 | 0.19357 | -0.12189 | -0.45989 | -0.8305 | -1.2517 | -1.7149 | -2.4657 | -4.7454 | -8.7247 | -12.5628 | -15.3447
|  | BITTERNE | LW |  |  | 1.9478 | 1.7386 | 1.4548 | 1.1455 | 0.64248 | 0.1093 | -0.45305 | -1.0535 | -1.7616 | -2.5574 | -4.7658 | -8.5164 | -11.826 | -14.4836 | 2.5713 | 2.4533 | 2.2801 | 2.0901 | 1.8224 | 1.514 | 1.1569 | 0.76749 | 0.30563 | -0.22502 | -1.573 | -3.4694 | -5.0796 | -6.4369 | 0.6593 | 0.47737 | 0.22299 | -0.055571 | -0.50559 | -0.98389 | -1.4927 | -2.0616 | -2.7257 | -3.4668 | -5.5069 | -8.6876 | -11.4038 | -13.5549
|  | BITTERNE | ST |  |  | 2.1498 | 2.0696 | 1.9766 | 1.876 | 1.723 | 1.552 | 1.3751 | 1.1807 | 0.96708 | 0.74499 | -0.32305 | -3.6846 | -6.3756 | -8.6838 | 2.6628 | 2.5986 | 2.5242 | 2.4424 | 2.3204 | 2.1837 | 2.0391 | 1.8785 | 1.6737 | 1.4526 | 0.45238 | -2.3719 | -4.822 | -7.7585 | 0.84391 | 0.78016 | 0.70454 | 0.62158 | 0.48792 | 0.33726 | 0.17973 | 0.0052157 | -0.18833 | -0.39982 | -1.3989 | -4.5405 | -6.7341 | -8.5698
|  | BITTERNE | SP |  |  | 2.1672 | 2.0812 | 1.9913 | 1.8929 | 1.7767 | 1.6574 | 1.5248 | 1.3814 | 1.2258 | 1.0498 | 0.29169 | -2.4293 | -4.9365 | -6.8226 | 2.6689 | 2.595 | 2.5158 | 2.4276 | 2.3301 | 2.2266 | 2.1086 | 1.9779 | 1.8333 | 1.6115 | 0.62736 | -2.4525 | -6.4523 | -12.1424 | 0.8597 | 0.78929 | 0.71571 | 0.63389 | 0.53606 | 0.43575 | 0.32118 | 0.19587 | 0.058598 | -0.098405 | -0.80979 | -3.3749 | -5.5337 | -7.0161
MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON | MINIMUM HEADROOM | SP 28349 03818 | NO | 6.7406 | 6.2662 | 5.7638 | 5.3489 | 4.7741 | 4.1811 | 3.5977 | 2.9818 | 2.2716 | 1.5338 | -0.10975 | -1.6833 | -2.369 | -3.4613 | 5.8065 | 5.5796 | 5.3347 | 5.1327 | 4.8706 | 4.5941 | 4.3068 | 3.9962 | 3.601 | 3.2033 | 2.4202 | 1.6592 | -0.016424 | -2.0075 | 4.9393 | 4.6213 | 4.2942 | 4.0139 | 3.6251 | 3.1829 | 2.6536 | 2.0954 | 1.4547 | 0.78528 | -0.73085 | -2.1849 | -2.8001 | -3.8041
|  | BLACK BOURTON | CT |  |  | 7.1356 | 6.8633 | 6.5704 | 6.3455 | 6.0145 | 5.6581 | 5.3048 | 4.9187 | 4.4956 | 3.8598 | 2.452 | 1.0941 | 0.80078 | 0.65514 | 5.924 | 5.7587 | 5.5806 | 5.4288 | 5.2428 | 5.0396 | 4.8293 | 4.5924 | 4.3154 | 3.9297 | 3.1331 | 2.2262 | 1.6717 | 0.91471 | 5.2165 | 5.04 | 4.8552 | 4.7133 | 4.4912 | 4.2566 | 4.025 | 3.7758 | 3.4505 | 2.8578 | 1.5931 | 0.36424 | 0.099325 | -0.030085
|  | BLACK BOURTON | LW |  |  | 6.7406 | 6.2662 | 5.7638 | 5.3489 | 4.7741 | 4.1811 | 3.5977 | 2.9818 | 2.2716 | 1.5338 | -0.10975 | -1.6833 | -1.8372 | -1.9977 | 5.8065 | 5.5796 | 5.3347 | 5.1327 | 4.8706 | 4.5941 | 4.3068 | 3.9962 | 3.601 | 3.2033 | 2.4202 | 1.6718 | 1.5892 | 1.5201 | 4.9393 | 4.6213 | 4.2942 | 4.0139 | 3.6251 | 3.1829 | 2.6536 | 2.0954 | 1.4547 | 0.78528 | -0.73085 | -2.1849 | -2.3233 | -2.4686
|  | BLACK BOURTON | ST |  |  | 7.2412 | 7.029 | 6.8125 | 6.6611 | 6.4428 | 6.2073 | 5.9661 | 5.7094 | 5.4358 | 5.1374 | 4.0165 | 2.1011 | 0.98975 | 0.3756 | 6.0151 | 5.896 | 5.7723 | 5.6812 | 5.5606 | 5.4272 | 5.2853 | 5.1297 | 4.9558 | 4.7781 | 4.0298 | 2.7194 | 1.8336 | 0.90335 | 5.2711 | 5.1292 | 4.9918 | 4.8891 | 4.7447 | 4.5899 | 4.4315 | 4.2632 | 4.0832 | 3.8731 | 3.04 | 1.278 | 0.2681 | -0.29488
|  | BLACK BOURTON | SP |  |  | 7.2929 | 7.1092 | 6.93 | 6.8111 | 6.4236 | 6.0236 | 5.6228 | 5.2059 | 4.7863 | 4.2865 | 2.7388 | -0.4908 | -2.369 | -3.4613 | 6.0329 | 5.9202 | 5.809 | 5.7295 | 5.5581 | 5.3762 | 5.1894 | 4.9871 | 4.7765 | 4.5227 | 3.6678 | 1.6592 | -0.016424 | -2.0075 | 5.3065 | 5.1865 | 5.0741 | 4.9927 | 4.7269 | 4.4537 | 4.18 | 3.8979 | 3.613 | 3.2699 | 1.8699 | -1.0645 | -2.8001 | -3.8041
MANNINGTON GSP | LYTCHETT | BLANDFORD | MINIMUM HEADROOM | ST 88810 05536 | YES | 25.0149 | 24.1636 | 23.2671 | 22.3092 | 20.9262 | 19.5424 | 18.1235 | 16.5881 | 14.8085 | 12.9531 | 8.4777 | 3.1809 | 0.79968 | -1.3008 | 29.2404 | 28.9112 | 28.6012 | 28.3342 | 28.0143 | 27.6248 | 26.9095 | 26.0734 | 24.9987 | 23.863 | 21.3675 | 18.6934 | 16.3625 | 14.2858 | 24.8567 | 24.1024 | 23.2869 | 22.421 | 21.179 | 19.915 | 18.6015 | 17.167 | 15.4805 | 13.727 | 9.6289 | 4.933 | 3.0842 | 1.4269
|  | BLANDFORD | CT |  |  | 25.4704 | 24.8978 | 24.2886 | 23.5329 | 22.5575 | 21.5838 | 20.6012 | 19.5154 | 18.2803 | 16.4793 | 12.2596 | 5.4671 | 0.79968 | -1.3008 | 29.2404 | 28.9112 | 28.6012 | 28.3342 | 28.0151 | 27.6391 | 27.302 | 26.8856 | 26.0983 | 25.0299 | 22.5181 | 18.8961 | 16.3625 | 14.2858 | 25.2362 | 24.6993 | 24.1416 | 23.4513 | 22.5531 | 21.6379 | 20.7101 | 19.6812 | 18.5228 | 16.8432 | 12.9275 | 6.9357 | 3.0842 | 1.4269
|  | BLANDFORD | LW |  |  | 25.0149 | 24.1636 | 23.2671 | 22.3092 | 20.9262 | 19.5424 | 18.1235 | 16.5881 | 14.8085 | 12.9531 | 8.4777 | 3.1809 | 1.583 | 0.58192 | 29.2539 | 28.9216 | 28.6055 | 28.3445 | 28.0143 | 27.6248 | 26.9095 | 26.0734 | 24.9987 | 23.863 | 21.3675 | 18.6934 | 18.0521 | 17.6789 | 24.8567 | 24.1024 | 23.2869 | 22.421 | 21.179 | 19.915 | 18.6015 | 17.167 | 15.4805 | 13.727 | 9.6289 | 4.933 | 3.5985 | 2.7782
|  | BLANDFORD | ST |  |  | 25.5647 | 25.27 | 24.8986 | 24.4752 | 23.8981 | 23.3209 | 22.7414 | 22.1018 | 21.4093 | 20.685 | 18.1235 | 13.4163 | 11.0471 | 9.5784 | 29.3151 | 29.0293 | 28.7733 | 28.5813 | 28.3224 | 28.0133 | 27.7435 | 27.4414 | 27.1588 | 26.8867 | 25.6492 | 22.2779 | 20.316 | 18.3919 | 25.4941 | 25.1166 | 24.7466 | 24.3717 | 23.8355 | 23.2846 | 22.7296 | 22.1169 | 21.4689 | 20.7972 | 18.3498 | 13.9249 | 11.7807 | 10.4877
|  | BLANDFORD | SP |  |  | 25.5702 | 25.2771 | 25.0177 | 24.6586 | 23.9964 | 23.313 | 22.672 | 21.9655 | 21.249 | 20.4395 | 17.9546 | 12.4347 | 9.3913 | 7.8956 | 29.3187 | 29.034 | 28.7792 | 28.5923 | 28.3502 | 28.0596 | 27.8163 | 27.5395 | 27.2996 | 27.0717 | 25.9421 | 21.7588 | 18.5403 | 15.0359 | 25.5503 | 25.19 | 24.8492 | 24.5228 | 23.9373 | 23.3173 | 22.7303 | 22.0717 | 21.4153 | 20.683 | 18.3564 | 13.1458 | 10.3263 | 8.9841
COWLEY GSP | WITNEY BSP | BLEDDINGTON | MINIMUM HEADROOM | SP 25641 22580 | NO | 9.5532 | 9.2421 | 8.9094 | 8.5719 | 8.1139 | 7.6459 | 7.1708 | 6.686 | 6.118 | 5.5469 | 4.2363 | 3.0378 | 2.869 | 2.2075 | 11.6935 | 11.5754 | 11.4357 | 11.2918 | 11.1062 | 10.9098 | 10.7018 | 10.4784 | 10.1774 | 9.8796 | 9.3772 | 8.8603 | 8.6745 | 8.2165 | 10.485 | 10.25 | 9.9706 | 9.6732 | 9.2741 | 8.8632 | 8.4421 | 8.0074 | 7.4795 | 6.9514 | 5.8301 | 4.8136 | 4.6723 | 4.1263
|  | BLEDDINGTON | CT |  |  | 9.8823 | 9.7486 | 9.5961 | 9.4201 | 9.1667 | 8.9014 | 8.6203 | 8.3263 | 7.9863 | 7.496 | 6.4334 | 5.0587 | 4.6987 | 4.6074 | 11.7754 | 11.7034 | 11.6156 | 11.5065 | 11.38 | 11.2428 | 11.096 | 10.9379 | 10.7356 | 10.4504 | 9.9474 | 9.4292 | 9.2412 | 9.0969 | 10.7178 | 10.6062 | 10.4751 | 10.3187 | 10.1113 | 9.8914 | 9.6388 | 9.3671 | 9.0488 | 8.5899 | 7.6214 | 6.4672 | 6.1681 | 6.093
|  | BLEDDINGTON | LW |  |  | 9.5532 | 9.2421 | 8.9094 | 8.5719 | 8.1139 | 7.6459 | 7.1708 | 6.686 | 6.118 | 5.5469 | 4.2363 | 3.0378 | 2.869 | 2.758 | 11.6935 | 11.5754 | 11.4357 | 11.2918 | 11.1062 | 10.9098 | 10.7018 | 10.4784 | 10.1774 | 9.8796 | 9.3772 | 8.8603 | 8.7882 | 8.743 | 10.485 | 10.25 | 9.9706 | 9.6732 | 9.2741 | 8.8632 | 8.4421 | 8.0074 | 7.4795 | 6.9514 | 5.8301 | 4.8136 | 4.6723 | 4.5817
|  | BLEDDINGTON | ST |  |  | 9.9541 | 9.8643 | 9.7664 | 9.6623 | 9.4898 | 9.3093 | 9.1266 | 8.9369 | 8.7278 | 8.5005 | 7.6348 | 6.2723 | 5.5421 | 5.0719 | 11.8277 | 11.7862 | 11.7376 | 11.6832 | 11.5996 | 11.511 | 11.4183 | 11.3188 | 11.2016 | 11.0892 | 10.5768 | 9.834 | 9.5196 | 9.2709 | 10.7841 | 10.7125 | 10.6327 | 10.5472 | 10.4074 | 10.2616 | 10.1129 | 9.9522 | 9.7582 | 9.5532 | 8.7334 | 7.4874 | 6.8804 | 6.4981
|  | BLEDDINGTON | SP |  |  | 9.9922 | 9.922 | 9.8461 | 9.7713 | 9.532 | 9.2736 | 9.0153 | 8.7468 | 8.4751 | 8.1256 | 6.9831 | 4.5311 | 3.0972 | 2.2075 | 11.8384 | 11.8002 | 11.7558 | 11.7119 | 11.6199 | 11.5194 | 11.42 | 11.3096 | 11.1942 | 11.0581 | 10.5594 | 9.3464 | 8.6745 | 8.2165 | 10.8127 | 10.7548 | 10.691 | 10.6286 | 10.4436 | 10.2495 | 10.0512 | 9.8192 | 9.5832 | 9.2836 | 8.2802 | 6.0688 | 4.8571 | 4.1263
BRAMLEY (FLEE) | ALTON | BORDON | MINIMUM HEADROOM | SU 82256 35269 | YES | 5.4593 | 4.1608 | 2.8279 | 1.5022 | -0.19264 | -2.0043 | -3.9639 | -6.182 | -8.8176 | -11.3805 | -17.373 | -23.8393 | -27.1832 | -29.4953 | 5.1115 | 4.1717 | 3.2604 | 2.3578 | 1.3468 | 0.27373 | -0.92556 | -2.3146 | -4.0441 | -5.6497 | -9.1627 | -12.8399 | -15.3962 | -17.5281 | 1.7692 | 0.50521 | -0.73943 | -1.9705 | -3.5281 | -5.1771 | -6.9709 | -9.0659 | -11.5821 | -13.9558 | -19.4266 | -25.3788 | -28.0259 | -30.0622
|  | BORDON | CT |  |  | 5.7026 | 4.6354 | 3.5407 | 2.3593 | 1.1283 | -0.21597 | -1.6513 | -3.3214 | -5.2631 | -7.8852 | -13.8462 | -21.9807 | -27.1832 | -29.4953 | 5.1662 | 4.2913 | 3.4592 | 2.5662 | 1.7141 | 0.80324 | -0.18169 | -1.3087 | -2.6258 | -4.3094 | -7.9149 | -12.5528 | -15.3962 | -17.5281 | 2.0435 | 0.97293 | -0.060073 | -1.1507 | -2.3361 | -3.6209 | -4.9926 | -6.5606 | -8.3699 | -10.8008 | -16.2354 | -23.6184 | -28.0259 | -30.0622
|  | BORDON | LW |  |  | 5.4593 | 4.1608 | 2.8279 | 1.5022 | -0.19264 | -2.0043 | -3.9639 | -6.182 | -8.8176 | -11.3805 | -17.373 | -23.8393 | -25.8019 | -26.7871 | 5.1115 | 4.1717 | 3.2604 | 2.3578 | 1.3468 | 0.27373 | -0.92556 | -2.3146 | -4.0441 | -5.6497 | -9.1627 | -12.8399 | -13.7312 | -14.1379 | 1.7692 | 0.50521 | -0.73943 | -1.9705 | -3.5281 | -5.1771 | -6.9709 | -9.0659 | -11.5821 | -13.9558 | -19.4266 | -25.3788 | -27.1251 | -27.9487
|  | BORDON | ST |  |  | 6.2418 | 5.5495 | 4.8726 | 4.2197 | 3.5488 | 2.8243 | 2.0307 | 1.1423 | 0.12051 | -0.9007 | -5.0016 | -11.1263 | -14.1972 | -15.948 | 5.5502 | 4.9301 | 4.376 | 3.8464 | 3.3287 | 2.79 | 2.197 | 1.5385 | 0.77296 | 0.040068 | -3.0265 | -7.6808 | -10.1024 | -12.0905 | 2.5291 | 1.8036 | 1.1589 | 0.55179 | -0.064499 | -0.70809 | -1.4108 | -2.2181 | -3.1747 | -4.1204 | -7.9914 | -13.8688 | -16.6799 | -18.2271
|  | BORDON | SP |  |  | 6.3115 | 5.6416 | 5.0246 | 4.4508 | 3.8534 | 3.221 | 2.5581 | 1.7874 | 0.94337 | 0.036882 | -2.9903 | -9.5907 | -13.0292 | -14.402 | 5.5861 | 4.9704 | 4.4466 | 3.9604 | 3.5144 | 3.0583 | 2.5725 | 2.0077 | 1.3825 | 0.72001 | -1.5882 | -6.9924 | -10.648 | -13.9993 | 2.5966 | 1.8966 | 1.3092 | 0.77648 | 0.21551 | -0.35468 | -0.94724 | -1.6258 | -2.3719 | -3.2063 | -6.033 | -12.4033 | -15.6649 | -16.9265
MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN | MINIMUM HEADROOM | SU 17186 41044 | YES | 13.404 | 13.29 | 13.1608 | 13.0188 | 12.8709 | 12.6753 | 12.3505 | 11.9689 | 11.4325 | 10.8862 | 9.7932 | 8.2161 | 7.5939 | 6.9985 | 15.3373 | 15.2355 | 15.1159 | 14.9847 | 14.8309 | 14.6712 | 14.4969 | 14.307 | 14.0719 | 13.8186 | 13.2177 | 12.4822 | 11.7736 | 11.1953 | 13.3513 | 13.209 | 13.0466 | 12.8685 | 12.6453 | 12.4167 | 12.1711 | 11.9059 | 11.5988 | 11.263 | 10.3796 | 9.2476 | 8.7039 | 8.2633
|  | BOSCOMBE DOWN | CT |  |  | 13.4241 | 13.3284 | 13.2214 | 13.0944 | 12.9828 | 12.8687 | 12.747 | 12.6126 | 12.3046 | 11.7582 | 10.5902 | 8.8461 | 7.5939 | 6.9985 | 15.3646 | 15.2806 | 15.1841 | 15.0645 | 14.9491 | 14.8302 | 14.7056 | 14.5683 | 14.4059 | 14.16 | 13.554 | 12.5158 | 11.7736 | 11.1953 | 13.4129 | 13.3091 | 13.1903 | 13.0467 | 12.8983 | 12.7483 | 12.5945 | 12.4264 | 12.2358 | 11.9273 | 11.1109 | 9.6417 | 8.7039 | 8.2633
|  | BOSCOMBE DOWN | LW |  |  | 13.404 | 13.29 | 13.1608 | 13.0188 | 12.8709 | 12.6753 | 12.3505 | 11.9689 | 11.4325 | 10.8862 | 9.7932 | 8.2161 | 7.7921 | 7.596 | 15.3373 | 15.2355 | 15.1159 | 14.9847 | 14.8309 | 14.6712 | 14.4969 | 14.307 | 14.0719 | 13.8186 | 13.2177 | 12.4822 | 12.2281 | 12.1144 | 13.3513 | 13.209 | 13.0466 | 12.8685 | 12.6453 | 12.4167 | 12.1711 | 11.9059 | 11.5988 | 11.263 | 10.3796 | 9.2476 | 8.8317 | 8.6498
|  | BOSCOMBE DOWN | ST |  |  | 13.4805 | 13.4211 | 13.3577 | 13.2894 | 13.2338 | 13.1795 | 13.1169 | 13.0446 | 12.9587 | 12.8558 | 12.3052 | 10.5777 | 9.6942 | 9.3592 | 15.4199 | 15.3724 | 15.319 | 15.2607 | 15.2036 | 15.1461 | 15.0811 | 15.0076 | 14.9204 | 14.8235 | 14.4079 | 13.4965 | 12.8822 | 12.3064 | 13.4819 | 13.4265 | 13.366 | 13.3003 | 13.2367 | 13.1735 | 13.1028 | 13.0228 | 12.9297 | 12.8158 | 12.3528 | 11.2694 | 10.5914 | 10.1464
|  | BOSCOMBE DOWN | SP |  |  | 13.4843 | 13.4271 | 13.3687 | 13.307 | 13.2614 | 13.218 | 13.1712 | 13.1162 | 13.058 | 12.985 | 12.7251 | 11.38 | 10.3473 | 9.9753 | 15.4238 | 15.3775 | 15.328 | 15.2753 | 15.2274 | 15.1781 | 15.1262 | 15.0654 | 14.9996 | 14.915 | 14.6005 | 13.6949 | 12.8962 | 12.0246 | 13.4909 | 13.4407 | 13.3886 | 13.3333 | 13.2772 | 13.2204 | 13.1628 | 13.0961 | 13.0257 | 12.9351 | 12.6177 | 11.7205 | 11.0921 | 10.8232
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST | MINIMUM HEADROOM | SZ 11636 92447 | YES | 16.4949 | 16.1812 | 15.7982 | 15.3782 | 14.6269 | 13.8288 | 12.9806 | 12.0742 | 11.0033 | 9.8643 | 6.5062 | 1.4754 | -3.0659 | -6.0931 | 21.129 | 20.9706 | 20.7887 | 20.5611 | 20.2505 | 19.9136 | 19.5555 | 19.161 | 18.6131 | 17.6928 | 14.8637 | 9.2968 | -0.16497 | -17.9788 | 16.9485 | 16.6739 | 16.3403 | 15.9741 | 15.305 | 14.5948 | 13.8406 | 13.0263 | 11.9878 | 10.8803 | 7.6761 | 3.1283 | -0.40704 | -2.9327
|  | BOSCOMBE EAST | CT |  |  | 16.6299 | 16.4019 | 16.1299 | 15.7516 | 15.2467 | 14.6977 | 14.1308 | 13.5073 | 12.7906 | 11.6652 | 8.3174 | 1.9352 | -3.0659 | -6.0931 | 21.13 | 20.9706 | 20.7887 | 20.5611 | 20.2505 | 19.9136 | 19.5555 | 19.161 | 18.6131 | 17.6928 | 14.8637 | 9.2968 | 2.8489 | -6.1905 | 17.0754 | 16.8844 | 16.6587 | 16.3541 | 15.9045 | 15.416 | 14.8696 | 14.2681 | 13.5763 | 12.4841 | 9.284 | 3.7028 | -0.40704 | -2.9327
|  | BOSCOMBE EAST | LW |  |  | 16.4949 | 16.1812 | 15.7982 | 15.3782 | 14.6269 | 13.8288 | 12.9806 | 12.0742 | 11.0033 | 9.8643 | 6.5062 | 1.4754 | -1.4087 | -3.4197 | 21.129 | 20.9904 | 20.8256 | 20.6421 | 20.3242 | 19.9852 | 19.6201 | 19.2293 | 18.7663 | 18.197 | 16.0951 | 13.2614 | 11.9156 | 10.9377 | 16.9485 | 16.6739 | 16.3403 | 15.9741 | 15.305 | 14.5948 | 13.8406 | 13.0263 | 11.9878 | 10.8803 | 7.6761 | 3.1283 | 0.75936 | -0.87137
|  | BOSCOMBE EAST | ST |  |  | 16.8384 | 16.74 | 16.6217 | 16.4825 | 16.2837 | 16.066 | 15.8231 | 15.5555 | 15.2293 | 14.8704 | 13.3182 | 9.0864 | 6.2441 | 4.2312 | 21.2233 | 21.1209 | 21.0075 | 20.8782 | 20.7045 | 20.5136 | 20.298 | 20.057 | 19.7741 | 19.4527 | 17.7779 | 12.56 | 6.6487 | -1.9341 | 17.2593 | 17.1806 | 17.0895 | 16.9826 | 16.8263 | 16.6548 | 16.4636 | 16.2526 | 15.9628 | 15.6205 | 14.1417 | 10.1851 | 7.6447 | 5.9105
|  | BOSCOMBE EAST | SP |  |  | 16.8713 | 16.7665 | 16.6479 | 16.5166 | 16.3584 | 16.1878 | 16.0031 | 15.7924 | 15.5521 | 15.2713 | 14.1715 | 10.7212 | 7.9038 | 6.365 | 21.2257 | 21.1155 | 20.988 | 20.845 | 20.648 | 20.4265 | 20.176 | 19.8935 | 19.5669 | 19.1615 | 17.0357 | 10.3758 | -0.16497 | -17.9788 | 17.2885 | 17.2092 | 17.1218 | 17.0245 | 16.8984 | 16.7636 | 16.6164 | 16.4505 | 16.2619 | 16.0112 | 14.9702 | 11.7502 | 9.1887 | 7.8709
MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY | MINIMUM HEADROOM | SZ 06207 92415 | YES | 4.8461 | 4.1817 | 3.3433 | 2.3692 | 0.80717 | -0.86808 | -2.6824 | -4.6281 | -6.8787 | -9.404 | -16.5426 | -25.9209 | -33.077 | -38.1898 | 13.7561 | 13.3717 | 12.8654 | 12.2503 | 11.3673 | 10.4039 | 9.332 | 8.1231 | 6.6662 | 5.0093 | 0.45538 | -6.9229 | -13.7164 | -25.4365 | 7.8017 | 7.2314 | 6.5256 | 5.6991 | 4.3044 | 2.8153 | 1.2171 | -0.52891 | -2.5607 | -4.8379 | -11.3013 | -19.7646 | -26.1703 | -30.5803
|  | BOURNE VALLEY | CT |  |  | 5.1242 | 4.6449 | 4.0664 | 3.2129 | 2.0894 | 0.87299 | -0.40798 | -1.7957 | -3.3464 | -5.7691 | -13.0335 | -24.5693 | -33.077 | -38.1898 | 13.8056 | 13.4458 | 13.0092 | 12.3603 | 11.5839 | 10.7331 | 9.7914 | 8.7406 | 7.5497 | 5.8607 | 0.75366 | -6.9229 | -13.7164 | -21.258 | 8.0863 | 7.696 | 7.2234 | 6.5297 | 5.5618 | 4.5159 | 3.3793 | 2.1292 | 0.74042 | -1.4493 | -8.0835 | -18.5028 | -26.1703 | -30.5803
|  | BOURNE VALLEY | LW |  |  | 4.8461 | 4.1817 | 3.3433 | 2.3692 | 0.80717 | -0.86808 | -2.6824 | -4.6281 | -6.8787 | -9.404 | -16.5426 | -25.9209 | -30.7223 | -34.0969 | 13.7561 | 13.3717 | 12.8654 | 12.2503 | 11.3673 | 10.4039 | 9.332 | 8.1231 | 6.6662 | 5.0093 | 0.45538 | -4.8999 | -7.2027 | -8.8552 | 7.8017 | 7.2314 | 6.5256 | 5.6991 | 4.3044 | 2.8153 | 1.2171 | -0.52891 | -2.5607 | -4.8379 | -11.3013 | -19.7646 | -23.8696 | -26.7146
|  | BOURNE VALLEY | ST |  |  | 5.5022 | 5.2564 | 4.9559 | 4.5717 | 4.0458 | 3.4598 | 2.8123 | 2.1012 | 1.3067 | 0.43837 | -3.1724 | -11.9367 | -17.1366 | -20.7661 | 14.045 | 13.8306 | 13.5686 | 13.2261 | 12.7766 | 12.2732 | 11.7083 | 11.0872 | 10.3966 | 9.6453 | 6.4604 | -1.1754 | -7.0417 | -13.9617 | 8.3994 | 8.2044 | 7.964 | 7.6447 | 7.2054 | 6.7142 | 6.171 | 5.5788 | 4.9276 | 4.1775 | 0.96827 | -7.0464 | -11.559 | -14.5699
|  | BOURNE VALLEY | SP |  |  | 5.5763 | 5.3199 | 5.0227 | 4.657 | 4.1634 | 3.6337 | 3.0628 | 2.4351 | 1.7688 | 1.0044 | -1.8522 | -9.3404 | -15.0059 | -17.9297 | 14.0757 | 13.8403 | 13.5589 | 13.2045 | 12.7702 | 12.2898 | 11.7565 | 11.1677 | 10.5307 | 9.7326 | 6.6884 | -1.5616 | -11.6274 | -25.4365 | 8.4632 | 8.267 | 8.0353 | 7.7377 | 7.3117 | 6.8543 | 6.3613 | 5.8247 | 5.2658 | 4.6144 | 2.1376 | -4.5569 | -9.6929 | -12.1478
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON | MINIMUM HEADROOM | ST 77363 30262 | YES | 1.4824 | 1.0727 | 0.57396 | 0.058962 | -0.68678 | -1.4688 | -2.2847 | -3.1559 | -4.2507 | -5.3704 | -8.0286 | -10.8462 | -11.6737 | -12.6198 | 2.4016 | 2.1973 | 1.9225 | 1.6335 | 1.2433 | 0.82598 | 0.37726 | -0.11503 | -0.76953 | -1.4398 | -2.8743 | -4.2438 | -4.9486 | -5.703 | -0.56598 | -0.94801 | -1.396 | -1.8573 | -2.5396 | -3.2516 | -3.988 | -4.768 | -5.7287 | -6.714 | -9.1809 | -11.8862 | -12.6881 | -13.5934
|  | BOURTON | CT |  |  | 1.8342 | 1.6233 | 1.3823 | 1.0262 | 0.55994 | 0.063136 | -0.48087 | -1.0707 | -1.7446 | -2.7911 | -5.3183 | -9.045 | -11.5579 | -12.6198 | 2.5141 | 2.3805 | 2.2231 | 1.9717 | 1.6894 | 1.3835 | 1.047 | 0.67442 | 0.23335 | -0.42421 | -1.9048 | -3.7466 | -4.9486 | -5.703 | -0.21096 | -0.39722 | -0.60721 | -0.90229 | -1.3134 | -1.7489 | -2.2255 | -2.7379 | -3.3165 | -4.222 | -6.5517 | -10.1126 | -12.585 | -13.5934
|  | BOURTON | LW |  |  | 1.4824 | 1.0727 | 0.57396 | 0.058962 | -0.68678 | -1.4688 | -2.2847 | -3.1559 | -4.2507 | -5.3704 | -8.0286 | -10.8462 | -11.6737 | -12.168 | 2.4016 | 2.1973 | 1.9225 | 1.6335 | 1.2433 | 0.82598 | 0.37726 | -0.11503 | -0.76953 | -1.4398 | -2.8743 | -4.2438 | -4.5836 | -4.7838 | -0.56598 | -0.94801 | -1.396 | -1.8573 | -2.5396 | -3.2516 | -3.988 | -4.768 | -5.7287 | -6.714 | -9.1809 | -11.8862 | -12.6881 | -13.1658
|  | BOURTON | ST |  |  | 1.9778 | 1.8534 | 1.7063 | 1.5515 | 1.289 | 1.0031 | 0.70401 | 0.37814 | 0.00084892 | -0.3947 | -2.0687 | -5.2039 | -6.7121 | -7.6017 | 2.6169 | 2.5443 | 2.4529 | 2.3545 | 2.1939 | 2.0146 | 1.8225 | 1.6091 | 1.3544 | 1.1019 | -0.048319 | -2.1793 | -3.1311 | -3.835 | -0.092044 | -0.20614 | -0.33729 | -0.47432 | -0.70587 | -0.9561 | -1.2164 | -1.498 | -1.8227 | -2.1743 | -3.6063 | -6.4513 | -7.873 | -8.7099
|  | BOURTON | SP |  |  | 2.0371 | 1.9214 | 1.7958 | 1.666 | 1.3527 | 1.0268 | 0.70099 | 0.34283 | -0.032845 | -0.49684 | -2.1253 | -6.0219 | -8.1866 | -9.2689 | 2.6395 | 2.5609 | 2.473 | 2.3804 | 2.2197 | 2.049 | 1.8759 | 1.6773 | 1.4618 | 1.2023 | 0.22336 | -2.3268 | -3.9076 | -5.1496 | -0.034003 | -0.13387 | -0.24152 | -0.3525 | -0.64449 | -0.94665 | -1.2486 | -1.576 | -1.9177 | -2.3454 | -3.8108 | -7.2339 | -9.2531 | -10.3008
MANNINGTON GSP | WAREHAM | BOVINGTON | MINIMUM HEADROOM | SY 83933 87831 | YES | 4.1491 | 4.0315 | 3.8048 | 3.4742 | 3.0127 | 2.4758 | 1.9111 | 1.3043 | 0.64634 | 0.0079527 | -1.5578 | -2.8282 | -3.3325 | -3.7597 | 3.5679 | 3.5006 | 3.3686 | 3.1589 | 2.882 | 2.5676 | 2.2265 | 1.8698 | 1.4833 | 1.1027 | 0.16005 | -0.59201 | -0.93675 | -1.2339 | 3.008 | 2.8844 | 2.6662 | 2.3455 | 1.8896 | 1.3694 | 0.81342 | 0.22303 | -0.41462 | -1.0379 | -2.6061 | -3.9372 | -4.4104 | -4.812
|  | BOVINGTON | CT |  |  | 4.2373 | 4.1678 | 4.0112 | 3.716 | 3.3319 | 2.8792 | 2.402 | 1.8925 | 1.3628 | 0.74487 | -0.8336 | -2.4122 | -3.3325 | -3.7597 | 3.6076 | 3.5617 | 3.4636 | 3.2672 | 3.0269 | 2.7532 | 2.4557 | 2.1483 | 1.8301 | 1.4629 | 0.51655 | -0.42756 | -0.93675 | -1.2339 | 3.106 | 3.0356 | 2.8895 | 2.6107 | 2.24 | 1.8111 | 1.3502 | 0.86388 | 0.35969 | -0.23891 | -1.7965 | -3.478 | -4.4104 | -4.812
|  | BOVINGTON | LW |  |  | 4.1491 | 4.0315 | 3.8048 | 3.4742 | 3.0127 | 2.4758 | 1.9111 | 1.3043 | 0.64634 | 0.0079527 | -1.5578 | -2.8282 | -3.2194 | -3.4211 | 3.5679 | 3.5006 | 3.3686 | 3.1589 | 2.882 | 2.5676 | 2.2265 | 1.8698 | 1.4833 | 1.1027 | 0.16005 | -0.59201 | -0.77653 | -0.86823 | 3.008 | 2.8844 | 2.6662 | 2.3455 | 1.8896 | 1.3694 | 0.81342 | 0.22303 | -0.41462 | -1.0379 | -2.6061 | -3.9372 | -4.3045 | -4.4924
|  | BOVINGTON | ST |  |  | 4.2891 | 4.2521 | 4.1573 | 3.9886 | 3.7461 | 3.4625 | 3.1579 | 2.8402 | 2.5219 | 2.2368 | 1.2884 | 0.031243 | -0.46873 | -0.78039 | 3.6411 | 3.6163 | 3.5553 | 3.4326 | 3.2697 | 3.0875 | 2.8836 | 2.6795 | 2.4752 | 2.2906 | 1.6729 | 0.82423 | 0.45373 | 0.17834 | 3.1574 | 3.1194 | 3.0356 | 2.8809 | 2.659 | 2.4088 | 2.1299 | 1.8461 | 1.5604 | 1.2963 | 0.39779 | -0.89426 | -1.425 | -1.7525
|  | BOVINGTON | SP |  |  | 4.3027 | 4.2667 | 4.1798 | 4.0274 | 3.8011 | 3.5441 | 3.2575 | 2.9559 | 2.6619 | 2.3823 | 1.5232 | 0.13741 | -0.55447 | -0.8509 | 3.6475 | 3.6224 | 3.5645 | 3.4498 | 3.299 | 3.1345 | 2.9432 | 2.7505 | 2.5627 | 2.3846 | 1.8329 | 0.92795 | 0.37874 | 0.016597 | 3.1718 | 3.1364 | 3.0615 | 2.9237 | 2.7117 | 2.4832 | 2.2191 | 1.9499 | 1.687 | 1.4282 | 0.62807 | -0.75621 | -1.484 | -1.793
AMERSHAM | LOUDWATER BSP | BOWERDEAN | MINIMUM HEADROOM | SU 87718 93880 | YES | 1.9459 | 0.83617 | -0.4122 | -1.5306 | -3.0744 | -4.6886 | -6.4509 | -8.3791 | -10.7393 | -12.9091 | -17.2975 | -22.8292 | -26.7646 | -29.3984 | 4.376 | 3.7356 | 3.0137 | 2.3165 | 1.4386 | 0.4998 | -0.56227 | -1.7649 | -3.3344 | -4.7351 | -7.2146 | -10.8194 | -14.2843 | -17.5118 | -0.38234 | -1.3034 | -2.3534 | -3.3367 | -4.7285 | -6.1779 | -7.7617 | -9.5729 | -11.8233 | -13.882 | -17.9417 | -22.9655 | -26.3555 | -28.6522
|  | BOWERDEAN | CT |  |  | 2.3228 | 1.4221 | 0.37343 | -0.57005 | -1.6363 | -2.7792 | -4.0099 | -5.3516 | -6.8616 | -9.195 | -13.9536 | -21.4415 | -26.7646 | -29.3984 | 4.4434 | 3.8624 | 3.1565 | 2.4624 | 1.7523 | 0.97966 | 0.12467 | -0.83571 | -1.9501 | -3.5333 | -6.5157 | -10.8194 | -14.2843 | -17.5118 | -0.029905 | -0.72236 | -1.603 | -2.4173 | -3.3789 | -4.4427 | -5.5962 | -6.869 | -8.3162 | -10.5324 | -14.9449 | -21.6599 | -26.3555 | -28.6522
|  | BOWERDEAN | LW |  |  | 1.9459 | 0.83617 | -0.4122 | -1.5306 | -3.0744 | -4.6886 | -6.4509 | -8.3791 | -10.7393 | -12.9091 | -17.2975 | -22.8292 | -24.9992 | -26.1418 | 4.376 | 3.7356 | 3.0137 | 2.3165 | 1.4386 | 0.4998 | -0.56227 | -1.7649 | -3.3344 | -4.7351 | -7.2146 | -10.0713 | -10.9896 | -11.4711 | -0.38234 | -1.3034 | -2.3534 | -3.3367 | -4.7285 | -6.1779 | -7.7617 | -9.5729 | -11.8233 | -13.882 | -17.9417 | -22.9655 | -24.8579 | -25.8383
|  | BOWERDEAN | ST |  |  | 2.8539 | 2.3767 | 1.828 | 1.3625 | 0.81702 | 0.208 | -0.4481 | -1.1348 | -1.8938 | -2.6594 | -6.2607 | -11.8604 | -14.6808 | -16.5911 | 4.827 | 4.5029 | 4.1197 | 3.776 | 3.3977 | 2.963 | 2.4624 | 1.9235 | 1.3117 | 0.72281 | -2.1982 | -6.7243 | -9.443 | -12.4551 | 0.42926 | 0.071095 | -0.34883 | -0.71577 | -1.1721 | -1.6967 | -2.2633 | -2.8619 | -3.5724 | -4.3004 | -7.7995 | -13.1081 | -15.6291 | -17.2826
|  | BOWERDEAN | SP |  |  | 2.9037 | 2.4589 | 1.9939 | 1.6239 | 1.0796 | 0.48985 | -0.11735 | -0.77931 | -1.4756 | -2.2664 | -5.2242 | -12.6285 | -15.6166 | -16.8467 | 4.8379 | 4.5178 | 4.1733 | 3.8766 | 3.5324 | 3.1529 | 2.7512 | 2.285 | 1.768 | 1.1661 | -1.2098 | -7.5343 | -11.7909 | -16.9363 | 0.47519 | 0.14745 | -0.19874 | -0.48322 | -0.94128 | -1.4568 | -1.9888 | -2.574 | -3.1931 | -3.9027 | -6.6553 | -13.7434 | -16.5293 | -17.6238
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL | MINIMUM HEADROOM | SU 86075 69397 | YES | 34.9496 | 33.4196 | 32.0803 | 30.5678 | 28.2298 | 26.0752 | 24.098 | 21.9275 | 19.23 | 16.4626 | 8.4042 | -0.23827 | -2.8064 | -5.1975 | 37.4182 | 36.3579 | 35.4222 | 34.515 | 33.3235 | 32.167 | 30.9579 | 29.6281 | 28.0038 | 26.3688 | 21.5771 | 14.9734 | 11.9825 | 7.7691 | 35.6568 | 34.292 | 33.0752 | 31.7065 | 29.6312 | 27.7092 | 25.8842 | 23.8655 | 21.3764 | 18.8151 | 11.4504 | 3.2552 | 1.4856 | -0.60666
|  | BRACKNELL | CT |  |  | 35.2475 | 33.9213 | 32.7698 | 31.4256 | 29.4655 | 27.7054 | 26.2313 | 24.5993 | 22.5504 | 19.9561 | 12.3395 | 2.1548 | -2.8064 | -5.1975 | 37.4661 | 36.4539 | 35.5491 | 34.6709 | 33.5772 | 32.5552 | 31.5171 | 30.3731 | 29.0106 | 27.428 | 22.7095 | 16.1127 | 11.9825 | 7.7691 | 35.8839 | 34.6942 | 33.6403 | 32.3989 | 30.6593 | 29.0865 | 27.7037 | 26.1547 | 24.2358 | 21.8258 | 14.8684 | 5.8572 | 1.4856 | -0.60666
|  | BRACKNELL | LW |  |  | 34.9496 | 33.4196 | 32.0803 | 30.5678 | 28.2298 | 26.0752 | 24.098 | 21.9275 | 19.23 | 16.4626 | 8.4042 | -0.23827 | -2.6536 | -3.8035 | 37.4182 | 36.3579 | 35.4222 | 34.515 | 33.3235 | 32.167 | 30.9579 | 29.6281 | 28.0038 | 26.3688 | 21.5771 | 14.9734 | 13.9543 | 13.373 | 35.6568 | 34.292 | 33.0752 | 31.7065 | 29.6312 | 27.7092 | 25.8842 | 23.8655 | 21.3764 | 18.8151 | 11.4504 | 3.2552 | 1.5118 | 0.51962
|  | BRACKNELL | ST |  |  | 35.8523 | 34.945 | 34.198 | 33.4061 | 32.2421 | 31.2406 | 30.3892 | 29.436 | 28.2232 | 26.9378 | 22.1497 | 10.5672 | 4.1791 | 2.9256 | 37.7373 | 36.9076 | 36.1932 | 35.5588 | 34.7765 | 34.0973 | 33.4389 | 32.7118 | 31.8675 | 31.0093 | 27.5115 | 18.1877 | 13.1747 | 12.0873 | 36.4879 | 35.6981 | 35.0276 | 34.3221 | 33.2866 | 32.3928 | 31.582 | 30.6587 | 29.5183 | 28.3366 | 23.8194 | 11.3993 | 5.2701 | 3.9497
|  | BRACKNELL | SP |  |  | 35.9208 | 35.0544 | 34.3614 | 33.6557 | 32.6949 | 31.8793 | 31.1915 | 30.4196 | 29.4809 | 28.4602 | 25.0315 | 17.8397 | 9.212 | 6.7378 | 37.7564 | 36.9463 | 36.251 | 35.6447 | 34.9317 | 34.3202 | 33.7312 | 33.0863 | 32.3771 | 31.6783 | 28.8081 | 22.5207 | 15.6564 | 7.7932 | 36.5499 | 35.7974 | 35.1768 | 34.5507 | 33.7187 | 33.0097 | 32.359 | 31.6101 | 30.73 | 29.7935 | 26.5944 | 18.8964 | 10.1188 | 7.7567
MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON | MINIMUM HEADROOM | ST 81260 60564 | NO | 16.4602 | 15.9883 | 15.4122 | 14.8002 | 13.8545 | 12.8749 | 11.8392 | 10.7368 | 9.4347 | 8.0338 | 4.8237 | 1.4069 | 0.40417 | -0.15366 | 21.3774 | 21.115 | 20.7965 | 20.4492 | 19.9635 | 19.4518 | 18.8905 | 18.2822 | 17.506 | 16.6692 | 14.9198 | 13.2442 | 12.0966 | 10.8187 | 17.7674 | 17.3356 | 16.8287 | 16.2857 | 15.4722 | 14.6249 | 13.7179 | 12.7463 | 11.5656 | 10.2939 | 7.3431 | 4.2464 | 3.3663 | 2.8832
|  | BRADFORD-ON-AVON | CT |  |  | 16.7946 | 16.5113 | 16.1895 | 15.7769 | 15.2204 | 14.6328 | 14.0035 | 13.3118 | 12.5217 | 11.1788 | 7.9313 | 3.7589 | 1.2182 | 0.052362 | 21.4845 | 21.2802 | 21.0461 | 20.7387 | 20.3814 | 19.9989 | 19.5918 | 19.1397 | 18.604 | 17.7651 | 15.8342 | 13.5984 | 12.0966 | 10.8187 | 18.0554 | 17.7868 | 17.48 | 17.0826 | 16.5616 | 16.01 | 15.4354 | 14.8039 | 14.071 | 12.847 | 9.9667 | 6.3457 | 4.1114 | 3.0949
|  | BRADFORD-ON-AVON | LW |  |  | 16.4602 | 15.9883 | 15.4122 | 14.8002 | 13.8545 | 12.8749 | 11.8392 | 10.7368 | 9.4347 | 8.0338 | 4.8237 | 1.4069 | 0.40417 | -0.15366 | 21.3774 | 21.115 | 20.7965 | 20.4492 | 19.9635 | 19.4518 | 18.8905 | 18.2822 | 17.506 | 16.6692 | 14.9198 | 13.2442 | 12.8255 | 12.5991 | 17.7674 | 17.3356 | 16.8287 | 16.2857 | 15.4722 | 14.6249 | 13.7179 | 12.7463 | 11.5656 | 10.2939 | 7.3431 | 4.2464 | 3.3663 | 2.8832
|  | BRADFORD-ON-AVON | ST |  |  | 17.0137 | 16.8634 | 16.692 | 16.508 | 16.2177 | 15.9157 | 15.584 | 15.2255 | 14.8213 | 14.3845 | 12.5238 | 8.7993 | 6.9087 | 5.6776 | 21.641 | 21.5313 | 21.4049 | 21.2658 | 21.0638 | 20.851 | 20.6111 | 20.348 | 20.0433 | 19.7437 | 18.3974 | 15.7374 | 14.3719 | 13.0723 | 18.2684 | 18.1291 | 17.9685 | 17.7952 | 17.5218 | 17.237 | 16.9224 | 16.5815 | 16.1947 | 15.7898 | 14.0287 | 10.5739 | 8.9828 | 7.9827
|  | BRADFORD-ON-AVON | SP |  |  | 17.063 | 16.9199 | 16.772 | 16.6109 | 16.2738 | 15.9177 | 15.5517 | 15.1313 | 14.6889 | 14.152 | 12.2963 | 7.8032 | 5.3828 | 4.1792 | 21.6579 | 21.5423 | 21.4191 | 21.2825 | 21.0825 | 20.8665 | 20.6431 | 20.388 | 20.1102 | 19.7868 | 18.5827 | 15.3893 | 13.329 | 11.4908 | 18.3117 | 18.1765 | 18.036 | 17.8825 | 17.5749 | 17.2491 | 16.9189 | 16.5535 | 16.1658 | 15.7007 | 14.0519 | 9.9432 | 7.7918 | 6.7244
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN | MINIMUM HEADROOM | SU 67431 58511 | YES | 9.8004 | 9.5909 | 9.3931 | 9.1789 | 8.8339 | 8.4774 | 8.0841 | 7.641 | 7.116 | 6.6113 | 5.531 | 4.1633 | 3.6682 | 3.1436 | 11.6514 | 11.5228 | 11.4042 | 11.2724 | 11.0837 | 10.8869 | 10.6592 | 10.3935 | 10.0505 | 9.7273 | 9.1151 | 8.3736 | 7.7754 | 7.2699 | 10.4732 | 10.2762 | 10.0909 | 9.8892 | 9.5706 | 9.2407 | 8.8738 | 8.458 | 7.9575 | 7.4783 | 6.4755 | 5.2183 | 4.7985 | 4.3499
|  | BRAMLEY GREEN | CT |  |  | 9.8849 | 9.7417 | 9.5742 | 9.4145 | 9.195 | 8.9654 | 8.7299 | 8.4517 | 8.128 | 7.6272 | 6.5566 | 4.8205 | 3.6682 | 3.1436 | 11.6581 | 11.5474 | 11.4157 | 11.2898 | 11.1501 | 11.0023 | 10.8393 | 10.6402 | 10.4005 | 10.0653 | 9.4118 | 8.4378 | 7.7754 | 7.2699 | 10.5433 | 10.4053 | 10.2428 | 10.0878 | 9.8825 | 9.6665 | 9.4427 | 9.1768 | 8.8655 | 8.3889 | 7.3919 | 5.8183 | 4.7985 | 4.3499
|  | BRAMLEY GREEN | LW |  |  | 9.8004 | 9.5909 | 9.3931 | 9.1789 | 8.8339 | 8.4774 | 8.0841 | 7.641 | 7.116 | 6.6113 | 5.531 | 4.1633 | 3.7032 | 3.496 | 11.6514 | 11.5228 | 11.4042 | 11.2724 | 11.0837 | 10.8869 | 10.6592 | 10.3935 | 10.0505 | 9.7273 | 9.1151 | 8.3736 | 8.1616 | 8.066 | 10.4732 | 10.2762 | 10.0909 | 9.8892 | 9.5706 | 9.2407 | 8.8738 | 8.458 | 7.9575 | 7.4783 | 6.4755 | 5.2183 | 4.8098 | 4.6289
|  | BRAMLEY GREEN | ST |  |  | 10.0194 | 9.9549 | 9.879 | 9.785 | 9.6819 | 9.5739 | 9.457 | 9.319 | 9.1588 | 8.99 | 8.1532 | 6.7951 | 6.1072 | 5.6696 | 11.7582 | 11.7052 | 11.6424 | 11.5639 | 11.4854 | 11.4022 | 11.31 | 11.199 | 11.0674 | 10.9427 | 10.2807 | 9.2583 | 8.7311 | 8.2512 | 10.6742 | 10.6128 | 10.5397 | 10.4488 | 10.3503 | 10.2471 | 10.1348 | 10.0017 | 9.8466 | 9.685 | 8.8669 | 7.5765 | 6.9511 | 6.5663
|  | BRAMLEY GREEN | SP |  |  | 10.0359 | 9.9838 | 9.9266 | 9.869 | 9.7603 | 9.66 | 9.554 | 9.426 | 9.286 | 9.1155 | 8.4767 | 6.799 | 5.96 | 5.5644 | 11.7641 | 11.7167 | 11.6632 | 11.6081 | 11.5333 | 11.4625 | 11.3865 | 11.2907 | 11.1827 | 11.0624 | 10.5899 | 9.2816 | 8.5677 | 8.0407 | 10.689 | 10.6391 | 10.5838 | 10.5282 | 10.4263 | 10.3323 | 10.233 | 10.1116 | 9.9782 | 9.817 | 9.207 | 7.5916 | 6.802 | 6.4428
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD | MINIMUM HEADROOM | SZ 64712 98665 | YES | 11.0664 | 10.5055 | 9.8415 | 9.1428 | 7.9305 | 6.639 | 5.2761 | 3.8171 | 2.2331 | 0.56477 | -4.8408 | -12.1869 | -16.6407 | -19.6757 | 18.9784 | 18.4365 | 17.8151 | 17.0691 | 16.1367 | 15.117 | 14.0037 | 12.7645 | 11.3359 | 9.6373 | 3.7895 | -14.0995 | -46.8255 | -105.8805 | 13.5856 | 13.103 | 12.5207 | 11.9018 | 10.866 | 9.7535 | 8.5662 | 7.2879 | 5.8612 | 4.3459 | -0.70498 | -7.4812 | -11.1908 | -13.795
|  | BRANDON ROAD | CT |  |  | 11.3345 | 10.9395 | 10.4674 | 9.8923 | 9.064 | 8.174 | 7.2964 | 6.3482 | 5.3248 | 3.6949 | -1.4697 | -10.5878 | -16.6407 | -19.6757 | 18.9784 | 18.4365 | 17.8151 | 17.0691 | 16.1367 | 15.117 | 14.0037 | 12.7645 | 11.3359 | 9.6373 | 3.7895 | -9.4518 | -27.9494 | -56.6527 | 13.786 | 13.4347 | 13.0105 | 12.479 | 11.75 | 10.9618 | 10.1717 | 9.3158 | 8.3707 | 6.9189 | 2.299 | -5.9004 | -11.1908 | -13.795
|  | BRANDON ROAD | LW |  |  | 11.0664 | 10.5055 | 9.8415 | 9.1428 | 7.9305 | 6.639 | 5.2761 | 3.8171 | 2.2331 | 0.56477 | -4.8408 | -12.1869 | -15.0697 | -16.631 | 19.1639 | 18.8592 | 18.4854 | 18.0782 | 17.477 | 16.8247 | 16.1034 | 15.3231 | 14.3991 | 13.4128 | 10.1372 | 5.9091 | 4.6035 | 3.8842 | 13.5856 | 13.103 | 12.5207 | 11.9018 | 10.866 | 9.7535 | 8.5662 | 7.2879 | 5.8612 | 4.3459 | -0.70498 | -7.4812 | -9.9739 | -11.287
|  | BRANDON ROAD | ST |  |  | 11.6914 | 11.5247 | 11.3244 | 11.1043 | 10.8248 | 10.5145 | 10.1768 | 9.796 | 9.3749 | 8.8812 | 6.9506 | 1.3276 | -2.4253 | -4.7392 | 19.1932 | 18.7853 | 18.3272 | 17.8109 | 17.1477 | 16.418 | 15.5919 | 14.6598 | 13.5983 | 12.5104 | 8.2874 | -4.0399 | -21.7975 | -50.133 | 14.1073 | 13.9589 | 13.778 | 13.5736 | 13.3128 | 13.0215 | 12.7019 | 12.3395 | 11.9273 | 11.458 | 9.5854 | 4.2302 | 0.97245 | -0.88762
|  | BRANDON ROAD | SP |  |  | 11.7584 | 11.5884 | 11.3937 | 11.1909 | 10.9808 | 10.7529 | 10.4989 | 10.221 | 9.9236 | 9.5495 | 8.1784 | 4.1245 | 0.53573 | -1.0677 | 19.1753 | 18.7135 | 18.1665 | 17.558 | 16.7077 | 15.7385 | 14.6261 | 13.3653 | 11.8702 | 10.2157 | 3.8475 | -14.0995 | -46.8255 | -105.8805 | 14.1671 | 14.0088 | 13.8274 | 13.6357 | 13.4365 | 13.2199 | 12.9765 | 12.7096 | 12.4172 | 12.06 | 10.7357 | 6.8051 | 3.3945 | 2.0167
BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD | MINIMUM HEADROOM | SU 88887 80726 | YES | 9.8425 | 9.604 | 9.2599 | 8.8699 | 8.1575 | 6.8169 | 5.4239 | 3.8725 | 2.0893 | 0.21064 | -4.919 | -9.7283 | -11.5707 | -13.1143 | 12.629 | 12.3315 | 11.9584 | 11.5299 | 10.968 | 10.3757 | 9.6795 | 8.9015 | 7.9772 | 7.013 | 4.3607 | 0.38214 | -3.0606 | -10.1181 | 9.1425 | 8.6045 | 7.8725 | 7.0197 | 5.891 | 4.7179 | 3.4819 | 2.0974 | 0.46268 | -1.2231 | -5.7396 | -10.0119 | -11.4104 | -12.6754
|  | BRAYWICK ROAD | CT |  |  | 9.8425 | 9.604 | 9.2599 | 8.8699 | 8.4669 | 7.9241 | 6.8736 | 5.6803 | 4.3036 | 2.4526 | -2.5897 | -8.3322 | -11.5707 | -13.1143 | 12.6834 | 12.4091 | 12.047 | 11.6295 | 11.1334 | 10.5279 | 9.9151 | 9.2222 | 8.4201 | 7.3936 | 4.4883 | 0.38214 | -3.0606 | -7.2325 | 9.3118 | 8.8835 | 8.2443 | 7.4902 | 6.5916 | 5.658 | 4.7299 | 3.6735 | 2.4468 | 0.79137 | -3.6397 | -8.7189 | -11.4104 | -12.6754
|  | BRAYWICK ROAD | LW |  |  | 9.8667 | 9.6213 | 9.2815 | 8.8907 | 8.1575 | 6.8169 | 5.4239 | 3.8725 | 2.0893 | 0.21064 | -4.919 | -9.7283 | -11.2405 | -11.9606 | 12.629 | 12.3315 | 11.9584 | 11.5299 | 10.968 | 10.3757 | 9.6795 | 8.9015 | 7.9772 | 7.013 | 4.3607 | 1.8592 | 1.157 | 0.80875 | 9.1425 | 8.6045 | 7.8725 | 7.0197 | 5.891 | 4.7179 | 3.4819 | 2.0974 | 0.46268 | -1.2231 | -5.7396 | -10.0119 | -11.2773 | -11.87
|  | BRAYWICK ROAD | ST |  |  | 9.9731 | 9.81 | 9.5601 | 9.2726 | 8.9522 | 8.6298 | 8.3008 | 7.9281 | 7.4788 | 6.9626 | 3.8696 | -0.59573 | -2.6625 | -3.8677 | 12.8405 | 12.6622 | 12.4417 | 12.1928 | 11.8984 | 11.5952 | 11.2252 | 10.7736 | 10.2471 | 9.6625 | 7.4601 | 3.7026 | 0.49737 | -3.5651 | 9.6602 | 9.4379 | 9.1074 | 8.7142 | 8.2303 | 7.734 | 7.2209 | 6.6373 | 5.958 | 5.1965 | 2.2548 | -1.8596 | -3.7182 | -4.7575
|  | BRAYWICK ROAD | SP |  |  | 9.9761 | 9.8212 | 9.5858 | 9.3176 | 9.0286 | 8.7412 | 8.4494 | 8.1182 | 7.7342 | 7.3017 | 5.4215 | 1.0628 | -1.3361 | -2.3663 | 12.8471 | 12.6754 | 12.4676 | 12.2382 | 11.9703 | 11.6881 | 11.3514 | 10.9208 | 10.4307 | 9.8504 | 7.7947 | 3.3314 | -2.1148 | -10.1181 | 9.6904 | 9.4839 | 9.2009 | 8.8759 | 8.4906 | 8.0858 | 7.6557 | 7.1625 | 6.6107 | 5.9652 | 3.7303 | -0.31534 | -2.5511 | -3.4667
EALING GSP | EALING (D) | BRENTFORD | MINIMUM HEADROOM | TQ 17659 78277 | YES | 17.4223 | 16.5986 | 15.6513 | 14.776 | 13.4918 | 12.1222 | 10.6621 | 9.1055 | 7.4489 | 5.744 | 0.095449 | -8.3542 | -13.0077 | -17.6027 | 15.0929 | 14.7252 | 14.3162 | 13.938 | 13.2541 | 12.477 | 11.6674 | 10.7789 | 9.7675 | 8.5315 | 4.2036 | -4.8656 | -20.0022 | -47.5147 | 9.851 | 9.1634 | 8.3624 | 7.6099 | 6.526 | 5.3649 | 4.1123 | 2.7711 | 1.3058 | -0.22003 | -5.2848 | -12.7904 | -16.4526 | -20.1868
|  | BRENTFORD | CT |  |  | 17.7845 | 17.1843 | 16.4772 | 15.7906 | 14.8748 | 13.887 | 12.9414 | 11.9208 | 10.7952 | 9.2241 | 4.036 | -5.8245 | -13.0077 | -17.6027 | 15.1405 | 14.8049 | 14.3926 | 13.9687 | 13.2541 | 12.477 | 11.6674 | 10.7789 | 9.7675 | 8.5315 | 4.2036 | -4.8656 | -15.2914 | -29.6687 | 10.129 | 9.6118 | 9.0063 | 8.3956 | 7.6056 | 6.7512 | 5.918 | 5.0161 | 4.0048 | 2.6179 | -1.971 | -10.4041 | -16.4416 | -20.1868
|  | BRENTFORD | LW |  |  | 17.4223 | 16.5986 | 15.6513 | 14.776 | 13.4918 | 12.1222 | 10.6621 | 9.1055 | 7.4489 | 5.744 | 0.095449 | -8.3542 | -12.7291 | -15.8655 | 15.0929 | 14.7252 | 14.3162 | 13.938 | 13.3869 | 12.7839 | 12.0073 | 11.1734 | 10.2275 | 9.2187 | 5.7523 | 0.85845 | -1.2798 | -2.8729 | 9.851 | 9.1634 | 8.3624 | 7.6099 | 6.526 | 5.3649 | 4.1123 | 2.7711 | 1.3058 | -0.22003 | -5.2848 | -12.7904 | -16.4526 | -19.0209
|  | BRENTFORD | ST |  |  | 18.23 | 17.9284 | 17.5843 | 17.3022 | 16.9302 | 16.5114 | 16.0622 | 15.57 | 15.0012 | 14.3795 | 11.9039 | 4.7056 | -0.51577 | -3.785 | 15.2708 | 15.0751 | 14.8591 | 14.6209 | 14.3219 | 13.9042 | 13.3598 | 12.7536 | 12.0456 | 11.2988 | 8.3798 | -0.15155 | -10.1937 | -24.0503 | 10.5412 | 10.2826 | 9.9846 | 9.7339 | 9.4086 | 9.04 | 8.6413 | 8.203 | 7.6865 | 7.1303 | 4.8559 | -1.6743 | -6.14 | -8.7696
|  | BRENTFORD | SP |  |  | 18.2998 | 18.0101 | 17.6932 | 17.4399 | 17.1534 | 16.8363 | 16.4888 | 16.1077 | 15.6921 | 15.1992 | 13.4177 | 7.931 | 2.5517 | -0.49334 | 15.275 | 15.0777 | 14.8545 | 14.6148 | 14.2978 | 13.7654 | 13.1631 | 12.4872 | 11.7088 | 10.7756 | 7.2192 | -3.1088 | -20.0022 | -47.5147 | 10.6026 | 10.3497 | 10.0728 | 9.8444 | 9.5878 | 9.3061 | 8.9983 | 8.6583 | 8.2808 | 7.8475 | 6.2554 | 1.3087 | -3.44 | -5.9478
LOVEDEAN GSP | HAVANT | BROCKHAMPTON | MINIMUM HEADROOM | SU 70868 05828 | YES | 15.6823 | 15.6327 | 15.5646 | 15.4837 | 15.308 | 15.0709 | 14.8556 | 14.6393 | 14.3535 | 14.0043 | 13.1312 | 11.1937 | 10.6785 | 10.3413 | 10.3782 | 10.3365 | 10.2851 | 10.2201 | 10.0479 | 9.8135 | 9.6159 | 9.4184 | 9.1611 | 8.8526 | 7.8827 | 6.3192 | 6.0038 | 4.0428 | 10.1955 | 10.1479 | 10.0822 | 10.0041 | 9.8313 | 9.5979 | 9.3875 | 9.1755 | 8.8961 | 8.5554 | 7.7081 | 6.8182 | 6.5524 | 6.269
|  | BROCKHAMPTON | CT |  |  | 15.6823 | 15.6354 | 15.5766 | 15.5019 | 15.3391 | 15.1214 | 14.9363 | 14.7568 | 14.5278 | 14.2309 | 13.5034 | 12.0911 | 10.9803 | 10.3413 | 10.3782 | 10.3365 | 10.2851 | 10.2201 | 10.0479 | 9.8165 | 9.6334 | 9.4542 | 9.2301 | 8.9494 | 8.2703 | 7.0328 | 6.0775 | 4.8934 | 10.1955 | 10.1503 | 10.0938 | 10.0215 | 9.8612 | 9.6463 | 9.4651 | 9.2885 | 9.0641 | 8.7737 | 8.0656 | 7.1263 | 6.7585 | 6.269
|  | BROCKHAMPTON | LW |  |  | 15.6871 | 15.6327 | 15.5646 | 15.4837 | 15.308 | 15.0709 | 14.8556 | 14.6393 | 14.3535 | 14.0043 | 13.1312 | 11.1937 | 10.6785 | 10.4033 | 10.3865 | 10.3437 | 10.2902 | 10.2264 | 10.0518 | 9.8135 | 9.6159 | 9.4184 | 9.1611 | 8.8526 | 7.8827 | 6.3192 | 6.0038 | 5.8218 | 10.2002 | 10.1479 | 10.0822 | 10.0041 | 9.8313 | 9.5979 | 9.3875 | 9.1755 | 8.8961 | 8.5554 | 7.7081 | 6.8182 | 6.5524 | 6.316
|  | BROCKHAMPTON | ST |  |  | 15.7289 | 15.7087 | 15.6832 | 15.6535 | 15.5318 | 15.3571 | 15.2184 | 15.0858 | 14.9034 | 14.6831 | 14.0723 | 12.8988 | 12.315 | 11.984 | 10.4154 | 10.395 | 10.3701 | 10.3412 | 10.2016 | 10.0043 | 9.8579 | 9.7159 | 9.5287 | 9.3094 | 8.7208 | 7.6245 | 6.8286 | 5.7938 | 10.2407 | 10.2215 | 10.1971 | 10.1686 | 10.048 | 9.8748 | 9.7385 | 9.6074 | 9.4284 | 9.2128 | 8.6176 | 7.4879 | 6.935 | 6.6618
|  | BROCKHAMPTON | SP |  |  | 15.7303 | 15.7123 | 15.6891 | 15.6628 | 15.5525 | 15.3918 | 15.2731 | 15.1625 | 15.0115 | 14.8314 | 14.4111 | 13.5343 | 12.8051 | 12.5219 | 10.4154 | 10.3958 | 10.3712 | 10.3432 | 10.2099 | 10.02 | 9.8853 | 9.7558 | 9.5874 | 9.3878 | 8.9022 | 7.8968 | 6.5022 | 4.0428 | 10.242 | 10.2249 | 10.2027 | 10.1775 | 10.068 | 9.9085 | 9.7917 | 9.682 | 9.5333 | 9.3565 | 8.9453 | 8.0997 | 7.4051 | 7.1402
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST | MINIMUM HEADROOM | SU 59381 02061 | YES | 7.5358 | 6.9489 | 6.2101 | 5.3615 | 4.1255 | 2.7845 | 1.3703 | -0.044189 | -1.5392 | -3.2285 | -8.2796 | -14.4292 | -18.5144 | -21.224 | 15.1083 | 14.7184 | 14.2242 | 13.6658 | 12.9329 | 12.1246 | 11.2587 | 10.3618 | 9.3371 | 8.1606 | 4.7795 | 0.048113 | -3.7476 | -11.0646 | 11.4818 | 10.9547 | 10.2819 | 9.5118 | 8.3985 | 7.1871 | 5.9016 | 4.5944 | 3.1718 | 1.5523 | -3.1871 | -8.6686 | -11.9444 | -14.2338
|  | BROCKHURST | CT |  |  | 7.7068 | 7.2329 | 6.6657 | 5.8938 | 4.9192 | 3.8545 | 2.753 | 1.6669 | 0.54758 | -1.0705 | -6.2456 | -13.7986 | -18.5144 | -21.224 | 15.1454 | 14.7773 | 14.3413 | 13.7733 | 13.1072 | 12.3721 | 11.5978 | 10.7737 | 9.8869 | 8.7157 | 4.974 | 0.048113 | -3.7476 | -8.0755 | 11.6299 | 11.2035 | 10.6897 | 9.9646 | 9.0718 | 8.0946 | 7.0751 | 6.0515 | 4.9718 | 3.4465 | -1.4004 | -7.9714 | -11.9444 | -14.2338
|  | BROCKHURST | LW |  |  | 7.5358 | 6.9489 | 6.2101 | 5.3615 | 4.1255 | 2.7845 | 1.3703 | -0.044189 | -1.5392 | -3.2285 | -8.2796 | -14.4292 | -17.0243 | -18.7395 | 15.1083 | 14.7184 | 14.2242 | 13.6658 | 12.9329 | 12.1246 | 11.2587 | 10.3618 | 9.3371 | 8.1606 | 4.7795 | 1.2459 | 0.048998 | -0.77569 | 11.4818 | 10.9547 | 10.2819 | 9.5118 | 8.3985 | 7.1871 | 5.9016 | 4.5944 | 3.1718 | 1.5523 | -3.1871 | -8.6686 | -10.8034 | -12.196
|  | BROCKHURST | ST |  |  | 7.9345 | 7.6177 | 7.2378 | 6.8095 | 6.2501 | 5.6265 | 4.965 | 4.306 | 3.6422 | 2.8902 | 0.092881 | -5.5104 | -8.4148 | -10.3901 | 15.2785 | 14.9994 | 14.6689 | 14.305 | 13.8481 | 13.336 | 12.7865 | 12.2179 | 11.6368 | 10.9804 | 8.591 | 3.6154 | 0.21807 | -3.7978 | 11.8452 | 11.5665 | 11.2284 | 10.8507 | 10.35 | 9.7901 | 9.1863 | 8.5656 | 7.9262 | 7.2193 | 4.5429 | -0.82936 | -3.3414 | -4.933
|  | BROCKHURST | SP |  |  | 7.9743 | 7.6533 | 7.2787 | 6.8631 | 6.3874 | 5.8576 | 5.2997 | 4.7384 | 4.1924 | 3.5534 | 1.3256 | -3.0402 | -5.9292 | -7.3477 | 15.2936 | 15.0041 | 14.6653 | 14.2965 | 13.8806 | 13.411 | 12.9078 | 12.3806 | 11.8528 | 11.1849 | 8.8374 | 3.763 | -2.3409 | -11.0646 | 11.8819 | 11.5973 | 11.2625 | 10.8952 | 10.475 | 10.0049 | 9.5053 | 8.989 | 8.4743 | 7.8781 | 5.7771 | 1.5035 | -1.2654 | -2.4766
MELKSHAM GSP | NORRINGTON | BROMHAM | MINIMUM HEADROOM | ST 98670 65994 | NO | 2.458 | 2.3562 | 2.2139 | 2.0604 | 1.8364 | 1.5936 | 1.3347 | 1.0419 | 0.68395 | 0.38107 | -0.22484 | -0.95712 | -1.1848 | -1.2946 | 3.2943 | 3.2202 | 3.1443 | 3.0576 | 2.9384 | 2.8134 | 2.6764 | 2.5167 | 2.3079 | 2.1355 | 1.8334 | 1.4726 | 1.3307 | 1.1045 | 2.4796 | 2.3458 | 2.2113 | 2.0682 | 1.8562 | 1.6366 | 1.4054 | 1.1481 | 0.84592 | 0.56364 | 0.012231 | -0.67775 | -0.89407 | -0.99216
|  | BROMHAM | CT |  |  | 2.5233 | 2.4873 | 2.4148 | 2.31 | 2.1731 | 2.0298 | 1.879 | 1.6901 | 1.4871 | 1.1803 | 0.62907 | -0.30784 | -0.93367 | -1.226 | 3.3344 | 3.2847 | 3.2231 | 3.1539 | 3.0711 | 2.984 | 2.8902 | 2.7707 | 2.641 | 2.4514 | 2.1466 | 1.665 | 1.3307 | 1.1045 | 2.5895 | 2.5195 | 2.4405 | 2.354 | 2.2298 | 2.1005 | 1.9656 | 1.7816 | 1.5841 | 1.2855 | 0.76853 | -0.072352 | -0.66062 | -0.9262
|  | BROMHAM | LW |  |  | 2.458 | 2.3562 | 2.2139 | 2.0604 | 1.8364 | 1.5936 | 1.3347 | 1.0419 | 0.68395 | 0.38107 | -0.22484 | -0.95712 | -1.1848 | -1.2946 | 3.2943 | 3.2202 | 3.1443 | 3.0576 | 2.9384 | 2.8134 | 2.6764 | 2.5167 | 2.3079 | 2.1355 | 1.8334 | 1.4726 | 1.3698 | 1.3226 | 2.4796 | 2.3458 | 2.2113 | 2.0682 | 1.8562 | 1.6366 | 1.4054 | 1.1481 | 0.84592 | 0.56364 | 0.012231 | -0.67775 | -0.89407 | -0.99216
|  | BROMHAM | ST |  |  | 2.5536 | 2.5368 | 2.5169 | 2.4957 | 2.4545 | 2.3809 | 2.3015 | 2.2088 | 2.1074 | 2.004 | 1.4853 | 0.82118 | 0.46911 | 0.22937 | 3.3757 | 3.3524 | 3.3236 | 3.2893 | 3.2438 | 3.1968 | 3.1451 | 3.0841 | 3.0155 | 2.9489 | 2.605 | 2.1569 | 1.9119 | 1.6973 | 2.6507 | 2.6181 | 2.579 | 2.5342 | 2.4701 | 2.4045 | 2.3349 | 2.2556 | 2.1709 | 2.08 | 1.5848 | 0.94002 | 0.61299 | 0.4018
|  | BROMHAM | SP |  |  | 2.5628 | 2.5514 | 2.5385 | 2.5264 | 2.4958 | 2.4621 | 2.4042 | 2.3285 | 2.2514 | 2.1467 | 1.7503 | 0.74612 | 0.28067 | 0.013407 | 3.3818 | 3.3623 | 3.3407 | 3.3187 | 3.2798 | 3.2413 | 3.2042 | 3.1543 | 3.1031 | 3.0376 | 2.7812 | 2.1078 | 1.7751 | 1.4925 | 2.6663 | 2.6427 | 2.6172 | 2.592 | 2.5342 | 2.4779 | 2.4241 | 2.358 | 2.2901 | 2.1942 | 1.8405 | 0.86357 | 0.43665 | 0.19777
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET | MINIMUM HEADROOM | SU 63480 52228 | YES | 17.742 | 17.4784 | 17.1907 | 16.8752 | 16.4174 | 15.9278 | 15.4085 | 14.6749 | 13.8136 | 12.9202 | 10.3826 | 6.8754 | 4.8036 | 2.8368 | 14.5792 | 14.4763 | 14.3607 | 14.2264 | 14.0753 | 13.9082 | 13.6685 | 13.3122 | 12.8676 | 12.2572 | 10.0822 | 7.5937 | 4.7351 | -2.4977 | 16.6721 | 16.4406 | 16.1891 | 15.9119 | 15.5077 | 15.0742 | 14.6119 | 13.9809 | 13.2092 | 12.4042 | 10.0666 | 6.8705 | 5.198 | 3.6485
|  | BROOK STREET | CT |  |  | 17.8833 | 17.7043 | 17.5025 | 17.2636 | 16.9281 | 16.5668 | 16.2186 | 15.6655 | 15.0065 | 14.1924 | 11.9444 | 7.9108 | 4.9492 | 2.8368 | 14.5792 | 14.4763 | 14.3607 | 14.2264 | 14.0753 | 13.9082 | 13.7248 | 13.4601 | 13.0668 | 12.6048 | 11.0201 | 8.2292 | 5.2484 | 1.2842 | 16.7947 | 16.6382 | 16.4615 | 16.2522 | 15.9564 | 15.6368 | 15.3154 | 14.823 | 14.232 | 13.5037 | 11.4477 | 7.8803 | 5.3965 | 3.6485
|  | BROOK STREET | LW |  |  | 17.742 | 17.4784 | 17.1907 | 16.8752 | 16.4174 | 15.9278 | 15.4085 | 14.6749 | 13.8136 | 12.9202 | 10.3826 | 6.8754 | 4.8036 | 3.1442 | 14.6062 | 14.5072 | 14.4039 | 14.2815 | 14.1385 | 13.9347 | 13.6685 | 13.3122 | 12.8676 | 12.2572 | 10.0822 | 7.5937 | 7.0458 | 6.592 | 16.6721 | 16.4406 | 16.1891 | 15.9119 | 15.5077 | 15.0742 | 14.6119 | 13.9809 | 13.2092 | 12.4042 | 10.0666 | 6.8705 | 5.198 | 3.8271
|  | BROOK STREET | ST |  |  | 18.0534 | 17.9793 | 17.899 | 17.8097 | 17.6727 | 17.5197 | 17.3528 | 17.0558 | 16.6753 | 16.2349 | 14.3228 | 8.6086 | 6.1304 | 5.4248 | 14.6554 | 14.5996 | 14.54 | 14.473 | 14.3802 | 14.2732 | 14.1496 | 13.9693 | 13.7179 | 13.4297 | 12.1538 | 7.7103 | 5.7638 | 2.8806 | 16.931 | 16.8719 | 16.8084 | 16.7374 | 16.6314 | 16.4993 | 16.3531 | 16.0957 | 15.7505 | 15.2508 | 13.2229 | 7.7579 | 5.4238 | 4.7965
|  | BROOK STREET | SP |  |  | 18.0775 | 18.0138 | 17.9476 | 17.8743 | 17.7812 | 17.6781 | 17.5667 | 17.3504 | 17.0846 | 16.7551 | 15.8459 | 11.754 | 8.3585 | 7.1988 | 14.6578 | 14.6068 | 14.5521 | 14.4904 | 14.4075 | 14.3122 | 14.2006 | 14.0381 | 13.8285 | 13.5928 | 12.7095 | 9.5935 | 4.7351 | -2.4977 | 16.9367 | 16.8854 | 16.8317 | 16.7717 | 16.6922 | 16.6026 | 16.5041 | 16.3363 | 16.1161 | 15.8223 | 14.6889 | 10.7884 | 7.5699 | 6.5055
MELKSHAM GSP | FROME BSP | BRUTON | MINIMUM HEADROOM | ST 69094 35148 | YES | 2.1885 | 1.9509 | 1.7044 | 1.5215 | 1.2823 | 1.0382 | 0.74942 | 0.4246 | 0.041881 | -0.31351 | -1.1829 | -2.5148 | -3.2916 | -3.7575 | -0.37414 | -0.5028 | -0.6369 | -0.74114 | -0.87812 | -1.0167 | -1.1692 | -1.3458 | -1.5607 | -1.7566 | -2.2043 | -2.8201 | -3.3037 | -3.6638 | -1.5143 | -1.7452 | -1.9847 | -2.1626 | -2.3949 | -2.631 | -2.8977 | -3.1997 | -3.5583 | -3.8891 | -4.6836 | -5.8367 | -6.526 | -6.9044
|  | BRUTON | CT |  |  | 2.4268 | 2.3128 | 2.1958 | 2.0702 | 1.9179 | 1.7624 | 1.5874 | 1.3827 | 1.1695 | 0.84813 | 0.15943 | -1.0987 | -2.0036 | -2.3828 | -0.25747 | -0.32773 | -0.40072 | -0.48377 | -0.57929 | -0.67775 | -0.78955 | -0.92108 | -1.0599 | -1.2738 | -1.7095 | -2.3425 | -2.809 | -3.101 | -1.2828 | -1.3937 | -1.5075 | -1.6296 | -1.7776 | -1.9289 | -2.0991 | -2.2981 | -2.5052 | -2.8175 | -3.489 | -4.6268 | -5.4264 | -5.7611
|  | BRUTON | LW |  |  | 2.1885 | 1.9509 | 1.7044 | 1.5215 | 1.2823 | 1.0382 | 0.74942 | 0.4246 | 0.041881 | -0.31351 | -1.1829 | -2.1699 | -2.4752 | -2.6987 | -0.37414 | -0.5028 | -0.6369 | -0.74114 | -0.87812 | -1.0167 | -1.1692 | -1.3458 | -1.5607 | -1.7566 | -2.2043 | -2.6905 | -2.8337 | -2.9343 | -1.5143 | -1.7452 | -1.9847 | -2.1626 | -2.3949 | -2.631 | -2.8977 | -3.1997 | -3.5583 | -3.8891 | -4.6836 | -5.5748 | -5.8464 | -6.0434
|  | BRUTON | ST |  |  | 2.4784 | 2.3981 | 2.3099 | 2.2149 | 2.0745 | 1.9276 | 1.7773 | 1.6159 | 1.454 | 1.3248 | 0.76114 | -0.13065 | -0.62827 | -0.96136 | -0.22245 | -0.26956 | -0.32216 | -0.38023 | -0.46218 | -0.54885 | -0.63907 | -0.73724 | -0.83992 | -0.92381 | -1.2979 | -1.91 | -2.2227 | -2.4983 | -1.2326 | -1.3106 | -1.3962 | -1.4885 | -1.6249 | -1.7676 | -1.9138 | -2.0706 | -2.228 | -2.3539 | -2.9022 | -3.759 | -4.2067 | -4.5015
|  | BRUTON | SP |  |  | 2.5095 | 2.4452 | 2.3777 | 2.3072 | 2.0791 | 1.8566 | 1.6335 | 1.3992 | 1.135 | 0.78689 | -0.32764 | -2.5148 | -3.2916 | -3.7575 | -0.20702 | -0.24721 | -0.29008 | -0.33592 | -0.46003 | -0.58115 | -0.70405 | -0.83515 | -0.97052 | -1.1334 | -1.6725 | -2.8201 | -3.3037 | -3.6638 | -1.2023 | -1.2648 | -1.3303 | -1.3988 | -1.6204 | -1.8365 | -2.0533 | -2.281 | -2.5274 | -2.8387 | -3.8433 | -5.8367 | -6.526 | -6.9044
COWLEY GSP | WITNEY BSP | BURFORD | MINIMUM HEADROOM | SP 25671 12529 | NO | 2.0987 | 1.8544 | 1.5979 | 1.4045 | 1.149 | 0.89355 | 0.63903 | 0.38088 | 0.08054 | -0.22 | -0.86898 | -1.2788 | -2.3778 | -3.0443 | 3.2243 | 3.1137 | 3.0029 | 2.9179 | 2.804 | 2.6896 | 2.5768 | 2.4614 | 2.3351 | 2.2007 | 1.8653 | 1.6954 | 1.2851 | 1.038 | 2.9942 | 2.8787 | 2.7241 | 2.5203 | 2.2472 | 1.9777 | 1.7144 | 1.4483 | 1.1499 | 0.84681 | 0.15966 | -0.2024 | -1.1582 | -1.7364
|  | BURFORD | CT |  |  | 2.2699 | 2.1695 | 2.029 | 1.9332 | 1.7878 | 1.6374 | 1.4809 | 1.3155 | 1.1409 | 0.89824 | 0.4041 | 0.23726 | 0.16204 | 0.1165 | 3.3098 | 3.248 | 3.1853 | 3.1452 | 3.0824 | 3.0173 | 2.9495 | 2.879 | 2.8084 | 2.7089 | 2.4707 | 2.2946 | 2.2539 | 2.2337 | 3.0673 | 3.0028 | 2.9289 | 2.8779 | 2.8042 | 2.727 | 2.6461 | 2.505 | 2.3395 | 2.1076 | 1.6145 | 1.4403 | 1.3605 | 1.3118
|  | BURFORD | LW |  |  | 2.0987 | 1.8544 | 1.5979 | 1.4045 | 1.149 | 0.89355 | 0.63903 | 0.38088 | 0.08054 | -0.22 | -0.86898 | -1.1175 | -1.1523 | -1.2206 | 3.2243 | 3.1137 | 3.0029 | 2.9179 | 2.804 | 2.6896 | 2.5768 | 2.4614 | 2.3351 | 2.2007 | 1.8653 | 1.6954 | 1.683 | 1.6604 | 2.9942 | 2.8787 | 2.7241 | 2.5203 | 2.2472 | 1.9777 | 1.7144 | 1.4483 | 1.1499 | 0.84681 | 0.15966 | -0.0547 | -0.081522 | -0.13846
|  | BURFORD | ST |  |  | 2.2951 | 2.2296 | 2.1483 | 2.0871 | 1.9812 | 1.8711 | 1.7552 | 1.6362 | 1.5138 | 1.3815 | 0.91852 | 0.18297 | -0.20564 | -0.36932 | 3.3281 | 3.2815 | 3.2367 | 3.21 | 3.1667 | 3.1203 | 3.0717 | 3.0203 | 2.9665 | 2.9014 | 2.6811 | 2.2428 | 2.0061 | 1.9379 | 3.0879 | 3.0496 | 2.9997 | 2.9696 | 2.9209 | 2.8683 | 2.8123 | 2.753 | 2.6661 | 2.5269 | 2.0681 | 1.3118 | 0.85859 | 0.6736
|  | BURFORD | SP |  |  | 2.2993 | 2.2563 | 2.2087 | 2.1622 | 1.9928 | 1.815 | 1.638 | 1.4555 | 1.2736 | 1.0455 | 0.32373 | -1.2788 | -2.3778 | -3.0443 | 3.3393 | 3.3 | 3.2625 | 3.2428 | 3.1727 | 3.0948 | 3.0142 | 2.931 | 2.8492 | 2.7435 | 2.4188 | 1.7483 | 1.2851 | 1.038 | 3.0883 | 3.0535 | 3.0216 | 3.0027 | 2.9289 | 2.8505 | 2.7632 | 2.5644 | 2.3678 | 2.1168 | 1.3397 | -0.2024 | -1.1582 | -1.7364
MANNINGTON GSP | WAREHAM | BUSHEY | MINIMUM HEADROOM | SY 97671 83532 | YES | 3.2742 | 3.2303 | 3.1746 | 3.1176 | 3.0383 | 2.9556 | 2.8672 | 2.7663 | 2.6418 | 2.5255 | 2.2667 | 1.9367 | 1.8473 | 1.7873 | 3.4666 | 3.4464 | 3.4141 | 3.3809 | 3.3358 | 3.2882 | 3.2367 | 3.1769 | 3.1033 | 3.0338 | 2.8875 | 2.7272 | 2.6879 | 2.6375 | 3.3382 | 3.3041 | 3.2659 | 3.2266 | 3.1699 | 3.1034 | 3.0127 | 2.91 | 2.7835 | 2.6652 | 2.3973 | 2.099 | 2.0198 | 1.9671
|  | BUSHEY | CT |  |  | 3.313 | 3.2889 | 3.2618 | 3.2208 | 3.1689 | 3.1145 | 3.0521 | 2.977 | 2.8995 | 2.7866 | 2.5592 | 2.2056 | 1.9298 | 1.809 | 3.4777 | 3.466 | 3.4526 | 3.4302 | 3.3984 | 3.365 | 3.327 | 3.2805 | 3.2324 | 3.1635 | 3.0289 | 2.831 | 2.705 | 2.6375 | 3.375 | 3.36 | 3.3427 | 3.3216 | 3.2882 | 3.2536 | 3.2124 | 3.137 | 3.0595 | 2.9463 | 2.7098 | 2.3389 | 2.0956 | 1.9895
|  | BUSHEY | LW |  |  | 3.2742 | 3.2303 | 3.1746 | 3.1176 | 3.0383 | 2.9556 | 2.8672 | 2.7663 | 2.6418 | 2.5255 | 2.2667 | 1.9367 | 1.8473 | 1.7873 | 3.4666 | 3.4464 | 3.4141 | 3.3809 | 3.3358 | 3.2882 | 3.2367 | 3.1769 | 3.1033 | 3.0338 | 2.8875 | 2.7272 | 2.6879 | 2.6624 | 3.3382 | 3.3041 | 3.2659 | 3.2266 | 3.1699 | 3.1034 | 3.0127 | 2.91 | 2.7835 | 2.6652 | 2.3973 | 2.099 | 2.0198 | 1.9671
|  | BUSHEY | ST |  |  | 3.3337 | 3.3197 | 3.3068 | 3.2907 | 3.2642 | 3.2334 | 3.2019 | 3.1676 | 3.1267 | 3.0863 | 2.9 | 2.6261 | 2.4845 | 2.3994 | 3.4881 | 3.4815 | 3.4755 | 3.4672 | 3.4544 | 3.4387 | 3.4188 | 3.3967 | 3.3706 | 3.3454 | 3.2265 | 3.0488 | 2.959 | 2.8991 | 3.3858 | 3.3783 | 3.3699 | 3.3606 | 3.344 | 3.3255 | 3.3069 | 3.2861 | 3.2631 | 3.2347 | 3.062 | 2.785 | 2.6373 | 2.5482
|  | BUSHEY | SP |  |  | 3.3415 | 3.3282 | 3.3154 | 3.3029 | 3.2748 | 3.2458 | 3.2183 | 3.1842 | 3.1506 | 3.1056 | 2.9464 | 2.5654 | 2.3574 | 2.2408 | 3.4909 | 3.4837 | 3.4768 | 3.4699 | 3.4578 | 3.4453 | 3.4296 | 3.4086 | 3.3876 | 3.3614 | 3.2644 | 3.0245 | 2.8915 | 2.8097 | 3.3902 | 3.3842 | 3.3782 | 3.3729 | 3.3538 | 3.3323 | 3.3123 | 3.2907 | 3.2679 | 3.234 | 3.1006 | 2.7157 | 2.496 | 2.3702
FAWLEY GSP | LANGLEY BSP | BUTTS ASH | MINIMUM HEADROOM | SU 41923 05772 | NO | 12.7016 | 12.3241 | 11.8077 | 11.2753 | 10.3477 | 9.3663 | 8.3077 | 7.1654 | 5.6927 | 4.095 | 0.3806 | -3.926 | -7.0959 | -8.7722 | 17.7872 | 17.5511 | 17.186 | 16.8065 | 16.264 | 15.6763 | 15.0136 | 14.2962 | 13.3465 | 12.3005 | 9.9686 | 7.5539 | 5.5589 | 3.978 | 13.96 | 13.6087 | 13.1207 | 12.6161 | 11.7602 | 10.8517 | 9.8493 | 8.7398 | 7.3412 | 5.8216 | 2.3478 | -1.5984 | -4.3201 | -5.7812
|  | BUTTS ASH | CT |  |  | 12.9117 | 12.672 | 12.3552 | 11.9127 | 11.3117 | 10.6703 | 9.9799 | 9.1789 | 8.2088 | 6.6219 | 2.6128 | -3.2458 | -7.0959 | -8.7722 | 17.8364 | 17.6436 | 17.3799 | 16.995 | 16.5678 | 16.1046 | 15.5983 | 15.0427 | 14.3492 | 13.314 | 10.6849 | 7.5539 | 5.5589 | 3.978 | 14.1417 | 13.9131 | 13.6096 | 13.1799 | 12.6139 | 12.0082 | 11.3077 | 10.5434 | 9.6113 | 8.1087 | 4.3595 | -0.93124 | -4.3201 | -5.7812
|  | BUTTS ASH | LW |  |  | 12.7016 | 12.3241 | 11.8077 | 11.2753 | 10.3477 | 9.3663 | 8.3077 | 7.1654 | 5.6927 | 4.095 | 0.3806 | -3.926 | -5.4681 | -5.9925 | 17.7872 | 17.5511 | 17.186 | 16.8065 | 16.264 | 15.6763 | 15.0136 | 14.2962 | 13.3465 | 12.3005 | 9.9686 | 7.6219 | 7.0144 | 6.8044 | 13.96 | 13.6087 | 13.1207 | 12.6161 | 11.7602 | 10.8517 | 9.8493 | 8.7398 | 7.3412 | 5.8216 | 2.3478 | -1.5984 | -2.9511 | -3.4022
|  | BUTTS ASH | ST |  |  | 13.1404 | 13.0414 | 12.8891 | 12.7356 | 12.4922 | 12.2262 | 11.9359 | 11.6121 | 11.229 | 10.7959 | 8.6859 | 4.1317 | 1.8826 | 0.45957 | 18.004 | 17.9146 | 17.7743 | 17.6308 | 17.4207 | 17.1892 | 16.9321 | 16.6426 | 16.2945 | 15.9355 | 14.2612 | 10.6644 | 8.9948 | 7.5733 | 14.36 | 14.2657 | 14.1197 | 13.9717 | 13.7376 | 13.4812 | 13.2005 | 12.8867 | 12.5138 | 12.0665 | 10.0052 | 5.6572 | 3.6245 | 2.3853
|  | BUTTS ASH | SP |  |  | 13.1846 | 13.0809 | 12.9342 | 12.7961 | 12.6061 | 12.3968 | 12.2082 | 11.9573 | 11.6769 | 11.3332 | 9.958 | 5.8362 | 3.6663 | 2.9483 | 18.025 | 17.9195 | 17.7707 | 17.6272 | 17.4683 | 17.2927 | 17.1175 | 16.8973 | 16.6458 | 16.3365 | 15.1001 | 11.3506 | 8.5483 | 5.816 | 14.4003 | 14.2995 | 14.1572 | 14.0225 | 13.8417 | 13.6424 | 13.4602 | 13.2193 | 12.9492 | 12.6212 | 11.2512 | 7.2469 | 5.1809 | 4.5314
MELKSHAM GSP | CHIPPENHAM | CALNE | MINIMUM HEADROOM | SU 00521 72497 | YES | 11.8419 | 11.3468 | 10.8137 | 10.2413 | 9.3673 | 8.4369 | 7.4214 | 6.3104 | 4.9113 | 3.4779 | 0.054647 | -3.6851 | -5.0466 | -6.4873 | 10.291 | 10.052 | 9.8047 | 9.5387 | 9.1175 | 8.6678 | 8.1806 | 7.653 | 7.0028 | 6.3227 | 4.1249 | 1.7052 | -0.51666 | -2.4835 | 7.916 | 7.4789 | 7.0311 | 6.5601 | 5.7489 | 4.8956 | 3.8791 | 2.7208 | 1.2726 | -0.21334 | -3.8615 | -7.8952 | -9.437 | -10.7142
|  | CALNE | CT |  |  | 12.0625 | 11.712 | 11.358 | 10.8934 | 10.291 | 9.6469 | 8.9588 | 8.184 | 7.2804 | 5.8745 | 2.4475 | -2.2584 | -5.0466 | -6.4873 | 10.3975 | 10.2212 | 10.0434 | 9.8241 | 9.5263 | 9.2058 | 8.8654 | 8.4879 | 8.0455 | 7.3775 | 5.0311 | 1.7188 | -0.51666 | -2.4835 | 8.2127 | 7.9466 | 7.6832 | 7.3487 | 6.7427 | 6.0948 | 5.4011 | 4.6195 | 3.7034 | 2.2891 | -1.2477 | -6.3824 | -9.437 | -10.7142
|  | CALNE | LW |  |  | 11.8419 | 11.3468 | 10.8137 | 10.2413 | 9.3673 | 8.4369 | 7.4214 | 6.3104 | 4.9113 | 3.4779 | 0.054647 | -3.6851 | -4.7432 | -5.1388 | 10.291 | 10.052 | 9.8047 | 9.5387 | 9.1175 | 8.6678 | 8.1806 | 7.653 | 7.0028 | 6.3227 | 4.1249 | 1.7052 | 1.149 | 0.93996 | 7.916 | 7.4789 | 7.0311 | 6.5601 | 5.7489 | 4.8956 | 3.8791 | 2.7208 | 1.2726 | -0.21334 | -3.8615 | -7.8952 | -9.0371 | -9.464
|  | CALNE | ST |  |  | 12.3761 | 12.2063 | 12.0438 | 11.8556 | 11.5822 | 11.2754 | 10.9361 | 10.5512 | 10.103 | 9.6299 | 7.4451 | 3.1081 | 1.2078 | 0.16522 | 10.5375 | 10.4446 | 10.3559 | 10.2562 | 10.1146 | 9.956 | 9.7801 | 9.5813 | 9.3395 | 9.0616 | 7.8815 | 4.5511 | 2.5187 | 0.6229 | 8.4389 | 8.3098 | 8.1878 | 8.0528 | 7.8443 | 7.6139 | 7.3645 | 7.0059 | 6.5472 | 6.0613 | 3.8208 | -0.66194 | -2.64 | -3.7464
|  | CALNE | SP |  |  | 12.4253 | 12.2581 | 12.1142 | 11.9618 | 11.7236 | 11.4644 | 11.1984 | 10.884 | 10.5373 | 10.1142 | 8.5103 | 4.1617 | 1.7831 | 0.93334 | 10.5598 | 10.4719 | 10.3919 | 10.3059 | 10.1764 | 10.0338 | 9.8833 | 9.7119 | 9.5164 | 9.2592 | 8.3048 | 5.0077 | 1.6599 | -1.8777 | 8.4898 | 8.3783 | 8.2813 | 8.18 | 7.9788 | 7.7586 | 7.5343 | 7.2847 | 6.9984 | 6.5707 | 4.9468 | 0.5198 | -1.9651 | -2.892
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY | MINIMUM HEADROOM | SU 86584 59452 | YES | 56.5797 | 56.3568 | 56.0935 | 55.82 | 55.5102 | 54.52 | 53.3272 | 51.9639 | 50.3128 | 48.7249 | 44.7995 | 39.3322 | 35.7509 | 33.1126 | 59.0183 | 58.7405 | 58.4412 | 58.1384 | 57.6806 | 57.1931 | 56.6557 | 56.0491 | 55.315 | 54.5076 | 52.0277 | 48.1767 | 44.7531 | 40.7645 | 58.1322 | 57.6239 | 57.0655 | 56.4582 | 55.5557 | 54.5863 | 53.5008 | 52.2457 | 50.6923 | 49.2104 | 45.5362 | 40.5315 | 37.5247 | 35.2725
|  | CAMBERLEY | CT |  |  | 56.5797 | 56.3568 | 56.0935 | 55.82 | 55.5339 | 55.2219 | 54.6767 | 53.7494 | 52.655 | 51.0105 | 47.1054 | 40.3877 | 35.7509 | 33.1126 | 59.046 | 58.7974 | 58.5121 | 58.2204 | 57.8601 | 57.4757 | 57.0681 | 56.6143 | 56.0785 | 55.1996 | 52.5518 | 48.1767 | 44.7531 | 41.308 | 58.2031 | 57.7866 | 57.2925 | 56.7406 | 56.0774 | 55.3618 | 54.5879 | 53.7128 | 52.6714 | 51.1385 | 47.639 | 41.5641 | 37.5247 | 35.2725
|  | CAMBERLEY | LW |  |  | 56.6096 | 56.3702 | 56.1067 | 55.8309 | 55.5102 | 54.52 | 53.3272 | 51.9639 | 50.3128 | 48.7249 | 44.7995 | 39.3322 | 36.7857 | 35.1134 | 59.0183 | 58.7405 | 58.4412 | 58.1384 | 57.6806 | 57.1931 | 56.6557 | 56.0491 | 55.315 | 54.5076 | 52.0277 | 48.8009 | 47.5484 | 46.7074 | 58.1322 | 57.6239 | 57.0655 | 56.4582 | 55.5557 | 54.5863 | 53.5008 | 52.2457 | 50.6923 | 49.2104 | 45.5362 | 40.5315 | 38.3476 | 36.9469
|  | CAMBERLEY | ST |  |  | 56.7422 | 56.6143 | 56.4688 | 56.3291 | 56.1691 | 55.9917 | 55.793 | 55.5631 | 55.256 | 54.9096 | 52.8631 | 47.3549 | 44.1171 | 42.1115 | 59.2174 | 59.0708 | 58.907 | 58.7511 | 58.5725 | 58.3793 | 58.1652 | 57.9213 | 57.6169 | 57.2759 | 55.7776 | 51.2999 | 48.1117 | 44.9059 | 58.5807 | 58.3888 | 58.1569 | 57.8982 | 57.5995 | 57.2701 | 56.9018 | 56.481 | 55.9569 | 55.4162 | 52.7416 | 47.6256 | 44.8327 | 43.1853
|  | CAMBERLEY | SP |  |  | 56.7553 | 56.6369 | 56.5027 | 56.3851 | 56.2595 | 56.1287 | 55.987 | 55.8218 | 55.6172 | 55.391 | 54.5195 | 49.5144 | 46.1305 | 44.5227 | 59.2326 | 59.0922 | 58.9367 | 58.7998 | 58.6507 | 58.495 | 58.3272 | 58.1297 | 57.8957 | 57.6022 | 56.4753 | 51.7904 | 46.7993 | 40.7645 | 58.6185 | 58.4355 | 58.2338 | 58.0363 | 57.8091 | 57.5738 | 57.3205 | 57.0056 | 56.6365 | 56.2149 | 54.5207 | 49.5489 | 46.4761 | 45.1108
WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 28.4515 | 28.4198 | 28.369 | 28.3086 | 28.1487 | 27.9406 | 27.7248 | 27.4962 | 27.2764 | 27.0422 | 26.2432 | 24.906 | 23.9125 | 23.0115 | 21.2393 | 21.1956 | 21.1409 | 21.0793 | 20.9959 | 20.9057 | 20.8079 | 20.7018 | 20.5863 | 20.4571 | 20.0102 | 18.9299 | 16.998 | 12.8551 | 24.5976 | 24.5346 | 24.4566 | 24.3696 | 24.2497 | 24.0815 | 23.8883 | 23.6831 | 23.4832 | 23.2682 | 22.5358 | 21.3678 | 20.6316 | 19.9905
|  | CANAL BANK 11kV | CT |  |  | 28.4515 | 28.4198 | 28.3692 | 28.3112 | 28.2468 | 28.1763 | 28.1011 | 28.0179 | 27.887 | 27.6873 | 27.0062 | 25.4406 | 24.0469 | 23.0115 | 21.2516 | 21.2118 | 21.1579 | 21.0966 | 21.0153 | 20.9276 | 20.8409 | 20.745 | 20.637 | 20.5028 | 20.0306 | 18.9299 | 17.6668 | 15.5721 | 24.6333 | 24.593 | 24.5353 | 24.4697 | 24.3798 | 24.2834 | 24.1938 | 24.0958 | 23.9861 | 23.8407 | 23.2227 | 21.8628 | 20.7685 | 19.9905
|  | CANAL BANK 11kV | LW |  |  | 28.4558 | 28.4201 | 28.369 | 28.3086 | 28.1487 | 27.9406 | 27.7248 | 27.4962 | 27.2764 | 27.0422 | 26.2432 | 24.906 | 23.9125 | 23.0619 | 21.2393 | 21.1956 | 21.1409 | 21.0793 | 20.9959 | 20.9057 | 20.8079 | 20.7018 | 20.5863 | 20.4571 | 20.0102 | 19.3358 | 18.9402 | 18.5912 | 24.5976 | 24.5346 | 24.4566 | 24.3696 | 24.2497 | 24.0815 | 23.8883 | 23.6831 | 23.4832 | 23.2682 | 22.5358 | 21.3678 | 20.6316 | 20.0205
|  | CANAL BANK 11kV | ST |  |  | 28.485 | 28.4701 | 28.4426 | 28.4123 | 28.3746 | 28.3315 | 28.2839 | 28.2295 | 28.1606 | 28.0765 | 27.7304 | 26.7257 | 25.8557 | 25.1409 | 21.2843 | 21.2624 | 21.2313 | 21.1969 | 21.1508 | 21.0994 | 21.0421 | 20.9773 | 20.8992 | 20.8071 | 20.447 | 19.41 | 18.2939 | 16.3613 | 24.6788 | 24.6638 | 24.6379 | 24.6095 | 24.5706 | 24.5266 | 24.4787 | 24.4244 | 24.3568 | 24.2725 | 23.9374 | 22.9875 | 22.2742 | 21.7527
|  | CANAL BANK 11kV | SP |  |  | 28.4901 | 28.4792 | 28.4538 | 28.4272 | 28.3958 | 28.3628 | 28.3269 | 28.2871 | 28.2401 | 28.187 | 27.9837 | 27.2301 | 26.1953 | 25.4733 | 21.2875 | 21.2675 | 21.236 | 21.2017 | 21.1501 | 21.0944 | 21.0322 | 20.9627 | 20.8825 | 20.7833 | 20.4113 | 19.3004 | 16.998 | 12.8551 | 24.6863 | 24.6763 | 24.6543 | 24.6312 | 24.5942 | 24.557 | 24.5172 | 24.4733 | 24.4235 | 24.3619 | 24.1413 | 23.4365 | 22.6461 | 22.1325
WILLESDEN GSP | ACTON LANE | CANAL BANK 6.6kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 25.8768 | 25.873 | 34.867 | 34.8598 | 34.8495 | 34.8336 | 34.8167 | 34.7984 | 34.7793 | 34.758 | 34.6847 | 34.5697 | 34.5003 | 34.4423 | 20.5204 | 20.5173 | 33.3121 | 33.3062 | 33.2994 | 33.292 | 33.283 | 33.2726 | 33.2594 | 33.2438 | 33.1891 | 33.1141 | 32.9705 | 32.7152 | 20.2122 | 20.209 | 33.0037 | 32.9973 | 32.9898 | 32.9814 | 32.9715 | 32.9605 | 32.9465 | 32.93 | 32.8718 | 32.7879 | 32.7471 | 32.7133
|  | CANAL BANK 6.6kV | CT |  |  | 25.8768 | 25.8731 | 34.8672 | 34.8604 | 34.8528 | 34.8445 | 34.8356 | 34.8257 | 34.8143 | 34.8004 | 34.7408 | 34.6119 | 34.5157 | 34.4451 | 20.5204 | 20.5173 | 33.3121 | 33.3062 | 33.2994 | 33.292 | 33.284 | 33.2751 | 33.2647 | 33.252 | 33.2073 | 33.1141 | 33.0058 | 32.868 | 20.2122 | 20.209 | 33.0037 | 32.9975 | 32.9907 | 32.9832 | 32.9751 | 32.9661 | 32.9556 | 32.943 | 32.8979 | 32.8105 | 32.7614 | 32.7234
|  | CANAL BANK 6.6kV | LW |  |  | 25.8771 | 25.873 | 34.867 | 34.8598 | 34.8495 | 34.8336 | 34.8167 | 34.7984 | 34.7793 | 34.758 | 34.6847 | 34.5697 | 34.5003 | 34.4423 | 20.5211 | 20.5178 | 33.3129 | 33.307 | 33.3001 | 33.2922 | 33.283 | 33.2726 | 33.2594 | 33.2438 | 33.1891 | 33.1145 | 33.0836 | 33.0588 | 20.2127 | 20.2091 | 33.0037 | 32.9973 | 32.9898 | 32.9814 | 32.9715 | 32.9605 | 32.9465 | 32.93 | 32.8718 | 32.7879 | 32.7471 | 32.7133
|  | CANAL BANK 6.6kV | ST |  |  | 25.8808 | 25.8792 | 34.876 | 34.8726 | 34.8682 | 34.8632 | 34.8577 | 34.8513 | 34.8432 | 34.8333 | 34.7923 | 34.675 | 34.5941 | 34.548 | 20.524 | 20.5227 | 33.32 | 33.317 | 33.3131 | 33.3086 | 33.3035 | 33.2976 | 33.2901 | 33.2808 | 33.2432 | 33.138 | 33.0395 | 32.9073 | 20.2159 | 20.2146 | 33.0118 | 33.0087 | 33.0048 | 33.0003 | 32.9953 | 32.9895 | 32.9821 | 32.973 | 32.9355 | 32.8289 | 32.7572 | 32.7179
|  | CANAL BANK 6.6kV | SP |  |  | 25.8814 | 25.8803 | 34.8774 | 34.8744 | 34.8708 | 34.867 | 34.8629 | 34.8583 | 34.8528 | 34.8465 | 34.8228 | 34.7381 | 34.6439 | 34.5941 | 20.5245 | 20.5235 | 33.321 | 33.3183 | 33.3148 | 33.3112 | 33.307 | 33.3024 | 33.2968 | 33.2902 | 33.2608 | 33.1483 | 32.9705 | 32.7152 | 20.2165 | 20.2156 | 33.0131 | 33.0104 | 33.0072 | 33.0039 | 33.0002 | 32.996 | 32.9911 | 32.9854 | 32.964 | 32.8879 | 32.8038 | 32.7611
COWLEY GSP | WITNEY BSP | CARTERTON | MINIMUM HEADROOM | SP 28261 07823 | NO | 12.7429 | 12.4147 | 12.0486 | 11.6538 | 11.166 | 10.6102 | 10.2771 | 9.9544 | 9.5955 | 9.1937 | 8.1176 | 6.6198 | 6.1162 | 5.6598 | 19.1343 | 18.9918 | 18.8 | 18.5954 | 18.3541 | 18.0772 | 17.9122 | 17.7512 | 17.559 | 17.3435 | 16.8009 | 16.0852 | 15.3164 | 13.837 | 14.4711 | 14.2033 | 13.8939 | 13.5593 | 13.1455 | 12.6743 | 12.3804 | 12.093 | 11.7662 | 11.399 | 10.4397 | 9.143 | 8.7264 | 8.3504
|  | CARTERTON | CT |  |  | 12.8938 | 12.643 | 12.3628 | 12.0401 | 11.649 | 11.1912 | 10.9631 | 10.748 | 10.512 | 10.1582 | 9.1948 | 7.8752 | 7.2917 | 6.8297 | 19.1343 | 19.0551 | 18.8897 | 18.6973 | 18.4813 | 18.23 | 18.0938 | 17.9621 | 17.8116 | 17.6011 | 17.0346 | 16.1949 | 15.5802 | 14.8144 | 14.6021 | 14.3939 | 14.1596 | 13.8838 | 13.5515 | 13.1634 | 12.9596 | 12.7649 | 12.5483 | 12.2233 | 11.3545 | 10.2111 | 9.7247 | 9.3452
|  | CARTERTON | LW |  |  | 12.7429 | 12.4147 | 12.0486 | 11.6538 | 11.166 | 10.6102 | 10.2771 | 9.9544 | 9.5955 | 9.1937 | 8.1176 | 6.6198 | 6.1162 | 5.6598 | 19.1394 | 18.9918 | 18.8 | 18.5954 | 18.3541 | 18.0772 | 17.9122 | 17.7512 | 17.559 | 17.3435 | 16.8009 | 16.0852 | 15.8236 | 15.5919 | 14.4711 | 14.2033 | 13.8939 | 13.5593 | 13.1455 | 12.6743 | 12.3804 | 12.093 | 11.7662 | 11.399 | 10.4397 | 9.143 | 8.7264 | 8.3504
|  | CARTERTON | ST |  |  | 12.9428 | 12.7598 | 12.567 | 12.366 | 12.1168 | 11.8266 | 11.6823 | 11.5463 | 11.3988 | 11.2384 | 10.682 | 9.4401 | 8.5667 | 7.9639 | 19.1537 | 19.0924 | 19.0222 | 18.8983 | 18.7443 | 18.5648 | 18.4722 | 18.3824 | 18.2816 | 18.1754 | 17.7774 | 16.8522 | 16.0976 | 15.288 | 14.651 | 14.5143 | 14.3624 | 14.2021 | 13.9944 | 13.7528 | 13.6262 | 13.5048 | 13.3717 | 13.2282 | 12.7128 | 11.5797 | 10.8382 | 10.3433
|  | CARTERTON | SP |  |  | 12.9608 | 12.7931 | 12.6227 | 12.4472 | 12.1431 | 11.8115 | 11.5922 | 11.3848 | 11.1685 | 10.9308 | 10.1876 | 8.5816 | 7.4709 | 6.7434 | 19.1545 | 19.0932 | 19.0307 | 18.9263 | 18.7667 | 18.5875 | 18.4729 | 18.3632 | 18.2446 | 18.1075 | 17.6443 | 16.495 | 15.3164 | 13.837 | 14.667 | 14.5426 | 14.411 | 14.2739 | 14.028 | 13.7603 | 13.5734 | 13.3953 | 13.2085 | 13.0031 | 12.3515 | 10.9114 | 9.9435 | 9.3366
AXMINSTER | YEOVIL BSP | CASTLE CARY | MINIMUM HEADROOM | ST 64534 31039 | YES | 8.5575 | 8.1549 | 7.7602 | 7.3766 | 6.8668 | 6.3423 | 5.8615 | 5.4262 | 4.9271 | 4.4198 | 3.2348 | 1.9701 | 1.049 | 0.26125 | 10.716 | 10.5068 | 10.3077 | 10.1177 | 9.863 | 9.5998 | 9.3563 | 9.1335 | 8.8779 | 8.6166 | 8.0076 | 7.3524 | 6.6716 | 6.1568 | 9.17 | 8.812 | 8.4563 | 8.1081 | 7.6123 | 7.1028 | 6.636 | 6.2124 | 5.7255 | 5.2295 | 4.0652 | 2.8241 | 1.8219 | 1.1339
|  | CASTLE CARY | CT |  |  | 8.8621 | 8.6157 | 8.4064 | 8.1678 | 7.8465 | 7.511 | 7.18 | 6.8713 | 6.5532 | 6.0937 | 5.0184 | 3.4387 | 2.9219 | 2.7914 | 10.8215 | 10.6668 | 10.542 | 10.3943 | 10.2249 | 10.0478 | 9.8694 | 9.69 | 9.4966 | 9.2321 | 8.674 | 7.9615 | 7.6261 | 7.4294 | 9.4359 | 9.2151 | 9.0255 | 8.8044 | 8.5126 | 8.2075 | 7.9051 | 7.6184 | 7.3197 | 6.8803 | 5.8267 | 4.2708 | 3.7647 | 3.6388
|  | CASTLE CARY | LW |  |  | 8.5575 | 8.1549 | 7.7602 | 7.3766 | 6.8668 | 6.3423 | 5.8615 | 5.4262 | 4.9271 | 4.4198 | 3.2348 | 1.9701 | 1.6707 | 1.5338 | 10.716 | 10.5068 | 10.3077 | 10.1177 | 9.863 | 9.5998 | 9.3563 | 9.1335 | 8.8779 | 8.6166 | 8.0076 | 7.3524 | 7.2021 | 7.132 | 9.17 | 8.812 | 8.4563 | 8.1081 | 7.6123 | 7.1028 | 6.636 | 6.2124 | 5.7255 | 5.2295 | 4.0652 | 2.8241 | 2.5341 | 2.4026
|  | CASTLE CARY | ST |  |  | 8.9482 | 8.7414 | 8.5754 | 8.4231 | 8.2043 | 7.9785 | 7.7531 | 7.5214 | 7.2791 | 7.0315 | 6.1093 | 4.646 | 3.9801 | 3.5359 | 10.8812 | 10.7531 | 10.6583 | 10.5743 | 10.4604 | 10.3427 | 10.2229 | 10.0968 | 9.9624 | 9.836 | 9.3227 | 8.5178 | 8.0762 | 7.7307 | 9.5208 | 9.3385 | 9.191 | 9.0548 | 8.8579 | 8.6548 | 8.4511 | 8.2394 | 8.0164 | 7.79 | 6.8932 | 5.4611 | 4.8114 | 4.3831
|  | CASTLE CARY | SP |  |  | 8.985 | 8.7923 | 8.6457 | 8.5154 | 8.1865 | 7.8509 | 7.5187 | 7.1845 | 6.8507 | 6.4575 | 5.2078 | 2.5686 | 1.049 | 0.26125 | 10.8942 | 10.7671 | 10.6769 | 10.5992 | 10.454 | 10.3056 | 10.139 | 9.9658 | 9.7911 | 9.5909 | 8.9567 | 7.5696 | 6.6716 | 6.1568 | 9.5531 | 9.382 | 9.251 | 9.1337 | 8.8431 | 8.5463 | 8.2522 | 7.9386 | 7.6117 | 7.2253 | 5.9977 | 3.4047 | 1.8219 | 1.1339
LALEHAM | STAINES | CAUSEWAY | MINIMUM HEADROOM | TQ 02763 71680 | NO | 33.4264 | 32.989 | 32.3049 | 31.7875 | 31.0268 | 29.9999 | 28.7541 | 27.3761 | 26.067 | 24.7366 | 21.2971 | 16.5368 | 13.2739 | 10.5862 | 36.6927 | 36.4507 | 36.1313 | 35.8702 | 35.5144 | 35.0451 | 34.4171 | 33.7042 | 32.9983 | 32.2674 | 30.3089 | 27.2418 | 24.2945 | 21.27 | 35.8196 | 35.6148 | 35.3291 | 35.0391 | 34.6168 | 34.0582 | 32.9666 | 31.7297 | 30.506 | 29.2536 | 26.0531 | 21.7709 | 19.0757 | 16.8278
|  | CAUSEWAY | CT |  |  | 33.5564 | 33.2181 | 32.6589 | 32.2059 | 31.6499 | 30.8469 | 29.8652 | 28.7669 | 27.8328 | 26.5442 | 23.1838 | 17.4634 | 13.2739 | 10.5862 | 36.7288 | 36.5147 | 36.2264 | 35.9766 | 35.6891 | 35.2759 | 34.7233 | 34.1065 | 33.5486 | 32.8163 | 30.8113 | 27.2418 | 24.2945 | 21.27 | 35.8196 | 35.6148 | 35.3291 | 35.0892 | 34.8517 | 34.5049 | 33.9573 | 32.9756 | 32.1028 | 30.8932 | 27.7738 | 22.6611 | 19.0757 | 16.8278
|  | CAUSEWAY | LW |  |  | 33.4264 | 32.989 | 32.3049 | 31.7875 | 31.0268 | 29.9999 | 28.7541 | 27.3761 | 26.067 | 24.7366 | 21.2971 | 16.5368 | 13.9835 | 12.1419 | 36.6927 | 36.4507 | 36.1313 | 35.8702 | 35.5144 | 35.0451 | 34.4171 | 33.7042 | 32.9983 | 32.2674 | 30.3089 | 27.7066 | 26.4881 | 25.5927 | 35.8452 | 35.627 | 35.3293 | 35.0391 | 34.6168 | 34.0582 | 32.9666 | 31.7297 | 30.506 | 29.2536 | 26.0531 | 21.7709 | 19.6318 | 18.1199
|  | CAUSEWAY | ST |  |  | 33.8134 | 33.6344 | 33.3276 | 33.1332 | 32.879 | 32.4598 | 31.9106 | 31.294 | 30.7999 | 30.2961 | 28.1762 | 23.2301 | 20.1991 | 18.2896 | 36.8539 | 36.7184 | 36.5485 | 36.4198 | 36.2741 | 36.058 | 35.7827 | 35.4128 | 35.0765 | 34.7234 | 33.2808 | 29.7338 | 27.0383 | 24.3022 | 35.9485 | 35.8222 | 35.6359 | 35.5182 | 35.3858 | 35.1638 | 34.8723 | 34.5444 | 34.2426 | 33.9123 | 32.1487 | 26.7316 | 23.9462 | 23.0114
|  | CAUSEWAY | SP |  |  | 33.8444 | 33.6684 | 33.3807 | 33.2117 | 32.9943 | 32.6539 | 32.1887 | 31.6683 | 31.2859 | 30.877 | 29.4337 | 25.13 | 21.8487 | 20.1427 | 36.8654 | 36.732 | 36.5672 | 36.4454 | 36.3125 | 36.1243 | 35.8815 | 35.5656 | 35.2843 | 34.9642 | 33.8111 | 30.3796 | 26.2352 | 21.2957 | 35.9562 | 35.834 | 35.6542 | 35.5476 | 35.4442 | 35.2624 | 35.0177 | 34.7462 | 34.5317 | 34.3096 | 33.5264 | 29.6175 | 26.0966 | 24.935
BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM | MINIMUM HEADROOM | SU 71512 75747 | YES | 15.7865 | 15.3486 | 14.8532 | 14.3112 | 13.3978 | 12.4255 | 11.3753 | 10.2545 | 8.8386 | 7.3105 | 3.7898 | -0.6849 | -4.4051 | -6.7687 | 20.0171 | 19.7376 | 19.407 | 19.0257 | 18.5627 | 18.0002 | 17.3717 | 16.6924 | 15.7609 | 14.7492 | 12.6069 | 9.0939 | 5.94 | 2.5831 | 16.8556 | 16.465 | 16.0248 | 15.5434 | 14.714 | 13.8327 | 12.8834 | 11.8716 | 10.606 | 9.1645 | 5.8692 | 1.827 | -1.3825 | -3.4814
|  | CAVERSHAM | CT |  |  | 15.8954 | 15.5528 | 15.1482 | 14.6849 | 14.0732 | 13.4199 | 12.7383 | 11.9975 | 11.1251 | 9.576 | 5.6966 | -0.10403 | -4.4051 | -6.7687 | 20.0171 | 19.7376 | 19.407 | 19.0257 | 18.5968 | 18.1333 | 17.6307 | 17.0778 | 16.4119 | 15.3376 | 12.7201 | 9.0939 | 5.94 | 2.6675 | 16.9646 | 16.6648 | 16.3109 | 15.9056 | 15.3582 | 14.7742 | 14.1667 | 13.5071 | 12.6905 | 11.2189 | 7.5864 | 2.4014 | -1.3825 | -3.4814
|  | CAVERSHAM | LW |  |  | 15.7865 | 15.3486 | 14.8532 | 14.3112 | 13.3978 | 12.4255 | 11.3753 | 10.2545 | 8.8386 | 7.3105 | 3.7898 | -0.6849 | -2.9628 | -4.2924 | 20.041 | 19.7625 | 19.4405 | 19.0818 | 18.5627 | 18.0002 | 17.3717 | 16.6924 | 15.7609 | 14.7492 | 12.6069 | 10.1916 | 9.144 | 8.4943 | 16.8556 | 16.465 | 16.0248 | 15.5434 | 14.714 | 13.8327 | 12.8834 | 11.8716 | 10.606 | 9.1645 | 5.8692 | 1.827 | -0.11082 | -1.2094
|  | CAVERSHAM | ST |  |  | 16.2504 | 16.1202 | 15.9528 | 15.7562 | 15.4978 | 15.21 | 14.8903 | 14.5356 | 14.1105 | 13.6643 | 11.5479 | 6.7634 | 4.1916 | 2.3729 | 20.2725 | 20.1443 | 19.9833 | 19.794 | 19.564 | 19.307 | 19.0169 | 18.6926 | 18.3028 | 17.9155 | 16.0876 | 12.0311 | 9.3564 | 6.3007 | 17.2789 | 17.1676 | 17.024 | 16.8551 | 16.6309 | 16.3812 | 16.1032 | 15.7945 | 15.4241 | 15.0297 | 13.0448 | 8.5316 | 6.2849 | 4.761
|  | CAVERSHAM | SP |  |  | 16.2717 | 16.1394 | 15.9983 | 15.8413 | 15.6416 | 15.4225 | 15.1982 | 14.9189 | 14.6035 | 14.2358 | 12.7566 | 8.3088 | 5.6776 | 4.4454 | 20.2748 | 20.1346 | 19.9794 | 19.8051 | 19.6233 | 19.4192 | 19.2018 | 18.9336 | 18.6257 | 18.25 | 16.7282 | 12.1928 | 7.9479 | 2.5831 | 17.299 | 17.1869 | 17.0672 | 16.9337 | 16.7602 | 16.57 | 16.3751 | 16.1322 | 15.8577 | 15.5344 | 14.2336 | 9.9754 | 7.5614 | 6.5205
MANNINGTON GSP | BOURNEMOUTH | CENTRAL | MINIMUM HEADROOM | SZ 10293 91931 | YES | 4.5013 | 3.8038 | 3.0126 | 2.1661 | 0.65559 | -0.94265 | -2.6451 | -4.4881 | -6.5725 | -8.7836 | -15.9282 | -25.5277 | -30.3122 | -34.3421 | 15.8736 | 15.5 | 15.0562 | 14.5473 | 13.821 | 13.0112 | 12.1086 | 11.114 | 9.9052 | 8.5969 | 4.0211 | -4.9245 | -13.3695 | -34.1607 | 8.0889 | 7.474 | 6.7451 | 5.9613 | 4.59 | 3.1332 | 1.571 | -0.12315 | -2.0596 | -4.1217 | -10.8095 | -19.6496 | -23.5039 | -26.7777
|  | CENTRAL | CT |  |  | 4.9074 | 4.4528 | 3.9468 | 3.2934 | 2.25 | 1.1348 | 0.043952 | -1.1612 | -2.5509 | -4.6199 | -11.1997 | -22.803 | -30.3122 | -34.3421 | 15.9092 | 15.5293 | 15.1041 | 14.5473 | 13.821 | 13.0295 | 12.1952 | 11.2634 | 10.1609 | 8.751 | 4.0211 | -4.9245 | -13.2476 | -24.0408 | 8.3978 | 7.9916 | 7.5326 | 6.9227 | 5.9902 | 4.9612 | 3.9461 | 2.8245 | 1.5222 | -0.39301 | -6.5035 | -17.0337 | -23.5039 | -26.7777
|  | CENTRAL | LW |  |  | 4.5013 | 3.8038 | 3.0126 | 2.1661 | 0.65559 | -0.94265 | -2.6451 | -4.4881 | -6.5725 | -8.7836 | -15.9282 | -25.5277 | -29.1654 | -31.3562 | 15.8736 | 15.5 | 15.0562 | 14.5697 | 13.8215 | 13.0112 | 12.1086 | 11.114 | 9.9052 | 8.5969 | 4.2081 | -1.4179 | -3.1091 | -4.1433 | 8.0889 | 7.474 | 6.7451 | 5.9613 | 4.59 | 3.1332 | 1.571 | -0.12315 | -2.0596 | -4.1217 | -10.8095 | -19.6496 | -22.7798 | -24.6159
|  | CENTRAL | ST |  |  | 5.3431 | 5.1442 | 4.9415 | 4.7135 | 4.3391 | 3.9351 | 3.4941 | 2.9884 | 2.358 | 1.6248 | -1.1863 | -9.0075 | -14.0446 | -16.9524 | 16.1658 | 15.9347 | 15.6936 | 15.42 | 15.0303 | 14.6058 | 14.1281 | 13.5813 | 12.9115 | 12.186 | 9.3509 | 1.4126 | -6.5289 | -16.7665 | 8.7894 | 8.612 | 8.428 | 8.2172 | 7.8774 | 7.5087 | 7.1024 | 6.6356 | 6.0478 | 5.3741 | 2.7478 | -4.5981 | -9.1188 | -11.5819
|  | CENTRAL | SP |  |  | 5.4335 | 5.2412 | 5.0431 | 4.8313 | 4.5356 | 4.2189 | 3.8801 | 3.4983 | 3.0437 | 2.4698 | 0.46012 | -5.3977 | -10.6785 | -13.0985 | 16.197 | 15.9447 | 15.6665 | 15.3617 | 14.9658 | 14.5254 | 14.0328 | 13.471 | 12.8023 | 11.9966 | 8.9643 | 0.094465 | -13.3695 | -34.1607 | 8.8697 | 8.6921 | 8.5056 | 8.3042 | 8.0365 | 7.7483 | 7.4379 | 7.0861 | 6.6633 | 6.1428 | 4.2916 | -1.1761 | -6.0755 | -8.186
NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE | MINIMUM HEADROOM | SU 42591 11255 | YES | 24.0233 | 22.8253 | 21.5134 | 20.6826 | 19.9383 | 19.1664 | 18.4364 | 17.591 | 16.6972 | 15.9154 | 13.4164 | 9.6988 | 7.6604 | 6.072 | 30.0061 | 29.5209 | 28.7705 | 28.2588 | 27.7934 | 27.3003 | 26.8248 | 26.2181 | 25.5027 | 24.842 | 22.5934 | 16.7286 | 5.1859 | -14.8234 | 24.4958 | 23.5299 | 22.4655 | 21.7785 | 21.1533 | 20.5005 | 19.876 | 19.1149 | 18.2728 | 17.5549 | 15.246 | 11.9352 | 10.2629 | 8.9719
|  | CENTRAL BRIDGE | CT |  |  | 24.2947 | 23.2391 | 22.0742 | 21.3767 | 20.8043 | 20.2125 | 19.7285 | 19.1391 | 18.4891 | 17.8145 | 15.6823 | 11.5391 | 8.5543 | 6.5046 | 30.0273 | 29.5209 | 28.7705 | 28.2588 | 27.7934 | 27.3003 | 26.8248 | 26.2181 | 25.5027 | 24.842 | 22.5934 | 17.4251 | 10.749 | 0.72033 | 24.704 | 23.8551 | 22.9196 | 22.3377 | 21.8527 | 21.3484 | 20.9279 | 20.3806 | 19.7486 | 19.1288 | 17.1614 | 13.546 | 11.0923 | 9.4284
|  | CENTRAL BRIDGE | LW |  |  | 24.0233 | 22.8253 | 21.5134 | 20.6826 | 19.9383 | 19.1664 | 18.4364 | 17.591 | 16.6972 | 15.9154 | 13.4164 | 9.6988 | 7.6604 | 6.072 | 30.0061 | 29.5751 | 28.8874 | 28.4622 | 28.1022 | 27.7269 | 27.3647 | 26.8941 | 26.3347 | 25.8781 | 24.3954 | 22.2935 | 21.2604 | 20.4379 | 24.4958 | 23.5299 | 22.4655 | 21.7785 | 21.1533 | 20.5005 | 19.876 | 19.1149 | 18.2728 | 17.5549 | 15.246 | 11.9352 | 10.2629 | 8.9719
|  | CENTRAL BRIDGE | ST |  |  | 24.6828 | 24.0177 | 23.3216 | 22.9569 | 22.6882 | 22.4108 | 22.1662 | 21.8425 | 21.4442 | 21.0892 | 19.8756 | 16.9333 | 14.7277 | 13.2487 | 30.1626 | 29.8459 | 29.4319 | 29.0854 | 28.7558 | 28.4042 | 28.0428 | 27.5654 | 26.9757 | 26.4722 | 24.6578 | 19.8095 | 13.2903 | 3.5073 | 25.0612 | 24.5541 | 24.0155 | 23.725 | 23.5014 | 23.2688 | 23.0609 | 22.7515 | 22.3495 | 22.0243 | 20.9016 | 18.2271 | 16.3474 | 15.1559
|  | CENTRAL BRIDGE | SP |  |  | 24.7287 | 24.1102 | 23.481 | 23.1598 | 22.961 | 22.757 | 22.575 | 22.3214 | 22.0145 | 21.7175 | 20.7704 | 18.2299 | 15.7028 | 14.0439 | 30.1647 | 29.8554 | 29.4461 | 29.0859 | 28.7067 | 28.284 | 27.8251 | 27.2352 | 26.5138 | 25.8467 | 23.3942 | 16.7286 | 5.1859 | -14.8234 | 25.0982 | 24.6305 | 24.1523 | 23.8985 | 23.7366 | 23.568 | 23.411 | 23.1572 | 22.8296 | 22.5567 | 21.6789 | 19.4308 | 17.2186 | 15.8443
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS | MINIMUM HEADROOM | ST 66140 01039 | YES | 0.71456 | 0.65225 | 0.58876 | 0.52458 | 0.43639 | 0.34726 | 0.25907 | 0.17684 | 0.087966 | -0.0022263 | -0.28804 | -0.60046 | -0.63593 | -0.66605 | 1.0296 | 1.0113 | 0.99246 | 0.97179 | 0.94518 | 0.91734 | 0.88828 | 0.85792 | 0.82083 | 0.78333 | 0.65571 | 0.53639 | 0.52018 | 0.46974 | 0.50485 | 0.44826 | 0.3906 | 0.33149 | 0.25114 | 0.16947 | 0.087904 | 0.010984 | -0.072644 | -0.15661 | -0.41018 | -0.68641 | -0.71374 | -0.73728
|  | CERNE ABBAS | CT |  |  | 0.79635 | 0.77544 | 0.75374 | 0.73165 | 0.68902 | 0.64537 | 0.59752 | 0.55021 | 0.50474 | 0.44275 | 0.24534 | -0.13464 | -0.21515 | -0.23855 | 1.048 | 1.0398 | 1.0303 | 1.0202 | 1.0051 | 0.98842 | 0.97089 | 0.95237 | 0.93363 | 0.90708 | 0.80629 | 0.65954 | 0.61413 | 0.58215 | 0.54467 | 0.53853 | 0.53206 | 0.51348 | 0.47356 | 0.43212 | 0.38708 | 0.34197 | 0.29829 | 0.23815 | 0.0502 | -0.27714 | -0.34844 | -0.36929
|  | CERNE ABBAS | LW |  |  | 0.71456 | 0.65225 | 0.58876 | 0.52458 | 0.43639 | 0.34726 | 0.25907 | 0.17684 | 0.087966 | -0.0022263 | -0.28804 | -0.60046 | -0.63593 | -0.66605 | 1.0296 | 1.0113 | 0.99246 | 0.97179 | 0.94518 | 0.91734 | 0.88828 | 0.85792 | 0.82083 | 0.78333 | 0.65571 | 0.53639 | 0.52018 | 0.50806 | 0.50485 | 0.44826 | 0.3906 | 0.33149 | 0.25114 | 0.16947 | 0.087904 | 0.010984 | -0.072644 | -0.15661 | -0.41018 | -0.68641 | -0.71374 | -0.73728
|  | CERNE ABBAS | ST |  |  | 0.80343 | 0.7868 | 0.77007 | 0.75312 | 0.72209 | 0.69075 | 0.65919 | 0.62709 | 0.59499 | 0.55615 | 0.43381 | 0.19656 | 0.041403 | -0.058093 | 1.0526 | 1.0474 | 1.042 | 1.036 | 1.026 | 1.0162 | 1.0043 | 0.9933 | 0.98076 | 0.96488 | 0.90948 | 0.78881 | 0.7204 | 0.66517 | 0.54695 | 0.54216 | 0.53736 | 0.53241 | 0.50899 | 0.48038 | 0.45048 | 0.42066 | 0.3901 | 0.35263 | 0.23224 | 0.014458 | -0.12319 | -0.21078
|  | CERNE ABBAS | SP |  |  | 0.81755 | 0.80722 | 0.79674 | 0.78609 | 0.74115 | 0.69637 | 0.65164 | 0.60605 | 0.56053 | 0.49585 | 0.29883 | -0.10738 | -0.42925 | -0.6473 | 1.0559 | 1.0521 | 1.048 | 1.0434 | 1.0314 | 1.0187 | 1.006 | 0.99242 | 0.97903 | 0.96026 | 0.89915 | 0.70606 | 0.56075 | 0.46974 | 0.55094 | 0.54785 | 0.54469 | 0.54147 | 0.52618 | 0.48581 | 0.44545 | 0.40405 | 0.36279 | 0.30425 | 0.12408 | -0.24962 | -0.53216 | -0.71293
IVER 132KV | CHALVEY BSP | CHALVEY | MINIMUM HEADROOM | SU 96669 79364 | YES | 42.5697 | 40.7536 | 38.7747 | 36.7033 | 33.9208 | 31.0249 | 28.2347 | 25.1623 | 21.5435 | 17.8312 | 8.119 | -3.5088 | -10.6841 | -15.3392 | 53.4558 | 52.2754 | 51.1 | 49.7178 | 48.189 | 46.5886 | 45.0413 | 43.3188 | 41.3464 | 38.8138 | 31.473 | 19.4586 | 5.3577 | -26.9701 | 44.7974 | 43.2626 | 41.5663 | 39.778 | 37.4073 | 34.9248 | 32.4836 | 29.7815 | 26.5522 | 23.1976 | 14.3375 | 3.6739 | -2.3892 | -6.3956
|  | CHALVEY | CT |  |  | 42.8911 | 41.2964 | 39.6299 | 37.691 | 35.437 | 33.0987 | 30.9787 | 28.6296 | 25.9665 | 22.3818 | 12.7327 | -1.6021 | -10.6841 | -15.3392 | 53.4558 | 52.2754 | 51.1 | 49.7178 | 48.189 | 46.5886 | 45.0413 | 43.3188 | 41.3464 | 38.8138 | 31.473 | 19.4586 | 7.2315 | -9.0577 | 45.022 | 43.6621 | 42.2366 | 40.5323 | 38.6 | 36.5744 | 34.6966 | 32.61 | 30.2246 | 27.0212 | 18.3667 | 5.5632 | -2.3892 | -6.3956
|  | CHALVEY | LW |  |  | 42.5697 | 40.7536 | 38.7747 | 36.7033 | 33.9208 | 31.0249 | 28.2347 | 25.1623 | 21.5435 | 17.8312 | 8.119 | -3.5088 | -8.2265 | -10.6315 | 53.4717 | 52.3437 | 51.1987 | 49.9837 | 48.4599 | 46.8679 | 45.2888 | 43.537 | 41.4164 | 39.0896 | 33.02 | 26.2087 | 23.9284 | 22.7058 | 44.7974 | 43.2626 | 41.5663 | 39.778 | 37.4073 | 34.9248 | 32.4836 | 29.7815 | 26.5522 | 23.1976 | 14.3375 | 3.6739 | -0.40976 | -2.4343
|  | CHALVEY | ST |  |  | 43.7207 | 42.7313 | 41.7812 | 40.8156 | 39.6558 | 38.4747 | 37.4098 | 36.2144 | 34.8027 | 33.3851 | 28.5244 | 17.1892 | 10.9489 | 7.1518 | 53.9042 | 53.0564 | 52.3047 | 51.5134 | 50.5897 | 49.6173 | 48.6385 | 47.5386 | 46.2481 | 44.9368 | 40.195 | 28.0444 | 16.5233 | 0.60383 | 45.7858 | 44.9635 | 44.1637 | 43.3374 | 42.3167 | 41.274 | 40.3108 | 39.2271 | 37.9417 | 36.6681 | 32.1068 | 21.6005 | 16.2347 | 13.1025
|  | CHALVEY | SP |  |  | 43.8149 | 42.8419 | 41.9452 | 41.0573 | 40.1529 | 39.2367 | 38.4207 | 37.4957 | 36.452 | 35.3422 | 31.9951 | 22.9786 | 16.2389 | 13.4427 | 53.9205 | 53.0627 | 52.2931 | 51.4941 | 50.6296 | 49.7134 | 48.7566 | 47.6711 | 46.4242 | 44.9786 | 39.9335 | 25.882 | 5.3577 | -26.9701 | 45.8672 | 45.0472 | 44.2867 | 43.5225 | 42.7444 | 41.9493 | 41.2152 | 40.377 | 39.4272 | 38.4264 | 35.2932 | 26.7077 | 20.5515 | 18.1954
NURSLING GSP | VELMORE BSP | CHANDLERSFORD | MINIMUM HEADROOM | SU 43494 21552 | YES | 15.7532 | 15.1608 | 14.5146 | 13.7722 | 12.632 | 11.3759 | 10.0229 | 8.621 | 6.7853 | 4.9189 | 0.55629 | -5.2479 | -8.9837 | -11.7548 | -0.72262 | -1.1138 | -1.5486 | -2.0469 | -2.7239 | -3.4757 | -4.3139 | -5.2028 | -6.4525 | -7.7208 | -10.4803 | -14.0487 | -17.0386 | -19.69 | -2.5962 | -3.1519 | -3.7618 | -4.4595 | -5.5121 | -6.6702 | -7.93 | -9.248 | -10.9995 | -12.7814 | -16.8686 | -22.1434 | -25.2517 | -27.5869
|  | CHANDLERSFORD | CT |  |  | 15.8804 | 15.4077 | 14.8797 | 14.2219 | 13.395 | 12.4678 | 11.5179 | 10.5233 | 9.3043 | 7.4274 | 2.9695 | -4.15 | -8.9837 | -11.7548 | -0.72262 | -1.0928 | -1.5045 | -2.0099 | -2.5749 | -3.206 | -3.8718 | -4.5914 | -5.4933 | -6.7961 | -9.7437 | -14.0487 | -17.0386 | -19.69 | -2.4931 | -2.9422 | -3.4467 | -4.0728 | -4.8442 | -5.706 | -6.5969 | -7.5426 | -8.7097 | -10.4982 | -14.67 | -21.08 | -25.2517 | -27.5869
|  | CHANDLERSFORD | LW |  |  | 15.7532 | 15.1608 | 14.5146 | 13.7722 | 12.632 | 11.3759 | 10.0229 | 8.621 | 6.7853 | 4.9189 | 0.55629 | -5.2479 | -7.9516 | -9.6926 | -0.717 | -1.1138 | -1.5486 | -2.0469 | -2.7239 | -3.4757 | -4.3139 | -5.2028 | -6.4525 | -7.7208 | -10.4803 | -13.8454 | -15.1258 | -15.9968 | -2.5962 | -3.1519 | -3.7618 | -4.4595 | -5.5121 | -6.6702 | -7.93 | -9.248 | -10.9995 | -12.7814 | -16.8686 | -22.1434 | -24.4263 | -25.8591
|  | CHANDLERSFORD | ST |  |  | 16.2881 | 16.0705 | 15.8277 | 15.528 | 15.1354 | 14.6755 | 14.1918 | 13.6923 | 13.0725 | 12.4279 | 9.3575 | 2.8345 | -0.76024 | -2.8575 | -0.42696 | -0.61351 | -0.8198 | -1.0678 | -1.375 | -1.73 | -2.1125 | -2.52 | -3.0301 | -3.5404 | -5.9986 | -11.0537 | -13.9675 | -16.3542 | -2.0973 | -2.2991 | -2.5273 | -2.8064 | -3.1715 | -3.5966 | -4.0495 | -4.5269 | -5.1234 | -5.7401 | -8.7039 | -14.8425 | -18.0178 | -19.7587
|  | CHANDLERSFORD | SP |  |  | 16.3247 | 16.1118 | 15.8966 | 15.6605 | 15.3622 | 15.0269 | 14.6755 | 14.3056 | 13.8665 | 13.3757 | 11.4034 | 5.4389 | 1.6162 | -0.11724 | -0.41355 | -0.60577 | -0.80182 | -1.0139 | -1.2497 | -1.513 | -1.7948 | -2.1063 | -2.4792 | -2.9046 | -4.6342 | -9.8418 | -14.0965 | -18.2119 | -2.0641 | -2.263 | -2.4652 | -2.6831 | -2.9561 | -3.2595 | -3.5825 | -3.9335 | -4.3526 | -4.8208 | -6.7101 | -12.3951 | -15.8943 | -17.3629
NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL | MINIMUM HEADROOM | SU 42849 11983 | YES | 3.2685 | 3.033 | 2.7677 | 2.4245 | 2.1257 | 1.8626 | 1.587 | 1.246 | 0.85766 | 0.47272 | -0.77405 | -2.9532 | -5.1308 | -6.7944 | 3.9404 | 3.8068 | 3.6582 | 3.4632 | 3.3003 | 3.1528 | 2.987 | 2.7529 | 2.5407 | 2.2864 | 1.4291 | -0.63491 | -4.7142 | -12.2389 | 0.28169 | 0.10749 | -0.08828 | -0.34011 | -0.58269 | -0.81495 | -1.059 | -1.3697 | -1.7165 | -2.063 | -3.1834 | -5.1056 | -6.9903 | -8.433
|  | CHAPEL | CT |  |  | 3.3417 | 3.1458 | 2.923 | 2.6177 | 2.3862 | 2.1945 | 1.9801 | 1.7061 | 1.4506 | 1.0917 | -0.067429 | -2.7555 | -5.1308 | -6.7944 | 3.9414 | 3.8068 | 3.6582 | 3.4632 | 3.3003 | 3.1528 | 2.987 | 2.7529 | 2.5407 | 2.2864 | 1.4291 | -0.63491 | -3.6713 | -7.789 | 0.3288 | 0.18125 | 0.014519 | -0.21243 | -0.38578 | -0.53184 | -0.71289 | -0.96322 | -1.1916 | -1.513 | -2.5492 | -4.9169 | -6.9903 | -8.433
|  | CHAPEL | LW |  |  | 3.2685 | 3.033 | 2.7677 | 2.4245 | 2.1257 | 1.8626 | 1.587 | 1.246 | 0.85766 | 0.47272 | -0.77405 | -2.9532 | -4.5643 | -5.7984 | 3.9404 | 3.8191 | 3.6833 | 3.5093 | 3.3659 | 3.239 | 3.1028 | 2.9009 | 2.7028 | 2.5001 | 1.8414 | 0.75074 | -0.015627 | -0.62204 | 0.28169 | 0.10749 | -0.08828 | -0.34011 | -0.58269 | -0.81495 | -1.059 | -1.3697 | -1.7165 | -2.063 | -3.1834 | -5.1056 | -6.5025 | -7.5667
|  | CHAPEL | ST |  |  | 3.4355 | 3.3234 | 3.2055 | 3.0542 | 2.9575 | 2.8843 | 2.8048 | 2.6736 | 2.5515 | 2.4056 | 1.8835 | 0.36533 | -1.0882 | -2.2317 | 3.9935 | 3.9015 | 3.8036 | 3.6828 | 3.5803 | 3.487 | 3.382 | 3.2118 | 3.0609 | 2.9001 | 2.3104 | 0.64365 | -2.0063 | -5.9019 | 0.40278 | 0.31851 | 0.22986 | 0.1162 | 0.040803 | -0.018107 | -0.082811 | -0.20174 | -0.3039 | -0.42668 | -0.86986 | -2.1399 | -3.3775 | -4.3428
|  | CHAPEL | SP |  |  | 3.4458 | 3.3432 | 3.2369 | 3.1036 | 3.0245 | 2.9676 | 2.9059 | 2.7969 | 2.7125 | 2.598 | 2.2163 | 1.0964 | -0.15279 | -1.0946 | 3.992 | 3.8998 | 3.7995 | 3.6781 | 3.5631 | 3.4502 | 3.3214 | 3.1249 | 2.946 | 2.7494 | 2.0235 | -0.2721 | -4.7142 | -12.2389 | 0.40973 | 0.33238 | 0.25237 | 0.15204 | 0.090881 | 0.045578 | -0.0041874 | -0.10429 | -0.17593 | -0.2702 | -0.5855 | -1.4998 | -2.5333 | -3.3251
COWLEY GSP | YARNTON BSP | CHARLBURY | MINIMUM HEADROOM | SP 36034 18376 | NO | 8.4615 | 8.091 | 7.6775 | 7.253 | 6.6366 | 6.0028 | 5.3447 | 4.6443 | 3.7941 | 2.9052 | 0.83503 | -1.6048 | -2.3031 | -2.5857 | 7.2213 | 7.0618 | 6.8676 | 6.657 | 6.3594 | 6.0469 | 5.7113 | 5.346 | 4.8641 | 4.3732 | 3.3895 | 2.3661 | 2.0245 | 1.5208 | 5.7424 | 5.398 | 5.0162 | 4.6247 | 4.0528 | 3.4657 | 2.8579 | 2.2126 | 1.4366 | 0.62212 | -1.3085 | -3.507 | -4.142 | -4.3887
|  | CHARLBURY | CT |  |  | 8.8073 | 8.6247 | 8.4124 | 8.1599 | 7.7951 | 7.4116 | 7.0166 | 6.5851 | 6.0862 | 5.2723 | 3.3388 | 0.21494 | -1.3984 | -1.5713 | 7.3013 | 7.1923 | 7.0585 | 6.8889 | 6.6943 | 6.4831 | 6.2609 | 6.0111 | 5.7011 | 5.2346 | 4.2064 | 2.7905 | 2.0245 | 1.6658 | 6.072 | 5.9053 | 5.7126 | 5.4851 | 5.15 | 4.7985 | 4.4371 | 4.0431 | 3.591 | 2.8497 | 1.0627 | -1.88 | -3.3177 | -3.4686
|  | CHARLBURY | LW |  |  | 8.4615 | 8.091 | 7.6775 | 7.253 | 6.6366 | 6.0028 | 5.3447 | 4.6443 | 3.7941 | 2.9052 | 0.83503 | -1.6048 | -2.3031 | -2.5857 | 7.2213 | 7.0618 | 6.8676 | 6.657 | 6.3594 | 6.0469 | 5.7113 | 5.346 | 4.8641 | 4.3732 | 3.3895 | 2.3661 | 2.1084 | 2.0098 | 5.7424 | 5.398 | 5.0162 | 4.6247 | 4.0528 | 3.4657 | 2.8579 | 2.2126 | 1.4366 | 0.62212 | -1.3085 | -3.507 | -4.142 | -4.3887
|  | CHARLBURY | ST |  |  | 8.902 | 8.7781 | 8.6393 | 8.4888 | 8.2627 | 8.0307 | 7.7865 | 7.5242 | 7.2391 | 6.9364 | 5.6963 | 3.5398 | 2.3689 | 1.5367 | 7.3815 | 7.3199 | 7.2449 | 7.1591 | 7.0375 | 6.911 | 6.7715 | 6.6172 | 6.4414 | 6.2732 | 5.4746 | 4.1251 | 3.4528 | 2.8477 | 6.1549 | 6.0399 | 5.9119 | 5.7738 | 5.566 | 5.3528 | 5.1291 | 4.8894 | 4.6296 | 4.3512 | 3.2269 | 1.2467 | 0.14161 | -0.64545
|  | CHARLBURY | SP |  |  | 8.943 | 8.8377 | 8.7227 | 8.6085 | 8.2556 | 7.8923 | 7.5357 | 7.1493 | 6.7556 | 6.2927 | 4.756 | 1.3601 | -0.43126 | -1.5582 | 7.3939 | 7.3323 | 7.2605 | 7.1882 | 7.0449 | 6.8932 | 6.7375 | 6.5446 | 6.3429 | 6.1152 | 5.3046 | 3.326 | 2.2932 | 1.5208 | 6.1935 | 6.0968 | 5.9918 | 5.8873 | 5.5571 | 5.2177 | 4.8843 | 4.5246 | 4.1586 | 3.7272 | 2.3043 | -0.81444 | -2.4697 | -3.464
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER | MINIMUM HEADROOM | SY 67309 93186 | YES | 5.5729 | 5.0742 | 4.5148 | 4.011 | 3.347 | 2.5379 | 1.7045 | 0.82374 | -0.85927 | -2.6634 | -8.4086 | -16.3228 | -17.1161 | -17.5456 | 8.8716 | 8.6348 | 8.3503 | 8.0907 | 7.7773 | 7.3626 | 6.9144 | 6.4286 | 5.4828 | 4.4731 | 1.53 | -2.4311 | -3.4063 | -4.2998 | 7.3091 | 6.8867 | 6.3926 | 5.9409 | 5.3586 | 4.6466 | 3.9003 | 3.1054 | 1.6062 | 0.012241 | -4.7898 | -11.3229 | -11.9643 | -12.3013
|  | CHARMINSTER | CT |  |  | 5.9883 | 5.7048 | 5.3914 | 5.091 | 4.7046 | 4.1766 | 3.621 | 3.0202 | 1.6812 | -0.027264 | -5.5771 | -14.4157 | -16.4734 | -16.8064 | 8.9907 | 8.8146 | 8.6176 | 8.4002 | 8.1712 | 7.8432 | 7.4884 | 7.096 | 6.2939 | 5.312 | 2.3087 | -2.1518 | -3.4063 | -4.2998 | 7.6235 | 7.3681 | 7.0822 | 6.7798 | 6.4186 | 5.9324 | 5.4162 | 4.8543 | 3.6654 | 2.1727 | -2.5019 | -9.7353 | -11.389 | -11.6539
|  | CHARMINSTER | LW |  |  | 5.5729 | 5.0742 | 4.5148 | 4.011 | 3.347 | 2.5379 | 1.7045 | 0.82374 | -0.85927 | -2.6634 | -8.4086 | -16.3228 | -17.1161 | -17.5456 | 8.8716 | 8.6348 | 8.3503 | 8.0907 | 7.7773 | 7.3626 | 6.9144 | 6.4286 | 5.4828 | 4.4731 | 1.53 | -2.4311 | -2.7676 | -2.9296 | 7.3091 | 6.8867 | 6.3926 | 5.9409 | 5.3586 | 4.6466 | 3.9003 | 3.1054 | 1.6062 | 0.012241 | -4.7898 | -11.3229 | -11.9643 | -12.3013
|  | CHARMINSTER | ST |  |  | 6.1668 | 5.9812 | 5.7831 | 5.6203 | 5.3998 | 5.0699 | 4.7258 | 4.3537 | 3.5415 | 2.6121 | -1.0822 | -6.9756 | -8.2634 | -9.0669 | 9.1252 | 9.0164 | 8.8958 | 8.7918 | 8.6558 | 8.4351 | 8.1973 | 7.9357 | 7.3956 | 6.8007 | 4.4152 | 0.72851 | -0.2565 | -1.2816 | 7.8195 | 7.6659 | 7.4964 | 7.3489 | 7.1441 | 6.8416 | 6.5237 | 6.1794 | 5.4611 | 4.6547 | 1.4612 | -3.513 | -4.5928 | -5.2498
|  | CHARMINSTER | SP |  |  | 6.2256 | 6.0654 | 5.8999 | 5.7724 | 5.478 | 5.0807 | 4.6709 | 4.2332 | 3.4401 | 2.4789 | -0.99981 | -7.4062 | -9.3361 | -10.4587 | 9.1445 | 9.0381 | 8.9224 | 8.8254 | 8.6803 | 8.4523 | 8.2059 | 7.9319 | 7.4201 | 6.8165 | 4.5657 | 0.37912 | -1.2818 | -3.1613 | 7.8658 | 7.7271 | 7.5815 | 7.4624 | 7.2137 | 6.8741 | 6.5212 | 6.1395 | 5.4562 | 4.6361 | 1.656 | -3.843 | -5.512 | -6.4458
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER | MINIMUM HEADROOM | SU 92198 07420 | NO | 4.4485 | 3.2976 | 1.9932 | 0.43245 | -1.4407 | -3.4348 | -5.5136 | -7.8272 | -10.2034 | -12.4302 | -17.4432 | -22.2126 | -24.3267 | -25.8803 | 11.386 | 10.6953 | 9.9234 | 9.0239 | 7.9978 | 6.9015 | 5.7385 | 4.4336 | 3.0034 | 1.6432 | -1.2136 | -3.8139 | -5.3712 | -6.6184 | 6.955 | 5.9695 | 4.8425 | 3.5004 | 1.8741 | 0.13665 | -1.6887 | -3.7258 | -5.8757 | -7.9096 | -12.4243 | -16.7501 | -18.5618 | -19.9318
|  | CHICHESTER | CT |  |  | 4.7179 | 3.7387 | 2.6656 | 1.2377 | -0.30504 | -1.9515 | -3.6454 | -5.5496 | -7.3522 | -9.5511 | -14.6516 | -20.7026 | -24.3267 | -25.8803 | 11.4552 | 10.8197 | 10.1489 | 9.269 | 8.3663 | 7.4053 | 6.4081 | 5.2849 | 4.1665 | 2.8046 | -0.20819 | -3.4797 | -5.3712 | -6.6184 | 7.1864 | 6.3529 | 5.4372 | 4.2081 | 2.876 | 1.4498 | -0.026745 | -1.691 | -3.3047 | -5.3128 | -9.9207 | -15.3584 | -18.5618 | -19.9318
|  | CHICHESTER | LW |  |  | 4.4485 | 3.2976 | 1.9932 | 0.43245 | -1.4407 | -3.4348 | -5.5136 | -7.8272 | -10.2034 | -12.4302 | -17.4432 | -22.2126 | -23.6552 | -24.3332 | 11.386 | 10.6953 | 9.9234 | 9.0239 | 7.9978 | 6.9015 | 5.7385 | 4.4336 | 3.0034 | 1.6432 | -1.2136 | -3.8139 | -4.4627 | -4.7573 | 6.955 | 5.9695 | 4.8425 | 3.5004 | 1.8741 | 0.13665 | -1.6887 | -3.7258 | -5.8757 | -7.9096 | -12.4243 | -16.7501 | -18.0239 | -18.6223
|  | CHICHESTER | ST |  |  | 5.2181 | 4.5895 | 3.9399 | 3.1566 | 2.2254 | 1.2466 | 0.24009 | -0.87437 | -1.8957 | -2.8272 | -6.1976 | -11.3347 | -13.6825 | -14.9655 | 11.8009 | 11.386 | 10.9686 | 10.4751 | 9.8788 | 9.2557 | 8.6082 | 7.8925 | 7.2083 | 6.5983 | 4.2292 | 0.52659 | -1.1183 | -2.2721 | 7.6682 | 7.1665 | 6.6479 | 6.0238 | 5.2491 | 4.4325 | 3.584 | 2.6431 | 1.7534 | 0.93356 | -2.158 | -6.9969 | -9.1342 | -10.2688
|  | CHICHESTER | SP |  |  | 5.2636 | 4.6627 | 4.0723 | 3.38 | 2.6132 | 1.8153 | 0.95258 | 0.004436 | -0.82673 | -1.6312 | -4.1832 | -9.4222 | -12.1836 | -13.2634 | 11.8163 | 11.4082 | 11.0185 | 10.5728 | 10.1019 | 9.6099 | 9.0598 | 8.447 | 7.8911 | 7.3638 | 5.5959 | 1.6358 | -0.6878 | -2.2452 | 7.7084 | 7.2304 | 6.7663 | 6.227 | 5.6138 | 4.9732 | 4.2627 | 3.4786 | 2.7711 | 2.0735 | -0.21447 | -5.1918 | -7.7858 | -8.7687
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL | MINIMUM HEADROOM | SY 65479 80511 | YES | 5.3467 | 4.9788 | 4.5043 | 3.9298 | 3.3959 | 2.8221 | 2.1991 | 1.5292 | 0.80182 | 0.039782 | -1.9816 | -4.4701 | -6.0151 | -7.0604 | 9.2086 | 9.1102 | 8.9908 | 8.7396 | 8.5486 | 8.2431 | 7.894 | 7.528 | 7.1222 | 6.6911 | 5.545 | 4.1266 | 2.9382 | 1.9123 | 7.5983 | 7.3203 | 6.9656 | 6.4664 | 6.0103 | 5.5218 | 4.9969 | 4.4414 | 3.8455 | 3.2199 | 1.4828 | -0.69327 | -2.1061 | -3.0442
|  | CHICKERELL | CT |  |  | 5.4358 | 5.1231 | 4.7468 | 4.2101 | 3.7951 | 3.3416 | 2.8546 | 2.3225 | 1.7868 | 1.0459 | -1.0427 | -4.1369 | -6.0151 | -7.0604 | 9.2086 | 9.1102 | 8.9983 | 8.7529 | 8.599 | 8.4291 | 8.1489 | 7.8414 | 7.5255 | 7.1002 | 5.8756 | 4.1266 | 2.9382 | 1.9123 | 7.6886 | 7.4651 | 7.1902 | 6.7352 | 6.3952 | 6.025 | 5.6269 | 5.2009 | 4.7737 | 4.169 | 2.4171 | -0.36236 | -2.1061 | -3.0442
|  | CHICKERELL | LW |  |  | 5.3467 | 4.9788 | 4.5043 | 3.9298 | 3.3959 | 2.8221 | 2.1991 | 1.5292 | 0.80182 | 0.039782 | -1.9816 | -4.4701 | -5.469 | -6.12 | 9.2138 | 9.1113 | 8.9908 | 8.7396 | 8.5486 | 8.2431 | 7.894 | 7.528 | 7.1222 | 6.6911 | 5.545 | 4.2113 | 3.7187 | 3.3912 | 7.5983 | 7.3203 | 6.9656 | 6.4664 | 6.0103 | 5.5218 | 4.9969 | 4.4414 | 3.8455 | 3.2199 | 1.4828 | -0.69327 | -1.5676 | -2.1137
|  | CHICKERELL | ST |  |  | 5.5382 | 5.3411 | 5.1119 | 4.8119 | 4.5777 | 4.3227 | 4.0468 | 3.7451 | 3.4506 | 3.1504 | 1.974 | -0.52567 | -1.7268 | -2.5229 | 9.2446 | 9.1723 | 9.0917 | 8.892 | 8.7936 | 8.6875 | 8.5723 | 8.4509 | 8.3058 | 8.1386 | 7.4035 | 5.6558 | 4.7748 | 3.853 | 7.7716 | 7.6436 | 7.4949 | 7.2302 | 7.0508 | 6.8562 | 6.6456 | 6.4243 | 6.2035 | 5.9646 | 5.0543 | 3.0618 | 1.9752 | 1.2587
|  | CHICKERELL | SP |  |  | 5.5612 | 5.367 | 5.1537 | 4.8749 | 4.6767 | 4.4631 | 4.2304 | 3.9756 | 3.7357 | 3.4786 | 2.5669 | 0.37519 | -0.91176 | -1.5387 | 9.2469 | 9.1756 | 9.0967 | 8.9004 | 8.8134 | 8.721 | 8.623 | 8.5286 | 8.4325 | 8.3131 | 7.699 | 6.0084 | 4.5688 | 2.8625 | 7.7921 | 7.6709 | 7.5375 | 7.2927 | 7.1358 | 6.9684 | 6.7879 | 6.6021 | 6.4218 | 6.2213 | 5.526 | 3.9009 | 2.8507 | 2.3417
AXMINSTER | YEOVIL BSP | CHILTON CANTELLO | MINIMUM HEADROOM | ST 57910 21616 | YES | 0.54657 | -0.16157 | -0.91176 | -1.7213 | -2.7667 | -3.8497 | -4.8483 | -5.6336 | -6.4013 | -7.0293 | -8.2613 | -11.3178 | -14.4245 | -15.1915 | 0.81626 | 0.53356 | 0.18162 | -0.22278 | -0.70528 | -1.2092 | -1.6938 | -2.1075 | -2.5564 | -2.9441 | -3.6918 | -4.7917 | -6.256 | -6.6897 | -1.5494 | -2.1931 | -2.8687 | -3.5913 | -4.499 | -5.4397 | -6.3106 | -7.0001 | -7.6857 | -8.252 | -9.3768 | -11.9985 | -14.7729 | -15.4533
|  | CHILTON CANTELLO | CT |  |  | 1.1062 | 0.68169 | 0.2376 | -0.29511 | -0.97263 | -1.6919 | -2.4063 | -3.0267 | -3.6446 | -4.2469 | -5.2981 | -6.5276 | -7.033 | -7.2215 | 0.96574 | 0.7957 | 0.61039 | 0.35532 | 0.0055198 | -0.36786 | -0.74256 | -1.083 | -1.4384 | -1.794 | -2.4534 | -3.2601 | -3.586 | -3.8035 | -0.99017 | -1.3523 | -1.7303 | -2.1799 | -2.7748 | -3.4054 | -4.0311 | -4.5624 | -5.0777 | -5.5782 | -6.5119 | -7.6838 | -8.167 | -8.3479
|  | CHILTON CANTELLO | LW |  |  | 0.54657 | -0.16157 | -0.91176 | -1.7213 | -2.7667 | -3.8497 | -4.8483 | -5.6336 | -6.4013 | -7.0293 | -8.2613 | -9.4875 | -9.6778 | -9.8603 | 0.81626 | 0.53356 | 0.18162 | -0.22278 | -0.70528 | -1.2092 | -1.6938 | -2.1075 | -2.5564 | -2.9441 | -3.6918 | -4.441 | -4.5152 | -4.5888 | -1.5494 | -2.1931 | -2.8687 | -3.5913 | -4.499 | -5.4397 | -6.3106 | -7.0001 | -7.6857 | -8.252 | -9.3768 | -10.4995 | -10.6628 | -10.8207
|  | CHILTON CANTELLO | ST |  |  | 1.206 | 0.87295 | 0.54443 | 0.18577 | -0.29055 | -0.79096 | -1.2973 | -1.8069 | -2.3571 | -2.907 | -4.6071 | -7.028 | -7.7012 | -7.9229 | 1.0171 | 0.8795 | 0.74255 | 0.5947 | 0.39294 | 0.12987 | -0.13887 | -0.4107 | -0.71002 | -1.0047 | -1.9404 | -3.3969 | -3.8964 | -4.1189 | -0.91097 | -1.1948 | -1.4714 | -1.7702 | -2.1753 | -2.6003 | -3.031 | -3.469 | -3.944 | -4.4349 | -5.9759 | -8.2504 | -8.9025 | -9.0956
|  | CHILTON CANTELLO | SP |  |  | 1.2687 | 0.97667 | 0.7 | 0.40181 | -0.26531 | -0.95357 | -1.6527 | -2.368 | -3.12 | -3.9748 | -6.4365 | -11.3178 | -14.4245 | -15.1915 | 1.0193 | 0.90864 | 0.79316 | 0.66412 | 0.41268 | 0.080775 | -0.25982 | -0.60286 | -0.9561 | -1.3429 | -2.452 | -4.7917 | -6.256 | -6.6897 | -0.84976 | -1.0912 | -1.3173 | -1.5585 | -2.1636 | -2.7855 | -3.4153 | -4.0494 | -4.6961 | -5.4387 | -7.6178 | -11.9985 | -14.7729 | -15.4533
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM | MINIMUM HEADROOM | SU 65105 55805 | YES | 16.5094 | 16.33 | 15.9856 | 15.2201 | 14.4519 | 13.6342 | 12.7467 | 11.9299 | 10.9235 | 9.9392 | 7.6942 | 4.8035 | 3.4323 | 2.5243 | 18.8038 | 18.6353 | 18.4327 | 18.2024 | 18.0234 | 17.6494 | 17.2088 | 16.7999 | 16.2872 | 15.7816 | 14.6034 | 13.0547 | 11.772 | 10.8008 | 17.2079 | 16.8303 | 16.2955 | 15.6311 | 14.9421 | 14.2065 | 13.4013 | 12.6414 | 11.6873 | 10.7513 | 8.645 | 5.9634 | 4.821 | 4.0317
|  | CHINEHAM | CT |  |  | 16.5094 | 16.33 | 16.0616 | 15.4265 | 14.8325 | 14.1993 | 13.5582 | 12.976 | 12.324 | 11.339 | 9.0739 | 5.5395 | 3.4323 | 2.5243 | 18.8038 | 18.6353 | 18.4327 | 18.2024 | 18.0297 | 17.7915 | 17.4432 | 17.1189 | 16.7532 | 16.24 | 15.022 | 13.0547 | 11.772 | 10.8008 | 17.258 | 16.9373 | 16.4266 | 15.8035 | 15.2708 | 14.7015 | 14.1208 | 13.5733 | 12.9562 | 12.0222 | 9.9038 | 6.6795 | 4.821 | 4.0317
|  | CHINEHAM | LW |  |  | 16.5253 | 16.3387 | 15.9856 | 15.2201 | 14.4519 | 13.6342 | 12.7467 | 11.9299 | 10.9235 | 9.9392 | 7.6942 | 4.8035 | 3.8917 | 3.5435 | 18.8117 | 18.6393 | 18.4434 | 18.2147 | 18.0234 | 17.6494 | 17.2088 | 16.7999 | 16.2872 | 15.7816 | 14.6034 | 13.1207 | 12.7049 | 12.5406 | 17.2079 | 16.8303 | 16.2955 | 15.6311 | 14.9421 | 14.2065 | 13.4013 | 12.6414 | 11.6873 | 10.7513 | 8.645 | 5.9634 | 5.1637 | 4.8658
|  | CHINEHAM | ST |  |  | 16.5923 | 16.4622 | 16.2569 | 16.0088 | 15.8561 | 15.6944 | 15.4332 | 15.146 | 14.8127 | 14.4806 | 12.9679 | 10.059 | 8.6286 | 7.8739 | 18.875 | 18.7498 | 18.6071 | 18.4443 | 18.3329 | 18.2158 | 18.0898 | 17.9794 | 17.8461 | 17.7115 | 16.8632 | 15.0208 | 13.9137 | 12.9923 | 17.5135 | 17.3481 | 17.0765 | 16.7329 | 16.4666 | 16.1793 | 15.8688 | 15.5977 | 15.28 | 14.9645 | 13.4856 | 10.7198 | 9.4312 | 8.7763
|  | CHINEHAM | SP |  |  | 16.5971 | 16.4699 | 16.2731 | 16.0378 | 15.9024 | 15.7614 | 15.6148 | 15.4739 | 15.1962 | 14.9108 | 13.8708 | 10.981 | 9.369 | 8.8137 | 18.8787 | 18.7552 | 18.6189 | 18.4661 | 18.3684 | 18.2675 | 18.1601 | 18.069 | 17.9631 | 17.8584 | 17.3254 | 15.4971 | 14.1322 | 12.9697 | 17.5368 | 17.3797 | 17.1484 | 16.8599 | 16.6387 | 16.4027 | 16.1469 | 15.9231 | 15.6627 | 15.3936 | 14.3931 | 11.5733 | 10.0465 | 9.5498
COWLEY GSP | YARNTON BSP | CHIPPING NORTON | MINIMUM HEADROOM | SP 31382 26792 | NO | 4.194 | 3.4873 | 2.6676 | 1.8288 | 0.75509 | -0.36322 | -1.4414 | -2.5596 | -3.7811 | -5.0036 | -7.9381 | -11.0918 | -11.8936 | -12.1476 | 7.9945 | 7.654 | 7.2563 | 6.8537 | 6.3751 | 5.8809 | 5.3883 | 4.87 | 4.2519 | 3.6272 | 2.2225 | 0.81672 | 0.491 | -0.50323 | 5.7602 | 5.1189 | 4.4027 | 3.67 | 2.7099 | 1.7294 | 0.78612 | -0.20012 | -1.2927 | -2.3929 | -5.0286 | -7.8644 | -8.5918 | -8.8234
|  | CHIPPING NORTON | CT |  |  | 4.6689 | 4.2072 | 3.6649 | 3.0536 | 2.2934 | 1.5025 | 0.76022 | -0.024613 | -0.85185 | -1.9242 | -4.4951 | -8.4591 | -10.1141 | -10.3168 | 8.1183 | 7.8441 | 7.5392 | 7.1862 | 6.8024 | 6.4013 | 6.0158 | 5.6014 | 5.1446 | 4.5776 | 3.2904 | 1.5501 | 0.62793 | 0.093158 | 6.2366 | 5.8329 | 5.3688 | 4.8448 | 4.179 | 3.487 | 2.8327 | 2.1394 | 1.4076 | 0.44133 | -1.915 | -5.5099 | -6.9657 | -7.1441
|  | CHIPPING NORTON | LW |  |  | 4.194 | 3.4873 | 2.6676 | 1.8288 | 0.75509 | -0.36322 | -1.4414 | -2.5596 | -3.7811 | -5.0036 | -7.9381 | -11.0918 | -11.8936 | -12.1476 | 7.9945 | 7.654 | 7.2563 | 6.8537 | 6.3751 | 5.8809 | 5.3883 | 4.87 | 4.2519 | 3.6272 | 2.2225 | 0.81672 | 0.491 | 0.38956 | 5.7602 | 5.1189 | 4.4027 | 3.67 | 2.7099 | 1.7294 | 0.78612 | -0.20012 | -1.2927 | -2.3929 | -5.0286 | -7.8644 | -8.5918 | -8.8234
|  | CHIPPING NORTON | ST |  |  | 4.7667 | 4.4073 | 4.0236 | 3.6409 | 3.139 | 2.6246 | 2.1395 | 1.6346 | 1.1163 | 0.61845 | -0.9228 | -3.7018 | -5.1689 | -6.1849 | 8.1957 | 7.9891 | 7.7793 | 7.5708 | 7.301 | 7.0253 | 6.7611 | 6.4822 | 6.1887 | 5.9219 | 5.008 | 3.3397 | 2.5296 | 1.7569 | 6.3142 | 6.0022 | 5.6905 | 5.3746 | 4.9492 | 4.5139 | 4.0979 | 3.6633 | 3.2143 | 2.7741 | 1.3851 | -1.1732 | -2.5429 | -3.4836
|  | CHIPPING NORTON | SP |  |  | 4.8283 | 4.4965 | 4.1583 | 3.8274 | 3.196 | 2.5468 | 1.9169 | 1.2741 | 0.63184 | -0.058931 | -2.1311 | -6.3772 | -8.8754 | -10.3027 | 8.2167 | 8.0119 | 7.8156 | 7.6244 | 7.3487 | 7.0598 | 6.7741 | 6.4756 | 6.1716 | 5.8594 | 4.8916 | 2.531 | 0.91411 | -0.50323 | 6.3735 | 6.0917 | 5.8199 | 5.5507 | 4.9982 | 4.4313 | 3.8753 | 3.3072 | 2.7376 | 2.1132 | 0.25878 | -3.5951 | -5.8421 | -7.1405
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE | MINIMUM HEADROOM | SU 80226 89155 | YES | 3.6497 | 3.5168 | 3.3809 | 3.239 | 3.0451 | 2.8448 | 2.6304 | 2.3773 | 2.09 | 1.867 | 1.3381 | 0.75823 | 0.58972 | 0.49236 | 2.6036 | 2.5625 | 2.519 | 2.4718 | 2.4091 | 2.3419 | 2.2661 | 2.1806 | 2.0844 | 1.9825 | 1.6731 | 1.3164 | 1.2257 | 1.1726 | 2.3143 | 2.1927 | 2.0686 | 1.9378 | 1.7623 | 1.5802 | 1.382 | 1.1407 | 0.86395 | 0.6585 | 0.20515 | -0.29349 | -0.43643 | -0.51796
|  | CHISBRIDGE | CT |  |  | 3.7568 | 3.6815 | 3.5956 | 3.5069 | 3.3901 | 3.2664 | 3.1203 | 2.9585 | 2.7912 | 2.5635 | 2.158 | 1.4848 | 1.0304 | 0.82646 | 2.6279 | 2.6021 | 2.5721 | 2.5392 | 2.4959 | 2.4507 | 2.3987 | 2.3413 | 2.2838 | 2.2026 | 1.9748 | 1.5754 | 1.3882 | 1.2918 | 2.4018 | 2.3303 | 2.2484 | 2.1636 | 2.0547 | 1.939 | 1.8016 | 1.6488 | 1.4905 | 1.2753 | 0.9058 | 0.3077 | -0.073634 | -0.24606
|  | CHISBRIDGE | LW |  |  | 3.6497 | 3.5168 | 3.3809 | 3.239 | 3.0451 | 2.8448 | 2.6304 | 2.3773 | 2.09 | 1.867 | 1.3381 | 0.75823 | 0.58972 | 0.49236 | 2.6036 | 2.5625 | 2.519 | 2.4718 | 2.4091 | 2.3419 | 2.2661 | 2.1806 | 2.0844 | 1.9825 | 1.6731 | 1.3164 | 1.2257 | 1.1726 | 2.3143 | 2.1927 | 2.0686 | 1.9378 | 1.7623 | 1.5802 | 1.382 | 1.1407 | 0.86395 | 0.6585 | 0.20515 | -0.29349 | -0.43643 | -0.51796
|  | CHISBRIDGE | ST |  |  | 3.827 | 3.7949 | 3.7532 | 3.7062 | 3.641 | 3.5722 | 3.4997 | 3.415 | 3.3224 | 3.2257 | 2.7635 | 2.2402 | 1.9332 | 1.739 | 2.6519 | 2.6395 | 2.6263 | 2.6123 | 2.5909 | 2.5663 | 2.5397 | 2.509 | 2.4734 | 2.4268 | 2.2427 | 1.8475 | 1.6285 | 1.5253 | 2.4693 | 2.4393 | 2.3997 | 2.3548 | 2.2939 | 2.2294 | 2.1612 | 2.0809 | 1.9932 | 1.9025 | 1.4599 | 0.97169 | 0.69374 | 0.51961
|  | CHISBRIDGE | SP |  |  | 3.8392 | 3.8155 | 3.7886 | 3.7588 | 3.6963 | 3.6372 | 3.5806 | 3.5086 | 3.4348 | 3.3289 | 2.9461 | 2.0671 | 1.6047 | 1.3034 | 2.655 | 2.6456 | 2.6356 | 2.6263 | 2.6056 | 2.5857 | 2.5653 | 2.5422 | 2.5172 | 2.4787 | 2.3526 | 2.0011 | 1.6962 | 1.5632 | 2.4797 | 2.4571 | 2.4315 | 2.4028 | 2.3451 | 2.2905 | 2.2384 | 2.1713 | 2.1023 | 2.0044 | 1.6465 | 0.82028 | 0.40185 | 0.13619
MINETY GSP | TOOTHILL BSP | CHISLEDON | MINIMUM HEADROOM | SU 18894 79934 | YES | 6.2769 | 1.8198 | -3.0916 | -8.1914 | -9.3852 | -10.7842 | -12.249 | -13.9249 | -15.8479 | -17.7531 | -23.7236 | -27.0395 | -27.8285 | -28.1903 | 6.4603 | 1.1494 | -4.4018 | -10.0516 | -10.6814 | -11.4129 | -12.1787 | -13.054 | -14.0737 | -15.0749 | -18.0993 | -19.8324 | -20.3757 | -20.741 | 5.7991 | 0.37929 | -5.4041 | -11.3441 | -12.3281 | -13.4789 | -14.6907 | -16.0829 | -17.6991 | -19.2847 | -24.1422 | -26.867 | -27.4785 | -27.7763
|  | CHISLEDON | CT |  |  | 6.3307 | 1.9131 | -2.9643 | -8.031 | -9.1389 | -10.4521 | -11.8191 | -13.3901 | -15.1615 | -17.0858 | -23.1428 | -26.8559 | -27.8285 | -28.1903 | 6.4705 | 1.1704 | -4.3779 | -10.0264 | -10.6231 | -11.3225 | -12.0482 | -12.8789 | -13.8158 | -14.8385 | -17.9141 | -19.8324 | -20.3757 | -20.741 | 5.8301 | 0.43965 | -5.3183 | -11.2248 | -12.1307 | -13.2071 | -14.3319 | -15.6295 | -17.0977 | -18.7052 | -23.6399 | -26.6782 | -27.4785 | -27.7763
|  | CHISLEDON | LW |  |  | 6.2769 | 1.8198 | -3.0916 | -8.1914 | -9.3852 | -10.7842 | -12.249 | -13.9249 | -15.8479 | -17.7531 | -23.7236 | -27.0395 | -27.5063 | -27.63 | 6.4603 | 1.1494 | -4.4018 | -10.0516 | -10.6814 | -11.4129 | -12.1787 | -13.054 | -14.0737 | -15.0749 | -18.0993 | -19.7941 | -20.0082 | -20.0641 | 5.7991 | 0.37929 | -5.4041 | -11.3441 | -12.3281 | -13.4789 | -14.6907 | -16.0829 | -17.6991 | -19.2847 | -24.1422 | -26.867 | -27.2529 | -27.3561
|  | CHISLEDON | ST |  |  | 6.4533 | 2.1654 | -2.411 | -7.0801 | -7.795 | -8.6349 | -9.4964 | -10.4989 | -11.6163 | -12.7595 | -16.8848 | -19.4803 | -20.036 | -20.33 | 6.5469 | 1.3188 | -4.0758 | -9.5244 | -9.9465 | -10.4476 | -10.9633 | -11.5456 | -12.2036 | -12.8679 | -15.3111 | -16.9525 | -17.3722 | -17.7064 | 5.957 | 0.69052 | -4.802 | -10.373 | -10.9674 | -11.6862 | -12.4225 | -13.2532 | -14.1779 | -15.1179 | -18.5577 | -20.7491 | -21.1976 | -21.4264
|  | CHISLEDON | SP |  |  | 6.4629 | 2.1878 | -2.338 | -6.9383 | -7.5234 | -8.2078 | -8.9623 | -9.8201 | -10.77 | -11.7594 | -15.1604 | -17.7166 | -18.2967 | -18.5023 | 6.5488 | 1.3261 | -4.0421 | -9.4551 | -9.7999 | -10.2041 | -10.6578 | -11.1769 | -11.7439 | -12.3411 | -14.4368 | -16.1999 | -16.731 | -17.1337 | 5.9632 | 0.7073 | -4.7357 | -10.2401 | -10.7001 | -11.2679 | -11.923 | -12.6593 | -13.4558 | -14.2844 | -17.149 | -19.413 | -19.9063 | -20.0689
BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM | MINIMUM HEADROOM | SU 97173 63223 | YES | 2.6044 | 2.2955 | 1.9924 | 1.6652 | 1.1062 | 0.52186 | -0.10361 | -0.77367 | -1.5493 | -2.2801 | -4.1897 | -6.8234 | -8.6334 | -9.9416 | 4.1949 | 3.9697 | 3.7424 | 3.4829 | 3.1305 | 2.7509 | 2.3053 | 1.8041 | 1.1328 | 0.6006 | -0.43161 | -1.7508 | -2.9902 | -3.9443 | 1.3051 | 0.98232 | 0.64518 | 0.27231 | -0.30382 | -0.91281 | -1.5908 | -2.3337 | -3.2554 | -4.047 | -5.84 | -8.2417 | -9.7439 | -10.8464
|  | CHOBHAM | CT |  |  | 2.8029 | 2.6126 | 2.4143 | 2.1973 | 1.8629 | 1.5053 | 1.1337 | 0.71903 | 0.26107 | -0.47211 | -2.2887 | -5.91 | -8.6334 | -9.9416 | 4.2169 | 4.0227 | 3.8033 | 3.5577 | 3.2863 | 2.9866 | 2.6529 | 2.2582 | 1.8013 | 1.2044 | 0.1135 | -1.6908 | -2.9902 | -3.9443 | 1.4648 | 1.2312 | 0.97394 | 0.6893 | 0.31494 | -0.09131 | -0.52711 | -1.0299 | -1.6334 | -2.5039 | -4.2463 | -7.4165 | -9.7439 | -10.8464
|  | CHOBHAM | LW |  |  | 2.6044 | 2.2955 | 1.9924 | 1.6652 | 1.1062 | 0.52186 | -0.10361 | -0.77367 | -1.5493 | -2.2801 | -4.1897 | -6.8234 | -7.8894 | -8.5502 | 4.1949 | 3.9697 | 3.7424 | 3.4829 | 3.1305 | 2.7509 | 2.3053 | 1.8041 | 1.1328 | 0.6006 | -0.43161 | -1.7508 | -2.1881 | -2.4618 | 1.3051 | 0.98232 | 0.64518 | 0.27231 | -0.30382 | -0.91281 | -1.5908 | -2.3337 | -3.2554 | -4.047 | -5.84 | -8.2417 | -9.1542 | -9.7173
|  | CHOBHAM | ST |  |  | 2.9529 | 2.8523 | 2.7491 | 2.6359 | 2.4799 | 2.3151 | 2.1349 | 1.937 | 1.7122 | 1.4519 | 0.30002 | -1.8792 | -3.3578 | -4.4082 | 4.3949 | 4.3016 | 4.192 | 4.0665 | 3.9145 | 3.7536 | 3.5669 | 3.3555 | 3.1082 | 2.8725 | 1.6152 | -0.11362 | -1.1103 | -1.9607 | 1.6545 | 1.5497 | 1.4331 | 1.2957 | 1.1096 | 0.91396 | 0.69308 | 0.44666 | 0.16314 | -0.13302 | -1.6751 | -3.932 | -5.1824 | -5.9717
|  | CHOBHAM | SP |  |  | 2.9785 | 2.8966 | 2.8204 | 2.7364 | 2.536 | 2.3369 | 2.1343 | 1.9006 | 1.6631 | 1.3677 | 0.33878 | -2.2014 | -3.6887 | -4.4597 | 4.4035 | 4.3146 | 4.2246 | 4.1199 | 3.9828 | 3.8398 | 3.6883 | 3.5024 | 3.298 | 3.0635 | 2.1343 | -0.21121 | -1.4164 | -2.3728 | 1.6777 | 1.5888 | 1.5021 | 1.4008 | 1.1963 | 0.99068 | 0.77904 | 0.52639 | 0.26226 | -0.059253 | -1.2513 | -4.1973 | -5.5638 | -6.2455
COWLEY GSP | DRAYTON BSP | CHOLSEY | MINIMUM HEADROOM | SU 58223 84685 | NO | 8.126 | 7.8334 | 7.5629 | 7.3101 | 6.9154 | 6.5019 | 6.0571 | 5.5911 | 4.9628 | 4.3632 | 3.1629 | 1.6677 | 0.99808 | 0.37874 | 9.5017 | 9.3569 | 9.2189 | 9.0884 | 8.9043 | 8.7064 | 8.4851 | 8.251 | 7.8999 | 7.5735 | 7.0317 | 6.3974 | 6.0496 | 5.7325 | 7.0984 | 6.8489 | 6.6087 | 6.3798 | 6.0345 | 5.6701 | 5.2729 | 4.8548 | 4.2685 | 3.703 | 2.599 | 1.2375 | 0.66193 | 0.11798
|  | CHOLSEY | CT |  |  | 8.2727 | 8.0624 | 7.877 | 7.6915 | 7.4381 | 7.1643 | 6.878 | 6.5613 | 6.1821 | 5.5704 | 4.3422 | 2.38 | 0.99808 | 0.37874 | 9.5374 | 9.4158 | 9.3039 | 9.1869 | 9.0517 | 8.9025 | 8.7417 | 8.5604 | 8.3332 | 7.987 | 7.3874 | 6.5838 | 6.0496 | 5.7325 | 7.2041 | 7.0183 | 6.8457 | 6.6658 | 6.4408 | 6.1912 | 5.9274 | 5.633 | 5.2736 | 4.7022 | 3.6182 | 1.8821 | 0.66193 | 0.11798
|  | CHOLSEY | LW |  |  | 8.126 | 7.8334 | 7.5629 | 7.3101 | 6.9154 | 6.5019 | 6.0571 | 5.5911 | 4.9628 | 4.3632 | 3.1629 | 1.6677 | 1.1555 | 0.86193 | 9.5017 | 9.3569 | 9.2189 | 9.0884 | 8.9043 | 8.7064 | 8.4851 | 8.251 | 7.8999 | 7.5735 | 7.0317 | 6.3974 | 6.2175 | 6.1186 | 7.0984 | 6.8489 | 6.6087 | 6.3798 | 6.0345 | 5.6701 | 5.2729 | 4.8548 | 4.2685 | 3.703 | 2.599 | 1.2375 | 0.78353 | 0.52625
|  | CHOLSEY | ST |  |  | 8.4117 | 8.2926 | 8.1945 | 8.1063 | 7.9742 | 7.8294 | 7.6766 | 7.5128 | 7.3263 | 7.1281 | 6.2252 | 4.7865 | 4.0568 | 3.5619 | 9.6227 | 9.554 | 9.4956 | 9.4418 | 9.3662 | 9.2818 | 9.1909 | 9.0906 | 8.9739 | 8.86 | 8.2978 | 7.4694 | 7.1168 | 6.8436 | 7.3395 | 7.2397 | 7.1521 | 7.0702 | 6.9501 | 6.8172 | 6.6751 | 6.5206 | 6.3427 | 6.1576 | 5.2844 | 3.9406 | 3.3187 | 2.9129
|  | CHOLSEY | SP |  |  | 8.435 | 8.3231 | 8.2391 | 8.1738 | 8.0321 | 7.8757 | 7.7168 | 7.5448 | 7.3596 | 7.1339 | 6.3178 | 4.3266 | 3.4404 | 2.9871 | 9.6308 | 9.5618 | 9.5077 | 9.4643 | 9.3959 | 9.3171 | 9.2375 | 9.1464 | 9.0452 | 8.9303 | 8.4837 | 7.2977 | 6.7985 | 6.4851 | 7.3574 | 7.2609 | 7.1841 | 7.1223 | 7.0047 | 6.869 | 6.7307 | 6.5775 | 6.4107 | 6.2108 | 5.469 | 3.6018 | 2.8125 | 2.4051
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH | MINIMUM HEADROOM | SZ 15698 93141 | YES | 6.0672 | 5.4662 | 4.7088 | 3.8824 | 2.605 | 1.2899 | -0.14216 | -1.6644 | -3.5026 | -5.5439 | -10.6901 | -16.6632 | -21.337 | -24.107 | 14.082 | 13.7269 | 13.2518 | 12.7261 | 12.0187 | 11.2741 | 10.4322 | 9.5282 | 8.302 | 6.9554 | 3.7989 | -0.30482 | -3.9961 | -7.5771 | 9.5809 | 9.0467 | 8.3453 | 7.5694 | 6.387 | 5.1603 | 3.8167 | 2.3912 | 0.65559 | -1.2209 | -5.9429 | -11.4419 | -15.5322 | -17.9305
|  | CHRISTCHURCH | CT |  |  | 6.3522 | 5.9302 | 5.4394 | 4.743 | 3.8853 | 3.0138 | 2.0592 | 1.0002 | -0.24201 | -2.2844 | -7.768 | -15.6683 | -21.337 | -24.107 | 14.1438 | 13.829 | 13.4607 | 12.9277 | 12.3488 | 11.747 | 11.0777 | 10.3335 | 9.4239 | 8.0533 | 4.4339 | -0.30482 | -3.9961 | -7.5771 | 9.8445 | 9.4577 | 8.9942 | 8.3272 | 7.5165 | 6.6851 | 5.7728 | 4.7953 | 3.6732 | 1.821 | -3.1867 | -10.5291 | -15.5322 | -17.9305
|  | CHRISTCHURCH | LW |  |  | 6.0672 | 5.4662 | 4.7088 | 3.8824 | 2.605 | 1.2899 | -0.14216 | -1.6644 | -3.5026 | -5.5439 | -10.6901 | -16.6632 | -19.0674 | -20.372 | 14.082 | 13.7269 | 13.2518 | 12.7261 | 12.0187 | 11.2741 | 10.4322 | 9.5282 | 8.302 | 6.9554 | 3.7989 | 0.52449 | -0.53092 | -1.096 | 9.5809 | 9.0467 | 8.3453 | 7.5694 | 6.387 | 5.1603 | 3.8167 | 2.3912 | 0.65559 | -1.2209 | -5.9429 | -11.4419 | -13.6119 | -14.7234
|  | CHRISTCHURCH | ST |  |  | 6.6725 | 6.4742 | 6.2417 | 5.9756 | 5.6104 | 5.2371 | 4.8161 | 4.3597 | 3.8191 | 3.2264 | 0.47316 | -5.8915 | -9.1004 | -11.1429 | 14.3553 | 14.1856 | 13.9853 | 13.7553 | 13.4511 | 13.1317 | 12.7676 | 12.375 | 11.908 | 11.4217 | 9.1756 | 3.9845 | 0.832 | -2.5299 | 10.1291 | 9.958 | 9.7568 | 9.5071 | 9.1529 | 8.7846 | 8.369 | 7.9237 | 7.396 | 6.8265 | 4.3407 | -1.5294 | -4.4108 | -6.2272
|  | CHRISTCHURCH | SP |  |  | 6.7251 | 6.5176 | 6.2986 | 6.0516 | 5.7616 | 5.4802 | 5.184 | 4.829 | 4.4419 | 3.9573 | 2.0766 | -3.5187 | -6.9668 | -8.3097 | 14.3744 | 14.1835 | 13.9746 | 13.7387 | 13.4902 | 13.2329 | 12.9553 | 12.6332 | 12.2711 | 11.8053 | 9.999 | 4.5038 | -0.86011 | -7.3977 | 10.1767 | 10.0001 | 9.8041 | 9.5691 | 9.2898 | 9.0119 | 8.7192 | 8.3747 | 7.9984 | 7.5343 | 5.7834 | 0.71174 | -2.5328 | -3.7208
LALEHAM | EAST BEDFONT A | CHURCH ROAD | MINIMUM HEADROOM | TQ 06820 71722 | YES | 1.4776 | 1.1227 | 0.65785 | -0.037128 | -1.043 | -1.939 | -2.9082 | -3.9635 | -5.3029 | -6.7718 | -10.1637 | -14.9455 | -18.9409 | -21.634 | 2.1138 | 1.9164 | 1.6484 | 1.2135 | 0.63648 | 0.10909 | -0.4799 | -1.1311 | -2.0055 | -2.9747 | -5.0329 | -8.2606 | -11.3065 | -14.526 | -0.79357 | -1.1337 | -1.5798 | -2.2245 | -3.1487 | -3.9807 | -4.8866 | -5.8756 | -7.1442 | -8.5397 | -11.7 | -16.0041 | -19.3622 | -21.632
|  | CHURCH ROAD | CT |  |  | 1.6079 | 1.3488 | 1.0373 | 0.38344 | -0.37731 | -1.0014 | -1.67 | -2.4065 | -3.3103 | -4.7768 | -8.4148 | -14.3762 | -18.9409 | -21.634 | 2.1557 | 1.9873 | 1.7764 | 1.3113 | 0.81317 | 0.37412 | -0.10478 | -0.63677 | -1.2952 | -2.2914 | -4.6758 | -8.2606 | -11.3065 | -14.2792 | -0.66501 | -0.9111 | -1.2078 | -1.8112 | -2.5207 | -3.1221 | -3.767 | -4.4773 | -5.3396 | -6.7275 | -10.1172 | -15.4318 | -19.3622 | -21.632
|  | CHURCH ROAD | LW |  |  | 1.4776 | 1.1227 | 0.65785 | -0.037128 | -1.043 | -1.939 | -2.9082 | -3.9635 | -5.3029 | -6.7718 | -10.1637 | -14.9455 | -17.5829 | -19.3071 | 2.1138 | 1.9164 | 1.6484 | 1.2135 | 0.63648 | 0.10909 | -0.4799 | -1.1311 | -2.0055 | -2.9747 | -5.0329 | -7.6746 | -8.9374 | -9.8015 | -0.79357 | -1.1337 | -1.5798 | -2.2245 | -3.1487 | -3.9807 | -4.8866 | -5.8756 | -7.1442 | -8.5397 | -11.7 | -16.0041 | -18.2331 | -19.6537
|  | CHURCH ROAD | ST |  |  | 1.8258 | 1.7055 | 1.5548 | 1.2603 | 0.87292 | 0.59105 | 0.27758 | -0.075585 | -0.4961 | -0.94258 | -2.9711 | -7.5304 | -10.2628 | -12.2786 | 2.2818 | 2.1936 | 2.0861 | 1.8933 | 1.6391 | 1.4152 | 1.1572 | 0.86525 | 0.51703 | 0.15107 | -1.5284 | -5.1915 | -7.6912 | -10.3979 | -0.45252 | -0.56307 | -0.7028 | -0.95646 | -1.3003 | -1.567 | -1.8649 | -2.2007 | -2.6009 | -3.0261 | -4.9651 | -9.2495 | -11.6393 | -13.3122
|  | CHURCH ROAD | SP |  |  | 1.8643 | 1.7337 | 1.584 | 1.3188 | 1.0045 | 0.77692 | 0.53892 | 0.25943 | -0.071997 | -0.43727 | -1.8674 | -6.2491 | -8.9932 | -10.5087 | 2.2987 | 2.2013 | 2.0888 | 1.9055 | 1.6962 | 1.5208 | 1.3228 | 1.0882 | 0.80522 | 0.46018 | -0.91644 | -5.1017 | -9.2327 | -14.526 | -0.41541 | -0.53574 | -0.67434 | -0.89959 | -1.1725 | -1.3865 | -1.6113 | -1.8755 | -2.1887 | -2.5362 | -3.8972 | -8.0272 | -10.5363 | -11.809
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN | MINIMUM HEADROOM | SP 02761 00827 | NO | 8.5277 | 8.2886 | 8.0724 | 7.8813 | 7.1163 | 6.1155 | 5.07 | 3.9721 | 2.7161 | 1.3037 | -2.573 | -7.3508 | -9.7842 | -10.8739 | 10.0458 | 9.818 | 9.64 | 9.4255 | 8.9915 | 8.5477 | 8.0761 | 7.558 | 6.8972 | 6.1584 | 4.1988 | 1.8174 | -1.0786 | -4.6568 | 5.4631 | 4.8711 | 4.2532 | 3.6426 | 2.7543 | 1.8445 | 0.89554 | -0.10039 | -1.2344 | -2.5119 | -6.0523 | -10.4332 | -12.6065 | -13.565
|  | CIRENCESTER TOWN | CT |  |  | 8.5277 | 8.2886 | 8.0835 | 7.8956 | 7.7278 | 7.5572 | 7.3691 | 6.841 | 6.079 | 4.8209 | 1.2823 | -5.1552 | -9.7842 | -10.8739 | 10.0458 | 9.818 | 9.64 | 9.4743 | 9.3251 | 9.1757 | 8.8854 | 8.4908 | 8.0148 | 7.3071 | 5.3178 | 1.8174 | -1.0786 | -3.2724 | 5.6579 | 5.4356 | 5.2195 | 4.8359 | 4.291 | 3.73 | 3.1531 | 2.535 | 1.8513 | 0.7176 | -2.4924 | -8.4082 | -12.6065 | -13.565
|  | CIRENCESTER TOWN | LW |  |  | 8.5383 | 8.2902 | 8.0724 | 7.8813 | 7.1163 | 6.1155 | 5.07 | 3.9721 | 2.7161 | 1.3037 | -2.573 | -7.3508 | -8.9004 | -10.0458 | 10.0627 | 9.8367 | 9.6583 | 9.4255 | 8.9915 | 8.5477 | 8.0761 | 7.558 | 6.8972 | 6.1584 | 4.1988 | 1.9073 | 1.2352 | 0.76296 | 5.4631 | 4.8711 | 4.2532 | 3.6426 | 2.7543 | 1.8445 | 0.89554 | -0.10039 | -1.2344 | -2.5119 | -6.0523 | -10.4332 | -11.8465 | -12.8699
|  | CIRENCESTER TOWN | ST |  |  | 8.6063 | 8.4133 | 8.2674 | 8.1573 | 8.0557 | 7.9556 | 7.8429 | 7.7137 | 7.5538 | 7.3793 | 5.7036 | 1.7249 | -0.66488 | -2.2782 | 10.1078 | 9.9162 | 9.7848 | 9.6806 | 9.5832 | 9.489 | 9.3829 | 9.2623 | 9.0273 | 8.748 | 7.5616 | 4.7234 | 2.552 | 0.14011 | 5.7339 | 5.556 | 5.4237 | 5.2402 | 4.9395 | 4.6301 | 4.2997 | 3.9438 | 3.5515 | 3.1188 | 1.4988 | -2.1185 | -4.3185 | -5.794
|  | CIRENCESTER TOWN | SP |  |  | 8.6096 | 8.4173 | 8.2723 | 8.1685 | 8.0839 | 8.0042 | 7.9187 | 7.7244 | 7.1147 | 6.4154 | 4.1573 | -0.8214 | -3.9184 | -5.6231 | 10.1086 | 9.9161 | 9.7829 | 9.6807 | 9.5947 | 9.5132 | 9.3068 | 8.9994 | 8.6751 | 8.2968 | 6.9166 | 3.369 | -0.17523 | -4.6568 | 5.7371 | 5.56 | 5.4286 | 5.3327 | 4.8727 | 4.3646 | 3.8504 | 3.3078 | 2.7529 | 2.1152 | 0.064352 | -4.4426 | -7.2799 | -8.8396
IVER 132KV | CIPPENHAM | CLARENCE ROAD | MINIMUM HEADROOM | SU 95654 76652 | YES | 10.2826 | 9.4879 | 34.3841 | 33.3804 | 31.6994 | 29.8392 | 27.8005 | 25.5791 | 23.0215 | 20.2511 | 12.8457 | 4.2569 | 0.022566 | -2.9248 | 21.2435 | 20.8371 | 44.7748 | 44.2513 | 43.4316 | 42.4672 | 41.3553 | 40.0759 | 38.506 | 36.7058 | 31.9838 | 25.1817 | 19.4864 | 10.6618 | 15.3529 | 14.593 | 38.1218 | 37.1457 | 35.5955 | 33.8778 | 31.9688 | 29.8702 | 27.3834 | 24.6737 | 17.5635 | 9.5233 | 6.3495 | 3.9367
|  | CLARENCE ROAD | CT |  |  | 10.6857 | 10.1546 | 35.2998 | 34.5099 | 33.378 | 32.0959 | 30.7592 | 29.2864 | 27.5991 | 24.9246 | 17.6648 | 6.7495 | 0.022566 | -2.9248 | 21.3201 | 20.9507 | 44.9074 | 44.376 | 43.6667 | 42.8286 | 41.8702 | 40.8024 | 39.5544 | 37.7002 | 32.5817 | 25.1817 | 19.4864 | 13.0991 | 15.6289 | 15.0939 | 38.8305 | 38.0177 | 36.9428 | 35.7177 | 34.4197 | 32.9822 | 31.3143 | 28.7168 | 21.7714 | 11.9726 | 6.3495 | 3.9367
|  | CLARENCE ROAD | LW |  |  | 10.2826 | 9.4879 | 34.3841 | 33.3804 | 31.6994 | 29.8392 | 27.8005 | 25.5791 | 23.0215 | 20.2511 | 12.8457 | 4.2569 | 1.4649 | 0.40484 | 21.2435 | 20.8371 | 44.7748 | 44.2513 | 43.4316 | 42.4672 | 41.3553 | 40.0759 | 38.506 | 36.7058 | 31.9838 | 26.9032 | 25.6899 | 25.2274 | 15.3529 | 14.593 | 38.1218 | 37.1457 | 35.5955 | 33.8778 | 31.9688 | 29.8702 | 27.3834 | 24.6737 | 17.5635 | 9.5233 | 7.1621 | 6.2878
|  | CLARENCE ROAD | ST |  |  | 11.2234 | 11.0131 | 36.538 | 36.2032 | 35.7606 | 35.2231 | 34.6066 | 33.9085 | 33.0675 | 32.1246 | 28.3841 | 19.9207 | 15.6926 | 13.343 | 21.5269 | 21.4188 | 45.5845 | 45.3058 | 44.9638 | 44.5591 | 44.0917 | 43.5226 | 42.807 | 42.0129 | 38.7493 | 30.9206 | 25.561 | 19.4938 | 16.1674 | 15.952 | 40.0706 | 39.7242 | 39.2782 | 38.7448 | 38.1289 | 37.4267 | 36.5732 | 35.65 | 31.7994 | 23.4896 | 19.6143 | 17.5707
|  | CLARENCE ROAD | SP |  |  | 11.3072 | 11.1076 | 36.6659 | 36.3845 | 36.005 | 35.5458 | 35.0401 | 34.4614 | 33.7903 | 32.9853 | 30.2462 | 22.9052 | 17.7077 | 15.8566 | 21.5305 | 21.4243 | 45.5978 | 45.3233 | 44.9997 | 44.6147 | 44.1798 | 43.6751 | 43.0446 | 42.2777 | 39.3857 | 31.113 | 22.0415 | 10.6618 | 16.2437 | 16.0254 | 40.1688 | 39.8714 | 39.5019 | 39.0635 | 38.5738 | 38.0078 | 37.342 | 36.5642 | 33.821 | 26.3305 | 21.3684 | 19.6689
MELKSHAM GSP | CHIPPENHAM | COCKLEBURY | MINIMUM HEADROOM | ST 92447 73890 | YES | 31.8302 | 30.9831 | 29.9359 | 28.8424 | 27.7438 | 26.7453 | 25.6719 | 24.53 | 23.1847 | 21.7716 | 18.1704 | 14.0514 | 11.9483 | 10.2912 | 8.498 | 8.0145 | 7.3994 | 6.7755 | 6.1745 | 5.6318 | 5.0264 | 4.3757 | 3.5425 | 2.679 | 0.6217 | -1.8667 | -4.327 | -7.5986 | 5.5768 | 4.8587 | 3.969 | 3.0462 | 2.1158 | 1.2608 | 0.32449 | -0.67652 | -1.9091 | -3.1878 | -6.4626 | -10.0849 | -11.7303 | -13.0378
|  | COCKLEBURY | CT |  |  | 32.1602 | 31.4757 | 30.6128 | 29.6704 | 28.9042 | 28.2452 | 27.5436 | 26.7676 | 25.8933 | 24.5491 | 21.0278 | 15.6567 | 11.9483 | 10.2912 | 8.5703 | 8.131 | 7.5693 | 6.9616 | 6.462 | 6.0212 | 5.5453 | 5.0148 | 4.4013 | 3.5269 | 1.277 | -1.8667 | -4.327 | -6.8152 | 5.804 | 5.2267 | 4.4936 | 3.6831 | 3.0132 | 2.4239 | 1.7939 | 1.0947 | 0.29678 | -0.91733 | -4.0329 | -8.6812 | -11.7303 | -13.0378
|  | COCKLEBURY | LW |  |  | 31.8302 | 30.9831 | 29.9359 | 28.8424 | 27.7438 | 26.7453 | 25.6719 | 24.53 | 23.1847 | 21.7716 | 18.1704 | 14.0514 | 12.6981 | 12.1023 | 8.498 | 8.0145 | 7.3994 | 6.7755 | 6.1745 | 5.6318 | 5.0264 | 4.3757 | 3.5425 | 2.679 | 0.6217 | -1.4263 | -1.9603 | -2.193 | 5.5768 | 4.8587 | 3.969 | 3.0462 | 2.1158 | 1.2608 | 0.32449 | -0.67652 | -1.9091 | -3.1878 | -6.4626 | -10.0849 | -11.2063 | -11.6943
|  | COCKLEBURY | ST |  |  | 32.4515 | 32.0403 | 31.4939 | 30.9605 | 30.5305 | 30.1892 | 29.8133 | 29.3976 | 28.9271 | 28.4401 | 26.4437 | 22.2533 | 20.1631 | 18.927 | 8.7845 | 8.513 | 8.1439 | 7.7867 | 7.4686 | 7.2068 | 6.9151 | 6.5907 | 6.2175 | 5.8451 | 4.2533 | 0.84792 | -1.3153 | -3.6422 | 6.095 | 5.7599 | 5.3138 | 4.8757 | 4.4976 | 4.1882 | 3.8457 | 3.4664 | 3.0331 | 2.5912 | 0.71719 | -3.1568 | -4.943 | -5.9531
|  | COCKLEBURY | SP |  |  | 32.5 | 32.1064 | 31.6221 | 31.1568 | 30.7127 | 30.3555 | 29.9768 | 29.5629 | 29.1092 | 28.6094 | 26.8578 | 22.584 | 20.0497 | 18.9907 | 8.7965 | 8.5264 | 8.1864 | 7.8589 | 7.5539 | 7.3016 | 7.0317 | 6.7251 | 6.3815 | 5.9931 | 4.5418 | 0.70406 | -2.9868 | -7.5986 | 6.1296 | 5.8098 | 5.4195 | 5.0416 | 4.6661 | 4.3578 | 4.0313 | 3.6688 | 3.2688 | 2.831 | 1.2566 | -2.6781 | -4.9327 | -5.8064
MELKSHAM GSP | FROME BSP | CODFORD | MINIMUM HEADROOM | ST 97372 39559 | YES | 2.6324 | 2.5301 | 2.4131 | 2.2931 | 2.1349 | 1.9708 | 1.7997 | 1.6151 | 1.3767 | 1.1528 | 0.62771 | 0.025955 | -0.10488 | -0.20928 | 1.3319 | 1.2906 | 1.2467 | 1.2021 | 1.1413 | 1.0784 | 1.0137 | 0.94587 | 0.86715 | 0.78759 | 0.55476 | 0.29526 | 0.24315 | 0.2026 | 1.6078 | 1.5966 | 1.5809 | 1.5354 | 1.3839 | 1.2194 | 1.0492 | 0.86678 | 0.63619 | 0.41879 | -0.067414 | -0.58635 | -0.69952 | -0.78843
|  | CODFORD | CT |  |  | 2.7344 | 2.6843 | 2.6285 | 2.5573 | 2.4625 | 2.3616 | 2.2498 | 2.1301 | 1.9791 | 1.7911 | 1.3898 | 0.78923 | 0.33064 | 0.20373 | 1.3783 | 1.3606 | 1.3414 | 1.3203 | 1.2865 | 1.2511 | 1.2121 | 1.1708 | 1.1272 | 1.0692 | 0.90176 | 0.59258 | 0.4195 | 0.3688 | 1.6078 | 1.5966 | 1.583 | 1.5618 | 1.5427 | 1.521 | 1.497 | 1.4064 | 1.2589 | 1.0751 | 0.68007 | 0.055751 | -0.33462 | -0.4433
|  | CODFORD | LW |  |  | 2.6324 | 2.5301 | 2.4131 | 2.2931 | 2.1349 | 1.9708 | 1.7997 | 1.6151 | 1.3767 | 1.1528 | 0.62771 | 0.025955 | -0.10488 | -0.20928 | 1.3319 | 1.2906 | 1.2467 | 1.2021 | 1.1413 | 1.0784 | 1.0137 | 0.94587 | 0.86715 | 0.78759 | 0.55476 | 0.29526 | 0.24315 | 0.2026 | 1.6098 | 1.5986 | 1.5809 | 1.5354 | 1.3839 | 1.2194 | 1.0492 | 0.86678 | 0.63619 | 0.41879 | -0.067414 | -0.58635 | -0.69952 | -0.78843
|  | CODFORD | ST |  |  | 2.7699 | 2.7426 | 2.7131 | 2.6786 | 2.6208 | 2.5601 | 2.4957 | 2.4272 | 2.3498 | 2.2672 | 1.9178 | 1.4256 | 1.1816 | 1.026 | 1.3908 | 1.3797 | 1.3697 | 1.3587 | 1.3385 | 1.3172 | 1.2953 | 1.2724 | 1.2466 | 1.2141 | 1.1002 | 0.87958 | 0.74542 | 0.67083 | 1.6177 | 1.6131 | 1.6074 | 1.5993 | 1.5881 | 1.576 | 1.5618 | 1.5463 | 1.5275 | 1.5109 | 1.1986 | 0.71437 | 0.47016 | 0.30621
|  | CODFORD | SP |  |  | 2.7834 | 2.7614 | 2.7379 | 2.715 | 2.6582 | 2.5959 | 2.5346 | 2.4671 | 2.3978 | 2.2994 | 1.9576 | 1.1401 | 0.68339 | 0.31591 | 1.3965 | 1.389 | 1.3824 | 1.3751 | 1.3528 | 1.3291 | 1.3063 | 1.281 | 1.256 | 1.2172 | 1.0936 | 0.80766 | 0.57646 | 0.43861 | 1.6181 | 1.6123 | 1.6057 | 1.5995 | 1.5924 | 1.5837 | 1.5748 | 1.5637 | 1.5518 | 1.5388 | 1.2223 | 0.42794 | -0.040897 | -0.35254
IVER 132KV | DENHAM | COKES LANE | MINIMUM HEADROOM | SU 99240 97483 | YES | 10.2479 | 10.0785 | 9.9144 | 9.7371 | 9.4686 | 9.1768 | 8.8074 | 8.3939 | 7.9209 | 7.5156 | 6.5075 | 5.0041 | 4.3081 | 3.7538 | 6.4756 | 6.3794 | 6.2888 | 6.1879 | 6.0513 | 5.8934 | 5.6932 | 5.4612 | 5.1771 | 4.9588 | 4.5059 | 3.8358 | 3.2466 | 2.6986 | 5.0703 | 4.9142 | 4.7636 | 4.6001 | 4.3553 | 4.0837 | 3.7491 | 3.3723 | 2.936 | 2.5696 | 1.6923 | 0.36859 | -0.22348 | -0.68459
|  | COKES LANE | CT |  |  | 10.328 | 10.2135 | 10.0745 | 9.9494 | 9.7807 | 9.5833 | 9.3271 | 9.0429 | 8.7293 | 8.2981 | 7.3045 | 5.5501 | 4.4553 | 3.7932 | 6.4828 | 6.3995 | 6.2959 | 6.2043 | 6.1034 | 5.9746 | 5.8157 | 5.6369 | 5.4354 | 5.18 | 4.6874 | 3.8456 | 3.2466 | 2.6986 | 5.1375 | 5.0297 | 4.898 | 4.7803 | 4.6251 | 4.4376 | 4.2054 | 3.9468 | 3.6602 | 3.2664 | 2.3992 | 0.88451 | -0.085829 | -0.64954
|  | COKES LANE | LW |  |  | 10.2479 | 10.0785 | 9.9144 | 9.7371 | 9.4686 | 9.1768 | 8.8074 | 8.3939 | 7.9209 | 7.5156 | 6.5075 | 5.0041 | 4.3081 | 3.7538 | 6.4756 | 6.3794 | 6.2888 | 6.1879 | 6.0513 | 5.8934 | 5.6932 | 5.4612 | 5.1771 | 4.9588 | 4.5059 | 3.8358 | 3.5214 | 3.2594 | 5.0703 | 4.9142 | 4.7636 | 4.6001 | 4.3553 | 4.0837 | 3.7491 | 3.3723 | 2.936 | 2.5696 | 1.6923 | 0.36859 | -0.22348 | -0.68459
|  | COKES LANE | ST |  |  | 10.424 | 10.3662 | 10.2918 | 10.2104 | 10.1177 | 10.0071 | 9.8581 | 9.6952 | 9.5152 | 9.3375 | 8.5053 | 7.3244 | 6.5634 | 5.9524 | 6.5608 | 6.5214 | 6.4679 | 6.4078 | 6.3454 | 6.2648 | 6.1643 | 6.0531 | 5.9274 | 5.8126 | 5.2301 | 4.473 | 3.963 | 3.4348 | 5.2325 | 5.1805 | 5.1121 | 5.0368 | 4.9516 | 4.8449 | 4.7122 | 4.5666 | 4.4047 | 4.2468 | 3.4872 | 2.4599 | 1.8206 | 1.3179
|  | COKES LANE | SP |  |  | 10.4297 | 10.3839 | 10.3318 | 10.2772 | 10.1584 | 10.021 | 9.8561 | 9.6711 | 9.4804 | 9.2717 | 8.5033 | 6.9002 | 6.1165 | 5.5398 | 6.5595 | 6.5255 | 6.4848 | 6.4413 | 6.3784 | 6.2973 | 6.2031 | 6.0924 | 5.9747 | 5.849 | 5.3551 | 4.256 | 3.6316 | 2.9354 | 5.237 | 5.1961 | 5.1489 | 5.0995 | 4.9933 | 4.8651 | 4.7211 | 4.558 | 4.3895 | 4.2051 | 3.5208 | 2.0824 | 1.4148 | 0.93903
LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK | MINIMUM HEADROOM | SU 65893 02686 | NO | 1.9157 | 1.6959 | 1.3711 | 1.003 | 0.39733 | -0.24671 | -0.94402 | -1.6899 | -2.5711 | -3.5601 | -6.6203 | -10.6879 | -14.346 | -16.6214 | 3.0817 | 2.912 | 2.6968 | 2.3819 | 2.0146 | 1.6153 | 1.1756 | 0.69056 | 0.13988 | -0.61151 | -3.2006 | -8.026 | -17.0565 | -33.7291 | 0.5589 | 0.37372 | 0.10525 | -0.19811 | -0.72922 | -1.2909 | -1.8914 | -2.5303 | -3.277 | -4.1095 | -6.9498 | -10.6381 | -13.7792 | -15.7796
|  | COLLEGE PARK | CT |  |  | 1.9977 | 1.8372 | 1.6255 | 1.2846 | 0.85756 | 0.39763 | -0.10124 | -0.64417 | -1.2515 | -2.2176 | -5.3534 | -10.4971 | -14.346 | -16.6214 | 3.0817 | 2.912 | 2.6968 | 2.3819 | 2.0146 | 1.6153 | 1.1756 | 0.69056 | 0.13988 | -0.61151 | -3.2006 | -8.026 | -13.9532 | -22.2335 | 0.64294 | 0.51486 | 0.34226 | 0.072516 | -0.28444 | -0.66719 | -1.0823 | -1.5318 | -2.0293 | -2.8581 | -5.7832 | -10.3982 | -13.7792 | -15.7796
|  | COLLEGE PARK | LW |  |  | 1.9157 | 1.6959 | 1.3711 | 1.003 | 0.39733 | -0.24671 | -0.94402 | -1.6899 | -2.5711 | -3.5601 | -6.6203 | -10.6879 | -12.9007 | -14.3727 | 3.1126 | 2.9858 | 2.7835 | 2.5493 | 2.2177 | 1.8617 | 1.4662 | 1.0409 | 0.5273 | -0.05782 | -1.9847 | -4.2886 | -5.348 | -6.0756 | 0.5589 | 0.37372 | 0.10525 | -0.19811 | -0.72922 | -1.2909 | -1.8914 | -2.5303 | -3.277 | -4.1095 | -6.9498 | -10.6381 | -12.5155 | -13.7337
|  | COLLEGE PARK | ST |  |  | 2.152 | 2.0811 | 1.977 | 1.8513 | 1.6874 | 1.506 | 1.3045 | 1.0813 | 0.82042 | 0.53836 | -0.65157 | -4.2575 | -6.5101 | -8.1752 | 3.1775 | 3.0622 | 2.9129 | 2.7382 | 2.5158 | 2.2712 | 1.9952 | 1.6874 | 1.3322 | 0.94729 | -0.58882 | -5.0866 | -10.4513 | -18.4638 | 0.77061 | 0.7181 | 0.63558 | 0.53555 | 0.40868 | 0.26821 | 0.11294 | -0.058621 | -0.259 | -0.48655 | -1.4261 | -4.7552 | -6.7034 | -8.0885
|  | COLLEGE PARK | SP |  |  | 2.1805 | 2.0963 | 1.9832 | 1.854 | 1.7277 | 1.5922 | 1.4492 | 1.2907 | 1.1104 | 0.89517 | 0.055481 | -2.5788 | -4.8193 | -5.9614 | 3.1806 | 3.0445 | 2.8674 | 2.6657 | 2.4224 | 2.1494 | 1.8443 | 1.5016 | 1.1046 | 0.58395 | -1.4398 | -7.2741 | -17.0565 | -33.7291 | 0.79466 | 0.73445 | 0.64722 | 0.54694 | 0.4501 | 0.34602 | 0.23658 | 0.11635 | -0.020418 | -0.19017 | -0.83913 | -3.1788 | -5.2089 | -6.1576
BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS | MINIMUM HEADROOM | SU 88285 81857 | YES | 11.7498 | 11.1674 | 10.5269 | 9.8172 | 8.8455 | 7.8292 | 6.8077 | 5.6813 | 4.3346 | 2.8534 | -0.74748 | -5.3202 | -8.5474 | -10.8458 | 16.9951 | 16.6594 | 16.2936 | 15.8877 | 15.3708 | 14.8261 | 14.2624 | 13.632 | 12.8298 | 11.8897 | 9.7422 | 6.6562 | 3.821 | 1.0607 | 13.3884 | 12.8794 | 12.3225 | 11.7062 | 10.8353 | 9.9249 | 9.0045 | 7.9921 | 6.7909 | 5.47 | 2.1728 | -1.9699 | -4.8382 | -6.8375
|  | CORDWALLIS | CT |  |  | 11.9198 | 11.4534 | 10.9359 | 10.3203 | 9.6163 | 8.8734 | 8.1826 | 7.4014 | 6.51 | 5.0694 | 1.3111 | -4.4126 | -8.5474 | -10.8458 | 17.0242 | 16.7091 | 16.3657 | 15.9592 | 15.5271 | 15.0677 | 14.6198 | 14.1093 | 13.5033 | 12.5554 | 10.1216 | 6.6562 | 3.821 | 1.0607 | 13.5534 | 13.1542 | 12.713 | 12.1877 | 11.5678 | 10.9137 | 10.3009 | 9.6093 | 8.823 | 7.5111 | 4.029 | -1.0989 | -4.8382 | -6.8375
|  | CORDWALLIS | LW |  |  | 11.7498 | 11.1674 | 10.5269 | 9.8172 | 8.8455 | 7.8292 | 6.8077 | 5.6813 | 4.3346 | 2.8534 | -0.74748 | -5.3202 | -7.5079 | -8.7981 | 16.9951 | 16.6594 | 16.2936 | 15.8877 | 15.3708 | 14.8261 | 14.2624 | 13.632 | 12.8298 | 11.8897 | 9.7422 | 7.2202 | 6.1799 | 5.5412 | 13.3884 | 12.8794 | 12.3225 | 11.7062 | 10.8353 | 9.9249 | 9.0045 | 7.9921 | 6.7909 | 5.47 | 2.1728 | -1.9699 | -3.842 | -4.9174
|  | CORDWALLIS | ST |  |  | 12.2341 | 11.9916 | 11.7228 | 11.4115 | 11.0701 | 10.7135 | 10.3758 | 9.9934 | 9.5337 | 9.0526 | 7.0785 | 2.7796 | 0.35377 | -1.3846 | 17.1912 | 17.0425 | 16.8475 | 16.6226 | 16.3783 | 16.122 | 15.8664 | 15.576 | 15.2274 | 14.8753 | 13.3565 | 9.8683 | 7.5529 | 4.998 | 13.8335 | 13.6349 | 13.4174 | 13.1657 | 12.8793 | 12.5799 | 12.2898 | 11.9614 | 11.5673 | 11.1507 | 9.3858 | 5.3569 | 3.2342 | 1.7675
|  | CORDWALLIS | SP |  |  | 12.2724 | 12.0399 | 11.7941 | 11.5297 | 11.2346 | 10.915 | 10.632 | 10.2958 | 9.9229 | 9.4879 | 7.9665 | 3.8789 | 1.2183 | -0.11034 | 17.203 | 17.0539 | 16.8619 | 16.6549 | 16.446 | 16.2208 | 16.0043 | 15.7475 | 15.4562 | 15.1049 | 13.8156 | 10.0372 | 6.4775 | 2.3364 | 13.8687 | 13.6805 | 13.4846 | 13.2753 | 13.0283 | 12.7589 | 12.5155 | 12.2265 | 11.9082 | 11.533 | 10.2128 | 6.4056 | 3.9686 | 2.8317
MANNINGTON GSP | LYTCHETT | CORFE MULLEN | MINIMUM HEADROOM | SY 98583 96071 | YES | 18.0997 | 17.7087 | 17.2132 | 16.751 | 15.9109 | 14.9745 | 13.9839 | 12.8871 | 11.5173 | 10.1556 | 7.0899 | 3.1703 | 0.10002 | -1.9432 | 22.4142 | 22.1771 | 21.8566 | 21.5466 | 21.0708 | 20.5311 | 19.9378 | 19.2602 | 18.3562 | 17.5103 | 15.8397 | 13.5762 | 11.4814 | 9.683 | 18.9346 | 18.59 | 18.1356 | 17.7024 | 16.9387 | 16.0901 | 15.1858 | 14.1795 | 12.9277 | 11.7166 | 8.9656 | 5.4409 | 2.8089 | 1.065
|  | CORFE MULLEN | CT |  |  | 18.2936 | 18.0244 | 17.6787 | 17.3068 | 16.734 | 16.0733 | 15.3808 | 14.5518 | 13.5906 | 12.156 | 8.937 | 3.9319 | 0.10002 | -1.9432 | 22.4469 | 22.2381 | 21.97 | 21.6545 | 21.265 | 20.8176 | 20.339 | 19.7786 | 19.1122 | 18.1849 | 16.2994 | 13.5762 | 11.4814 | 9.683 | 19.1123 | 18.8637 | 18.5447 | 18.1875 | 17.6614 | 17.0589 | 16.426 | 15.6988 | 14.8571 | 13.583 | 10.7004 | 6.1337 | 2.8089 | 1.065
|  | CORFE MULLEN | LW |  |  | 18.0997 | 17.7087 | 17.2132 | 16.751 | 15.9109 | 14.9745 | 13.9839 | 12.8871 | 11.5173 | 10.1556 | 7.0899 | 3.1703 | 1.3624 | 0.15273 | 22.4142 | 22.1771 | 21.8566 | 21.5466 | 21.0708 | 20.5311 | 19.9378 | 19.2602 | 18.3562 | 17.5103 | 15.8397 | 13.7992 | 12.9921 | 12.4478 | 18.9346 | 18.59 | 18.1356 | 17.7024 | 16.9387 | 16.0901 | 15.1858 | 14.1795 | 12.9277 | 11.7166 | 8.9656 | 5.4409 | 3.8733 | 2.8602
|  | CORFE MULLEN | ST |  |  | 18.5035 | 18.3633 | 18.1858 | 18.0211 | 17.7442 | 17.4081 | 17.0619 | 16.6738 | 16.2374 | 15.772 | 13.5338 | 10.0415 | 8.0727 | 6.63 | 22.6156 | 22.5067 | 22.3676 | 22.2249 | 22.009 | 21.7496 | 21.4764 | 21.1663 | 20.8094 | 20.4591 | 18.7829 | 16.2049 | 14.6449 | 13.0385 | 19.2969 | 19.1818 | 19.0352 | 18.8806 | 18.6288 | 18.3266 | 18.0131 | 17.66 | 17.2597 | 16.8394 | 14.917 | 11.8054 | 10.0902 | 8.8253
|  | CORFE MULLEN | SP |  |  | 18.5365 | 18.3984 | 18.2422 | 18.1056 | 17.8237 | 17.5002 | 17.1636 | 16.7832 | 16.3818 | 15.9255 | 14.2017 | 10.0319 | 8.0529 | 6.9347 | 22.6288 | 22.5105 | 22.3756 | 22.2441 | 22.0524 | 21.8303 | 21.5888 | 21.3085 | 21.004 | 20.6603 | 19.3056 | 15.8965 | 13.5665 | 10.8467 | 19.3265 | 19.2145 | 19.0845 | 18.9559 | 18.7056 | 18.4221 | 18.1239 | 17.7843 | 17.4246 | 17.0149 | 15.4788 | 11.8077 | 10.0217 | 9.0662
MELKSHAM GSP | NORRINGTON | CORSHAM | MINIMUM HEADROOM | ST 86766 69583 | NO | 2.8918 | 2.6111 | 2.2795 | 1.9229 | 1.3533 | 0.74973 | 0.088517 | -0.62323 | -1.4928 | -2.4459 | -4.7906 | -7.3837 | -8.832 | -9.8148 | 2.5298 | 2.3705 | 2.1755 | 1.9616 | 1.6517 | 1.3186 | 0.9426 | 0.53281 | 0.0094338 | -0.57275 | -1.9562 | -3.6773 | -5.2252 | -6.65 | 0.50137 | 0.25185 | -0.034866 | -0.34176 | -0.85381 | -1.3939 | -1.9917 | -2.643 | -3.4398 | -4.3469 | -6.5487 | -8.9347 | -10.2437 | -11.1591
|  | CORSHAM | CT |  |  | 3.0278 | 2.8387 | 2.6109 | 2.3238 | 1.9401 | 1.5304 | 1.091 | 0.60882 | 0.055666 | -0.87307 | -3.2651 | -6.6715 | -8.832 | -9.8148 | 2.5606 | 2.424 | 2.2587 | 2.0491 | 1.8012 | 1.5335 | 1.2393 | 0.9133 | 0.53205 | -0.058418 | -1.5724 | -3.6773 | -5.2252 | -6.65 | 0.64247 | 0.48288 | 0.29386 | 0.059941 | -0.27572 | -0.64862 | -1.0554 | -1.515 | -2.0446 | -2.9272 | -5.1758 | -8.2718 | -10.2437 | -11.1591
|  | CORSHAM | LW |  |  | 2.8918 | 2.6111 | 2.2795 | 1.9229 | 1.3533 | 0.74973 | 0.088517 | -0.62323 | -1.4928 | -2.4459 | -4.7906 | -7.3837 | -8.2891 | -8.6661 | 2.5298 | 2.3705 | 2.1755 | 1.9616 | 1.6517 | 1.3186 | 0.9426 | 0.53281 | 0.0094338 | -0.57275 | -1.9562 | -3.3866 | -3.8145 | -4.0015 | 0.50137 | 0.25185 | -0.034866 | -0.34176 | -0.85381 | -1.3939 | -1.9917 | -2.643 | -3.4398 | -4.3469 | -6.5487 | -8.9347 | -9.7357 | -10.0679
|  | CORSHAM | ST |  |  | 3.2063 | 3.1279 | 3.03 | 2.9179 | 2.7488 | 2.5603 | 2.3517 | 2.1188 | 1.8345 | 1.5305 | 0.15799 | -2.8653 | -4.3123 | -5.1631 | 2.6747 | 2.609 | 2.5283 | 2.4351 | 2.3068 | 2.1628 | 2.0006 | 1.8175 | 1.5929 | 1.3636 | 0.32562 | -2.0048 | -3.3986 | -4.7743 | 0.79258 | 0.72589 | 0.64485 | 0.55281 | 0.41168 | 0.25481 | 0.081733 | -0.11061 | -0.36629 | -0.65019 | -1.9796 | -4.8733 | -6.1941 | -6.9425
|  | CORSHAM | SP |  |  | 3.2326 | 3.1594 | 3.0744 | 2.9784 | 2.8355 | 2.6864 | 2.5197 | 2.3315 | 2.1119 | 1.8461 | 0.8497 | -1.931 | -3.6034 | -4.2344 | 2.6833 | 2.616 | 2.5368 | 2.4465 | 2.3382 | 2.2221 | 2.089 | 1.936 | 1.7558 | 1.5425 | 0.71893 | -1.6531 | -3.7794 | -6.0977 | 0.81808 | 0.75899 | 0.69106 | 0.61454 | 0.49052 | 0.3611 | 0.21825 | 0.058913 | -0.12804 | -0.36139 | -1.2881 | -3.9677 | -5.5524 | -6.1242
EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD | MINIMUM HEADROOM | SP 59021 31128 | NO | 0.31038 | 0.22004 | 0.12721 | 0.029393 | -0.27768 | -0.54857 | -0.63088 | -0.72086 | -0.81153 | -0.92269 | -1.2623 | -1.9989 | -2.3962 | -2.6222 | 2.0017 | 1.953 | 1.9035 | 1.8495 | 1.7865 | 1.7073 | 1.6428 | 1.5446 | 1.4174 | 1.321 | 1.1588 | 0.85702 | 0.65945 | 0.54097 | 0.93127 | 0.84713 | 0.76107 | 0.66937 | 0.46423 | 0.24807 | 0.17743 | 0.097857 | -0.017926 | -0.17112 | -0.48104 | -1.1109 | -1.4426 | -1.6263
|  | COTTISFORD | CT |  |  | 0.48028 | 0.43164 | 0.37349 | 0.31667 | 0.24317 | 0.16744 | 0.080469 | -0.018816 | -0.12703 | -0.26811 | -0.54381 | -1.0389 | -1.2435 | -1.2963 | 2.0426 | 2.0055 | 1.9588 | 1.9139 | 1.8644 | 1.8121 | 1.7501 | 1.6765 | 1.5918 | 1.4865 | 1.3409 | 1.1068 | 0.98881 | 0.89923 | 1.0584 | 1.0076 | 0.94505 | 0.88483 | 0.8119 | 0.73612 | 0.64762 | 0.54453 | 0.42887 | 0.28031 | 0.038933 | -0.36948 | -0.53642 | -0.58105
|  | COTTISFORD | LW |  |  | 0.31038 | 0.22004 | 0.12721 | 0.029393 | -0.086813 | -0.20713 | -0.3371 | -0.48915 | -0.67323 | -0.83285 | -1.2061 | -1.6409 | -1.7161 | -1.7739 | 2.0017 | 1.953 | 1.9035 | 1.8495 | 1.7865 | 1.7193 | 1.6428 | 1.5446 | 1.4174 | 1.321 | 1.1588 | 0.96492 | 0.93027 | 0.90726 | 0.93127 | 0.84713 | 0.76107 | 0.66937 | 0.56119 | 0.44819 | 0.32372 | 0.17192 | -0.017926 | -0.17112 | -0.48104 | -0.84614 | -0.91063 | -0.95789
|  | COTTISFORD | ST |  |  | 0.43011 | 0.3998 | 0.36437 | 0.32649 | 0.27758 | 0.22685 | 0.17157 | 0.11298 | 0.044468 | -0.029682 | -0.34089 | -0.7644 | -0.99366 | -1.1213 | 2.0491 | 2.0306 | 2.0057 | 1.9775 | 1.9465 | 1.9135 | 1.8763 | 1.8356 | 1.7851 | 1.7379 | 1.4943 | 1.2167 | 1.0752 | 0.96299 | 1.033 | 1.0048 | 0.96949 | 0.93071 | 0.88373 | 0.83459 | 0.78044 | 0.72238 | 0.65237 | 0.58134 | 0.24977 | -0.14187 | -0.33264 | -0.43554
|  | COTTISFORD | SP |  |  | 0.36268 | 0.27451 | 0.18491 | 0.092963 | -0.27768 | -0.54857 | -0.63088 | -0.72086 | -0.81153 | -0.92269 | -1.2623 | -1.9989 | -2.3962 | -2.6222 | 2.0297 | 1.995 | 1.9581 | 1.918 | 1.7989 | 1.7073 | 1.6691 | 1.6239 | 1.5764 | 1.5231 | 1.3277 | 0.85702 | 0.65945 | 0.54097 | 0.98127 | 0.90885 | 0.83451 | 0.75689 | 0.46423 | 0.24807 | 0.17743 | 0.097857 | 0.016814 | -0.080602 | -0.39878 | -1.1109 | -1.4426 | -1.6263
BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES | MINIMUM HEADROOM | SU 70990 69570 | YES | 26.3437 | 25.9928 | 25.571 | 25.021 | 24.4645 | 23.9956 | 23.4231 | 22.8667 | 21.9702 | 21.0611 | 17.5417 | 14.438 | 13.8885 | 13.6766 | 17.3397 | 17.015 | 16.6323 | 16.1357 | 15.6552 | 15.2753 | 14.7978 | 14.3898 | 13.8131 | 13.0564 | 10.1122 | 7.6481 | 7.1721 | 6.9988 | 16.9843 | 16.6277 | 16.21 | 15.6804 | 15.1485 | 14.6989 | 14.1479 | 13.6578 | 13.0053 | 12.3913 | 9.5227 | 6.5256 | 5.9894 | 5.7905
|  | COURAGES | CT |  |  | 26.3437 | 25.9928 | 25.571 | 25.0271 | 24.5214 | 24.1145 | 23.6104 | 23.1283 | 22.3517 | 21.5997 | 18.6778 | 15.4745 | 14.9017 | 14.6944 | 17.3461 | 17.0327 | 16.6577 | 16.1688 | 15.7042 | 15.3437 | 14.9009 | 14.5316 | 14.0367 | 13.4543 | 10.9696 | 8.4326 | 8.0048 | 7.8414 | 17.0177 | 16.6903 | 16.298 | 15.7938 | 15.3039 | 14.9013 | 14.4224 | 14.0106 | 13.4593 | 12.9243 | 10.6158 | 7.5244 | 6.9803 | 6.7871
|  | COURAGES | LW |  |  | 26.3605 | 26.0006 | 25.5712 | 25.021 | 24.4645 | 23.9956 | 23.4231 | 22.8667 | 21.9702 | 21.0611 | 17.5417 | 14.438 | 14.2144 | 14.069 | 17.3397 | 17.015 | 16.6323 | 16.1357 | 15.6552 | 15.2753 | 14.7978 | 14.3898 | 13.8131 | 13.0564 | 10.1122 | 7.6481 | 7.4876 | 7.3836 | 16.9843 | 16.6277 | 16.21 | 15.6804 | 15.1485 | 14.6989 | 14.1479 | 13.6578 | 13.0053 | 12.3913 | 9.5227 | 6.5256 | 6.3162 | 6.1816
|  | COURAGES | ST |  |  | 26.4304 | 26.1304 | 25.7708 | 25.303 | 24.8679 | 24.536 | 24.1083 | 23.7558 | 23.2516 | 22.7852 | 20.1916 | 15.757 | 13.8885 | 13.6766 | 17.4181 | 17.1415 | 16.8099 | 16.3748 | 15.9689 | 15.6714 | 15.2877 | 14.9806 | 14.5557 | 14.176 | 12.1174 | 8.613 | 7.1721 | 6.9988 | 17.1236 | 16.8494 | 16.5185 | 16.0896 | 15.6912 | 15.3865 | 14.9953 | 14.676 | 14.2274 | 13.8175 | 11.9499 | 7.7889 | 5.9894 | 5.7905
|  | COURAGES | SP |  |  | 26.4395 | 26.1465 | 25.7935 | 25.3334 | 24.9175 | 24.6122 | 24.217 | 23.9058 | 23.4754 | 23.1051 | 21.4751 | 18.4798 | 15.9259 | 15.3222 | 17.4263 | 17.1533 | 16.8252 | 16.3942 | 16.0003 | 15.7192 | 15.3551 | 15.0727 | 14.6913 | 14.3575 | 12.9274 | 10.7024 | 8.7209 | 8.2231 | 17.1378 | 16.8697 | 16.5456 | 16.1246 | 15.7431 | 15.462 | 15.0986 | 14.8139 | 14.4247 | 14.0831 | 12.6439 | 10.3978 | 7.9588 | 7.3813
BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE | MINIMUM HEADROOM | SU 85415 55937 | YES | 13.7835 | 13.4023 | 12.8478 | 12.3146 | 11.6528 | 10.9396 | 10.1517 | 9.3047 | 8.1897 | 7.0465 | 4.3106 | 0.82791 | -1.9636 | -3.6149 | 16.5688 | 16.3332 | 15.9505 | 15.5446 | 15.1225 | 14.663 | 14.1458 | 13.5867 | 12.8158 | 12.0277 | 10.2453 | 7.5875 | 5.4093 | 3.191 | 14.6895 | 14.3595 | 13.8683 | 13.3771 | 12.7685 | 12.1138 | 11.3936 | 10.6214 | 9.578 | 8.4856 | 5.9109 | 2.7121 | 0.24298 | -1.2461
|  | COVE | CT |  |  | 13.8312 | 13.5043 | 13.035 | 12.5277 | 12.0211 | 11.4701 | 10.8848 | 10.2519 | 9.4856 | 8.3254 | 5.4437 | 1.0254 | -1.9636 | -3.6149 | 16.5688 | 16.3332 | 15.9779 | 15.5528 | 15.1784 | 14.7697 | 14.3327 | 13.859 | 13.2742 | 12.4512 | 10.4576 | 7.5875 | 5.4093 | 3.2873 | 14.7359 | 14.4569 | 14.0428 | 13.5778 | 13.1147 | 12.6122 | 12.0802 | 11.4994 | 10.7638 | 9.659 | 6.9517 | 2.9368 | 0.24298 | -1.2461
|  | COVE | LW |  |  | 13.7835 | 13.4023 | 12.8478 | 12.3146 | 11.6528 | 10.9396 | 10.1517 | 9.3047 | 8.1897 | 7.0465 | 4.3106 | 0.82791 | -0.76809 | -1.739 | 16.58 | 16.3366 | 15.9505 | 15.5446 | 15.1225 | 14.663 | 14.1458 | 13.5867 | 12.8158 | 12.0277 | 10.2453 | 8.1736 | 7.3712 | 6.8684 | 14.6895 | 14.3595 | 13.8683 | 13.3771 | 12.7685 | 12.1138 | 11.3936 | 10.6214 | 9.578 | 8.4856 | 5.9109 | 2.7121 | 1.3238 | 0.49722
|  | COVE | ST |  |  | 14.0477 | 13.8848 | 13.6079 | 13.3334 | 13.086 | 12.8101 | 12.5036 | 12.182 | 11.7877 | 11.3686 | 9.4626 | 5.4887 | 3.3665 | 2.057 | 16.7234 | 16.5997 | 16.3743 | 16.1229 | 15.9068 | 15.6674 | 15.4026 | 15.1249 | 14.7849 | 14.4297 | 12.8247 | 9.5433 | 7.493 | 5.493 | 14.9328 | 14.8033 | 14.5647 | 14.3086 | 14.0837 | 13.8335 | 13.5571 | 13.2678 | 12.9092 | 12.523 | 10.7086 | 6.9365 | 5.024 | 3.8927
|  | COVE | SP |  |  | 14.0666 | 13.8975 | 13.6372 | 13.3759 | 13.188 | 12.9806 | 12.7648 | 12.5341 | 12.2604 | 11.9491 | 10.7531 | 7.2445 | 5.0508 | 4.1181 | 16.731 | 16.5972 | 16.3764 | 16.1276 | 15.9563 | 15.7678 | 15.5711 | 15.3606 | 15.1102 | 14.8026 | 13.6125 | 10.1773 | 6.9562 | 3.191 | 14.9504 | 14.8169 | 14.5944 | 14.3512 | 14.1796 | 13.991 | 13.796 | 13.589 | 13.3407 | 13.0569 | 11.9657 | 8.5902 | 6.5424 | 5.7225
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL | MINIMUM HEADROOM | SP 56113 03074 | NO | 5.7623 | 5.1604 | 4.3057 | 3.3262 | 1.8717 | 0.24018 | -1.6144 | -3.4075 | -5.5779 | -7.7469 | -13.8208 | -21.1767 | -26.4499 | -29.96 | 13.862 | 13.4882 | 12.9474 | 12.3541 | 11.4952 | 10.5222 | 9.4292 | 8.3769 | 7.0399 | 5.6148 | 1.7565 | -4.8195 | -10.8862 | -23.5227 | 7.9983 | 7.4455 | 6.6909 | 5.8433 | 4.517 | 3.0403 | 1.3898 | -0.2127 | -2.1554 | -4.1181 | -9.6872 | -16.465 | -21.1487 | -24.1987
|  | COWLEY LOCAL | CT |  |  | 5.9102 | 5.4666 | 4.8467 | 3.9822 | 2.8726 | 1.6044 | 0.14858 | -1.2306 | -2.7829 | -4.9081 | -10.7622 | -20.0166 | -26.4499 | -29.96 | 13.8632 | 13.5028 | 13.0128 | 12.3939 | 11.6041 | 10.7046 | 9.6995 | 8.7323 | 7.5504 | 6.022 | 1.8079 | -4.8195 | -10.8862 | -18.1085 | 8.1525 | 7.7559 | 7.2124 | 6.4898 | 5.4991 | 4.3748 | 3.1049 | 1.8977 | 0.52636 | -1.3874 | -6.8259 | -15.3767 | -21.1487 | -24.1987
|  | COWLEY LOCAL | LW |  |  | 5.7623 | 5.1604 | 4.3057 | 3.3262 | 1.8717 | 0.24018 | -1.6144 | -3.4075 | -5.5779 | -7.7469 | -13.8208 | -21.1767 | -24.271 | -26.3378 | 13.862 | 13.4882 | 12.9474 | 12.3541 | 11.4952 | 10.5222 | 9.4292 | 8.3769 | 7.0399 | 5.6148 | 1.7565 | -2.4694 | -3.9069 | -4.8763 | 7.9983 | 7.4455 | 6.6909 | 5.8433 | 4.517 | 3.0403 | 1.3898 | -0.2127 | -2.1554 | -4.1181 | -9.6872 | -16.465 | -19.2044 | -20.9337
|  | COWLEY LOCAL | ST |  |  | 6.2949 | 6.0559 | 5.7045 | 5.2947 | 4.6838 | 3.9713 | 3.1434 | 2.3824 | 1.4715 | 0.52565 | -2.6899 | -9.8425 | -14.1269 | -16.6415 | 14.083 | 13.8446 | 13.5123 | 13.1579 | 12.6297 | 12.021 | 11.3392 | 10.6948 | 9.893 | 9.047 | 6.2482 | -0.41549 | -6.0534 | -12.8916 | 8.4964 | 8.2802 | 7.9734 | 7.6351 | 7.1039 | 6.4897 | 5.7999 | 5.1567 | 4.3551 | 3.4949 | 0.63454 | -6.0781 | -9.9043 | -12.0314
|  | COWLEY LOCAL | SP |  |  | 6.5067 | 6.2588 | 5.9161 | 5.5238 | 4.9774 | 4.3563 | 3.6403 | 3.003 | 2.255 | 1.439 | -0.98075 | -6.7181 | -11.0241 | -13.0134 | 14.1632 | 13.9097 | 13.5634 | 13.1975 | 12.6897 | 12.1084 | 11.4594 | 10.8518 | 10.1034 | 9.2258 | 6.4908 | -0.52546 | -9.8517 | -23.5227 | 8.705 | 8.4886 | 8.195 | 7.8782 | 7.3926 | 6.8474 | 6.2478 | 5.7039 | 5.0383 | 4.2938 | 2.165 | -3.0943 | -7.045 | -8.752
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD | MINIMUM HEADROOM | SU 78275 50779 | YES | 2.3284 | 2.1763 | 2.0118 | 1.8145 | 1.5441 | 1.2908 | 0.80019 | 0.25297 | -0.42943 | -1.0603 | -2.3531 | -4.0435 | -4.8806 | -5.5245 | 5.288 | 5.2006 | 5.1085 | 4.9865 | 4.8443 | 4.7224 | 4.4849 | 4.1518 | 3.7009 | 3.2968 | 2.5681 | 1.6527 | 0.81118 | 0.14234 | 3.5734 | 3.2977 | 3.0008 | 2.6597 | 2.1929 | 1.7801 | 1.3218 | 0.80843 | 0.15819 | -0.43905 | -1.6345 | -3.1861 | -3.9007 | -4.4672
|  | COXMOOR WOOD | CT |  |  | 2.3921 | 2.2785 | 2.145 | 1.985 | 1.7917 | 1.6467 | 1.5001 | 1.169 | 0.7363 | 0.089697 | -1.2264 | -3.411 | -4.8806 | -5.5245 | 5.3026 | 5.2248 | 5.1357 | 5.021 | 4.9051 | 4.8118 | 4.6917 | 4.4391 | 4.124 | 3.6929 | 2.8916 | 1.6667 | 0.81118 | 0.14234 | 3.6475 | 3.4277 | 3.1618 | 2.8735 | 2.5456 | 2.2613 | 1.962 | 1.6227 | 1.2078 | 0.5947 | -0.62484 | -2.6001 | -3.9007 | -4.4672
|  | COXMOOR WOOD | LW |  |  | 2.3284 | 2.1763 | 2.0118 | 1.8145 | 1.5441 | 1.2908 | 0.80019 | 0.25297 | -0.42943 | -1.0603 | -2.3531 | -4.0435 | -4.6198 | -4.8986 | 5.288 | 5.2006 | 5.1085 | 4.9865 | 4.8443 | 4.7224 | 4.4849 | 4.1518 | 3.7009 | 3.2968 | 2.5681 | 1.6527 | 1.3926 | 1.2707 | 3.5734 | 3.2977 | 3.0008 | 2.6597 | 2.1929 | 1.7801 | 1.3218 | 0.80843 | 0.15819 | -0.43905 | -1.6345 | -3.1861 | -3.698 | -3.943
|  | COXMOOR WOOD | ST |  |  | 2.4644 | 2.3985 | 2.3234 | 2.2248 | 2.1241 | 2.058 | 1.9852 | 1.9063 | 1.8167 | 1.7075 | 0.96209 | -0.60865 | -1.4273 | -1.9576 | 5.3514 | 5.3043 | 5.2521 | 5.1744 | 5.1052 | 5.0541 | 4.997 | 4.9357 | 4.8645 | 4.7852 | 4.0868 | 2.8909 | 2.2237 | 1.5951 | 3.8274 | 3.7204 | 3.5875 | 3.4218 | 3.2422 | 3.1087 | 2.9576 | 2.7902 | 2.5914 | 2.3887 | 1.3648 | -0.097745 | -0.83623 | -1.3038
|  | COXMOOR WOOD | SP |  |  | 2.4734 | 2.4154 | 2.3521 | 2.2682 | 2.17 | 2.1043 | 2.0352 | 1.9598 | 1.8783 | 1.7776 | 1.4043 | -0.59867 | -1.5157 | -1.9427 | 5.3539 | 5.31 | 5.2632 | 5.1927 | 5.1294 | 5.0833 | 5.0338 | 4.979 | 4.9188 | 4.8477 | 4.4671 | 2.8474 | 1.8947 | 0.9776 | 3.8391 | 3.7438 | 3.6381 | 3.5089 | 3.3548 | 3.2381 | 3.1154 | 2.9656 | 2.7982 | 2.6022 | 1.8542 | -0.074623 | -0.93729 | -1.3263
MANNINGTON GSP | LYTCHETT | CREEKMOOR | MINIMUM HEADROOM | SZ 00552 94121 | YES | 10.559 | 10.3778 | 10.2044 | 10.0245 | 9.8134 | 9.3673 | 8.4943 | 7.5424 | 6.2944 | 4.9889 | 1.785 | -2.2436 | -5.5659 | -7.5887 | 9.2055 | 8.925 | 8.6115 | 8.2917 | 7.8474 | 7.3564 | 6.7972 | 6.1713 | 5.3381 | 4.4695 | 2.4638 | -0.07692 | -2.2166 | -4.0639 | 6.6866 | 6.2966 | 5.8778 | 5.4632 | 4.7806 | 4.0401 | 3.2262 | 2.3346 | 1.2058 | 0.028117 | -2.9462 | -6.6152 | -9.5231 | -11.2473
|  | CREEKMOOR | CT |  |  | 10.559 | 10.3778 | 10.2125 | 10.0345 | 9.8437 | 9.6295 | 9.393 | 8.8708 | 8.0136 | 6.7094 | 3.315 | -1.8658 | -5.5659 | -7.5887 | 9.2115 | 8.9504 | 8.6943 | 8.3626 | 7.9943 | 7.5923 | 7.1444 | 6.6324 | 6.0106 | 5.1357 | 2.9311 | -0.07692 | -2.2166 | -4.0639 | 6.7749 | 6.4584 | 6.1549 | 5.7829 | 5.3051 | 4.7861 | 4.2141 | 3.5714 | 2.8078 | 1.6269 | -1.5495 | -6.233 | -9.5231 | -11.2473
|  | CREEKMOOR | LW |  |  | 10.5762 | 10.3837 | 10.2044 | 10.0245 | 9.8134 | 9.3673 | 8.4943 | 7.5424 | 6.2944 | 4.9889 | 1.785 | -2.2436 | -4.0508 | -5.1568 | 9.2055 | 8.925 | 8.6115 | 8.2917 | 7.8474 | 7.3564 | 6.7972 | 6.1713 | 5.3381 | 4.4695 | 2.4638 | 0.19029 | -0.63768 | -1.1633 | 6.6866 | 6.2966 | 5.8778 | 5.4632 | 4.7806 | 4.0401 | 3.2262 | 2.3346 | 1.2058 | 0.028117 | -2.9462 | -6.6152 | -8.177 | -9.1248
|  | CREEKMOOR | ST |  |  | 10.6653 | 10.5507 | 10.4638 | 10.3917 | 10.2922 | 10.174 | 10.0381 | 9.8835 | 9.6336 | 9.3876 | 8.1559 | 4.186 | 1.961 | 0.53258 | 9.397 | 9.2614 | 9.1316 | 9.0017 | 8.8206 | 8.6124 | 8.3761 | 8.1117 | 7.7772 | 7.4494 | 5.914 | 2.642 | 0.82648 | -0.82947 | 7.0101 | 6.8595 | 6.7207 | 6.5874 | 6.39 | 6.1627 | 5.9071 | 5.6229 | 5.2616 | 4.8922 | 3.198 | -0.776 | -2.7441 | -3.9483
|  | CREEKMOOR | SP |  |  | 10.6727 | 10.5605 | 10.4758 | 10.4098 | 10.3349 | 10.2461 | 10.1498 | 10.0394 | 9.8608 | 9.6966 | 9.0476 | 5.7693 | 3.4579 | 2.4912 | 9.4126 | 9.2673 | 9.1323 | 9.0058 | 8.8679 | 8.7116 | 8.5418 | 8.3403 | 8.0898 | 7.8049 | 6.6471 | 3.2774 | 0.38932 | -2.6421 | 7.0388 | 6.8863 | 6.7523 | 6.6332 | 6.4799 | 6.3083 | 6.1241 | 5.9103 | 5.6391 | 5.3498 | 4.2005 | 0.71543 | -1.4259 | -2.2525
MINETY GSP | CIRENCESTER BSP | CRICKLADE | MINIMUM HEADROOM | SU 09400 93270 | NO | 3.4179 | 3.1025 | 2.7733 | 2.429 | 1.8991 | 1.3522 | 0.776 | 0.14908 | -0.56738 | -1.244 | -2.8122 | -4.6708 | -5.2309 | -5.4878 | 3.4519 | 3.304 | 3.1473 | 2.9799 | 2.7365 | 2.4824 | 2.2062 | 1.8981 | 1.5217 | 1.1683 | 0.4251 | -0.44065 | -0.81175 | -1.3205 | 1.0076 | 0.71328 | 0.40135 | 0.070544 | -0.41493 | -0.91936 | -1.4642 | -2.071 | -2.812 | -3.4954 | -4.8907 | -6.5099 | -6.9678 | -7.1736
|  | CRICKLADE | CT |  |  | 3.6837 | 3.5188 | 3.3274 | 3.1213 | 2.8125 | 2.4911 | 2.1619 | 1.7849 | 1.3734 | 0.73158 | -0.72118 | -3.1645 | -4.7163 | -5.3346 | 3.5362 | 3.439 | 3.3234 | 3.1966 | 3.0337 | 2.8622 | 2.6802 | 2.4666 | 2.2283 | 1.8077 | 1.0159 | -0.035194 | -0.81175 | -1.3205 | 1.199 | 1.0241 | 0.81494 | 0.58624 | 0.28235 | -0.036119 | -0.37164 | -0.76709 | -1.209 | -1.8809 | -3.233 | -5.278 | -6.5149 | -7.0033
|  | CRICKLADE | LW |  |  | 3.4179 | 3.1025 | 2.7733 | 2.429 | 1.8991 | 1.3522 | 0.776 | 0.14908 | -0.56738 | -1.244 | -2.8122 | -4.6708 | -5.2309 | -5.4878 | 3.4519 | 3.304 | 3.1473 | 2.9799 | 2.7365 | 2.4824 | 2.2062 | 1.8981 | 1.5217 | 1.1683 | 0.4251 | -0.44065 | -0.6799 | -0.79069 | 1.0076 | 0.71328 | 0.40135 | 0.070544 | -0.41493 | -0.91936 | -1.4642 | -2.071 | -2.812 | -3.4954 | -4.8907 | -6.5099 | -6.9678 | -7.1736
|  | CRICKLADE | ST |  |  | 3.7979 | 3.7546 | 3.664 | 3.5615 | 3.4079 | 3.2444 | 3.0729 | 2.8846 | 2.6776 | 2.4519 | 1.4579 | -0.16575 | -1.1087 | -1.751 | 3.6194 | 3.5746 | 3.5178 | 3.4521 | 3.3652 | 3.271 | 3.1694 | 3.0556 | 2.9254 | 2.7933 | 2.165 | 0.98047 | 0.44686 | -0.00091851 | 1.3655 | 1.2865 | 1.1906 | 1.0783 | 0.92286 | 0.75572 | 0.5773 | 0.37828 | 0.15112 | -0.07946 | -1.1895 | -2.8324 | -3.6286 | -4.1366
|  | CRICKLADE | SP |  |  | 3.8018 | 3.7776 | 3.7467 | 3.6816 | 3.5314 | 3.3818 | 3.23 | 3.0562 | 2.8741 | 2.6234 | 1.7492 | -0.38237 | -1.5729 | -2.2454 | 3.6322 | 3.5942 | 3.5487 | 3.498 | 3.4181 | 3.3378 | 3.2536 | 3.1543 | 3.0465 | 2.9102 | 2.4095 | 0.91577 | 0.10781 | -0.49887 | 1.3946 | 1.3316 | 1.2628 | 1.1849 | 1.0408 | 0.8991 | 0.75318 | 0.57946 | 0.39371 | 0.15012 | -0.74179 | -2.9995 | -4.0908 | -4.6531
MELKSHAM GSP | FROME BSP | CROCKERTON | MINIMUM HEADROOM | ST 87736 43371 | YES | 4.2526 | 3.6605 | 3.0065 | 2.3272 | 1.3184 | 0.28667 | -0.77833 | -1.8861 | -3.169 | -4.5561 | -8.2654 | -12.53 | -13.7875 | -15.1521 | 1.3749 | 1.1599 | 0.88759 | 0.60042 | 0.15715 | -0.35246 | -0.91111 | -1.5035 | -2.2512 | -3.0762 | -4.9916 | -6.9173 | -8.3559 | -10.079 | -1.0785 | -1.155 | -1.255 | -1.6094 | -2.5196 | -3.4527 | -4.4213 | -5.4308 | -6.6097 | -7.8875 | -11.262 | -15.097 | -16.2102 | -17.3887
|  | CROCKERTON | CT |  |  | 4.8097 | 4.5937 | 4.2974 | 3.9113 | 3.3198 | 2.7033 | 2.0592 | 1.3701 | 0.60546 | -0.5999 | -3.9025 | -9.6135 | -13.5974 | -15.1521 | 1.3749 | 1.3097 | 1.2322 | 1.0461 | 0.71213 | 0.35173 | -0.037995 | -0.47449 | -1.0047 | -1.7769 | -3.7232 | -6.4143 | -8.3559 | -9.8079 | -1.0785 | -1.155 | -1.2466 | -1.3741 | -1.5071 | -1.6556 | -1.9386 | -2.5964 | -3.3598 | -4.5401 | -7.613 | -12.5213 | -16.0195 | -17.3887
|  | CROCKERTON | LW |  |  | 4.2526 | 3.6605 | 3.0065 | 2.3272 | 1.3184 | 0.28667 | -0.77833 | -1.8861 | -3.169 | -4.5561 | -8.2654 | -12.53 | -13.7875 | -14.6493 | 1.3906 | 1.1599 | 0.88759 | 0.60042 | 0.15715 | -0.35246 | -0.91111 | -1.5035 | -2.2512 | -3.0762 | -4.9916 | -6.9173 | -7.3978 | -7.7082 | -1.065 | -1.1481 | -1.255 | -1.6094 | -2.5196 | -3.4527 | -4.4213 | -5.4308 | -6.6097 | -7.8875 | -11.262 | -15.097 | -16.2102 | -16.9693
|  | CROCKERTON | ST |  |  | 4.8846 | 4.8322 | 4.6367 | 4.4343 | 4.0943 | 3.7383 | 3.3688 | 2.978 | 2.5421 | 2.05 | 0.17861 | -3.659 | -5.8692 | -7.2815 | 1.4341 | 1.4044 | 1.37 | 1.332 | 1.2532 | 1.0733 | 0.8409 | 0.58751 | 0.29063 | -0.018603 | -1.3775 | -4.1665 | -5.6915 | -7.1008 | -1.0056 | -1.0385 | -1.0771 | -1.1198 | -1.19 | -1.2709 | -1.3657 | -1.4738 | -1.6179 | -1.9148 | -3.7357 | -7.4778 | -9.3436 | -10.5389
|  | CROCKERTON | SP |  |  | 4.8881 | 4.8546 | 4.8023 | 4.6412 | 4.1591 | 3.6606 | 3.1637 | 2.6297 | 2.0903 | 1.4017 | -0.851 | -5.8338 | -9.01 | -10.7442 | 1.4359 | 1.4063 | 1.3747 | 1.3371 | 1.2756 | 1.057 | 0.83516 | 0.57867 | 0.27839 | -0.090488 | -1.426 | -4.8165 | -7.4545 | -10.079 | -1.0021 | -1.0348 | -1.0691 | -1.11 | -1.1606 | -1.2188 | -1.2805 | -1.3566 | -1.8292 | -2.4492 | -4.4932 | -9.0904 | -11.9606 | -13.5008
BRAMLEY (FLEE) | PYESTOCK BSP | Crookham (Church) | MINIMUM HEADROOM | SU 81702 53403 | YES | 17.3305 | 16.9085 | 16.4296 | 15.9374 | 15.1328 | 14.2849 | 13.3741 | 12.3843 | 11.0087 | 9.7307 | 7.4343 | 4.3928 | 1.9976 | 0.50553 | 21.0464 | 20.7655 | 20.4022 | 20.0391 | 19.6105 | 19.0966 | 18.5323 | 17.9094 | 16.9564 | 16.0892 | 14.7484 | 12.1946 | 9.898 | 7.1525 | 18.5049 | 18.1255 | 17.6684 | 17.2211 | 16.4732 | 15.694 | 14.8635 | 13.9631 | 12.7325 | 11.5828 | 9.4599 | 6.6666 | 4.448 | 3.0903
|  | Crookham (Church) | CT |  |  | 17.4182 | 17.0817 | 16.6723 | 16.2458 | 15.701 | 15.1243 | 14.5405 | 13.8827 | 12.9927 | 11.6465 | 9.0099 | 4.944 | 1.9976 | 0.50553 | 21.0464 | 20.7655 | 20.4022 | 20.0391 | 19.63 | 19.199 | 18.749 | 18.2364 | 17.5312 | 16.57 | 14.7964 | 12.1946 | 9.898 | 7.4536 | 18.5932 | 18.2946 | 17.9044 | 17.5209 | 17.0153 | 16.4885 | 15.9606 | 15.3679 | 14.5746 | 13.3598 | 10.8934 | 7.1742 | 4.448 | 3.0903
|  | Crookham (Church) | LW |  |  | 17.3305 | 16.9085 | 16.4296 | 15.9374 | 15.1328 | 14.2849 | 13.3741 | 12.3843 | 11.0087 | 9.7307 | 7.4343 | 4.3928 | 3.0262 | 2.2611 | 21.0706 | 20.788 | 20.4394 | 20.0982 | 19.6105 | 19.0966 | 18.5323 | 17.9094 | 16.9564 | 16.0892 | 14.7484 | 13.1286 | 12.5255 | 12.1755 | 18.5049 | 18.1255 | 17.6684 | 17.2211 | 16.4732 | 15.694 | 14.8635 | 13.9631 | 12.7325 | 11.5828 | 9.4599 | 6.6666 | 5.4348 | 4.7664
|  | Crookham (Church) | ST |  |  | 17.7349 | 17.601 | 17.4158 | 17.214 | 16.961 | 16.7012 | 16.4114 | 16.0915 | 15.7115 | 15.3132 | 13.2682 | 9.9615 | 8.2581 | 7.1139 | 21.2746 | 21.1404 | 20.9404 | 20.7402 | 20.4984 | 20.2538 | 19.9815 | 19.6795 | 19.3205 | 18.9687 | 17.1952 | 14.2889 | 12.33 | 10.0219 | 18.8741 | 18.7551 | 18.5637 | 18.3798 | 18.1411 | 17.9032 | 17.6427 | 17.3556 | 17.017 | 16.6575 | 14.8456 | 11.7107 | 10.1988 | 9.2224
|  | Crookham (Church) | SP |  |  | 17.7531 | 17.6276 | 17.4687 | 17.3225 | 17.1441 | 16.9456 | 16.7591 | 16.5267 | 16.2498 | 15.9298 | 14.613 | 10.7789 | 9.2271 | 8.5129 | 21.2756 | 21.1389 | 20.9467 | 20.7768 | 20.5854 | 20.3776 | 20.1729 | 19.922 | 19.628 | 19.2983 | 17.9488 | 14.0533 | 11.1218 | 7.1525 | 18.8915 | 18.7809 | 18.6131 | 18.4781 | 18.3051 | 18.1215 | 17.9518 | 17.7426 | 17.4949 | 17.2069 | 16.0392 | 12.4398 | 11.0008 | 10.3786
BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE | MINIMUM HEADROOM | SU 84470 64352 | YES | 5.8973 | 4.5031 | 2.9894 | 1.4405 | -0.47381 | -2.5493 | -4.8727 | -7.2682 | -10.0323 | -12.3144 | -17.309 | -23.1978 | -26.416 | -28.6677 | 14.0036 | 13.0761 | 12.0326 | 11.0701 | 9.9795 | 8.7819 | 7.4201 | 5.9656 | 4.1702 | 2.7419 | -0.030923 | -3.6872 | -6.7597 | -9.4511 | 8.4899 | 7.1923 | 5.7736 | 4.3776 | 2.6462 | 0.77791 | -1.3158 | -3.5101 | -6.0933 | -8.2135 | -12.72 | -18.0475 | -20.683 | -22.5373
|  | CROWTHORNE | CT |  |  | 6.1591 | 4.9323 | 3.4872 | 2.0939 | 0.61752 | -1.011 | -2.7951 | -4.6052 | -6.5188 | -8.9817 | -14.0367 | -21.5685 | -26.416 | -28.6677 | 14.0036 | 13.1013 | 12.0326 | 11.0701 | 10.1106 | 9.0656 | 7.9137 | 6.696 | 5.3664 | 3.7393 | 0.71689 | -3.6872 | -6.7597 | -9.4511 | 8.6677 | 7.5341 | 6.1831 | 4.926 | 3.5885 | 2.1231 | 0.52111 | -1.1362 | -2.9119 | -5.211 | -9.7734 | -16.521 | -20.683 | -22.5373
|  | CROWTHORNE | LW |  |  | 5.8973 | 4.5031 | 2.9894 | 1.4405 | -0.47381 | -2.5493 | -4.8727 | -7.2682 | -10.0323 | -12.3144 | -17.309 | -23.1978 | -25.1951 | -26.0591 | 14.0115 | 13.0761 | 12.0564 | 11.0901 | 9.9795 | 8.7819 | 7.4201 | 5.9656 | 4.1702 | 2.7419 | -0.030923 | -3.2088 | -4.1209 | -4.5244 | 8.4899 | 7.1923 | 5.7736 | 4.3776 | 2.6462 | 0.77791 | -1.3158 | -3.5101 | -6.0933 | -8.2135 | -12.72 | -18.0475 | -19.8058 | -20.5579
|  | CROWTHORNE | ST |  |  | 6.785 | 6.0575 | 5.2023 | 4.4045 | 3.573 | 2.6508 | 1.6252 | 0.64596 | -0.38471 | -1.3224 | -5.6333 | -11.1685 | -14.0236 | -15.8027 | 14.5024 | 13.9397 | 13.2491 | 12.6328 | 12.0111 | 11.3438 | 10.6074 | 9.8784 | 9.0867 | 8.3954 | 5.0831 | 0.75229 | -1.8485 | -4.4201 | 9.3346 | 8.6813 | 7.8792 | 7.1521 | 6.398 | 5.5831 | 4.6825 | 3.8027 | 2.8584 | 1.9981 | -2.0689 | -7.2424 | -9.8251 | -11.3869
|  | CROWTHORNE | SP |  |  | 6.8385 | 6.1606 | 5.4154 | 4.763 | 4.0373 | 3.2652 | 2.3781 | 1.5126 | 0.64034 | -0.22627 | -3.3678 | -10.1383 | -12.9809 | -14.2686 | 14.5171 | 13.9752 | 13.3519 | 12.8306 | 12.3038 | 11.7499 | 11.1232 | 10.4794 | 9.8112 | 9.1553 | 6.6864 | 0.93182 | -2.5082 | -6.177 | 9.3801 | 8.7722 | 8.0827 | 7.5069 | 6.8583 | 6.1823 | 5.4203 | 4.6535 | 3.8679 | 3.0783 | 0.17476 | -6.2857 | -8.9436 | -10.1087
EALING GSP | EALING (D) | DEAN GARDENS | MINIMUM HEADROOM | TQ 16546 80368 | YES | 8.2004 | 7.9535 | 7.8077 | 7.6945 | 7.4985 | 7.2801 | 7.0463 | 6.8084 | 6.5497 | 6.2881 | 5.4004 | 3.7755 | 2.2508 | 1.033 | 10.1111 | 9.9539 | 9.8503 | 9.7528 | 9.6265 | 9.4835 | 9.3305 | 9.166 | 8.9829 | 8.7659 | 8.0192 | 6.2426 | 2.7456 | -3.5146 | 8.7345 | 8.5337 | 8.4084 | 8.3071 | 8.1326 | 7.9391 | 7.7301 | 7.518 | 7.282 | 7.0422 | 6.2322 | 4.8075 | 3.6125 | 2.6312
|  | DEAN GARDENS | CT |  |  | 8.2396 | 8.0159 | 7.897 | 7.8047 | 7.6618 | 7.497 | 7.3347 | 7.1679 | 6.991 | 6.7303 | 5.874 | 3.9624 | 2.2508 | 1.033 | 10.1111 | 9.9539 | 9.8503 | 9.7528 | 9.6265 | 9.4835 | 9.3305 | 9.166 | 8.9829 | 8.7659 | 8.0192 | 6.2426 | 3.9275 | 0.55729 | 8.7682 | 8.5878 | 8.4866 | 8.4033 | 8.2758 | 8.1296 | 7.9848 | 7.8349 | 7.6742 | 7.4371 | 6.6624 | 5.0043 | 3.6125 | 2.6312
|  | DEAN GARDENS | LW |  |  | 8.2004 | 7.9535 | 7.8077 | 7.6945 | 7.4985 | 7.2801 | 7.0463 | 6.8084 | 6.5497 | 6.2881 | 5.4004 | 3.7755 | 2.5933 | 1.6586 | 10.129 | 9.9966 | 9.9182 | 9.8546 | 9.7592 | 9.6524 | 9.532 | 9.4105 | 9.2683 | 9.1222 | 8.6214 | 7.7608 | 7.2037 | 6.7443 | 8.7345 | 8.5337 | 8.4084 | 8.3071 | 8.1326 | 7.9391 | 7.7301 | 7.518 | 7.282 | 7.0422 | 6.2322 | 4.8075 | 3.8356 | 3.0806
|  | DEAN GARDENS | ST |  |  | 8.3491 | 8.2112 | 8.1501 | 8.1134 | 8.059 | 7.9903 | 7.9167 | 7.8415 | 7.7572 | 7.6653 | 7.2995 | 6.0934 | 5.0002 | 4.1675 | 10.1807 | 10.071 | 9.9992 | 9.9355 | 9.8501 | 9.7513 | 9.6405 | 9.5201 | 9.3837 | 9.2476 | 8.7202 | 7.109 | 4.9748 | 1.8365 | 8.8722 | 8.7716 | 8.7241 | 8.6932 | 8.6461 | 8.5872 | 8.5232 | 8.457 | 8.3813 | 8.2983 | 7.9676 | 6.9053 | 5.9923 | 5.3258
|  | DEAN GARDENS | SP |  |  | 8.3576 | 8.2247 | 8.1682 | 8.1345 | 8.0922 | 8.0408 | 7.9826 | 7.9235 | 7.8627 | 7.7895 | 7.5179 | 6.5877 | 5.5838 | 4.8612 | 10.1785 | 10.0657 | 9.9865 | 9.913 | 9.8126 | 9.6962 | 9.5612 | 9.4121 | 9.243 | 9.0602 | 8.3569 | 6.2807 | 2.7456 | -3.5146 | 8.88 | 8.7837 | 8.7403 | 8.712 | 8.6764 | 8.6339 | 8.5845 | 8.5333 | 8.4798 | 8.4145 | 8.1731 | 7.3631 | 6.5134 | 5.9362
COWLEY GSP | YARNTON BSP | DEDDINGTON | MINIMUM HEADROOM | SP 46729 30325 | YES | -0.81259 | -1.3163 | -1.4931 | -1.6745 | -1.9072 | -2.2942 | -3.1597 | -4.0406 | -4.9271 | -5.9365 | -9.0763 | -11.5195 | -12.218 | -12.6506 | 1.8394 | 1.6515 | 1.5545 | 1.4536 | 1.3273 | 1.1914 | 0.9963 | 0.63756 | 0.27427 | -0.13713 | -1.4253 | -2.6809 | -3.1457 | -3.5475 | 0.020263 | -0.42776 | -0.59071 | -0.75814 | -0.97239 | -1.2894 | -2.0517 | -2.8291 | -3.6119 | -4.5031 | -7.2489 | -9.4585 | -10.0895 | -10.4729
|  | DEDDINGTON | CT |  |  | 0.02088 | -0.19729 | -0.30288 | -0.41791 | -0.56613 | -0.7228 | -0.896 | -1.1095 | -1.3576 | -1.6837 | -2.2631 | -3.1217 | -3.5713 | -3.7321 | 2.079 | 1.9712 | 1.8905 | 1.8005 | 1.7008 | 1.5953 | 1.4799 | 1.3323 | 1.155 | 0.9303 | 0.5876 | 0.12872 | -0.16407 | -0.42525 | 0.74927 | 0.55125 | 0.45072 | 0.34083 | 0.19909 | 0.047501 | -0.11646 | -0.32004 | -0.55806 | -0.87015 | -1.4079 | -2.1833 | -2.5722 | -2.7076
|  | DEDDINGTON | LW |  |  | -0.81259 | -1.3163 | -1.4931 | -1.6745 | -1.9072 | -2.1522 | -2.4136 | -2.7178 | -3.0888 | -3.4256 | -4.1369 | -4.9414 | -5.1208 | -5.2688 | 1.8394 | 1.6515 | 1.5545 | 1.4536 | 1.3273 | 1.1914 | 1.0405 | 0.85319 | 0.6073 | 0.39719 | 0.060662 | -0.30479 | -0.3841 | -0.44465 | 0.020263 | -0.42776 | -0.59071 | -0.75814 | -0.97239 | -1.1986 | -1.4409 | -1.7252 | -2.075 | -2.3903 | -3.0371 | -3.7649 | -3.9254 | -4.0558
|  | DEDDINGTON | ST |  |  | -0.0059373 | -0.27002 | -0.5415 | -0.81767 | -1.2095 | -1.5832 | -1.7177 | -1.8352 | -1.9644 | -2.1049 | -2.7116 | -3.5769 | -4.033 | -4.3354 | 2.1038 | 2.0062 | 1.9017 | 1.7897 | 1.6371 | 1.4868 | 1.4053 | 1.3213 | 1.2262 | 1.133 | 0.67228 | 0.066113 | -0.24603 | -0.55289 | 0.73187 | 0.4981 | 0.25703 | 0.010876 | -0.33773 | -0.67096 | -0.79505 | -0.90551 | -1.0273 | -1.1587 | -1.7371 | -2.5456 | -2.955 | -3.2221
|  | DEDDINGTON | SP |  |  | 0.067234 | -0.1406 | -0.35007 | -0.56098 | -1.4219 | -2.2942 | -3.1597 | -4.0406 | -4.9271 | -5.9365 | -9.0763 | -11.5195 | -12.218 | -12.6506 | 2.126 | 2.0436 | 1.9581 | 1.87 | 1.585 | 1.2934 | 0.9963 | 0.63756 | 0.27427 | -0.13713 | -1.4253 | -2.6809 | -3.1457 | -3.5475 | 0.79619 | 0.61151 | 0.42512 | 0.23722 | -0.52084 | -1.2894 | -2.0517 | -2.8291 | -3.6119 | -4.5031 | -7.2489 | -9.4585 | -10.0895 | -10.4729
IVER 132KV | DENHAM | DENHAM AVENUE | MINIMUM HEADROOM | TQ 03761 86587 | YES | 3.1146 | 2.9805 | 2.8117 | 2.6277 | 2.3431 | 2.0137 | 1.6543 | 1.2573 | 0.75632 | 0.25103 | -0.94913 | -2.3341 | -3.0168 | -3.5014 | 2.563 | 2.5015 | 2.4273 | 2.3454 | 2.2164 | 2.064 | 1.893 | 1.6575 | 1.3295 | 0.99802 | 0.27248 | -0.5148 | -1.1396 | -1.6651 | 1.1717 | 1.046 | 0.88602 | 0.71099 | 0.44544 | 0.14043 | -0.19477 | -0.56689 | -1.0409 | -1.5187 | -2.6299 | -3.8988 | -4.4691 | -4.8865
|  | DENHAM AVENUE | CT |  |  | 3.1725 | 3.0785 | 2.9667 | 2.8111 | 2.6098 | 2.3696 | 2.1118 | 1.8219 | 1.485 | 0.98063 | -0.24731 | -1.9747 | -3.0168 | -3.5014 | 2.5826 | 2.5343 | 2.4775 | 2.4032 | 2.3028 | 2.184 | 2.0487 | 1.8562 | 1.6157 | 1.2775 | 0.49992 | -0.50857 | -1.1396 | -1.6651 | 1.2211 | 1.131 | 1.0235 | 0.87236 | 0.68107 | 0.45613 | 0.21381 | -0.059741 | -0.3796 | -0.85596 | -1.9934 | -3.5553 | -4.4691 | -4.8865
|  | DENHAM AVENUE | LW |  |  | 3.1146 | 2.9805 | 2.8117 | 2.6277 | 2.3431 | 2.0137 | 1.6543 | 1.2573 | 0.75632 | 0.25103 | -0.94913 | -2.3341 | -2.795 | -3.0009 | 2.563 | 2.5015 | 2.4273 | 2.3454 | 2.2164 | 2.064 | 1.893 | 1.6575 | 1.3295 | 0.99802 | 0.27248 | -0.5148 | -0.71781 | -0.81248 | 1.1717 | 1.046 | 0.88602 | 0.71099 | 0.44544 | 0.14043 | -0.19477 | -0.56689 | -1.0409 | -1.5187 | -2.6299 | -3.8988 | -4.2986 | -4.4716
|  | DENHAM AVENUE | ST |  |  | 3.2635 | 3.2236 | 3.1743 | 3.1179 | 3.0301 | 2.9183 | 2.7947 | 2.6557 | 2.4896 | 2.312 | 1.5031 | 0.063243 | -0.61948 | -1.0153 | 2.6252 | 2.6023 | 2.5757 | 2.5452 | 2.5018 | 2.4476 | 2.3814 | 2.3067 | 2.2165 | 2.1124 | 1.512 | 0.4033 | -0.16308 | -0.654 | 1.3088 | 1.2709 | 1.2237 | 1.1694 | 1.0851 | 0.98085 | 0.86466 | 0.73345 | 0.57598 | 0.40898 | -0.36175 | -1.7255 | -2.3404 | -2.6796
|  | DENHAM AVENUE | SP |  |  | 3.2794 | 3.2386 | 3.1929 | 3.1425 | 3.0715 | 2.985 | 2.89 | 2.7842 | 2.6637 | 2.5179 | 1.9518 | 0.48751 | -0.30437 | -0.61371 | 2.6312 | 2.6084 | 2.5827 | 2.5537 | 2.5174 | 2.4737 | 2.4216 | 2.3628 | 2.2951 | 2.2093 | 1.8124 | 0.5664 | -0.34402 | -1.2336 | 1.3232 | 1.2836 | 1.2391 | 1.1898 | 1.123 | 1.044 | 0.95624 | 0.85778 | 0.74515 | 0.60931 | 0.077722 | -1.3273 | -2.0699 | -2.3442
MELKSHAM GSP | NORRINGTON | DEVIZES | MINIMUM HEADROOM | SU 00106 60986 | NO | -3.2582 | -4.1204 | -4.9774 | -5.8326 | -7.1547 | -8.5171 | -9.9421 | -11.4348 | -13.1647 | -15.0114 | -19.79 | -25.3561 | -27.5757 | -29.8392 | 2.0004 | 1.517 | 1.0217 | 0.51602 | -0.16912 | -0.88872 | -1.6827 | -2.5344 | -3.6078 | -4.7799 | -7.3704 | -10.0182 | -12.7069 | -15.1592 | -6.1979 | -6.9792 | -7.7638 | -8.5491 | -9.7482 | -10.9862 | -12.2883 | -13.6558 | -15.2542 | -16.9662 | -21.3308 | -26.3544 | -28.282 | -30.2779
|  | DEVIZES | CT |  |  | -2.5947 | -3.1082 | -3.5663 | -4.1097 | -4.9168 | -5.7488 | -6.6293 | -7.5677 | -8.6036 | -10.2722 | -14.8474 | -22.2948 | -27.5757 | -29.8392 | 2.1797 | 1.7964 | 1.4477 | 0.99345 | 0.46703 | -0.084315 | -0.68517 | -1.3398 | -2.1083 | -3.2368 | -6.0708 | -9.8302 | -12.7069 | -15.1592 | -5.6192 | -6.0938 | -6.5216 | -7.037 | -7.7811 | -8.5493 | -9.3652 | -10.2368 | -11.2059 | -12.7548 | -16.9779 | -23.6204 | -28.282 | -30.2779
|  | DEVIZES | LW |  |  | -3.2582 | -4.1204 | -4.9774 | -5.8326 | -7.1547 | -8.5171 | -9.9421 | -11.4348 | -13.1647 | -15.0114 | -19.79 | -25.3561 | -27.1994 | -28.0627 | 2.0004 | 1.517 | 1.0217 | 0.51602 | -0.16912 | -0.88872 | -1.6827 | -2.5344 | -3.6078 | -4.7799 | -7.3704 | -10.0182 | -10.7555 | -11.0943 | -6.1979 | -6.9792 | -7.7638 | -8.5491 | -9.7482 | -10.9862 | -12.2883 | -13.6558 | -15.2542 | -16.9662 | -21.3308 | -26.3544 | -27.9904 | -28.7536
|  | DEVIZES | ST |  |  | -2.335 | -2.6897 | -2.976 | -3.2475 | -3.6621 | -4.0852 | -4.5273 | -5.0045 | -5.5299 | -6.1094 | -8.4026 | -13.2703 | -15.9736 | -17.8937 | 2.3797 | 2.1139 | 1.8984 | 1.6857 | 1.389 | 1.0796 | 0.7412 | 0.36584 | -0.060581 | -0.48304 | -2.3556 | -6.1756 | -8.3878 | -10.7441 | -5.3726 | -5.6969 | -5.9615 | -6.2137 | -6.597 | -6.989 | -7.401 | -7.8472 | -8.3408 | -8.8794 | -11.0435 | -15.6824 | -18.0498 | -19.7261
|  | DEVIZES | SP |  |  | -2.2324 | -2.5574 | -2.8038 | -3.0255 | -3.5244 | -4.0099 | -4.5055 | -5.0335 | -5.5931 | -6.2805 | -8.6164 | -14.0866 | -17.4642 | -19.2653 | 2.4165 | 2.1446 | 1.9278 | 1.7256 | 1.4347 | 1.1426 | 0.83551 | 0.48892 | 0.10875 | -0.34432 | -2.0518 | -6.6018 | -10.3279 | -14.5358 | -5.2814 | -5.5818 | -5.8123 | -6.0206 | -6.4718 | -6.9114 | -7.3612 | -7.8432 | -8.3554 | -8.9815 | -11.1288 | -16.2237 | -19.3429 | -20.9302
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH | MINIMUM HEADROOM | SU 19288 83540 | YES | 19.6638 | 19.6075 | 19.5439 | 19.4693 | 19.3659 | 19.251 | 19.1198 | 18.9758 | 18.8117 | 18.6095 | 17.9728 | 17.083 | 16.6102 | 16.1281 | 16.199 | 16.159 | 16.1038 | 16.0423 | 15.9523 | 15.8563 | 15.7481 | 15.6318 | 15.4902 | 15.3262 | 14.8808 | 14.1553 | 13.4245 | 12.7279 | 15.3256 | 15.2635 | 15.1744 | 15.0757 | 14.9291 | 14.7737 | 14.5984 | 14.4106 | 14.1797 | 13.9134 | 13.2175 | 12.1951 | 11.2903 | 10.6243
|  | DORCAN SOUTH | CT |  |  | 19.6683 | 19.629 | 19.5785 | 19.5159 | 19.4379 | 19.3518 | 19.2589 | 19.1573 | 19.052 | 18.8901 | 18.376 | 17.3721 | 16.6102 | 16.1281 | 16.2073 | 16.1728 | 16.1332 | 16.0721 | 16.0006 | 15.921 | 15.8364 | 15.7438 | 15.6411 | 15.4771 | 14.9751 | 14.1553 | 13.4245 | 12.7279 | 15.3438 | 15.2946 | 15.2377 | 15.1438 | 15.0338 | 14.911 | 14.7811 | 14.6393 | 14.4808 | 14.2252 | 13.5155 | 12.292 | 11.2903 | 10.6243
|  | DORCAN SOUTH | LW |  |  | 19.6638 | 19.6075 | 19.5439 | 19.4693 | 19.3659 | 19.251 | 19.1198 | 18.9758 | 18.8117 | 18.6095 | 17.9728 | 17.083 | 16.6202 | 16.2957 | 16.199 | 16.159 | 16.1038 | 16.0423 | 15.9523 | 15.8563 | 15.7481 | 15.6318 | 15.4902 | 15.3262 | 14.8808 | 14.2406 | 13.8439 | 13.5395 | 15.3256 | 15.2635 | 15.1744 | 15.0757 | 14.9291 | 14.7737 | 14.5984 | 14.4106 | 14.1797 | 13.9134 | 13.2175 | 12.1951 | 11.5319 | 11.05
|  | DORCAN SOUTH | ST |  |  | 19.6905 | 19.6738 | 19.6561 | 19.6364 | 19.6095 | 19.5705 | 19.5258 | 19.4748 | 19.4145 | 19.3337 | 19.014 | 18.1129 | 17.5627 | 17.2668 | 16.2327 | 16.215 | 16.1944 | 16.1713 | 16.1369 | 16.099 | 16.0563 | 16.0096 | 15.9537 | 15.8928 | 15.6289 | 14.8822 | 14.3 | 13.6875 | 15.3843 | 15.362 | 15.3351 | 15.3047 | 15.2554 | 15.2014 | 15.1404 | 15.0744 | 14.9942 | 14.9147 | 14.555 | 13.6047 | 13.0053 | 12.5348
|  | DORCAN SOUTH | SP |  |  | 19.6919 | 19.675 | 19.6575 | 19.6383 | 19.6173 | 19.5929 | 19.5608 | 19.5241 | 19.4853 | 19.4334 | 19.2444 | 18.5844 | 17.9152 | 17.6176 | 16.2372 | 16.2164 | 16.1944 | 16.1699 | 16.1441 | 16.1149 | 16.0835 | 16.0477 | 16.0078 | 15.9521 | 15.7266 | 14.9881 | 14.095 | 12.9933 | 15.3931 | 15.3657 | 15.3374 | 15.3057 | 15.2714 | 15.2324 | 15.1909 | 15.1433 | 15.0901 | 15.0302 | 14.7789 | 13.9543 | 13.3291 | 12.951
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER TOWN | MINIMUM HEADROOM | SY 69113 90401 | YES | 10.4465 | 9.7877 | 8.8814 | 7.9774 | 6.764 | 5.4847 | 4.1048 | 2.6335 | 0.92236 | -0.91779 | -6.1955 | -12.2086 | -15.0076 | -16.8102 | 13.563 | 13.3723 | 13.115 | 12.7968 | 12.5252 | 12.1371 | 11.3784 | 10.5617 | 9.5459 | 8.3307 | 5.0375 | 1.0531 | -2.3797 | -7.0095 | 11.0473 | 10.4528 | 9.6268 | 8.7728 | 7.6561 | 6.4723 | 5.181 | 3.8009 | 2.157 | 0.3781 | -4.606 | -10.1068 | -12.346 | -13.8645
|  | DORCHESTER TOWN | CT |  |  | 10.8221 | 10.3933 | 9.7626 | 9.0604 | 8.2828 | 7.4487 | 6.5784 | 5.6317 | 4.5359 | 2.8161 | -2.3028 | -10.2046 | -15.0076 | -16.8102 | 13.563 | 13.3723 | 13.115 | 12.7968 | 12.5252 | 12.2217 | 11.8698 | 11.3946 | 10.562 | 9.3583 | 5.8993 | 1.0531 | -2.3797 | -5.9308 | 11.1662 | 10.905 | 10.3766 | 9.684 | 8.9391 | 8.1357 | 7.2922 | 6.3752 | 5.297 | 3.6396 | -1.1466 | -8.2607 | -12.346 | -13.8645
|  | DORCHESTER TOWN | LW |  |  | 10.4465 | 9.7877 | 8.8814 | 7.9774 | 6.764 | 5.4847 | 4.1048 | 2.6335 | 0.92236 | -0.91779 | -6.1955 | -12.2086 | -13.9926 | -14.8326 | 13.601 | 13.4066 | 13.1448 | 12.8384 | 12.5595 | 12.1371 | 11.3784 | 10.5617 | 9.5459 | 8.3307 | 5.0375 | 1.6379 | 1.0146 | 0.69951 | 11.0473 | 10.4528 | 9.6268 | 8.7728 | 7.6561 | 6.4723 | 5.181 | 3.8009 | 2.157 | 0.3781 | -4.606 | -10.1068 | -11.6331 | -12.3433
|  | DORCHESTER TOWN | ST |  |  | 11.1285 | 10.9097 | 10.5824 | 10.2694 | 9.9413 | 9.579 | 9.1716 | 8.7154 | 8.1636 | 7.5187 | 4.9439 | -2.104 | -6.4204 | -7.4522 | 13.7042 | 13.6006 | 13.4544 | 13.2824 | 13.131 | 12.9554 | 12.7473 | 12.511 | 12.1818 | 11.8024 | 9.871 | 3.7043 | 0.83003 | -2.2394 | 11.3738 | 11.2406 | 11.0513 | 10.8532 | 10.5568 | 10.1966 | 9.7901 | 9.3363 | 8.7841 | 8.1566 | 5.4049 | -2.5586 | -6.1202 | -6.839
|  | DORCHESTER TOWN | SP |  |  | 11.2015 | 11.0038 | 10.7122 | 10.44 | 10.1361 | 9.8111 | 9.4625 | 9.0647 | 8.6152 | 8.0631 | 6.1064 | 0.89267 | -3.5531 | -5.1312 | 13.7103 | 13.6114 | 13.4683 | 13.3036 | 13.1785 | 13.0371 | 12.8784 | 12.6947 | 12.4576 | 12.1897 | 10.6584 | 5.3595 | -0.28645 | -7.0095 | 11.3863 | 11.2657 | 11.0872 | 10.9072 | 10.7319 | 10.4211 | 10.0892 | 9.7066 | 9.2702 | 8.7448 | 6.8398 | 1.7462 | -3.3551 | -4.6838
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE | MINIMUM HEADROOM | SU 61604 50238 | YES | 17.6488 | 16.9441 | 16.0537 | 15.1189 | 13.6164 | 12.0252 | 10.3198 | 8.4379 | 5.9772 | 3.5615 | -1.7621 | -8.164 | -14.0202 | -17.1505 | 5.5511 | 5.0645 | 4.4165 | 3.7367 | 2.8363 | 1.8662 | 0.78896 | -0.42928 | -2.0643 | -3.626 | -6.8147 | -11.4864 | -15.4641 | -19.2663 | 9.591 | 8.9274 | 8.0779 | 7.2038 | 5.8256 | 4.3653 | 2.7915 | 0.99136 | -1.3517 | -3.6241 | -8.5625 | -14.3829 | -19.2109 | -21.8689
|  | DOWN GRANGE | CT |  |  | 17.7881 | 17.2064 | 16.4775 | 15.6178 | 14.5316 | 13.3745 | 12.1716 | 10.7291 | 9.0146 | 6.4431 | 0.65355 | -7.8888 | -14.0202 | -17.1505 | 5.5511 | 5.0645 | 4.4518 | 3.7367 | 2.9644 | 2.1377 | 1.2531 | 0.23218 | -1.0041 | -2.7173 | -6.4138 | -11.4864 | -15.4641 | -19.2663 | 9.7053 | 9.151 | 8.4494 | 7.6368 | 6.6307 | 5.5599 | 4.3933 | 3.0353 | 1.4133 | -0.99962 | -6.3572 | -14.0269 | -19.2109 | -21.8689
|  | DOWN GRANGE | LW |  |  | 17.6488 | 16.9441 | 16.0537 | 15.1189 | 13.6164 | 12.0252 | 10.3198 | 8.4379 | 5.9772 | 3.5615 | -1.7621 | -8.164 | -11.0318 | -12.3874 | 5.5734 | 5.0741 | 4.4165 | 3.7413 | 2.8363 | 1.8662 | 0.78896 | -0.42928 | -2.0643 | -3.626 | -6.8147 | -10.2864 | -11.5537 | -12.1917 | 9.591 | 8.9274 | 8.0779 | 7.2038 | 5.8256 | 4.3653 | 2.7915 | 0.99136 | -1.3517 | -3.6241 | -8.5625 | -14.3829 | -16.8517 | -17.9828
|  | DOWN GRANGE | ST |  |  | 18.2387 | 17.9558 | 17.576 | 17.1887 | 16.7093 | 16.1934 | 15.6347 | 15.0116 | 14.294 | 13.5272 | 10.0384 | 3.7448 | 0.37444 | -1.9772 | 5.9028 | 5.6404 | 5.2884 | 4.9389 | 4.515 | 4.0603 | 3.5603 | 3.0002 | 2.3515 | 1.7089 | -1.1738 | -6.3449 | -9.5901 | -13.1534 | 10.1407 | 9.8734 | 9.5067 | 9.1502 | 8.7048 | 8.2275 | 7.7084 | 7.128 | 6.4561 | 5.7049 | 2.354 | -3.5962 | -6.5774 | -8.5789
|  | DOWN GRANGE | SP |  |  | 18.2722 | 17.9862 | 17.6304 | 17.2892 | 16.913 | 16.5142 | 16.1037 | 15.6105 | 15.0593 | 14.4459 | 12.1576 | 6.0503 | 3.11 | 1.8947 | 5.9124 | 5.6325 | 5.2825 | 4.9527 | 4.6232 | 4.2717 | 3.8993 | 3.4487 | 2.9367 | 2.3306 | 0.06454 | -6.0223 | -11.1421 | -17.7302 | 10.1712 | 9.8989 | 9.5541 | 9.2412 | 8.8985 | 8.5373 | 8.1645 | 7.7122 | 7.2044 | 6.6405 | 4.426 | -1.4771 | -4.2158 | -5.2622
MINETY GSP | STRATTON (2 X 90) | DRAKES WAY | MINIMUM HEADROOM | SU 16899 85647 | YES | 7.5497 | 7.4564 | 7.3475 | 7.2127 | 7.0674 | 6.8896 | 6.6738 | 6.355 | 5.9461 | 5.4024 | 3.2551 | 0.65541 | -0.050015 | -0.86765 | 9.5313 | 9.4582 | 9.3736 | 9.2699 | 9.1575 | 9.0126 | 8.8302 | 8.5693 | 8.1988 | 7.7627 | 6.1002 | 4.1393 | 3.6007 | 2.375 | 8.6959 | 8.5548 | 8.3909 | 8.193 | 7.9537 | 7.6764 | 7.3479 | 6.9769 | 6.4556 | 5.8675 | 3.7727 | 1.2898 | 0.74581 | 0.3065
|  | DRAKES WAY | CT |  |  | 7.5497 | 7.4564 | 7.3475 | 7.2127 | 7.0674 | 6.9052 | 6.7261 | 6.5312 | 6.2567 | 5.8962 | 4.2244 | 1.4518 | 0.20074 | -0.86765 | 9.5313 | 9.4582 | 9.3736 | 9.2699 | 9.1575 | 9.0319 | 8.8863 | 8.6748 | 8.3914 | 8.0665 | 6.8287 | 4.7719 | 4.1274 | 3.2439 | 8.6959 | 8.5548 | 8.3909 | 8.193 | 7.9741 | 7.7294 | 7.4581 | 7.1624 | 6.7696 | 6.3128 | 4.7056 | 2.1017 | 1.283 | 0.81353
|  | DRAKES WAY | LW |  |  | 7.5674 | 7.4674 | 7.358 | 7.2237 | 7.068 | 6.8896 | 6.6738 | 6.355 | 5.9461 | 5.4024 | 3.2551 | 0.65541 | -0.050015 | -0.59334 | 9.5473 | 9.471 | 9.3875 | 9.2867 | 9.1604 | 9.0126 | 8.8302 | 8.5693 | 8.1988 | 7.7627 | 6.1002 | 4.1393 | 3.7663 | 3.4758 | 8.7199 | 8.5648 | 8.3977 | 8.1949 | 7.9537 | 7.6764 | 7.3479 | 6.9769 | 6.4556 | 5.8675 | 3.7727 | 1.2898 | 0.79728 | 0.41705
|  | DRAKES WAY | ST |  |  | 7.6248 | 7.5769 | 7.5252 | 7.4665 | 7.3886 | 7.2991 | 7.1932 | 7.069 | 6.887 | 6.6737 | 5.6636 | 1.9631 | 0.078209 | -0.40659 | 9.5914 | 9.5547 | 9.515 | 9.4694 | 9.4078 | 9.3368 | 9.2535 | 9.156 | 9.0134 | 8.8449 | 7.8645 | 5.0546 | 3.6007 | 3.2024 | 8.8194 | 8.7537 | 8.6829 | 8.6008 | 8.4901 | 8.3604 | 8.207 | 8.0271 | 7.7599 | 7.4378 | 6.0887 | 2.5359 | 0.74581 | 0.3065
|  | DRAKES WAY | SP |  |  | 7.6317 | 7.5899 | 7.5431 | 7.4922 | 7.4324 | 7.3668 | 7.2933 | 7.2114 | 7.0963 | 6.9689 | 6.4841 | 4.3471 | 1.8855 | 1.1094 | 9.5965 | 9.5643 | 9.5278 | 9.4871 | 9.4378 | 9.3833 | 9.3207 | 9.2484 | 9.1551 | 9.0348 | 8.5766 | 6.8638 | 4.9254 | 2.375 | 8.8294 | 8.7742 | 8.7114 | 8.6423 | 8.5588 | 8.4661 | 8.3602 | 8.2419 | 8.0769 | 7.8879 | 7.1847 | 4.8382 | 2.4906 | 1.7698
NURSLING GSP | WINCHESTER | DUNBRIDGE | MINIMUM HEADROOM | SU 31520 26244 | YES | 15.972 | 15.5519 | 15.1433 | 14.7248 | 14.1512 | 13.5751 | 12.9493 | 12.2357 | 11.4407 | 10.8385 | 9.4187 | 7.7732 | 7.3392 | 7.1077 | 18.9206 | 18.6877 | 18.4698 | 18.2389 | 17.9403 | 17.6404 | 17.2922 | 16.8691 | 16.3693 | 16.0333 | 15.4108 | 14.6688 | 14.4762 | 14.0895 | 16.1035 | 15.7224 | 15.353 | 14.9758 | 14.4575 | 13.9369 | 13.374 | 12.7355 | 12.0278 | 11.4834 | 10.1704 | 8.6522 | 8.2543 | 8.0427
|  | DUNBRIDGE | CT |  |  | 16.2961 | 16.0544 | 15.8088 | 15.5592 | 15.2204 | 14.8724 | 14.4929 | 14.0358 | 13.573 | 12.955 | 11.8513 | 9.8208 | 8.5057 | 7.9415 | 18.953 | 18.8321 | 18.6482 | 18.4604 | 18.2501 | 18.0317 | 17.7822 | 17.4636 | 17.1425 | 16.7468 | 16.1847 | 15.2175 | 14.5582 | 14.0895 | 16.4036 | 16.1865 | 15.968 | 15.7469 | 15.4426 | 15.1306 | 14.7917 | 14.3866 | 13.9799 | 13.4497 | 12.4115 | 10.5359 | 9.326 | 8.8074
|  | DUNBRIDGE | LW |  |  | 15.972 | 15.5519 | 15.1433 | 14.7248 | 14.1512 | 13.5751 | 12.9493 | 12.2357 | 11.4407 | 10.8385 | 9.4187 | 7.7732 | 7.3392 | 7.1077 | 18.9206 | 18.6877 | 18.4698 | 18.2389 | 17.9403 | 17.6404 | 17.2922 | 16.8691 | 16.3693 | 16.0333 | 15.4108 | 14.6688 | 14.4762 | 14.3745 | 16.1035 | 15.7224 | 15.353 | 14.9758 | 14.4575 | 13.9369 | 13.374 | 12.7355 | 12.0278 | 11.4834 | 10.1704 | 8.6522 | 8.2543 | 8.0427
|  | DUNBRIDGE | ST |  |  | 16.4839 | 16.3571 | 16.23 | 16.0954 | 15.9028 | 15.7053 | 15.4982 | 15.269 | 15.0169 | 14.7604 | 13.5453 | 12.2058 | 11.4074 | 10.8786 | 19.0044 | 18.944 | 18.9012 | 18.8403 | 18.7136 | 18.5833 | 18.4415 | 18.2795 | 18.093 | 17.9266 | 17.0355 | 16.1423 | 15.6209 | 15.1609 | 16.5692 | 16.4531 | 16.3392 | 16.2201 | 16.0472 | 15.8703 | 15.6852 | 15.481 | 15.2571 | 15.0264 | 13.9723 | 12.7366 | 11.9855 | 11.4993
|  | DUNBRIDGE | SP |  |  | 16.5331 | 16.4319 | 16.3478 | 16.264 | 16.0885 | 15.9272 | 15.765 | 15.5699 | 15.3784 | 15.0927 | 14.069 | 11.7522 | 10.5167 | 9.7266 | 19.0036 | 18.9461 | 18.9098 | 18.8773 | 18.8057 | 18.7054 | 18.6017 | 18.4692 | 18.3357 | 18.1675 | 17.5043 | 15.9487 | 15.278 | 14.8162 | 16.6146 | 16.5221 | 16.4466 | 16.3723 | 16.214 | 16.0687 | 15.9225 | 15.7481 | 15.5768 | 15.3197 | 14.407 | 12.349 | 11.1955 | 10.4699
MANNINGTON GSP | REDHILL BSP | EAST HOWE | MINIMUM HEADROOM | SZ 06789 95116 | YES | 8.5686 | 7.7761 | 6.9442 | 6.0408 | 4.6484 | 3.1661 | 1.5705 | -0.1505 | -2.2055 | -4.4253 | -10.0767 | -17.2544 | -24.5317 | -28.5366 | 15.4962 | 14.9989 | 14.4466 | 13.847 | 13.053 | 12.1994 | 11.2552 | 10.2246 | 8.9645 | 7.4895 | 3.896 | -0.80717 | -5.026 | -8.8277 | 10.7598 | 10.059 | 9.2886 | 8.4497 | 7.1812 | 5.8289 | 4.3645 | 2.7809 | 0.87741 | -1.1952 | -6.4511 | -12.8623 | -19.1809 | -22.6207
|  | EAST HOWE | CT |  |  | 8.7672 | 8.1183 | 7.5454 | 6.7152 | 5.6982 | 4.6131 | 3.415 | 2.1154 | 0.65514 | -1.5437 | -7.6675 | -17.2544 | -24.5317 | -28.5366 | 15.544 | 15.0912 | 14.6737 | 14.0567 | 13.3914 | 12.6807 | 11.8942 | 11.0355 | 10.0528 | 8.6087 | 4.5413 | -0.80717 | -5.026 | -8.8277 | 10.9316 | 10.3594 | 9.8325 | 9.0519 | 8.1166 | 7.1188 | 6.014 | 4.8136 | 3.4574 | 1.419 | -4.2683 | -12.8405 | -19.1809 | -22.6207
|  | EAST HOWE | LW |  |  | 8.5686 | 7.7761 | 6.9442 | 6.0408 | 4.6484 | 3.1661 | 1.5705 | -0.1505 | -2.2055 | -4.4253 | -10.0767 | -17.1886 | -20.9529 | -23.2509 | 15.4962 | 14.9989 | 14.4466 | 13.847 | 13.053 | 12.1994 | 11.2552 | 10.2246 | 8.9645 | 7.4895 | 3.896 | 0.01212 | -1.7358 | -2.8488 | 10.7598 | 10.059 | 9.2886 | 8.4497 | 7.1812 | 5.8289 | 4.3645 | 2.7809 | 0.87741 | -1.1952 | -6.4511 | -12.8623 | -16.1017 | -18.0372
|  | EAST HOWE | ST |  |  | 9.0847 | 8.6743 | 8.3383 | 7.9837 | 7.5075 | 6.9916 | 6.4252 | 5.802 | 5.0967 | 4.3967 | 1.7396 | -5.1228 | -9.1247 | -12.103 | 15.7586 | 15.454 | 15.1863 | 14.9043 | 14.5402 | 14.1472 | 13.7115 | 13.2307 | 12.6833 | 12.1462 | 10.0079 | 4.5465 | 1.2209 | -2.1857 | 11.2359 | 10.8889 | 10.5862 | 10.2656 | 9.8316 | 9.3616 | 8.8422 | 8.269 | 7.6169 | 6.9712 | 4.4427 | -1.8358 | -5.4162 | -8.0207
|  | EAST HOWE | SP |  |  | 9.1411 | 8.7204 | 8.3829 | 8.043 | 7.6374 | 7.2254 | 6.7842 | 6.2838 | 5.7437 | 5.173 | 3.2689 | -2.1055 | -5.9787 | -7.8176 | 15.7819 | 15.457 | 15.1744 | 14.889 | 14.5879 | 14.2756 | 13.938 | 13.5485 | 13.1242 | 12.6235 | 10.8386 | 5.6223 | 0.24337 | -6.1345 | 11.287 | 10.927 | 10.6205 | 10.3119 | 9.9501 | 9.5835 | 9.1888 | 8.7367 | 8.2477 | 7.7262 | 5.9342 | 0.96721 | -2.3917 | -3.9446
MELKSHAM GSP | NORRINGTON | EASTERTON | MINIMUM HEADROOM | SU 01568 54730 | NO | 6.0999 | 5.7047 | 5.2632 | 4.8101 | 4.2141 | 3.592 | 2.9427 | 2.2301 | 1.3538 | 0.57991 | -1.1003 | -2.7812 | -3.1242 | -3.3229 | 4.3683 | 4.1841 | 3.9581 | 3.7195 | 3.4216 | 3.1035 | 2.757 | 2.3585 | 1.84 | 1.3879 | 0.6334 | -0.079152 | -0.21524 | -0.40428 | 2.0662 | 1.7097 | 1.3073 | 0.89299 | 0.35117 | -0.21577 | -0.81054 | -1.4671 | -2.2814 | -3.0135 | -4.5076 | -6.0096 | -6.313 | -6.4876
|  | EASTERTON | CT |  |  | 6.4822 | 6.3081 | 6.0934 | 5.8227 | 5.4663 | 5.092 | 4.6696 | 4.1921 | 3.639 | 2.9264 | 1.5771 | -0.34309 | -1.5835 | -2.0851 | 4.4875 | 4.3704 | 4.2308 | 4.0445 | 3.832 | 3.6059 | 3.3516 | 3.0552 | 2.6966 | 2.2416 | 1.5064 | 0.59526 | 0.0045639 | -0.40428 | 2.3959 | 2.2211 | 2.0186 | 1.7603 | 1.428 | 1.0785 | 0.68419 | 0.23603 | -0.28738 | -0.96205 | -2.1998 | -3.893 | -4.9523 | -5.3929
|  | EASTERTON | LW |  |  | 6.0999 | 5.7047 | 5.2632 | 4.8101 | 4.2141 | 3.592 | 2.9427 | 2.2301 | 1.3538 | 0.57991 | -1.1003 | -2.7812 | -3.1242 | -3.3229 | 4.3683 | 4.1841 | 3.9581 | 3.7195 | 3.4216 | 3.1035 | 2.757 | 2.3585 | 1.84 | 1.3879 | 0.6334 | -0.079152 | -0.21524 | -0.29035 | 2.0662 | 1.7097 | 1.3073 | 0.89299 | 0.35117 | -0.21577 | -0.81054 | -1.4671 | -2.2814 | -3.0135 | -4.5076 | -6.0096 | -6.313 | -6.4876
|  | EASTERTON | ST |  |  | 6.5114 | 6.5006 | 6.4609 | 6.3427 | 6.1308 | 5.9104 | 5.6777 | 5.4253 | 5.1417 | 4.8483 | 3.5716 | 1.9553 | 1.2098 | 0.76107 | 4.5902 | 4.534 | 4.4638 | 4.3832 | 4.2555 | 4.1209 | 3.9739 | 3.8111 | 3.6233 | 3.4453 | 2.5921 | 1.5346 | 1.0684 | 0.66554 | 2.5498 | 2.4667 | 2.3672 | 2.2559 | 2.0589 | 1.8537 | 1.6359 | 1.3988 | 1.1311 | 0.85744 | -0.35674 | -1.8705 | -2.5361 | -2.9307
|  | EASTERTON | SP |  |  | 6.51 | 6.4966 | 6.4806 | 6.4643 | 6.3031 | 6.1235 | 5.9353 | 5.7305 | 5.5173 | 5.1958 | 4.0505 | 1.3084 | -0.10723 | -1.0402 | 4.6078 | 4.5533 | 4.491 | 4.4261 | 4.3239 | 4.2183 | 4.108 | 3.9817 | 3.8451 | 3.6687 | 2.9887 | 1.2608 | 0.48865 | -0.070277 | 2.599 | 2.5305 | 2.4549 | 2.3773 | 2.213 | 2.0473 | 1.874 | 1.6839 | 1.4849 | 1.19 | 0.12639 | -2.4424 | -3.7154 | -4.5018
BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD | MINIMUM HEADROOM | SU 86148 67194 | YES | 10.8502 | 10.2621 | 9.6377 | 8.9755 | 7.8307 | 6.5899 | 5.1191 | 3.5404 | 1.6756 | -0.29073 | -5.4034 | -11.8493 | -16.3516 | -18.8912 | 16.1525 | 15.7232 | 15.2508 | 14.7424 | 14.0392 | 13.269 | 12.3313 | 11.3021 | 10.006 | 8.636 | 5.3586 | 1.0072 | -2.419 | -5.5161 | 12.5113 | 11.9682 | 11.3965 | 10.7613 | 9.6987 | 8.5497 | 7.193 | 5.7292 | 3.9395 | 1.9896 | -2.8522 | -8.8439 | -12.5902 | -14.6564
|  | EASTHAMPSTEAD | CT |  |  | 10.985 | 10.501 | 10.045 | 9.4347 | 8.6182 | 7.7148 | 6.6538 | 5.4934 | 4.2003 | 2.1953 | -3.1582 | -11.1717 | -16.3516 | -18.8912 | 16.1623 | 15.7421 | 15.3432 | 14.7967 | 14.1927 | 13.5258 | 12.7485 | 11.8798 | 10.8756 | 9.511 | 5.9434 | 1.0072 | -2.419 | -5.5161 | 12.6373 | 12.189 | 11.7602 | 11.1658 | 10.3953 | 9.5472 | 8.5624 | 7.4787 | 6.1719 | 4.2629 | -0.78015 | -8.0924 | -12.5902 | -14.6564
|  | EASTHAMPSTEAD | LW |  |  | 10.8502 | 10.2621 | 9.6377 | 8.9755 | 7.8307 | 6.5899 | 5.1191 | 3.5404 | 1.6756 | -0.29073 | -5.4034 | -11.8493 | -14.2678 | -15.2812 | 16.1525 | 15.7232 | 15.2508 | 14.7424 | 14.0392 | 13.269 | 12.3313 | 11.3021 | 10.006 | 8.636 | 5.3586 | 1.5324 | 0.42202 | -0.056666 | 12.5113 | 11.9682 | 11.3965 | 10.7613 | 9.6987 | 8.5497 | 7.193 | 5.7292 | 3.9395 | 1.9896 | -2.8522 | -8.8439 | -10.9565 | -11.8103
|  | EASTHAMPSTEAD | ST |  |  | 11.3016 | 11.0093 | 10.7734 | 10.531 | 10.2206 | 9.869 | 9.4005 | 8.8881 | 8.3038 | 7.7558 | 5.3512 | -0.57596 | -3.5541 | -5.5029 | 16.3792 | 16.101 | 15.8778 | 15.6486 | 15.3606 | 15.0356 | 14.6228 | 14.1644 | 13.6306 | 13.1323 | 10.9657 | 6.1031 | 3.2776 | 0.35289 | 12.9141 | 12.6337 | 12.4177 | 12.2013 | 11.9272 | 11.5942 | 11.1621 | 10.6852 | 10.1333 | 9.6089 | 7.1929 | 1.5201 | -1.1562 | -2.8305
|  | EASTHAMPSTEAD | SP |  |  | 11.3576 | 11.0425 | 10.8004 | 10.5641 | 10.3072 | 10.0308 | 9.6687 | 9.2583 | 8.8267 | 8.399 | 6.8239 | 1.6851 | -1.5047 | -2.6545 | 16.4109 | 16.1057 | 15.865 | 15.6269 | 15.3849 | 15.1239 | 14.7961 | 14.4254 | 14.0147 | 13.5579 | 11.814 | 6.6492 | 1.7853 | -3.8005 | 12.9634 | 12.6641 | 12.4438 | 12.2336 | 12.0074 | 11.7488 | 11.4207 | 11.0448 | 10.6427 | 10.2335 | 8.6803 | 3.628 | 0.58264 | -0.44766
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH | MINIMUM HEADROOM | SU 45426 18958 | YES | 11.1379 | 9.7519 | 8.1751 | 6.7489 | 4.7943 | 2.8216 | 0.7799 | -1.2136 | -3.6614 | -6.0946 | -11.8841 | -18.7031 | -23.5378 | -26.248 | 21.3474 | 20.3683 | 19.2642 | 18.3136 | 17.1696 | 16.0135 | 14.7836 | 13.5377 | 11.8794 | 10.2414 | 6.6486 | 1.1903 | -3.6023 | -10.7115 | 14.7533 | 13.5135 | 12.1081 | 10.7992 | 9.0018 | 7.1634 | 5.2159 | 3.2823 | 0.88942 | -1.4916 | -6.98 | -13.1737 | -16.9473 | -19.2438
|  | EASTLEIGH NORTH | CT |  |  | 11.4593 | 10.2825 | 8.9805 | 7.7051 | 6.2265 | 4.7506 | 3.2489 | 1.7654 | 0.10287 | -2.3537 | -8.3988 | -17.5399 | -23.5378 | -26.248 | 21.3888 | 20.4416 | 19.4277 | 18.4422 | 17.4169 | 16.3892 | 15.3313 | 14.2378 | 12.9385 | 11.1944 | 7.0185 | 1.1903 | -3.6023 | -8.9236 | 15.0294 | 13.9751 | 12.8201 | 11.5494 | 10.1405 | 8.7144 | 7.2545 | 5.8184 | 4.1715 | 1.7785 | -3.9641 | -11.9792 | -16.9473 | -19.2438
|  | EASTLEIGH NORTH | LW |  |  | 11.1379 | 9.7519 | 8.1751 | 6.7489 | 4.7943 | 2.8216 | 0.7799 | -1.2136 | -3.6614 | -6.0946 | -11.8841 | -18.7031 | -21.3272 | -22.3199 | 21.3474 | 20.3683 | 19.2642 | 18.3136 | 17.1696 | 16.0135 | 14.7836 | 13.5377 | 11.8794 | 10.2414 | 6.6486 | 2.894 | 1.7812 | 1.3363 | 14.7533 | 13.5135 | 12.1081 | 10.7992 | 9.0018 | 7.1634 | 5.2159 | 3.2823 | 0.88942 | -1.4916 | -6.98 | -13.1737 | -15.3627 | -16.1784
|  | EASTLEIGH NORTH | ST |  |  | 11.8626 | 11.0238 | 10.1334 | 9.4513 | 8.679 | 7.9316 | 7.1788 | 6.4839 | 5.7209 | 4.9036 | 1.6355 | -5.3754 | -8.8285 | -11.0903 | 21.6748 | 20.9521 | 20.1978 | 19.6224 | 18.9761 | 18.3451 | 17.6934 | 17.0542 | 16.3357 | 15.6332 | 12.6611 | 6.3728 | 2.1121 | -2.9635 | 15.4124 | 14.676 | 13.9058 | 13.327 | 12.6481 | 11.9091 | 11.1469 | 10.4152 | 9.5962 | 8.7807 | 5.4033 | -1.3844 | -4.4979 | -6.3867
|  | EASTLEIGH NORTH | SP |  |  | 11.9201 | 11.0952 | 10.2457 | 9.6288 | 8.9902 | 8.3846 | 7.7866 | 7.244 | 6.6644 | 6.0304 | 3.8208 | -2.5133 | -6.1342 | -7.4517 | 21.6919 | 20.9552 | 20.2033 | 19.6476 | 19.0887 | 18.5469 | 17.9891 | 17.4354 | 16.824 | 16.1346 | 13.6615 | 6.4614 | -0.81223 | -10.7115 | 15.4642 | 14.7377 | 14.004 | 13.4852 | 12.9427 | 12.3744 | 11.7912 | 11.2319 | 10.6232 | 9.9656 | 7.6628 | 1.2904 | -2.1369 | -3.3213
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY | MINIMUM HEADROOM | SZ 66357 99040 | YES | 21.3504 | 21.1588 | 20.9182 | 20.6535 | 20.186 | 19.6819 | 19.1469 | 18.5383 | 17.8339 | 17.0739 | 14.6354 | 10.8748 | 7.7737 | 5.5133 | 17.0807 | 16.9485 | 16.7952 | 16.5958 | 16.3383 | 16.0591 | 15.7565 | 15.3908 | 14.9735 | 14.4234 | 12.6625 | 8.8696 | 3.3218 | -7.7458 | 15.2067 | 15.0338 | 14.8132 | 14.5691 | 14.1445 | 13.6846 | 13.193 | 12.6318 | 11.9765 | 11.2671 | 8.9902 | 5.6024 | 3.0376 | 1.1487
|  | EASTNEY | CT |  |  | 21.4267 | 21.2869 | 21.1181 | 20.8827 | 20.5508 | 20.1942 | 19.8234 | 19.3873 | 18.8955 | 18.139 | 15.771 | 11.2706 | 7.7737 | 5.5133 | 17.0807 | 16.9485 | 16.7952 | 16.5958 | 16.3383 | 16.0591 | 15.7565 | 15.3908 | 14.9735 | 14.4234 | 12.6625 | 8.8696 | 4.4949 | -1.487 | 15.2724 | 15.1456 | 14.9908 | 14.7703 | 14.4654 | 14.1368 | 13.7926 | 13.3871 | 12.9267 | 12.2261 | 10.0355 | 6.0234 | 3.0376 | 1.1487
|  | EASTNEY | LW |  |  | 21.3504 | 21.1588 | 20.9182 | 20.6535 | 20.186 | 19.6819 | 19.1469 | 18.5383 | 17.8339 | 17.0739 | 14.6354 | 10.8748 | 8.6623 | 7.0308 | 17.0986 | 16.9987 | 16.872 | 16.7306 | 16.4999 | 16.2494 | 15.9784 | 15.6538 | 15.2688 | 14.8459 | 13.5068 | 11.4043 | 10.3269 | 9.5097 | 15.2067 | 15.0338 | 14.8132 | 14.5691 | 14.1445 | 13.6846 | 13.193 | 12.6318 | 11.9765 | 11.2671 | 8.9902 | 5.6024 | 3.7489 | 2.4101
|  | EASTNEY | ST |  |  | 21.5559 | 21.495 | 21.4263 | 21.3418 | 21.2215 | 21.0908 | 20.9471 | 20.7543 | 20.5227 | 20.2501 | 19.2926 | 16.3951 | 14.1594 | 12.5589 | 17.15 | 17.0596 | 16.9599 | 16.8435 | 16.6895 | 16.5215 | 16.3324 | 16.0885 | 15.8028 | 15.4883 | 14.4015 | 11.25 | 7.2522 | 1.5937 | 15.3951 | 15.3429 | 15.2833 | 15.2081 | 15.0984 | 14.9787 | 14.8457 | 14.6665 | 14.4497 | 14.1957 | 13.299 | 10.6506 | 8.7324 | 7.4257
|  | EASTNEY | SP |  |  | 21.5782 | 21.5133 | 21.4383 | 21.3537 | 21.2638 | 21.1611 | 21.0534 | 20.9001 | 20.7193 | 20.4945 | 19.7839 | 17.6921 | 15.6148 | 14.341 | 17.1511 | 17.0498 | 16.9299 | 16.7946 | 16.6226 | 16.4248 | 16.203 | 15.9212 | 15.5901 | 15.194 | 13.8088 | 9.9398 | 3.3218 | -7.7458 | 15.4162 | 15.3593 | 15.2928 | 15.2167 | 15.1364 | 15.0437 | 14.9453 | 14.8046 | 14.637 | 14.4283 | 13.7695 | 11.8679 | 10.0358 | 8.993
LALEHAM | STAINES | EGHAM | MINIMUM HEADROOM | TQ 01030 71404 | YES | 4.203 | 3.0323 | 1.8594 | 0.73284 | 25.1496 | 23.4917 | 21.7603 | 20.2129 | 18.4087 | 16.631 | 11.9378 | 6.4745 | 4.2138 | 2.648 | 13.6861 | 13.0569 | 12.4059 | 11.7351 | 36.8715 | 35.9628 | 34.9889 | 34.0802 | 32.9503 | 31.8386 | 29.0204 | 24.9034 | 21.3166 | 15.6646 | 5.9306 | 4.899 | 3.8413 | 2.8156 | 27.4152 | 25.9439 | 24.3943 | 22.9705 | 21.285 | 19.6182 | 15.2497 | 10.2303 | 8.4804 | 7.2023
|  | EGHAM | CT |  |  | 4.5659 | 3.6046 | 2.6024 | 1.5975 | 26.3584 | 25.0609 | 23.755 | 22.6795 | 21.462 | 19.7616 | 15.2874 | 8.4147 | 4.2138 | 2.648 | 13.752 | 13.1769 | 12.5376 | 11.8478 | 37.0639 | 36.2406 | 35.3839 | 34.6173 | 33.7182 | 32.5634 | 29.531 | 24.9034 | 21.3166 | 17.4305 | 6.1921 | 5.3284 | 4.4604 | 3.5696 | 28.4754 | 27.3262 | 26.1601 | 25.1656 | 24.0252 | 22.4324 | 18.271 | 12.0348 | 8.4804 | 7.2023
|  | EGHAM | LW |  |  | 4.203 | 3.0323 | 1.8594 | 0.73284 | 25.1496 | 23.4917 | 21.7603 | 20.2129 | 18.4087 | 16.631 | 11.9378 | 6.4745 | 4.8847 | 4.1521 | 13.6861 | 13.0569 | 12.4059 | 11.7351 | 36.8715 | 35.9628 | 34.9889 | 34.0802 | 32.9503 | 31.8386 | 29.0204 | 25.9531 | 25.2738 | 24.9804 | 5.9306 | 4.899 | 3.8413 | 2.8156 | 27.4152 | 25.9439 | 24.3943 | 22.9705 | 21.285 | 19.6182 | 15.2497 | 10.2303 | 8.8548 | 8.2553
|  | EGHAM | ST |  |  | 5.0115 | 4.3931 | 3.8348 | 3.3306 | 28.6647 | 27.9498 | 27.2208 | 26.6462 | 26.0031 | 25.3514 | 22.6699 | 17.0766 | 14.313 | 12.8901 | 13.8914 | 13.5106 | 13.221 | 12.8567 | 38.4187 | 37.963 | 37.4193 | 36.9427 | 36.3968 | 35.8634 | 33.6057 | 28.6976 | 25.2483 | 21.4064 | 6.6836 | 6.1686 | 5.6874 | 5.2326 | 30.6479 | 30.0327 | 29.3987 | 28.871 | 28.272 | 27.6617 | 25.1012 | 19.7906 | 17.2658 | 16.0231
|  | EGHAM | SP |  |  | 5.0768 | 4.4974 | 3.9924 | 3.5579 | 28.9386 | 28.2895 | 27.6273 | 27.0883 | 26.5299 | 25.9251 | 23.8035 | 18.3783 | 14.9764 | 13.6817 | 13.8934 | 13.5155 | 13.2283 | 12.9177 | 38.4947 | 38.057 | 37.5979 | 37.1495 | 36.6473 | 36.1128 | 34.1123 | 28.6302 | 22.9348 | 15.6646 | 6.7374 | 6.2515 | 5.8192 | 5.4322 | 30.9069 | 30.3615 | 29.7971 | 29.3115 | 28.8014 | 28.2445 | 26.2583 | 21.101 | 17.8968 | 16.7251
MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE | MINIMUM HEADROOM | SZ 08757 91379 | YES | 10.7398 | 10.3265 | 9.8791 | 9.3933 | 8.6081 | 7.9381 | 7.2386 | 6.4931 | 5.6763 | 4.9111 | 2.4732 | -1.1863 | -3.2649 | -5.3247 | 7.2865 | 7.135 | 6.9757 | 6.7989 | 6.543 | 6.2707 | 5.912 | 5.5255 | 5.0836 | 4.645 | 3.069 | -0.38022 | -4.8127 | -13.6088 | 6.8005 | 6.4966 | 6.1222 | 5.713 | 5.0475 | 4.4645 | 3.8541 | 3.2034 | 2.498 | 1.8389 | -0.25217 | -3.2472 | -4.8623 | -6.4714
|  | ELECTRIC HOUSE | CT |  |  | 10.9718 | 10.6846 | 10.3625 | 9.9994 | 9.4086 | 8.9384 | 8.4941 | 8.0143 | 7.4471 | 6.7622 | 4.6228 | 0.23723 | -3.1334 | -5.3247 | 7.3003 | 7.1527 | 6.99 | 6.808 | 6.5579 | 6.289 | 5.9423 | 5.5624 | 5.1242 | 4.645 | 3.069 | -0.38022 | -4.0809 | -8.8736 | 6.839 | 6.6673 | 6.4788 | 6.242 | 5.748 | 5.3422 | 4.9588 | 4.5452 | 4.0786 | 3.4976 | 1.6873 | -1.9738 | -4.6618 | -6.4714
|  | ELECTRIC HOUSE | LW |  |  | 10.7398 | 10.3265 | 9.8791 | 9.3933 | 8.6081 | 7.9381 | 7.2386 | 6.4931 | 5.6763 | 4.9111 | 2.4732 | -1.1863 | -3.2649 | -4.8876 | 7.2865 | 7.135 | 6.9757 | 6.7989 | 6.543 | 6.2707 | 5.912 | 5.5255 | 5.0836 | 4.6676 | 3.3013 | 1.2976 | 0.28498 | -0.53248 | 6.8005 | 6.4966 | 6.1222 | 5.713 | 5.0475 | 4.4645 | 3.8541 | 3.2034 | 2.498 | 1.8389 | -0.25217 | -3.2472 | -4.8623 | -6.2003
|  | ELECTRIC HOUSE | ST |  |  | 11.1455 | 11.0215 | 10.8765 | 10.7206 | 10.4656 | 10.286 | 10.0915 | 9.8743 | 9.6012 | 9.3064 | 8.2368 | 5.2208 | 2.8477 | 1.3148 | 7.3772 | 7.2868 | 7.1904 | 7.0851 | 6.931 | 6.8023 | 6.6571 | 6.4928 | 6.1946 | 5.8966 | 4.7947 | 1.636 | -1.9087 | -6.4416 | 6.937 | 6.8373 | 6.7326 | 6.6204 | 6.4516 | 6.329 | 6.1921 | 6.0373 | 5.833 | 5.6102 | 4.7378 | 1.8184 | -0.047343 | -1.0483
|  | ELECTRIC HOUSE | SP |  |  | 11.1486 | 11.0396 | 10.9256 | 10.8047 | 10.6272 | 10.5018 | 10.366 | 10.2156 | 10.0403 | 9.8192 | 9.0673 | 6.6728 | 4.1323 | 2.5656 | 7.3791 | 7.2933 | 7.1983 | 7.0943 | 6.9446 | 6.8144 | 6.6679 | 6.451 | 6.1313 | 5.7939 | 4.5626 | 0.92659 | -4.8127 | -13.6088 | 6.9456 | 6.8552 | 6.7606 | 6.6596 | 6.5171 | 6.4197 | 6.3132 | 6.1936 | 6.0461 | 5.8894 | 5.3686 | 3.5334 | 0.89109 | 0.0089376
BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD | MINIMUM HEADROOM | SU 81057 68532 | YES | 10.5879 | 9.8511 | 9.107 | 8.211 | 6.639 | 5.0195 | 3.3532 | 1.5737 | -0.6219 | -2.6512 | -7.5654 | -13.3293 | -16.0788 | -18.279 | 17.7374 | 17.2985 | 16.8543 | 16.3157 | 15.4631 | 14.574 | 13.6301 | 12.607 | 11.2319 | 9.9563 | 7.0416 | 3.0877 | -0.36414 | -4.153 | 11.8728 | 11.2366 | 10.5924 | 9.8168 | 8.5221 | 7.1801 | 5.7769 | 4.2662 | 2.315 | 0.50803 | -3.669 | -8.7466 | -11.0636 | -12.9024
|  | ELMS ROAD | CT |  |  | 10.8495 | 10.2953 | 9.6682 | 8.9292 | 7.7438 | 6.5296 | 5.3577 | 4.0922 | 2.5384 | 0.56736 | -4.2489 | -11.5031 | -16.0788 | -18.279 | 17.76 | 17.3517 | 16.8817 | 16.3456 | 15.6077 | 14.8423 | 14.0674 | 13.2182 | 12.1457 | 10.8384 | 7.708 | 3.0877 | -0.36414 | -3.8258 | 12.0277 | 11.5219 | 10.9404 | 10.2701 | 9.2693 | 8.2394 | 7.2249 | 6.1204 | 4.7349 | 2.9825 | -1.1222 | -7.0461 | -11.0636 | -12.9024
|  | ELMS ROAD | LW |  |  | 10.5879 | 9.8511 | 9.107 | 8.211 | 6.639 | 5.0195 | 3.3532 | 1.5737 | -0.6219 | -2.6512 | -7.5654 | -13.3293 | -15.3035 | -16.296 | 17.7374 | 17.2985 | 16.8543 | 16.3157 | 15.4631 | 14.574 | 13.6301 | 12.607 | 11.2319 | 9.9563 | 7.0416 | 3.8031 | 2.9081 | 2.448 | 11.8728 | 11.2366 | 10.5924 | 9.8168 | 8.5221 | 7.1801 | 5.7769 | 4.2662 | 2.315 | 0.50803 | -3.669 | -8.7466 | -10.4636 | -11.3084
|  | ELMS ROAD | ST |  |  | 11.3207 | 11.051 | 10.746 | 10.3406 | 9.6942 | 9.0334 | 8.3726 | 7.661 | 6.826 | 6.0464 | 2.8673 | -3.1357 | -6.2611 | -7.9695 | 18.1005 | 17.8949 | 17.6525 | 17.3383 | 16.8817 | 16.4075 | 15.9154 | 15.3774 | 14.7362 | 14.1379 | 11.5859 | 6.5938 | 3.3188 | 0.016301 | 12.4863 | 12.2517 | 11.9772 | 11.6127 | 11.049 | 10.4698 | 9.8822 | 9.2453 | 8.4929 | 7.7915 | 4.8035 | -0.6747 | -3.2786 | -4.6103
|  | ELMS ROAD | SP |  |  | 11.3772 | 11.1377 | 10.8916 | 10.5764 | 9.9687 | 9.356 | 8.7472 | 8.0799 | 7.325 | 6.6007 | 4.1404 | -1.8996 | -5.4727 | -6.9478 | 18.12 | 17.9228 | 17.7055 | 17.4378 | 17.0304 | 16.606 | 16.16 | 15.6582 | 15.0769 | 14.4959 | 12.3927 | 6.7887 | 1.729 | -4.153 | 12.5313 | 12.3191 | 12.0975 | 11.817 | 11.3145 | 10.8034 | 10.2837 | 9.7046 | 9.0436 | 8.4098 | 6.1944 | 0.56433 | -2.5914 | -3.7998
LOVEDEAN GSP | HAVANT | EMSWORTH | MINIMUM HEADROOM | SU 74861 05807 | YES | 1.1417 | 0.78023 | 0.28822 | -0.25816 | -1.0976 | -2.0099 | -2.9843 | -4.0144 | -5.3136 | -6.7354 | -10.6056 | -14.7119 | -17.0033 | -18.5955 | 2.9553 | 2.7452 | 2.4556 | 2.1302 | 1.6749 | 1.1777 | 0.63612 | 0.0041816 | -0.84467 | -1.8348 | -4.4839 | -7.0116 | -8.8283 | -10.4119 | -0.45783 | -0.77875 | -1.2053 | -1.6808 | -2.4228 | -3.2247 | -4.0786 | -5.0066 | -6.1785 | -7.5581 | -11.3071 | -15.1267 | -16.9932 | -18.37
|  | EMSWORTH | CT |  |  | 1.2626 | 0.99287 | 0.62451 | 0.12272 | -0.50375 | -1.1881 | -1.892 | -2.6384 | -3.5377 | -4.9208 | -8.7768 | -13.9293 | -17.0033 | -18.5955 | 2.9754 | 2.7889 | 2.5443 | 2.2248 | 1.847 | 1.4353 | 1.0034 | 0.48091 | -0.1658 | -1.1387 | -3.84 | -7.0116 | -8.8283 | -10.4119 | -0.34597 | -0.58218 | -0.89545 | -1.3037 | -1.8393 | -2.4221 | -3.0217 | -3.6955 | -4.5698 | -5.9084 | -9.6375 | -14.3701 | -16.9932 | -18.37
|  | EMSWORTH | LW |  |  | 1.1417 | 0.78023 | 0.28822 | -0.25816 | -1.0976 | -2.0099 | -2.9843 | -4.0144 | -5.3136 | -6.7354 | -10.6056 | -14.7119 | -16.119 | -16.9359 | 2.9553 | 2.7452 | 2.4556 | 2.1302 | 1.6749 | 1.1777 | 0.63612 | 0.0041816 | -0.84467 | -1.8348 | -4.4839 | -6.9665 | -7.595 | -7.9752 | -0.45783 | -0.77875 | -1.2053 | -1.6808 | -2.4228 | -3.2247 | -4.0786 | -5.0066 | -6.1785 | -7.5581 | -11.3071 | -15.1267 | -16.3316 | -17.015
|  | EMSWORTH | ST |  |  | 1.5257 | 1.4091 | 1.243 | 1.0489 | 0.76386 | 0.43068 | 0.066907 | -0.33769 | -0.85506 | -1.4233 | -3.7865 | -8.9243 | -11.2616 | -12.4074 | 3.1435 | 3.0537 | 2.9324 | 2.7901 | 2.5887 | 2.3664 | 2.1198 | 1.8065 | 1.3985 | 0.94375 | -0.91721 | -5.3767 | -7.2337 | -8.2116 | -0.10947 | -0.20705 | -0.34035 | -0.49827 | -0.73745 | -1.0029 | -1.296 | -1.6532 | -2.1175 | -2.6505 | -4.9744 | -9.9108 | -12.0247 | -12.9948
|  | EMSWORTH | SP |  |  | 1.5566 | 1.4425 | 1.2896 | 1.1181 | 0.904 | 0.66047 | 0.40432 | 0.10649 | -0.26831 | -0.70551 | -2.3365 | -6.44 | -9.1607 | -10.0796 | 3.1558 | 3.063 | 2.9435 | 2.8085 | 2.6542 | 2.4841 | 2.3016 | 2.053 | 1.7355 | 1.3539 | -0.062504 | -3.5407 | -6.4292 | -8.7949 | -0.081052 | -0.17472 | -0.29488 | -0.43151 | -0.60621 | -0.7961 | -0.99943 | -1.2666 | -1.6078 | -2.0201 | -3.5721 | -7.5509 | -10.1081 | -10.9129
MELKSHAM GSP | AMESBURY | ENFORD | MINIMUM HEADROOM | SU 13728 51712 | YES | 4.8327 | 4.8252 | 4.8118 | 4.682 | 4.4211 | 4.1491 | 3.8653 | 3.5766 | 3.2008 | 2.8297 | 1.9418 | 1.3002 | 1.2336 | 1.2121 | 4.827 | 4.7574 | 4.6715 | 4.5804 | 4.4649 | 4.3416 | 4.2079 | 4.0577 | 3.8489 | 3.6409 | 3.2071 | 2.8964 | 2.8659 | 2.7059 | 4.6214 | 4.4869 | 4.3215 | 4.1403 | 3.8975 | 3.6455 | 3.3852 | 3.1217 | 2.7813 | 2.4408 | 1.612 | 1.009 | 0.94754 | 0.92811
|  | ENFORD | CT |  |  | 4.8327 | 4.8255 | 4.8154 | 4.7992 | 4.7837 | 4.7602 | 4.6175 | 4.4245 | 4.1971 | 3.8823 | 3.1524 | 2.559 | 2.354 | 2.2733 | 4.8778 | 4.8376 | 4.7875 | 4.7166 | 4.6336 | 4.5449 | 4.4461 | 4.3425 | 4.2101 | 4.0302 | 3.6294 | 3.3023 | 3.1583 | 3.0316 | 4.7528 | 4.6886 | 4.6113 | 4.507 | 4.3725 | 4.2301 | 4.0718 | 3.9074 | 3.7001 | 3.4047 | 2.7321 | 2.1947 | 2.0115 | 1.9362
|  | ENFORD | LW |  |  | 4.8338 | 4.8252 | 4.8118 | 4.682 | 4.4211 | 4.1491 | 3.8653 | 3.5766 | 3.2008 | 2.8297 | 1.9418 | 1.3002 | 1.2336 | 1.2121 | 4.827 | 4.7574 | 4.6715 | 4.5804 | 4.4649 | 4.3416 | 4.2079 | 4.0577 | 3.8489 | 3.6409 | 3.2071 | 2.8964 | 2.8659 | 2.8566 | 4.6214 | 4.4869 | 4.3215 | 4.1403 | 3.8975 | 3.6455 | 3.3852 | 3.1217 | 2.7813 | 2.4408 | 1.612 | 1.009 | 0.94754 | 0.92811
|  | ENFORD | ST |  |  | 4.8396 | 4.8367 | 4.8325 | 4.8274 | 4.8191 | 4.8097 | 4.7992 | 4.7876 | 4.7708 | 4.6492 | 4.1159 | 3.2656 | 2.8837 | 2.6388 | 4.906 | 4.8841 | 4.8576 | 4.8283 | 4.7801 | 4.7281 | 4.6728 | 4.6127 | 4.5424 | 4.4721 | 4.1622 | 3.6276 | 3.4061 | 3.2194 | 4.7945 | 4.7578 | 4.7159 | 4.6707 | 4.5928 | 4.5102 | 4.4245 | 4.3329 | 4.2261 | 4.1128 | 3.6264 | 2.8316 | 2.4921 | 2.2708
|  | ENFORD | SP |  |  | 4.8397 | 4.8354 | 4.8308 | 4.8258 | 4.8202 | 4.8136 | 4.8069 | 4.7985 | 4.7401 | 4.5642 | 3.9715 | 2.6075 | 1.8332 | 1.3768 | 4.9119 | 4.8889 | 4.8642 | 4.8379 | 4.7884 | 4.7356 | 4.6821 | 4.6222 | 4.5581 | 4.4801 | 4.1871 | 3.3944 | 2.9796 | 2.7059 | 4.8094 | 4.7759 | 4.7407 | 4.7038 | 4.6129 | 4.5171 | 4.421 | 4.3172 | 4.2068 | 4.0415 | 3.4947 | 2.2418 | 1.5156 | 1.0822
COWLEY GSP | YARNTON BSP | EYNSHAM | MINIMUM HEADROOM | SP 42236 10266 | NO | 11.6289 | 11.0758 | 10.2702 | 9.2434 | 7.7187 | 5.9829 | 4.1335 | 2.1996 | 0.16964 | -1.9192 | -6.4296 | -9.9148 | -11.3459 | -11.6709 | 15.2944 | 15.1209 | 14.7871 | 14.3814 | 13.6324 | 12.656 | 11.5925 | 10.4809 | 9.2754 | 8.053 | 5.5528 | 3.8405 | 2.6476 | 1.9985 | 12.789 | 12.3168 | 11.6168 | 10.7357 | 9.4411 | 7.9718 | 6.3953 | 4.7417 | 2.9672 | 1.1465 | -2.7109 | -5.6819 | -6.8284 | -7.1048
|  | EYNSHAM | CT |  |  | 11.9495 | 11.5667 | 10.9462 | 10.0795 | 8.8131 | 7.3389 | 5.7681 | 4.1181 | 2.427 | 0.40128 | -4.012 | -8.5588 | -11.3459 | -11.6709 | 15.2944 | 15.1209 | 14.7884 | 14.3828 | 13.8838 | 13.0852 | 12.1378 | 11.1447 | 10.0971 | 8.8843 | 6.3301 | 4.0557 | 2.6476 | 1.9985 | 13.043 | 12.7097 | 12.1656 | 11.4111 | 10.3319 | 9.082 | 7.7434 | 6.3327 | 4.8669 | 3.0966 | -0.71385 | -4.5353 | -6.8284 | -7.1048
|  | EYNSHAM | LW |  |  | 11.6289 | 11.0758 | 10.2702 | 9.2434 | 7.7187 | 5.9829 | 4.1335 | 2.1996 | 0.16964 | -1.9192 | -6.4296 | -9.9148 | -10.9844 | -11.5924 | 15.2994 | 15.1229 | 14.7871 | 14.3814 | 13.6324 | 12.656 | 11.5925 | 10.4809 | 9.2754 | 8.053 | 5.5528 | 3.8405 | 3.3769 | 3.1235 | 12.789 | 12.3168 | 11.6168 | 10.7357 | 9.4411 | 7.9718 | 6.3953 | 4.7417 | 2.9672 | 1.1465 | -2.7109 | -5.6819 | -6.5714 | -7.0727
|  | EYNSHAM | ST |  |  | 12.0277 | 11.7339 | 11.248 | 10.6366 | 9.7336 | 8.7034 | 7.5991 | 6.4581 | 5.2948 | 4.1233 | 1.2219 | -1.6655 | -3.139 | -4.1793 | 15.3251 | 15.1727 | 14.8669 | 14.4975 | 14.0244 | 13.4847 | 12.9103 | 12.2942 | 11.4891 | 10.697 | 8.7083 | 6.7764 | 5.8294 | 4.9137 | 13.1326 | 12.8925 | 12.4818 | 11.9732 | 11.2079 | 10.3408 | 9.405 | 8.4364 | 7.4372 | 6.4399 | 3.8577 | 1.1964 | -0.049583 | -0.90635
|  | EYNSHAM | SP |  |  | 12.0593 | 11.787 | 11.3397 | 10.7844 | 9.826 | 8.7587 | 7.5873 | 6.3964 | 5.1891 | 3.9545 | 0.93754 | -2.813 | -4.665 | -5.7312 | 15.3257 | 15.1744 | 14.8714 | 14.508 | 14.0518 | 13.5312 | 12.9696 | 12.3718 | 11.5684 | 10.7575 | 8.7985 | 6.3999 | 4.9896 | 3.6303 | 13.1586 | 12.9343 | 12.5577 | 12.1007 | 11.3157 | 10.4448 | 9.4661 | 8.4685 | 7.4471 | 6.4062 | 3.8026 | 0.3569 | -1.2813 | -2.1763
MINETY GSP | CIRENCESTER BSP | FAIRFORD | MINIMUM HEADROOM | SP 14418 00559 | NO | 19.9163 | 19.4763 | 18.9893 | 18.4904 | 17.7987 | 17.0824 | 16.3338 | 15.5135 | 14.5162 | 13.5723 | 11.4094 | 8.9209 | 8.3218 | 7.8935 | 23.8117 | 23.5991 | 23.3555 | 23.0968 | 22.756 | 22.3969 | 22.0083 | 21.567 | 20.9991 | 20.4811 | 19.4818 | 18.3928 | 18.1546 | 17.7643 | 20.9688 | 20.5701 | 20.1249 | 19.6676 | 19.0383 | 18.385 | 17.6985 | 16.9421 | 16.0137 | 15.1407 | 13.1927 | 10.9912 | 10.4916 | 10.1401
|  | FAIRFORD | CT |  |  | 20.3301 | 20.1085 | 19.8633 | 19.5666 | 19.149 | 18.7155 | 18.2416 | 17.712 | 17.1088 | 16.259 | 14.3754 | 11.2016 | 9.5274 | 9.1422 | 23.9509 | 23.8122 | 23.6551 | 23.4551 | 23.2156 | 22.9639 | 22.6841 | 22.3627 | 21.9798 | 21.4734 | 20.4935 | 19.0396 | 18.2047 | 17.7643 | 21.3284 | 21.1216 | 20.8914 | 20.6097 | 20.2232 | 19.8212 | 19.3806 | 18.8858 | 18.3175 | 17.5232 | 15.8068 | 12.9838 | 11.5069 | 11.1779
|  | FAIRFORD | LW |  |  | 19.9163 | 19.4763 | 18.9893 | 18.4904 | 17.7987 | 17.0824 | 16.3338 | 15.5135 | 14.5162 | 13.5723 | 11.4094 | 8.9209 | 8.3218 | 7.8935 | 23.8117 | 23.5991 | 23.3555 | 23.0968 | 22.756 | 22.3969 | 22.0083 | 21.567 | 20.9991 | 20.4811 | 19.4818 | 18.3928 | 18.1546 | 17.9941 | 20.9688 | 20.5701 | 20.1249 | 19.6676 | 19.0383 | 18.385 | 17.6985 | 16.9421 | 16.0137 | 15.1407 | 13.1927 | 10.9912 | 10.4916 | 10.1401
|  | FAIRFORD | ST |  |  | 20.4652 | 20.3299 | 20.1809 | 20.0143 | 19.7623 | 19.4977 | 19.2244 | 18.9253 | 18.5976 | 18.2508 | 16.7906 | 14.642 | 13.449 | 12.6287 | 24.0479 | 23.9707 | 23.8822 | 23.7783 | 23.6336 | 23.4788 | 23.3145 | 23.1299 | 22.9226 | 22.7201 | 21.774 | 20.4536 | 19.7664 | 19.1594 | 21.4595 | 21.3364 | 21.1995 | 21.0449 | 20.8126 | 20.568 | 20.3144 | 20.0357 | 19.7291 | 19.4081 | 18.0287 | 16.0381 | 14.9758 | 14.2535
|  | FAIRFORD | SP |  |  | 20.5141 | 20.4001 | 20.2815 | 20.1586 | 19.8168 | 19.4662 | 19.1186 | 18.7434 | 18.3583 | 17.8719 | 16.2349 | 12.6231 | 10.7065 | 9.4888 | 24.0651 | 23.9902 | 23.9101 | 23.8251 | 23.6615 | 23.491 | 23.3195 | 23.1251 | 22.9209 | 22.6786 | 21.7985 | 19.6933 | 18.6443 | 17.8531 | 21.5026 | 21.397 | 21.2865 | 21.1717 | 20.8644 | 20.5487 | 20.2355 | 19.895 | 19.5449 | 19.1049 | 17.6083 | 14.2707 | 12.5491 | 11.4731
MINETY GSP | STRATTON (2 X 60) | FARINGDON | MINIMUM HEADROOM | SU 28819 94924 | NO | -0.11394 | -0.82443 | 10.8901 | 10.2328 | 9.2976 | 8.3124 | 7.2799 | 6.1605 | 4.8952 | 3.676 | 0.8067 | -2.6427 | -3.6891 | -4.6538 | 2.4954 | 2.1149 | 17.2438 | 16.8811 | 16.4048 | 15.8936 | 15.3362 | 14.7118 | 13.9285 | 13.2055 | 11.6979 | 10.0056 | 8.411 | 6.8832 | -0.60913 | -1.2301 | 13.661 | 13.0685 | 12.2268 | 11.3394 | 10.4042 | 9.3856 | 8.1966 | 7.0583 | 4.447 | 1.3435 | 0.41168 | -0.41226
|  | FARINGDON | CT |  |  | 0.28257 | -0.21219 | 11.7085 | 11.2465 | 10.6385 | 9.9883 | 9.3159 | 8.5659 | 7.7472 | 6.5874 | 3.9352 | -0.36434 | -3.3943 | -4.6538 | 2.6025 | 2.2828 | 17.4644 | 17.1445 | 16.7745 | 16.3758 | 15.9508 | 15.4669 | 14.9086 | 14.1647 | 12.5806 | 10.1937 | 8.411 | 6.8832 | -0.24077 | -0.6745 | 14.3935 | 13.9671 | 13.4118 | 12.8185 | 12.2018 | 11.5103 | 10.7409 | 9.6518 | 7.2066 | 3.3383 | 0.70013 | -0.41226
|  | FARINGDON | LW |  |  | -0.11394 | -0.82443 | 10.8901 | 10.2328 | 9.2976 | 8.3124 | 7.2799 | 6.1605 | 4.8952 | 3.676 | 0.8067 | -2.6427 | -3.6891 | -4.1824 | 2.4954 | 2.1149 | 17.2438 | 16.8811 | 16.4048 | 15.8936 | 15.3362 | 14.7118 | 13.9285 | 13.2055 | 11.6979 | 10.0056 | 9.5616 | 9.3599 | -0.60913 | -1.2301 | 13.661 | 13.0685 | 12.2268 | 11.3394 | 10.4042 | 9.3856 | 8.1966 | 7.0583 | 4.447 | 1.3435 | 0.41168 | -0.025754
|  | FARINGDON | ST |  |  | 0.58657 | 0.30498 | 12.4392 | 12.1901 | 11.8589 | 11.4983 | 11.1226 | 10.7063 | 10.2867 | 9.8527 | 8.0223 | 4.9966 | 3.4409 | 2.4086 | 2.8154 | 2.6359 | 17.9574 | 17.7803 | 17.5607 | 17.3194 | 17.0613 | 16.7696 | 16.4615 | 16.1609 | 14.8073 | 12.5191 | 11.1348 | 9.6562 | 0.030113 | -0.19739 | 15.0812 | 14.8674 | 14.5726 | 14.2468 | 13.9056 | 13.5253 | 13.1338 | 12.7289 | 10.9833 | 8.1295 | 6.7215 | 5.8066
|  | FARINGDON | SP |  |  | 0.65042 | 0.39142 | 12.5731 | 12.3838 | 12.0292 | 11.6534 | 11.2801 | 10.8522 | 10.445 | 9.9606 | 8.2812 | 4.2588 | 2.136 | 1.0049 | 2.8391 | 2.6618 | 18.0017 | 17.8528 | 17.6411 | 17.4127 | 17.1771 | 16.8978 | 16.6207 | 16.3062 | 15.1373 | 12.0782 | 9.9169 | 7.5505 | 0.089859 | -0.11535 | 15.2071 | 15.0472 | 14.7313 | 14.3975 | 14.0664 | 13.6835 | 13.3122 | 12.8689 | 11.3096 | 7.5174 | 5.5574 | 4.5403
LOVEDEAN GSP | WYMERING BSP | FARLINGTON | MINIMUM HEADROOM | SU 67400 04843 | NO | 14.5167 | 14.4243 | 14.2849 | 14.0609 | 13.8308 | 13.6166 | 13.3957 | 13.1678 | 12.9416 | 12.665 | 11.8279 | 10.2792 | 8.5164 | 7.2211 | 12.9005 | 12.8356 | 12.7224 | 12.5255 | 12.2896 | 12.0729 | 11.8441 | 11.6079 | 11.3656 | 11.064 | 10.1108 | 8.851 | 8.3091 | 6.1271 | 10.9753 | 10.8879 | 10.7465 | 10.5163 | 10.2879 | 9.9801 | 9.6494 | 9.3083 | 8.9951 | 8.592 | 7.2038 | 5.4752 | 4.8089 | 3.8281
|  | FARLINGTON | CT |  |  | 14.5167 | 14.4283 | 14.2978 | 14.0806 | 13.8646 | 13.6711 | 13.4823 | 13.2927 | 13.1256 | 12.9087 | 12.2405 | 10.4281 | 8.5164 | 7.2211 | 12.9005 | 12.8356 | 12.725 | 12.5304 | 12.3332 | 12.1418 | 11.9513 | 11.7609 | 11.5869 | 11.3549 | 10.6393 | 9.3771 | 8.3091 | 6.754 | 10.9753 | 10.8916 | 10.7589 | 10.5351 | 10.3202 | 10.1331 | 9.9501 | 9.7457 | 9.5317 | 9.2014 | 8.0852 | 6.1049 | 4.8223 | 3.8281
|  | FARLINGTON | LW |  |  | 14.52 | 14.4243 | 14.2849 | 14.0609 | 13.8308 | 13.6166 | 13.3957 | 13.1678 | 12.9416 | 12.665 | 11.8279 | 10.2792 | 9.0169 | 8.0578 | 12.9046 | 12.8373 | 12.7224 | 12.5255 | 12.2896 | 12.0729 | 11.8441 | 11.6079 | 11.3656 | 11.064 | 10.1108 | 8.851 | 8.4091 | 8.072 | 10.9781 | 10.8879 | 10.7465 | 10.5163 | 10.2879 | 9.9801 | 9.6494 | 9.3083 | 8.9951 | 8.592 | 7.2038 | 5.4752 | 4.8089 | 4.3253
|  | FARLINGTON | ST |  |  | 14.5657 | 14.5072 | 14.4106 | 14.2407 | 14.068 | 13.9204 | 13.7799 | 13.6407 | 13.5169 | 13.371 | 12.8411 | 11.5751 | 10.8004 | 10.356 | 12.9315 | 12.885 | 12.7949 | 12.6308 | 12.4801 | 12.3631 | 12.2526 | 12.1485 | 12.0336 | 11.878 | 11.3153 | 9.9955 | 9.2644 | 8.2349 | 11.0137 | 10.9611 | 10.8662 | 10.6901 | 10.5169 | 10.3742 | 10.2378 | 10.1047 | 9.9841 | 9.8419 | 9.328 | 7.6675 | 6.6413 | 6.1583
|  | FARLINGTON | SP |  |  | 14.5671 | 14.5093 | 14.4145 | 14.2469 | 14.086 | 13.9534 | 13.8299 | 13.7106 | 13.6175 | 13.5099 | 13.1619 | 12.194 | 11.2096 | 10.7332 | 12.9324 | 12.8856 | 12.7961 | 12.6327 | 12.4894 | 12.3816 | 12.2808 | 12.1879 | 12.1121 | 12.0234 | 11.6579 | 10.6619 | 8.9454 | 6.1271 | 11.0152 | 10.9627 | 10.8692 | 10.6961 | 10.5344 | 10.4063 | 10.2863 | 10.1724 | 10.0816 | 9.9763 | 9.6384 | 8.5802 | 7.3888 | 6.9185
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH | MINIMUM HEADROOM | SU 88404 53930 | YES | 12.742 | 11.2024 | 9.8554 | 8.2316 | 6.3986 | 4.4515 | 2.3275 | 0.024548 | -2.7606 | -5.6552 | -11.8232 | -18.0038 | -21.4251 | -23.5651 | 18.8006 | 17.9037 | 17.0989 | 16.1481 | 15.1229 | 14.027 | 12.8101 | 11.4868 | 9.8009 | 8.0294 | 4.3018 | 0.098105 | -3.0681 | -6.0129 | 12.2045 | 10.9285 | 9.7747 | 8.3846 | 6.7846 | 5.0783 | 3.205 | 1.1697 | -1.3305 | -3.9392 | -9.5279 | -15.1805 | -18.0908 | -19.9535
|  | FARNBOROUGH | CT |  |  | 12.8711 | 11.4426 | 10.2229 | 8.6597 | 7.1212 | 5.4822 | 3.7521 | 1.8548 | -0.367 | -3.2203 | -9.4736 | -17.0122 | -21.4251 | -23.5651 | 18.8006 | 17.9187 | 17.1412 | 16.1601 | 15.2255 | 14.2265 | 13.1602 | 11.9894 | 10.5905 | 8.8178 | 4.8762 | 0.098105 | -3.0681 | -6.0129 | 12.3113 | 11.1341 | 10.0955 | 8.754 | 7.4173 | 5.9873 | 4.4729 | 2.8077 | 0.83787 | -1.7237 | -7.3797 | -14.2008 | -18.0908 | -19.9535
|  | FARNBOROUGH | LW |  |  | 12.742 | 11.2024 | 9.8554 | 8.2316 | 6.3986 | 4.4515 | 2.3275 | 0.024548 | -2.7606 | -5.6552 | -11.8232 | -18.0038 | -20.1795 | -21.2908 | 18.803 | 17.9037 | 17.0989 | 16.1481 | 15.1229 | 14.027 | 12.8101 | 11.4868 | 9.8009 | 8.0294 | 4.3018 | 0.63927 | -0.42438 | -0.97473 | 12.2045 | 10.9285 | 9.7747 | 8.3846 | 6.7846 | 5.0783 | 3.205 | 1.1697 | -1.3305 | -3.9392 | -9.5279 | -15.1805 | -17.0824 | -18.0364
|  | FARNBOROUGH | ST |  |  | 13.3741 | 12.4946 | 11.7876 | 10.9347 | 10.0741 | 9.1581 | 8.1665 | 7.0724 | 5.8096 | 4.4881 | 0.59383 | -5.8876 | -9.0447 | -10.7709 | 19.1471 | 18.6038 | 18.1353 | 17.5751 | 16.9892 | 16.3641 | 15.6836 | 14.9307 | 14.0541 | 13.1508 | 10.2261 | 5.0076 | 1.9799 | -0.81637 | 12.7949 | 12.1354 | 11.5781 | 10.9015 | 10.1848 | 9.4169 | 8.5797 | 7.6507 | 6.5666 | 5.4302 | 1.8807 | -4.229 | -7.0954 | -8.5973
|  | FARNBOROUGH | SP |  |  | 13.4202 | 12.5797 | 11.9376 | 11.176 | 10.5076 | 9.7898 | 8.9832 | 8.0905 | 7.0936 | 6.0313 | 3.2939 | -2.3906 | -5.8861 | -7.1979 | 19.167 | 18.638 | 18.2001 | 17.6862 | 17.23 | 16.7323 | 16.1591 | 15.5182 | 14.793 | 14.0001 | 11.7173 | 6.3872 | 1.6663 | -3.387 | 12.8375 | 12.2132 | 11.7167 | 11.126 | 10.5947 | 10.0168 | 9.354 | 8.6136 | 7.7794 | 6.8841 | 4.447 | -0.97128 | -4.2712 | -5.4546
BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM | MINIMUM HEADROOM | SU 84517 47217 | YES | 8.2099 | 7.311 | 6.5957 | 5.8397 | 4.7615 | 3.6143 | 2.3672 | 1.0306 | -0.47237 | -1.96 | -6.0032 | -10.8093 | -12.8452 | -14.5194 | 8.9743 | 8.3958 | 7.9423 | 7.4786 | 6.885 | 6.2576 | 5.5461 | 4.7103 | 3.677 | 2.7043 | 0.21238 | -2.9367 | -5.5454 | -8.1571 | 4.6374 | 3.765 | 3.0651 | 2.3296 | 1.3282 | 0.2655 | -0.921 | -2.2056 | -3.7074 | -5.1393 | -8.9154 | -13.2856 | -14.8166 | -16.1415
|  | FARNHAM | CT |  |  | 8.4599 | 7.7261 | 7.1479 | 6.5492 | 5.8114 | 5.012 | 4.1726 | 3.2249 | 2.1873 | 0.71395 | -3.1125 | -9.1712 | -12.8452 | -14.5194 | 9.019 | 8.4652 | 8.0164 | 7.5693 | 7.0775 | 6.5394 | 5.9155 | 5.2382 | 4.4646 | 3.4675 | 0.91549 | -2.9367 | -5.5454 | -8.1571 | 4.7985 | 4.058 | 3.4507 | 2.8327 | 2.1138 | 1.3405 | 0.51062 | -0.38409 | -1.3744 | -2.7629 | -6.337 | -11.7811 | -14.8166 | -16.1415
|  | FARNHAM | LW |  |  | 8.2099 | 7.311 | 6.5957 | 5.8397 | 4.7615 | 3.6143 | 2.3672 | 1.0306 | -0.47237 | -1.96 | -6.0032 | -10.8093 | -12.2142 | -12.9306 | 8.9743 | 8.3958 | 7.9423 | 7.4786 | 6.885 | 6.2576 | 5.5461 | 4.7103 | 3.677 | 2.7043 | 0.21238 | -2.5341 | -3.1319 | -3.431 | 4.6374 | 3.765 | 3.0651 | 2.3296 | 1.3282 | 0.2655 | -0.921 | -2.2056 | -3.7074 | -5.1393 | -8.9154 | -13.2856 | -14.4666 | -15.0602
|  | FARNHAM | ST |  |  | 8.8704 | 8.4295 | 8.1232 | 7.8143 | 7.4629 | 7.0817 | 6.667 | 6.2018 | 5.6953 | 5.1493 | 2.5509 | -2.9037 | -6.0347 | -6.6222 | 9.2681 | 8.8969 | 8.6383 | 8.3892 | 8.1005 | 7.7977 | 7.462 | 7.0819 | 6.6508 | 6.2192 | 4.0946 | -0.2603 | -2.9666 | -5.4407 | 4.9882 | 4.6499 | 4.4407 | 4.1824 | 3.818 | 3.432 | 3.0068 | 2.5235 | 1.9816 | 1.428 | -1.0883 | -6.7214 | -9.7328 | -10.1233
|  | FARNHAM | SP |  |  | 8.9214 | 8.5179 | 8.262 | 8.0129 | 7.6943 | 7.3568 | 7.0051 | 6.6139 | 6.2168 | 5.7493 | 4.0416 | -0.83772 | -3.9952 | -5.1359 | 9.2844 | 8.9275 | 8.6872 | 8.4645 | 8.2084 | 7.9374 | 7.6458 | 7.3148 | 6.9589 | 6.5693 | 5.0327 | 0.53058 | -3.5451 | -7.8082 | 4.9976 | 4.6743 | 4.4805 | 4.3107 | 4.0594 | 3.7334 | 3.3894 | 2.9965 | 2.585 | 2.1188 | 0.38644 | -4.2945 | -7.2906 | -8.3357
IVER 132KV | SLOUGH | FARNHAM ROYAL | MINIMUM HEADROOM | SU 95597 82844 | YES | 18.9308 | 18.1607 | 17.2808 | 16.2254 | 6.3628 | -3.5989 | -17.7098 | -19.7498 | -22.2347 | -24.7424 | -31.415 | -40.2507 | -46.9989 | -51.2618 | 21.0904 | 20.5876 | 20.0058 | 19.3136 | 8.1277 | -3.1273 | -19.5733 | -20.8503 | -22.4742 | -24.1004 | -28.2336 | -34.7576 | -40.5998 | -46.5333 | 14.0614 | 13.3901 | 12.6484 | 11.7288 | -0.038031 | -11.8999 | -28.9525 | -30.874 | -33.2341 | -35.6127 | -41.8741 | -49.9538 | -55.6826 | -59.3204
|  | FARNHAM ROYAL | CT |  |  | 19.1773 | 18.5934 | 17.9554 | 17.0043 | 7.6067 | -1.8772 | -15.4308 | -16.8853 | -18.5511 | -21.0917 | -27.9013 | -39.1238 | -46.9989 | -51.2618 | 21.1093 | 20.6377 | 20.1269 | 19.3893 | 8.3395 | -2.7767 | -19.0288 | -20.1022 | -21.3539 | -23.0803 | -27.6286 | -34.7576 | -40.5998 | -46.5313 | 14.3215 | 13.8304 | 13.3074 | 12.4082 | 1.0571 | -10.3766 | -26.9219 | -28.3087 | -29.9038 | -32.3038 | -38.6674 | -48.806 | -55.6826 | -59.3204
|  | FARNHAM ROYAL | LW |  |  | 18.9308 | 18.1607 | 17.2808 | 16.2254 | 6.3628 | -3.5989 | -17.7098 | -19.7498 | -22.2347 | -24.7424 | -31.415 | -40.2507 | -44.4337 | -46.7513 | 21.0904 | 20.5876 | 20.0058 | 19.3136 | 8.1277 | -3.1273 | -19.5733 | -20.8503 | -22.4742 | -24.1004 | -28.2336 | -33.2731 | -35.2956 | -36.4725 | 14.0614 | 13.3901 | 12.6484 | 11.7288 | -0.038031 | -11.8999 | -28.9525 | -30.874 | -33.2341 | -35.6127 | -41.8741 | -49.9538 | -53.5641 | -55.5084
|  | FARNHAM ROYAL | ST |  |  | 19.6805 | 19.4063 | 19.1166 | 18.7188 | 10.0083 | 1.2558 | -11.5629 | -12.1984 | -12.9624 | -13.7701 | -17.4815 | -25.7376 | -30.6515 | -34.0416 | 21.4606 | 21.2035 | 20.936 | 20.5929 | 9.9388 | -0.75116 | -16.5576 | -17.1202 | -17.7974 | -18.4873 | -21.659 | -28.6085 | -33.6571 | -39.2667 | 14.7361 | 14.5011 | 14.2657 | 13.9605 | 3.3299 | -7.3963 | -23.2503 | -23.8627 | -24.6018 | -25.3742 | -28.9594 | -36.7425 | -41.0998 | -43.992
|  | FARNHAM ROYAL | SP |  |  | 19.7508 | 19.4703 | 19.2006 | 18.8517 | 10.2465 | 1.6314 | -11.0318 | -11.51 | -12.0447 | -12.6968 | -15.2389 | -22.571 | -27.4769 | -29.8346 | 21.4908 | 21.2133 | 20.9394 | 20.6097 | 10.0281 | -0.57486 | -16.2784 | -16.7423 | -17.2718 | -17.9381 | -20.5831 | -28.2219 | -36.2414 | -46.5333 | 14.7984 | 14.5657 | 14.3522 | 14.0911 | 3.5402 | -7.0369 | -22.7365 | -23.1934 | -23.7061 | -24.3274 | -26.7637 | -33.7664 | -38.3 | -40.3403
LALEHAM | EAST BEDFONT A | FELTHAM | MINIMUM HEADROOM | TQ 10628 72811 | YES | 20.8206 | 20.5719 | 19.9826 | 19.1219 | 18.0331 | 16.8781 | 15.6732 | 14.3604 | 13.3124 | 12.3974 | 9.7816 | 6.2133 | 3.5093 | 1.2532 | 16.5065 | 16.4433 | 16.0865 | 15.5611 | 14.9513 | 14.2905 | 13.6016 | 12.8608 | 12.2711 | 11.6668 | 9.7664 | 6.0984 | 0.83907 | -10.1269 | 14.0354 | 13.7979 | 13.2248 | 12.4635 | 11.5142 | 10.5014 | 9.4347 | 8.2777 | 7.3359 | 6.4952 | 4.0771 | 0.92486 | -1.2938 | -3.1656
|  | FELTHAM | CT |  |  | 20.9754 | 20.8137 | 20.3221 | 19.5269 | 18.5833 | 17.5726 | 16.5557 | 15.4387 | 14.5994 | 13.7274 | 11.1589 | 6.8949 | 3.5093 | 1.2532 | 16.5065 | 16.4433 | 16.0904 | 15.5611 | 14.9513 | 14.2905 | 13.6016 | 12.8608 | 12.2711 | 11.6668 | 9.7664 | 6.0984 | 1.8615 | -3.8231 | 14.1635 | 14.0013 | 13.526 | 12.8209 | 12.0003 | 11.1153 | 10.217 | 9.236 | 8.4846 | 7.6882 | 5.3218 | 1.5709 | -1.2938 | -3.1656
|  | FELTHAM | LW |  |  | 20.8206 | 20.5719 | 19.9826 | 19.1219 | 18.0331 | 16.8781 | 15.6732 | 14.3604 | 13.3124 | 12.3974 | 9.7816 | 6.2133 | 3.9256 | 2.2648 | 16.5226 | 16.4452 | 16.0865 | 15.588 | 14.9894 | 14.3471 | 13.6647 | 12.9377 | 12.362 | 11.8468 | 10.3576 | 8.4514 | 7.3227 | 6.4718 | 14.0354 | 13.7979 | 13.2248 | 12.4635 | 11.5142 | 10.5014 | 9.4347 | 8.2777 | 7.3359 | 6.4952 | 4.0771 | 0.92486 | -0.97178 | -2.3219
|  | FELTHAM | ST |  |  | 21.1276 | 21.0601 | 20.7792 | 20.3832 | 19.8157 | 19.2054 | 18.5764 | 17.8884 | 17.4015 | 17.0052 | 15.728 | 12.7666 | 10.5725 | 8.9678 | 16.5518 | 16.5084 | 16.3342 | 15.9753 | 15.5285 | 15.0421 | 14.5241 | 13.9701 | 13.5394 | 13.1527 | 11.8397 | 8.6239 | 4.7285 | -0.69158 | 14.3233 | 14.2589 | 13.9959 | 13.6134 | 13.1289 | 12.6042 | 12.0562 | 11.4616 | 11.0311 | 10.6706 | 9.482 | 6.8163 | 4.971 | 3.6734
|  | FELTHAM | SP |  |  | 21.1567 | 21.0975 | 20.8386 | 20.4739 | 20.0066 | 19.508 | 18.9646 | 18.3833 | 17.9981 | 17.6717 | 16.6871 | 14.3921 | 12.2084 | 10.8356 | 16.5586 | 16.5164 | 16.3385 | 15.9745 | 15.5482 | 15.0774 | 14.5526 | 13.9951 | 13.5502 | 13.1005 | 11.5487 | 7.5575 | 0.83907 | -10.1269 | 14.3517 | 14.2886 | 14.0449 | 13.6929 | 13.3054 | 12.8856 | 12.4157 | 11.9184 | 11.582 | 11.2866 | 10.3752 | 8.3233 | 6.3835 | 5.2399
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN | MINIMUM HEADROOM | SU 06593 00685 | YES | 24.5241 | 24.1156 | 23.2647 | 22.41 | 20.9329 | 19.4098 | 17.5681 | 15.5459 | 13.0394 | 10.5326 | 4.3041 | -2.5008 | -6.3792 | -8.6941 | 30.6102 | 30.4215 | 30.1081 | 29.8001 | 29.2715 | 28.7419 | 27.9022 | 26.6401 | 25.0168 | 23.4481 | 19.6867 | 15.6423 | 12.6951 | 10.2718 | 26.6413 | 26.3072 | 25.8246 | 25.3737 | 24.0028 | 22.5471 | 20.8104 | 18.9106 | 16.5386 | 14.179 | 8.433 | 2.3166 | -0.88309 | -2.7834
|  | FERNDOWN | CT |  |  | 24.5241 | 24.3147 | 23.9772 | 23.266 | 22.1924 | 21.0937 | 19.725 | 18.1961 | 16.3282 | 13.8495 | 7.251 | -1.4431 | -6.3792 | -8.6941 | 30.6102 | 30.4215 | 30.1081 | 29.8001 | 29.2715 | 28.7514 | 28.1128 | 27.4683 | 26.2924 | 24.7202 | 20.5764 | 15.6423 | 12.6951 | 10.2718 | 26.7761 | 26.5353 | 26.1682 | 25.7904 | 25.1129 | 24.0425 | 22.7347 | 21.2831 | 19.5064 | 17.1795 | 11.0801 | 3.3196 | -0.88309 | -2.7834
|  | FERNDOWN | LW |  |  | 24.549 | 24.1156 | 23.2647 | 22.41 | 20.9329 | 19.4098 | 17.5681 | 15.5459 | 13.0394 | 10.5326 | 4.3041 | -2.5008 | -4.413 | -5.3551 | 30.6357 | 30.4443 | 30.1131 | 29.8211 | 29.2814 | 28.7419 | 27.9022 | 26.6401 | 25.0168 | 23.4481 | 19.6867 | 15.9634 | 15.0919 | 14.6702 | 26.6413 | 26.3072 | 25.8246 | 25.3737 | 24.0028 | 22.5471 | 20.8104 | 18.9106 | 16.5386 | 14.179 | 8.433 | 2.3166 | 0.627 | -0.17608
|  | FERNDOWN | ST |  |  | 24.6532 | 24.5235 | 24.2858 | 24.0964 | 23.6823 | 23.1675 | 22.3387 | 21.4344 | 20.3422 | 19.3451 | 15.2578 | 8.174 | 5.3351 | 3.5788 | 30.7123 | 30.5866 | 30.352 | 30.1695 | 29.7393 | 29.3208 | 28.7873 | 28.2548 | 27.5741 | 27.0467 | 24.9342 | 19.8107 | 17.4681 | 15.2146 | 26.9328 | 26.7879 | 26.5368 | 26.3333 | 25.8739 | 25.4291 | 24.8542 | 24.2654 | 23.3098 | 22.3758 | 18.5163 | 11.901 | 9.3224 | 7.7787
|  | FERNDOWN | SP |  |  | 24.6626 | 24.5319 | 24.2927 | 24.1128 | 23.7346 | 23.3838 | 22.7079 | 21.9346 | 21.0113 | 20.1485 | 17.0174 | 10.4256 | 7.4334 | 6.3476 | 30.718 | 30.59 | 30.3514 | 30.1732 | 29.7698 | 29.3861 | 28.898 | 28.4134 | 27.8081 | 27.3526 | 25.8083 | 20.6594 | 16.9234 | 13.0267 | 26.9636 | 26.8288 | 26.5861 | 26.4025 | 25.9685 | 25.562 | 25.0422 | 24.5155 | 23.864 | 23.1605 | 20.2388 | 14.0155 | 11.176 | 10.1904
BRAMLEY (FLEE) | FERNHURST | FIVE OAKS | MINIMUM HEADROOM | TQ 10647 29057 | YES | 4.5791 | 3.8007 | 2.8585 | 1.8739 | 0.60689 | -0.67675 | -1.5557 | -2.408 | -3.2277 | -3.9023 | -5.3898 | -7.5677 | -10.3254 | -11.5865 | 9.403 | 9.041 | 8.5924 | 8.1191 | 7.5397 | 6.9448 | 6.4961 | 6.0266 | 5.5118 | 5.1103 | 4.3131 | 3.4026 | 2.1259 | 1.4141 | 6.4892 | 5.7983 | 4.9836 | 4.1311 | 3.0203 | 1.8964 | 1.1088 | 0.35261 | -0.37377 | -0.97795 | -2.3416 | -4.3314 | -6.8649 | -7.9906
|  | FIVE OAKS | CT |  |  | 5.3137 | 4.9073 | 4.3125 | 3.6859 | 2.8462 | 1.9614 | 1.4137 | 0.85009 | 0.33017 | -0.32367 | -1.627 | -2.9788 | -3.6192 | -3.885 | 9.6305 | 9.3941 | 9.0474 | 8.6855 | 8.257 | 7.7987 | 7.4862 | 7.1321 | 6.7773 | 6.3477 | 5.5772 | 4.7535 | 4.3313 | 3.9916 | 7.1668 | 6.8176 | 6.3228 | 5.7802 | 5.0524 | 4.2835 | 3.7869 | 3.2728 | 2.7903 | 2.1676 | 0.99875 | -0.22663 | -0.79582 | -1.0324
|  | FIVE OAKS | LW |  |  | 4.5791 | 3.8007 | 2.8585 | 1.8739 | 0.60689 | -0.67675 | -1.5557 | -2.408 | -3.2277 | -3.9023 | -5.3898 | -6.8661 | -7.1618 | -7.271 | 9.403 | 9.041 | 8.5924 | 8.1191 | 7.5397 | 6.9448 | 6.4961 | 6.0266 | 5.5118 | 5.1103 | 4.3131 | 3.5187 | 3.3678 | 3.312 | 6.4892 | 5.7983 | 4.9836 | 4.1311 | 3.0203 | 1.8964 | 1.1088 | 0.35261 | -0.37377 | -0.97795 | -2.3416 | -3.6913 | -3.9561 | -4.0557
|  | FIVE OAKS | ST |  |  | 5.4893 | 5.1829 | 4.7612 | 4.3187 | 3.7551 | 3.171 | 2.7487 | 2.2771 | 1.8103 | 1.303 | -0.62489 | -2.9045 | -3.8072 | -4.3182 | 9.7936 | 9.6342 | 9.4032 | 9.1535 | 8.8538 | 8.5418 | 8.3171 | 8.0579 | 7.7876 | 7.5114 | 6.3032 | 4.9816 | 4.4259 | 4.0001 | 7.3167 | 7.055 | 6.7144 | 6.3564 | 5.8883 | 5.4034 | 5.0288 | 4.6139 | 4.1917 | 3.7352 | 1.9567 | -0.11976 | -0.92873 | -1.3809
|  | FIVE OAKS | SP |  |  | 5.5709 | 5.3257 | 4.9838 | 4.6372 | 3.8408 | 3.0247 | 2.3542 | 1.6338 | 0.91053 | 0.076616 | -2.5987 | -7.5677 | -10.3254 | -11.5865 | 9.8211 | 9.687 | 9.4948 | 9.2971 | 8.9438 | 8.5768 | 8.2894 | 7.9639 | 7.6289 | 7.245 | 5.93 | 3.4026 | 2.1259 | 1.4141 | 7.3916 | 7.1857 | 6.9167 | 6.6442 | 5.9593 | 5.258 | 4.6528 | 4.0075 | 3.3536 | 2.5981 | 0.17106 | -4.3314 | -6.8649 | -7.9906
AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH | MINIMUM HEADROOM | SU 90667 89318 | YES | 19.5252 | 19.1308 | 18.6815 | 18.1915 | 17.4108 | 16.5814 | 15.6827 | 14.6942 | 13.4415 | 12.225 | 9.5812 | 6.2354 | 4.312 | 2.7954 | 22.2013 | 21.9769 | 21.7155 | 21.425 | 21.0046 | 20.5508 | 20.0454 | 19.4797 | 18.718 | 17.983 | 16.4858 | 14.5748 | 12.6816 | 11.0827 | 19.5591 | 19.2144 | 18.8287 | 18.4105 | 17.7129 | 16.9729 | 16.1521 | 15.225 | 14.0294 | 12.8721 | 10.4097 | 7.3418 | 5.6859 | 4.3623
|  | FLACKWELL HEATH | CT |  |  | 19.7082 | 19.4362 | 19.1132 | 18.7223 | 18.1993 | 17.6417 | 17.0674 | 16.4158 | 15.6174 | 14.3756 | 11.6335 | 7.2976 | 4.312 | 2.7954 | 22.2462 | 22.0558 | 21.8285 | 21.551 | 21.2231 | 20.8698 | 20.4943 | 20.0635 | 19.5259 | 18.7495 | 17.0912 | 14.5748 | 12.6816 | 11.0827 | 19.7501 | 19.5259 | 19.2626 | 18.9482 | 18.4568 | 17.9294 | 17.3827 | 16.7601 | 15.9915 | 14.8097 | 12.2511 | 8.3301 | 5.6859 | 4.3623
|  | FLACKWELL HEATH | LW |  |  | 19.5252 | 19.1308 | 18.6815 | 18.1915 | 17.4108 | 16.5814 | 15.6827 | 14.6942 | 13.4415 | 12.225 | 9.5812 | 6.2354 | 4.9557 | 4.2499 | 22.2013 | 21.9769 | 21.7155 | 21.425 | 21.0046 | 20.5508 | 20.0454 | 19.4797 | 18.718 | 17.983 | 16.4858 | 14.6803 | 14.0773 | 13.7431 | 19.5591 | 19.2144 | 18.8287 | 18.4105 | 17.7129 | 16.9729 | 16.1521 | 15.225 | 14.0294 | 12.8721 | 10.4097 | 7.3418 | 6.2178 | 5.6088
|  | FLACKWELL HEATH | ST |  |  | 19.9602 | 19.8533 | 19.7068 | 19.5376 | 19.3089 | 19.0616 | 18.7824 | 18.4766 | 18.1121 | 17.723 | 15.8547 | 12.5052 | 10.7706 | 9.6342 | 22.4096 | 22.3221 | 22.2083 | 22.0761 | 21.9107 | 21.7302 | 21.5233 | 21.2946 | 21.0189 | 20.7384 | 19.3813 | 16.9114 | 15.4189 | 13.9345 | 19.9613 | 19.8692 | 19.7514 | 19.6162 | 19.4288 | 19.2263 | 18.9994 | 18.7182 | 18.364 | 17.9906 | 16.1754 | 12.9896 | 11.4269 | 10.4369
|  | FLACKWELL HEATH | SP |  |  | 19.9643 | 19.892 | 19.772 | 19.6433 | 19.4522 | 19.2422 | 19.0245 | 18.7715 | 18.4892 | 18.1385 | 16.7991 | 13.0707 | 11.1648 | 10.2942 | 22.4232 | 22.3317 | 22.2276 | 22.1136 | 21.9788 | 21.829 | 21.6698 | 21.4802 | 21.2644 | 21.0028 | 19.9755 | 17.0337 | 14.9017 | 12.6533 | 19.9931 | 19.9086 | 19.8139 | 19.713 | 19.551 | 19.3735 | 19.1895 | 18.9805 | 18.7385 | 18.405 | 17.1207 | 13.5273 | 11.7427 | 10.9638
NURSLING GSP | ROWNHAMS | FLETCHWOOD | MINIMUM HEADROOM | SU 33800 12142 | YES | 11.0995 | 10.5048 | 9.7589 | 8.9631 | 7.7274 | 6.2904 | 4.6991 | 2.9789 | 0.88439 | -1.0983 | -5.9504 | -11.2155 | -13.8818 | -15.5051 | 17.4918 | 17.1245 | 16.6256 | 16.0658 | 15.3285 | 14.4496 | 13.4392 | 12.3285 | 10.8813 | 9.5549 | 6.8018 | 4.0044 | 1.8408 | 0.15674 | 13.0785 | 12.5322 | 11.8287 | 11.0668 | 9.9622 | 8.6805 | 7.2348 | 5.6455 | 3.6277 | 1.7452 | -2.3991 | -6.8314 | -8.9183 | -10.3432
|  | FLETCHWOOD | CT |  |  | 11.3846 | 10.9774 | 10.453 | 9.7943 | 8.9398 | 7.8915 | 6.7264 | 5.4404 | 4.0103 | 1.9398 | -3.1027 | -9.9018 | -13.8818 | -15.5051 | 17.5407 | 17.2255 | 16.8086 | 16.2496 | 15.6473 | 14.9074 | 14.0733 | 13.1392 | 12.0804 | 10.6399 | 7.5891 | 4.0044 | 1.8408 | 0.15674 | 13.261 | 12.8563 | 12.3358 | 11.6561 | 10.8495 | 9.8734 | 8.7812 | 7.5515 | 6.1661 | 4.1776 | -0.19882 | -5.6181 | -8.9183 | -10.3432
|  | FLETCHWOOD | LW |  |  | 11.0995 | 10.5048 | 9.7589 | 8.9631 | 7.7274 | 6.2904 | 4.6991 | 2.9789 | 0.88439 | -1.0983 | -5.9504 | -11.2155 | -12.7832 | -13.2683 | 17.4918 | 17.1245 | 16.6256 | 16.0658 | 15.3285 | 14.4496 | 13.4392 | 12.3285 | 10.8813 | 9.5549 | 6.8018 | 4.0673 | 3.4388 | 3.255 | 13.0785 | 12.5322 | 11.8287 | 11.0668 | 9.9622 | 8.6805 | 7.2348 | 5.6455 | 3.6277 | 1.7452 | -2.3991 | -6.8314 | -8.1333 | -8.531
|  | FLETCHWOOD | ST |  |  | 11.7004 | 11.5083 | 11.2267 | 10.8868 | 10.4478 | 9.8552 | 9.1916 | 8.4975 | 7.7055 | 6.9339 | 3.4238 | -1.4818 | -3.6882 | -5.0904 | 17.7804 | 17.635 | 17.4021 | 17.1043 | 16.7531 | 16.2827 | 15.7524 | 15.1961 | 14.5512 | 13.9638 | 11.1753 | 7.4033 | 5.6877 | 4.0808 | 13.5926 | 13.4106 | 13.1409 | 12.8072 | 12.3818 | 11.8196 | 11.1887 | 10.5203 | 9.7467 | 9.0149 | 5.5228 | 0.83412 | -0.97926 | -2.0499
|  | FLETCHWOOD | SP |  |  | 11.7548 | 11.5712 | 11.3223 | 11.0397 | 10.6353 | 10.1179 | 9.5233 | 8.9075 | 8.2432 | 7.5278 | 4.7916 | -0.74695 | -3.0498 | -3.9153 | 17.8005 | 17.646 | 17.4238 | 17.1585 | 16.858 | 16.4699 | 16.0197 | 15.5408 | 15.0176 | 14.4645 | 12.2827 | 7.4947 | 4.8073 | 2.05 | 13.6365 | 13.4533 | 13.2116 | 12.9345 | 12.5632 | 12.099 | 11.5616 | 10.9884 | 10.3668 | 9.7004 | 7.0874 | 1.4798 | -0.60685 | -1.3417
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE | MINIMUM HEADROOM | SU 14069 15523 | YES | 7.843 | 7.545 | 7.071 | 6.5596 | 5.9127 | 5.1631 | 4.2959 | 3.3148 | 2.2435 | 1.2059 | -1.5033 | -4.0791 | -4.9642 | -5.8519 | 10.5284 | 10.4133 | 10.2037 | 10.0033 | 9.7479 | 9.4639 | 9.1356 | 8.749 | 8.1184 | 7.5069 | 6.0494 | 4.7586 | 4.0538 | 3.392 | 8.714 | 8.4446 | 8.0173 | 7.5592 | 6.9806 | 6.3153 | 5.545 | 4.6659 | 3.6803 | 2.7293 | 0.34177 | -1.9114 | -2.6157 | -3.3995
|  | FORDINGBRIDGE | CT |  |  | 8.0813 | 7.9132 | 7.5851 | 7.1785 | 6.7255 | 6.1764 | 5.5147 | 4.7453 | 3.9642 | 2.9444 | 0.42945 | -2.8458 | -4.9642 | -5.8519 | 10.5759 | 10.4959 | 10.3183 | 10.1495 | 9.9444 | 9.7167 | 9.4556 | 9.1441 | 8.7937 | 8.1727 | 6.7349 | 5.0648 | 4.0538 | 3.392 | 8.9074 | 8.7483 | 8.4516 | 8.0855 | 7.6723 | 7.1807 | 6.5939 | 5.908 | 5.2036 | 4.2725 | 2.0143 | -0.85667 | -2.6157 | -3.3995
|  | FORDINGBRIDGE | LW |  |  | 7.843 | 7.545 | 7.071 | 6.5596 | 5.9127 | 5.1631 | 4.2959 | 3.3148 | 2.2435 | 1.2059 | -1.5033 | -4.0791 | -4.811 | -5.1801 | 10.5284 | 10.4133 | 10.2037 | 10.0033 | 9.7479 | 9.4639 | 9.1356 | 8.749 | 8.1184 | 7.5069 | 6.0494 | 4.7586 | 4.4518 | 4.2998 | 8.714 | 8.4446 | 8.0173 | 7.5592 | 6.9806 | 6.3153 | 5.545 | 4.6659 | 3.6803 | 2.7293 | 0.34177 | -1.9114 | -2.5256 | -2.8332
|  | FORDINGBRIDGE | ST |  |  | 8.1987 | 8.1067 | 7.9 | 7.679 | 7.4066 | 7.0746 | 6.6805 | 6.2246 | 5.7622 | 5.3035 | 3.5766 | 1.0968 | -0.13093 | -0.83706 | 10.6392 | 10.5999 | 10.4778 | 10.3795 | 10.2469 | 10.1048 | 9.9399 | 9.7323 | 9.5191 | 9.2811 | 8.3855 | 6.6573 | 5.8138 | 5.1934 | 9.0234 | 8.9383 | 8.7577 | 8.5673 | 8.3219 | 8.0307 | 7.6899 | 7.2935 | 6.8847 | 6.4778 | 4.9019 | 2.5733 | 1.4545 | 0.82856
|  | FORDINGBRIDGE | SP |  |  | 8.2343 | 8.1542 | 7.9688 | 7.7822 | 7.4855 | 7.1537 | 6.7585 | 6.3106 | 5.881 | 5.4196 | 3.9056 | 1.0653 | -0.51088 | -1.2593 | 10.6496 | 10.6181 | 10.5041 | 10.4172 | 10.2844 | 10.149 | 9.9965 | 9.8073 | 9.6286 | 9.4347 | 8.7681 | 6.8112 | 5.5637 | 4.591 | 9.0532 | 8.9776 | 8.8163 | 8.6593 | 8.3969 | 8.1118 | 7.7749 | 7.3906 | 7.0186 | 6.6146 | 5.2663 | 2.6048 | 1.1443 | 0.47116
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK | MINIMUM HEADROOM | SU 66139 00180 | YES | 10.2132 | 9.4697 | 8.6062 | 7.6651 | 6.1546 | 4.5346 | 2.8326 | 1.0394 | -1.0288 | -3.2536 | -10.5161 | -19.4748 | -25.9509 | -30.2796 | 4.4114 | 3.8757 | 3.3029 | 2.5513 | 1.6282 | 0.62289 | -0.45444 | -1.6246 | -2.9603 | -4.6752 | -10.635 | -21.6121 | -41.5127 | -78.832 | -2.1431 | -2.7899 | -3.5642 | -4.4145 | -5.774 | -7.2357 | -8.7863 | -10.429 | -12.3403 | -14.4061 | -21.1493 | -29.3397 | -34.725 | -38.2397
|  | FRATTON PARK | CT |  |  | 10.4361 | 9.8396 | 9.2135 | 8.3585 | 7.2446 | 6.0392 | 4.8085 | 3.507 | 2.0409 | -0.12296 | -7.268 | -18.3717 | -25.9509 | -30.2796 | 4.4114 | 3.8757 | 3.3029 | 2.5513 | 1.6282 | 0.62289 | -0.45444 | -1.6246 | -2.9603 | -4.6752 | -10.635 | -21.6121 | -34.6322 | -53.2617 | -1.9502 | -2.4663 | -3.0199 | -3.8004 | -4.809 | -5.9022 | -7.0285 | -8.2268 | -9.5856 | -11.5763 | -18.1585 | -28.1756 | -34.725 | -38.2397
|  | FRATTON PARK | LW |  |  | 10.2132 | 9.4697 | 8.6062 | 7.6651 | 6.1546 | 4.5346 | 2.8326 | 1.0394 | -1.0288 | -3.2536 | -10.5161 | -19.4748 | -23.4813 | -25.9264 | 4.4883 | 4.0716 | 3.5751 | 3.0264 | 2.2268 | 1.363 | 0.42963 | -0.56128 | -1.79 | -3.1527 | -7.6405 | -12.8251 | -14.7042 | -15.8861 | -2.1431 | -2.7899 | -3.5642 | -4.4145 | -5.774 | -7.2357 | -8.7863 | -10.429 | -12.3403 | -14.4061 | -21.1493 | -29.3397 | -32.7649 | -34.8012
|  | FRATTON PARK | ST |  |  | 10.8409 | 10.5287 | 10.2212 | 9.8853 | 9.4253 | 8.9128 | 8.3817 | 7.8088 | 7.1439 | 6.4146 | 3.5003 | -3.9828 | -8.7386 | -11.8158 | 4.6557 | 4.2841 | 3.8959 | 3.4633 | 2.883 | 2.2423 | 1.5395 | 0.7606 | -0.13682 | -1.0753 | -4.7351 | -14.8985 | -27.0854 | -45.2425 | -1.5648 | -1.813 | -2.0663 | -2.3492 | -2.7539 | -3.2066 | -3.6837 | -4.2051 | -4.816 | -5.4831 | -8.1783 | -15.1802 | -19.3879 | -21.9754
|  | FRATTON PARK | SP |  |  | 10.9046 | 10.5808 | 10.2713 | 9.9414 | 9.5895 | 9.1999 | 8.7968 | 8.37 | 7.8883 | 7.3312 | 5.2427 | 0.0089244 | -4.5336 | -6.6197 | 4.6554 | 4.2442 | 3.7967 | 3.3016 | 2.6557 | 1.9211 | 1.0993 | 0.18626 | -0.87089 | -2.0949 | -6.8092 | -19.6862 | -41.5127 | -78.832 | -1.5053 | -1.7674 | -2.0253 | -2.305 | -2.6055 | -2.9402 | -3.2944 | -3.6753 | -4.1093 | -4.6136 | -6.5173 | -11.4301 | -15.6138 | -17.3889
COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD | MINIMUM HEADROOM | SP 50426 08256 | YES | 9.3728 | 9.1257 | 8.7009 | 8.2929 | 7.7575 | 7.2109 | 6.6356 | 6.0156 | 5.2694 | 4.4353 | 2.0013 | -1.2426 | -3.4247 | -5.2375 | 8.2029 | 8.0406 | 7.7699 | 7.5008 | 7.2259 | 6.9376 | 6.6341 | 6.2943 | 5.8659 | 5.2948 | 3.5005 | 0.12317 | -4.5931 | -13.6702 | 5.7659 | 5.5421 | 5.171 | 4.8088 | 4.3331 | 3.8427 | 3.3196 | 2.7531 | 2.0614 | 1.2924 | -0.96433 | -3.8906 | -5.6171 | -7.0827
|  | FRENCHAY ROAD | CT |  |  | 9.5106 | 9.3393 | 8.9852 | 8.6521 | 8.2943 | 7.9327 | 7.5846 | 7.1981 | 6.6871 | 5.8885 | 3.5801 | -0.39876 | -3.4247 | -5.2375 | 8.2029 | 8.0406 | 7.7699 | 7.5008 | 7.2259 | 6.9376 | 6.6341 | 6.2943 | 5.8659 | 5.2948 | 3.5005 | 0.12317 | -3.5525 | -8.4279 | 5.8799 | 5.7214 | 5.4141 | 5.1184 | 4.7935 | 4.4617 | 4.1398 | 3.7827 | 3.3171 | 2.5925 | 0.46502 | -3.0902 | -5.6171 | -7.0827
|  | FRENCHAY ROAD | LW |  |  | 9.3728 | 9.1257 | 8.7009 | 8.2929 | 7.7575 | 7.2109 | 6.6356 | 6.0156 | 5.2694 | 4.4353 | 2.0013 | -1.2426 | -2.8993 | -4.0879 | 8.2106 | 8.0764 | 7.8408 | 7.6109 | 7.3434 | 7.0642 | 6.7569 | 6.4202 | 5.9849 | 5.4957 | 4.0389 | 2.2395 | 1.4523 | 0.87498 | 5.7659 | 5.5421 | 5.171 | 4.8088 | 4.3331 | 3.8427 | 3.3196 | 2.7531 | 2.0614 | 1.2924 | -0.96433 | -3.8906 | -5.2876 | -6.2696
|  | FRENCHAY ROAD | ST |  |  | 9.6849 | 9.6151 | 9.4351 | 9.2736 | 9.1307 | 8.9874 | 8.8301 | 8.6493 | 8.3822 | 8.0646 | 7.0499 | 4.2395 | 2.3796 | 1.128 | 8.3149 | 8.2166 | 8.0505 | 7.8848 | 7.7158 | 7.5371 | 7.3353 | 7.1051 | 6.8054 | 6.4835 | 5.3455 | 2.1285 | -1.2807 | -5.9547 | 6.0456 | 5.9833 | 5.838 | 5.7016 | 5.5727 | 5.4409 | 5.2951 | 5.1275 | 4.8851 | 4.6026 | 3.6576 | 1.0486 | -0.56122 | -1.595
|  | FRENCHAY ROAD | SP |  |  | 9.7049 | 9.6387 | 9.4725 | 9.3254 | 9.2012 | 9.0724 | 8.9339 | 8.7732 | 8.5537 | 8.2688 | 7.4427 | 5.1682 | 3.1182 | 2.0087 | 8.3139 | 8.2071 | 8.0315 | 7.854 | 7.6769 | 7.4825 | 7.2613 | 7.0063 | 6.6874 | 6.3021 | 4.9595 | 1.1671 | -4.5931 | -13.6702 | 6.0636 | 6.0031 | 5.8675 | 5.7426 | 5.6333 | 5.5188 | 5.3938 | 5.2477 | 5.0517 | 4.8021 | 4.0468 | 1.9491 | 0.097701 | -0.83553
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER | MINIMUM HEADROOM | SZ 34325 86965 | NO | 7.7314 | 7.3593 | 6.8944 | 6.3964 | 5.6621 | 4.9621 | 4.2257 | 3.4515 | 2.5844 | 1.6223 | -1.1637 | -4.0496 | -5.6336 | -6.665 | 10.8373 | 10.6705 | 10.438 | 10.1775 | 9.8253 | 9.4883 | 9.1146 | 8.7167 | 8.2519 | 7.7318 | 6.2833 | 5.0893 | 4.1614 | 3.4532 | 8.0322 | 7.7159 | 7.301 | 6.8529 | 6.2091 | 5.5898 | 4.9276 | 4.2293 | 3.4366 | 2.5545 | 0.036628 | -2.3986 | -3.6928 | -4.592
|  | FRESHWATER | CT |  |  | 8.0976 | 7.9145 | 7.6939 | 7.3561 | 6.8975 | 6.4755 | 6.0113 | 5.5109 | 4.9572 | 4.1018 | 1.4317 | -2.6509 | -5.6336 | -6.665 | 10.9619 | 10.8591 | 10.731 | 10.5111 | 10.2539 | 10.0136 | 9.7453 | 9.4538 | 9.1206 | 8.6491 | 7.1536 | 5.3986 | 4.1614 | 3.4532 | 8.3266 | 8.1647 | 7.9677 | 7.6548 | 7.2395 | 6.8518 | 6.4241 | 5.9631 | 5.4503 | 4.6658 | 2.2131 | -1.2455 | -3.6928 | -4.592
|  | FRESHWATER | LW |  |  | 7.7314 | 7.3593 | 6.8944 | 6.3964 | 5.6621 | 4.9621 | 4.2257 | 3.4515 | 2.5844 | 1.6223 | -1.1637 | -4.0496 | -5.0702 | -5.731 | 10.8373 | 10.6705 | 10.438 | 10.1775 | 9.8253 | 9.4883 | 9.1146 | 8.7167 | 8.2519 | 7.7318 | 6.2833 | 5.0893 | 4.7127 | 4.4714 | 8.0322 | 7.7159 | 7.301 | 6.8529 | 6.2091 | 5.5898 | 4.9276 | 4.2293 | 3.4366 | 2.5545 | 0.036628 | -2.3986 | -3.2321 | -3.7813
|  | FRESHWATER | ST |  |  | 8.1557 | 8.0173 | 7.8621 | 7.6994 | 7.4286 | 7.184 | 6.9221 | 6.6424 | 6.3404 | 6.0176 | 4.7822 | 2.0353 | 0.65447 | -0.3985 | 11.0114 | 10.9406 | 10.8585 | 10.7709 | 10.6158 | 10.4728 | 10.3124 | 10.139 | 9.9475 | 9.7597 | 8.9814 | 7.2161 | 6.439 | 5.7501 | 8.3909 | 8.2747 | 8.1438 | 8.0058 | 7.7617 | 7.5369 | 7.2921 | 7.0306 | 6.7487 | 6.455 | 5.3115 | 2.7428 | 1.5198 | 0.65348
|  | FRESHWATER | SP |  |  | 8.1952 | 8.0684 | 7.9308 | 7.7802 | 7.4058 | 7.0456 | 6.6954 | 6.3095 | 5.9125 | 5.4477 | 3.9297 | 0.76023 | -1.1928 | -2.2585 | 11.0258 | 10.9504 | 10.8665 | 10.7707 | 10.5982 | 10.4346 | 10.2718 | 10.0832 | 9.8836 | 9.6514 | 8.8353 | 6.9267 | 5.5675 | 4.4725 | 8.4235 | 8.3112 | 8.1907 | 8.0565 | 7.74 | 7.4322 | 7.1325 | 6.797 | 6.4496 | 6.0464 | 4.7007 | 1.7843 | 0.033819 | -0.84045
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY | MINIMUM HEADROOM | SU 87745 57942 | YES | 9.831 | 9.3466 | 8.7946 | 8.1509 | 7.0977 | 5.9649 | 4.7007 | 3.2958 | 1.4682 | -0.27562 | -4.0398 | -9.188 | -12.8571 | -15.3672 | 15.2418 | 14.9341 | 14.5629 | 14.0891 | 13.4953 | 12.8 | 11.9961 | 11.0856 | 9.8221 | 8.6372 | 6.2965 | 2.6127 | -0.51251 | -3.5605 | 11.2612 | 10.7777 | 10.2195 | 9.5683 | 8.5764 | 7.5145 | 6.3212 | 4.9896 | 3.2345 | 1.5661 | -1.9597 | -6.6705 | -9.7508 | -11.7915
|  | FRIMLEY | CT |  |  | 9.9425 | 9.5647 | 9.1091 | 8.4995 | 7.7496 | 6.9447 | 6.071 | 5.0828 | 3.8764 | 2.0544 | -1.8908 | -8.391 | -12.8571 | -15.3672 | 15.2418 | 14.9341 | 14.5629 | 14.0891 | 13.5496 | 12.9632 | 12.3067 | 11.5564 | 10.6231 | 9.3421 | 6.7106 | 2.6127 | -0.51251 | -3.5605 | 11.3346 | 10.9414 | 10.4626 | 9.859 | 9.1474 | 8.3822 | 7.5462 | 6.5975 | 5.4321 | 3.6931 | 0.0080048 | -5.8634 | -9.7508 | -11.7915
|  | FRIMLEY | LW |  |  | 9.831 | 9.3466 | 8.7946 | 8.1509 | 7.0977 | 5.9649 | 4.7007 | 3.2958 | 1.4682 | -0.27562 | -4.0398 | -9.188 | -11.4604 | -12.8361 | 15.2555 | 14.9365 | 14.5664 | 14.1197 | 13.4953 | 12.8 | 11.9961 | 11.0856 | 9.8221 | 8.6372 | 6.2965 | 3.3299 | 2.2741 | 1.6131 | 11.2612 | 10.7777 | 10.2195 | 9.5683 | 8.5764 | 7.5145 | 6.3212 | 4.9896 | 3.2345 | 1.5661 | -1.9597 | -6.6705 | -8.6191 | -9.7692
|  | FRIMLEY | ST |  |  | 10.3068 | 10.1609 | 9.9657 | 9.7074 | 9.4144 | 9.0895 | 8.6951 | 8.2371 | 7.683 | 7.1009 | 4.1672 | -1.1684 | -4.0769 | -5.8792 | 15.5014 | 15.3588 | 15.1739 | 14.9298 | 14.6666 | 14.3746 | 14.0444 | 13.651 | 13.1562 | 12.6639 | 10.1972 | 5.7766 | 2.9627 | 0.14247 | 11.7161 | 11.5656 | 11.3595 | 11.0899 | 10.7821 | 10.4403 | 10.0557 | 9.6103 | 9.0702 | 8.508 | 5.6504 | 0.6022 | -1.9851 | -3.5084
|  | FRIMLEY | SP |  |  | 10.3345 | 10.1953 | 10.0355 | 9.8304 | 9.6007 | 9.3625 | 9.114 | 8.776 | 8.3841 | 7.9237 | 6.0567 | 0.58903 | -2.3617 | -3.6417 | 15.508 | 15.3613 | 15.1903 | 14.9724 | 14.753 | 14.5199 | 14.269 | 13.9578 | 13.599 | 13.1606 | 11.364 | 6.1366 | 1.9816 | -2.7332 | 11.7406 | 11.5936 | 11.4243 | 11.2109 | 10.9731 | 10.7271 | 10.4695 | 10.1376 | 9.7574 | 9.3125 | 7.5024 | 2.224 | -0.51385 | -1.6217
MELKSHAM GSP | FROME BSP | FROME | MINIMUM HEADROOM | ST 78850 48051 | YES | 29.9085 | 28.4834 | 26.8054 | 24.8674 | 22.4378 | 20.044 | 17.6783 | 15.1682 | 12.256 | 9.1676 | 1.1569 | -7.2343 | -10.6081 | -13.1857 | 39.5993 | 38.7497 | 37.7346 | 36.5804 | 35.2166 | 33.8839 | 32.5125 | 31.0358 | 29.2412 | 27.3033 | 22.5739 | 17.8444 | 13.9179 | 10.3996 | 32.9775 | 31.7565 | 30.3348 | 28.7126 | 26.5833 | 24.4931 | 22.4147 | 20.2182 | 17.6897 | 14.8756 | 7.4937 | -0.090292 | -3.157 | -5.6987
|  | FROME | CT |  |  | 30.4998 | 29.3849 | 28.1152 | 26.4108 | 24.5323 | 22.7133 | 20.9648 | 19.098 | 17.0212 | 14.0503 | 6.0087 | -4.5848 | -10.6081 | -13.1857 | 39.7627 | 39.0047 | 38.156 | 37.0233 | 35.8424 | 34.7071 | 33.5666 | 32.3324 | 30.9235 | 28.996 | 23.9375 | 17.8444 | 13.9179 | 10.3996 | 33.578 | 32.6605 | 31.613 | 30.2388 | 28.6454 | 27.1109 | 25.6191 | 23.9738 | 22.0367 | 19.2572 | 11.8351 | 2.3445 | -3.157 | -5.6987
|  | FROME | LW |  |  | 29.9085 | 28.4834 | 26.8054 | 24.8674 | 22.4378 | 20.044 | 17.6783 | 15.1682 | 12.256 | 9.1676 | 1.1569 | -7.2343 | -9.5271 | -10.6295 | 39.5993 | 38.7497 | 37.7346 | 36.5804 | 35.2166 | 33.8839 | 32.5125 | 31.0358 | 29.2412 | 27.3033 | 22.5739 | 18.0622 | 17.0644 | 16.6078 | 32.9775 | 31.7565 | 30.3348 | 28.7126 | 26.5833 | 24.4931 | 22.4147 | 20.2182 | 17.6897 | 14.8756 | 7.4937 | -0.090292 | -2.1204 | -3.0912
|  | FROME | ST |  |  | 30.9056 | 30.1898 | 29.403 | 28.4753 | 27.3696 | 26.3353 | 25.3375 | 24.296 | 23.1453 | 21.9415 | 17.2743 | 9.0376 | 5.4933 | 3.367 | 40.0697 | 39.5642 | 39.0087 | 38.3683 | 37.5942 | 36.8766 | 36.1498 | 35.3823 | 34.509 | 33.6159 | 30.0854 | 23.7852 | 20.4986 | 17.1446 | 33.9014 | 33.3259 | 32.7002 | 31.9864 | 31.0998 | 30.2803 | 29.4648 | 28.6122 | 27.6554 | 26.6173 | 22.2478 | 14.5352 | 11.3179 | 9.4427
|  | FROME | SP |  |  | 31.023 | 30.2729 | 29.4854 | 28.5986 | 27.3547 | 26.1797 | 25.036 | 23.8457 | 22.6007 | 21.3477 | 17.4293 | 9.2936 | 4.9857 | 3.2248 | 40.1156 | 39.5806 | 39.016 | 38.3943 | 37.6256 | 36.9157 | 36.1858 | 35.4067 | 34.5594 | 33.6489 | 30.5563 | 23.6959 | 18.1063 | 11.7194 | 34.0133 | 33.412 | 32.7865 | 32.1059 | 31.0462 | 30.0478 | 29.0544 | 28.025 | 26.9367 | 25.8302 | 22.5142 | 14.949 | 10.899 | 9.3023
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE | MINIMUM HEADROOM | SU 84935 93873 | YES | 10.583 | 10.0167 | 9.3511 | 8.6254 | 7.5404 | 6.4381 | 5.26 | 3.9762 | 2.3804 | 0.70229 | -3.403 | -8.2058 | -10.8896 | -12.8119 | 10.4402 | 10.1094 | 9.7048 | 9.2554 | 8.6519 | 8.0266 | 7.3314 | 6.5584 | 5.5367 | 4.4582 | 1.7678 | -2.9985 | -8.3188 | -19.7878 | 6.5354 | 6.0305 | 5.4385 | 4.7927 | 3.8053 | 2.7982 | 1.7242 | 0.55695 | -0.88449 | -2.4016 | -6.1646 | -10.5979 | -13.139 | -14.8196
|  | FRYERS LANE | CT |  |  | 10.8373 | 10.4312 | 9.9622 | 9.3609 | 8.6082 | 7.8529 | 7.0649 | 6.1897 | 5.1598 | 3.5149 | -0.62548 | -6.8629 | -10.8896 | -12.8119 | 10.4652 | 10.1381 | 9.7597 | 9.2708 | 8.7188 | 8.1468 | 7.5268 | 6.8281 | 5.9894 | 4.7966 | 1.7678 | -2.9985 | -7.5837 | -13.3299 | 6.7787 | 6.425 | 6.0154 | 5.49 | 4.8146 | 4.1329 | 3.4224 | 2.6353 | 1.7118 | 0.22645 | -3.5539 | -9.3609 | -13.139 | -14.8196
|  | FRYERS LANE | LW |  |  | 10.583 | 10.0167 | 9.3511 | 8.6254 | 7.5404 | 6.4381 | 5.26 | 3.9762 | 2.3804 | 0.70229 | -3.403 | -8.2058 | -9.7962 | -10.5989 | 10.4402 | 10.1094 | 9.7048 | 9.2554 | 8.6519 | 8.0266 | 7.3314 | 6.5584 | 5.5367 | 4.4582 | 1.9901 | -0.66694 | -1.3604 | -1.7023 | 6.5354 | 6.0305 | 5.4385 | 4.7927 | 3.8053 | 2.7982 | 1.7242 | 0.55695 | -0.88449 | -2.4016 | -6.1646 | -10.5979 | -12.0724 | -12.8103
|  | FRYERS LANE | ST |  |  | 11.1681 | 10.9806 | 10.7517 | 10.492 | 10.1575 | 9.8259 | 9.4582 | 9.0492 | 8.5561 | 8.0235 | 5.6335 | 0.69842 | -1.7279 | -3.1615 | 10.6934 | 10.5148 | 10.2987 | 10.0503 | 9.7367 | 9.4115 | 9.0416 | 8.6261 | 8.1289 | 7.6181 | 5.3466 | 0.34047 | -3.8711 | -9.4684 | 7.0757 | 6.9183 | 6.725 | 6.5046 | 6.2125 | 5.9183 | 5.5912 | 5.2276 | 4.7886 | 4.3081 | 2.1708 | -2.2959 | -4.5493 | -5.8891
|  | FRYERS LANE | SP |  |  | 11.2207 | 11.0373 | 10.8328 | 10.6104 | 10.3083 | 10.0258 | 9.7241 | 9.3799 | 8.986 | 8.502 | 6.7078 | 1.8312 | -0.99315 | -2.1047 | 10.7096 | 10.5171 | 10.2946 | 10.0473 | 9.7419 | 9.4257 | 9.0758 | 8.6706 | 8.1959 | 7.6259 | 5.4151 | -0.82455 | -8.3188 | -19.7878 | 7.1241 | 6.9724 | 6.8022 | 6.6162 | 6.3503 | 6.0972 | 5.8258 | 5.5174 | 5.1647 | 4.7278 | 3.1165 | -1.241 | -3.8042 | -4.8174
COWLEY GSP | DRAYTON BSP | FULSCOT | MINIMUM HEADROOM | SU 54413 89511 | NO | 7.7696 | 6.8184 | 5.7524 | 4.5871 | 3.1762 | 1.5595 | -0.14403 | -1.9266 | -3.8027 | -5.6383 | -9.6461 | -13.575 | -15.4559 | -16.9808 | 12.4876 | 11.9526 | 11.3498 | 10.6916 | 9.9371 | 9.0689 | 8.1359 | 7.1497 | 6.0436 | 4.9412 | 2.631 | 0.38676 | -1.6242 | -3.3762 | 9.5201 | 8.7318 | 7.8213 | 6.8177 | 5.5868 | 4.1807 | 2.6879 | 1.1167 | -0.57486 | -2.2438 | -5.8865 | -9.4502 | -11.0094 | -12.2943
|  | FULSCOT | CT |  |  | 8.012 | 7.2107 | 6.3111 | 5.2741 | 4.1492 | 2.8365 | 1.484 | 0.05739 | -1.3419 | -3.1282 | -7.2337 | -12.2457 | -15.4559 | -16.9808 | 12.5429 | 12.0463 | 11.4925 | 10.8499 | 10.1911 | 9.4301 | 8.6325 | 7.7808 | 6.9134 | 5.813 | 3.2864 | 0.38676 | -1.6242 | -3.3762 | 9.7447 | 9.0731 | 8.3099 | 7.4165 | 6.4399 | 5.3059 | 4.1302 | 2.8806 | 1.634 | 0.013765 | -3.7271 | -8.227 | -11.0094 | -12.2943
|  | FULSCOT | LW |  |  | 7.7696 | 6.8184 | 5.7524 | 4.5871 | 3.1762 | 1.5595 | -0.14403 | -1.9266 | -3.8027 | -5.6383 | -9.6461 | -13.575 | -14.9243 | -15.5976 | 12.4876 | 11.9526 | 11.3498 | 10.6916 | 9.9371 | 9.0689 | 8.1359 | 7.1497 | 6.0436 | 4.9412 | 2.631 | 0.50826 | -0.101 | -0.39771 | 9.5201 | 8.7318 | 7.8213 | 6.8177 | 5.5868 | 4.1807 | 2.6879 | 1.1167 | -0.57486 | -2.2438 | -5.8865 | -9.4502 | -10.6314 | -11.2142
|  | FULSCOT | ST |  |  | 8.2074 | 7.9044 | 7.3973 | 6.8406 | 6.1979 | 5.4372 | 4.6401 | 3.8159 | 3.0235 | 2.2597 | -0.17871 | -4.4117 | -6.3886 | -7.5436 | 12.7981 | 12.5051 | 12.1787 | 11.8204 | 11.4013 | 10.9109 | 10.3905 | 9.8466 | 9.3043 | 8.7895 | 6.9909 | 3.7051 | 1.9596 | 0.3091 | 10.0886 | 9.7398 | 9.3392 | 8.8959 | 8.3586 | 7.7265 | 7.0572 | 6.3589 | 5.6718 | 5.005 | 2.7571 | -1.2374 | -3.0208 | -4.0287
|  | FULSCOT | SP |  |  | 8.2086 | 7.9121 | 7.5249 | 7.0404 | 6.5185 | 5.8997 | 5.231 | 4.5305 | 3.8787 | 3.2028 | 1.3067 | -2.8441 | -5.3122 | -6.3033 | 12.8143 | 12.5282 | 12.2269 | 11.9048 | 11.575 | 11.1809 | 10.7438 | 10.2732 | 9.8193 | 9.3407 | 7.8757 | 4.3451 | 1.4735 | -1.4333 | 10.1309 | 9.807 | 9.4545 | 9.0789 | 8.6595 | 8.164 | 7.6174 | 7.0354 | 6.4821 | 5.8987 | 4.1851 | 0.24385 | -2.0723 | -2.964
COWLEY GSP | WITNEY BSP | FYFIELD | MINIMUM HEADROOM | SU 42256 99551 | NO | 5.5437 | 5.1803 | 4.7105 | 4.1222 | 3.3396 | 2.5312 | 1.6915 | 0.7732 | -0.23642 | -1.0683 | -2.8442 | -4.9483 | -5.559 | -5.9646 | 5.7707 | 5.5847 | 5.3366 | 5.0225 | 4.629 | 4.2192 | 3.7776 | 3.2842 | 2.6764 | 2.196 | 1.3984 | 0.47238 | -0.022909 | -0.61153 | 2.6983 | 2.3659 | 1.9477 | 1.432 | 0.74334 | 0.030455 | -0.71536 | -1.5328 | -2.4541 | -3.2166 | -4.8018 | -6.682 | -7.2108 | -7.5519
|  | FYFIELD | CT |  |  | 5.8566 | 5.6609 | 5.3575 | 4.9351 | 4.394 | 3.83 | 3.2524 | 2.5866 | 1.9206 | 1.1443 | -0.43316 | -3.1772 | -5.0561 | -5.7614 | 5.8529 | 5.7154 | 5.5115 | 5.2392 | 4.9309 | 4.6074 | 4.2684 | 3.866 | 3.4341 | 2.9427 | 2.1276 | 0.86989 | -0.022909 | -0.61153 | 2.9679 | 2.7838 | 2.511 | 2.1399 | 1.6656 | 1.1699 | 0.65931 | 0.067266 | -0.53742 | -1.2546 | -2.6736 | -5.1104 | -6.7615 | -7.3541
|  | FYFIELD | LW |  |  | 5.5437 | 5.1803 | 4.7105 | 4.1222 | 3.3396 | 2.5312 | 1.6915 | 0.7732 | -0.23642 | -1.0683 | -2.8442 | -4.9483 | -5.559 | -5.9646 | 5.7707 | 5.5847 | 5.3366 | 5.0225 | 4.629 | 4.2192 | 3.7776 | 3.2842 | 2.6764 | 2.196 | 1.3984 | 0.47238 | 0.23629 | 0.093663 | 2.6983 | 2.3659 | 1.9477 | 1.432 | 0.74334 | 0.030455 | -0.71536 | -1.5328 | -2.4541 | -3.2166 | -4.8018 | -6.682 | -7.2108 | -7.5519
|  | FYFIELD | ST |  |  | 6.0073 | 5.903 | 5.7308 | 5.4801 | 5.1555 | 4.8169 | 4.4718 | 4.0901 | 3.7229 | 3.3969 | 2.1148 | 0.34322 | -0.67606 | -1.3458 | 5.9697 | 5.9027 | 5.792 | 5.6289 | 5.4288 | 5.218 | 4.9984 | 4.7527 | 4.5066 | 4.3008 | 3.3783 | 2.213 | 1.5696 | 0.98231 | 3.1135 | 3.0175 | 2.8696 | 2.6595 | 2.3821 | 2.0914 | 1.7928 | 1.4621 | 1.1364 | 0.84093 | -0.36137 | -1.9951 | -2.9032 | -3.4919
|  | FYFIELD | SP |  |  | 6.0474 | 5.9658 | 5.8306 | 5.6367 | 5.2816 | 4.9217 | 4.5594 | 4.1554 | 3.7768 | 3.374 | 2.0732 | -0.78456 | -2.2633 | -3.179 | 5.9798 | 5.9185 | 5.8246 | 5.6934 | 5.5037 | 5.3088 | 5.1062 | 4.8696 | 4.6439 | 4.4213 | 3.6417 | 1.7655 | 0.86438 | 0.11604 | 3.1482 | 3.072 | 2.958 | 2.8008 | 2.5009 | 2.1962 | 1.8873 | 1.5406 | 1.2101 | 0.84996 | -0.33521 | -2.9838 | -4.3128 | -5.1239
LOVEDEAN GSP | HAVANT | GABLE HEAD | MINIMUM HEADROOM | SZ 72204 99904 | YES | 17.0689 | 16.569 | 15.8311 | 15.0112 | 14.0842 | 13.0917 | 11.9156 | 10.6277 | 9.1868 | 7.6781 | 4.4572 | 0.92189 | -1.8928 | -3.553 | 14.8144 | 14.5255 | 14.0812 | 13.5882 | 13.0695 | 12.506 | 11.8244 | 11.0693 | 10.1698 | 9.2108 | 7.321 | 5.3105 | 3.4635 | 2.0316 | 11.1426 | 10.7009 | 10.0462 | 9.3169 | 8.4701 | 7.5618 | 6.49 | 5.3144 | 3.9728 | 2.5596 | -0.42186 | -3.6243 | -6.0532 | -7.4948
|  | GABLE HEAD | CT |  |  | 17.2387 | 16.8537 | 16.3044 | 15.5531 | 14.8999 | 14.1972 | 13.3298 | 12.3629 | 11.3668 | 9.8275 | 6.3034 | 1.5012 | -1.8928 | -3.553 | 14.8506 | 14.5948 | 14.2411 | 13.7404 | 13.3199 | 12.8655 | 12.3111 | 11.6899 | 11.0223 | 10.0326 | 7.8641 | 5.3105 | 3.4635 | 2.0316 | 11.2873 | 10.9474 | 10.4677 | 9.7939 | 9.1905 | 8.5414 | 7.749 | 6.8648 | 5.9381 | 4.4991 | 1.2293 | -3.0761 | -6.0532 | -7.4948
|  | GABLE HEAD | LW |  |  | 17.0689 | 16.569 | 15.8311 | 15.0112 | 14.0842 | 13.0917 | 11.9156 | 10.6277 | 9.1868 | 7.6781 | 4.4572 | 0.92189 | -0.61376 | -1.4064 | 14.8144 | 14.5255 | 14.0812 | 13.5882 | 13.0695 | 12.506 | 11.8244 | 11.0693 | 10.1698 | 9.2108 | 7.321 | 5.4736 | 4.7828 | 4.4175 | 11.1426 | 10.7009 | 10.0462 | 9.3169 | 8.4701 | 7.5618 | 6.49 | 5.3144 | 3.9728 | 2.5596 | -0.42186 | -3.6243 | -4.9633 | -5.6419
|  | GABLE HEAD | ST |  |  | 17.5023 | 17.3044 | 17.0036 | 16.6644 | 16.3617 | 16.0182 | 15.5796 | 15.0855 | 14.5948 | 14.0999 | 12.1542 | 8.3337 | 6.5021 | 5.1736 | 15.0283 | 14.8937 | 14.6934 | 14.465 | 14.2446 | 13.9933 | 13.6796 | 13.3256 | 12.9596 | 12.6083 | 11.1266 | 8.2885 | 6.9431 | 5.6331 | 11.5401 | 11.3783 | 11.1331 | 10.8533 | 10.5763 | 10.2613 | 9.8671 | 9.4226 | 8.9703 | 8.5162 | 6.6583 | 3.0376 | 1.4109 | 0.2596
|  | GABLE HEAD | SP |  |  | 17.5427 | 17.3372 | 17.055 | 16.7494 | 16.5312 | 16.2953 | 15.9623 | 15.5841 | 15.2321 | 14.8184 | 13.4425 | 9.7734 | 7.8878 | 7.0923 | 15.0451 | 14.8955 | 14.6975 | 14.4818 | 14.3214 | 14.1473 | 13.9077 | 13.6301 | 13.3603 | 13.0463 | 11.9315 | 8.8419 | 6.7563 | 4.7283 | 11.5768 | 11.4053 | 11.1762 | 10.927 | 10.7319 | 10.5216 | 10.2299 | 9.8964 | 9.5785 | 9.2016 | 7.9021 | 4.3692 | 2.6102 | 1.9106
LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD | MINIMUM HEADROOM | SU 64771 01769 | NO | 11.3671 | 10.8401 | 10.1423 | 9.1091 | 7.6543 | 5.822 | 3.9036 | 1.818 | -0.67612 | -3.2464 | -11.8702 | -22.853 | -29.4865 | -33.14 | 10.4954 | 10.0574 | 9.5483 | 8.745 | 7.7845 | 6.5973 | 5.3212 | 3.9087 | 2.282 | 0.39893 | -6.0732 | -18.0745 | -37.1533 | -73.584 | 6.4379 | 5.9895 | 5.4233 | 4.609 | 3.3539 | 1.7487 | 0.060286 | -1.7756 | -3.9881 | -6.267 | -13.8922 | -23.553 | -29.3515 | -32.469
|  | GAMBLE ROAD | CT |  |  | 11.5636 | 11.1633 | 10.6735 | 9.7246 | 8.5714 | 7.0544 | 5.4687 | 3.7236 | 1.7394 | -0.81566 | -9.2926 | -22.3051 | -29.4865 | -33.14 | 10.4954 | 10.0574 | 9.5483 | 8.745 | 7.7845 | 6.5973 | 5.3212 | 3.9087 | 2.282 | 0.39893 | -6.0732 | -18.0745 | -30.7343 | -48.7323 | 6.6355 | 6.3102 | 5.9147 | 5.198 | 4.2182 | 2.9105 | 1.5347 | 0.018719 | -1.7159 | -3.9827 | -11.4828 | -23.0998 | -29.3515 | -32.469
|  | GAMBLE ROAD | LW |  |  | 11.3671 | 10.8401 | 10.1423 | 9.1091 | 7.6543 | 5.822 | 3.9036 | 1.818 | -0.67612 | -3.2464 | -11.8702 | -22.853 | -26.6145 | -28.6136 | 10.5805 | 10.2691 | 9.8501 | 9.2329 | 8.4325 | 7.4294 | 6.3517 | 5.1797 | 3.7504 | 2.2677 | -2.7683 | -8.9067 | -10.6853 | -11.6582 | 6.4379 | 5.9895 | 5.4233 | 4.609 | 3.3539 | 1.7487 | 0.060286 | -1.7756 | -3.9881 | -6.267 | -13.8922 | -23.553 | -26.8566 | -28.5708
|  | GAMBLE ROAD | ST |  |  | 11.8241 | 11.6151 | 11.3608 | 10.9149 | 10.3394 | 9.5261 | 8.6838 | 7.7489 | 6.6606 | 5.5067 | 1.1952 | -7.2105 | -11.6698 | -14.282 | 10.6498 | 10.3228 | 9.9499 | 9.4425 | 8.7755 | 7.9424 | 7.0404 | 6.0349 | 4.8656 | 3.6666 | -0.84193 | -11.3425 | -23.3452 | -40.9466 | 6.8605 | 6.7001 | 6.5073 | 6.1943 | 5.7799 | 5.1937 | 4.5088 | 3.7455 | 2.8402 | 1.8726 | -1.7587 | -9.1804 | -13.1034 | -15.3085
|  | GAMBLE ROAD | SP |  |  | 11.8708 | 11.6555 | 11.3953 | 10.9675 | 10.517 | 9.8725 | 9.1766 | 8.4116 | 7.5458 | 6.6028 | 3.2224 | -2.936 | -6.7843 | -8.4958 | 10.6396 | 10.2782 | 9.8447 | 9.2828 | 8.5454 | 7.6273 | 6.5919 | 5.4346 | 4.0905 | 2.6275 | -2.8826 | -16.1209 | -37.1533 | -73.584 | 6.9009 | 6.745 | 6.5575 | 6.2689 | 5.9495 | 5.5082 | 4.9631 | 4.3566 | 3.6576 | 2.889 | 0.076798 | -5.3145 | -8.7379 | -10.1591
IVER 132KV | DENHAM | GERRARDS CROSS | MINIMUM HEADROOM | SU 99973 87964 | YES | 1.1463 | 0.81051 | 0.49068 | 0.12763 | -0.43509 | -1.0767 | -1.8069 | -2.6822 | -3.7404 | -4.5521 | -6.4235 | -8.658 | -9.7451 | -10.626 | 0.91324 | 0.7047 | 0.44178 | 0.20673 | -0.04175 | -0.42131 | -0.88571 | -1.4716 | -2.2436 | -2.7918 | -3.9223 | -5.2098 | -6.3623 | -7.4934 | -1.9301 | -2.249 | -2.5518 | -2.8975 | -3.4212 | -4.0353 | -4.7412 | -5.5939 | -6.6551 | -7.4585 | -9.2923 | -11.3712 | -12.2764 | -13.0365
|  | GERRARDS CROSS | CT |  |  | 1.2278 | 0.97104 | 0.65122 | 0.36541 | -0.00019588 | -0.43701 | -0.9537 | -1.5103 | -2.1874 | -3.1353 | -4.9963 | -7.8774 | -9.7451 | -10.626 | 0.91324 | 0.7047 | 0.44178 | 0.20673 | -0.04175 | -0.35863 | -0.75885 | -1.195 | -1.75 | -2.4349 | -3.6341 | -5.2098 | -6.3623 | -7.4934 | -1.8661 | -2.1151 | -2.4267 | -2.7043 | -3.0499 | -3.4785 | -3.992 | -4.5477 | -5.2461 | -6.1841 | -8.0047 | -10.6404 | -12.2764 | -13.0365
|  | GERRARDS CROSS | LW |  |  | 1.1463 | 0.81051 | 0.49068 | 0.12763 | -0.43509 | -1.0767 | -1.8069 | -2.6822 | -3.7404 | -4.5521 | -6.4235 | -8.658 | -9.479 | -9.8492 | 0.93792 | 0.71966 | 0.51639 | 0.27659 | -0.036249 | -0.42131 | -0.88571 | -1.4716 | -2.2436 | -2.7918 | -3.9223 | -5.0915 | -5.4084 | -5.5621 | -1.9301 | -2.249 | -2.5518 | -2.8975 | -3.4212 | -4.0353 | -4.7412 | -5.5939 | -6.6551 | -7.4585 | -9.2923 | -11.3712 | -12.0836 | -12.3959
|  | GERRARDS CROSS | ST |  |  | 1.5148 | 1.4239 | 1.2928 | 1.1439 | 0.9777 | 0.75964 | 0.50097 | 0.20222 | -0.20904 | -0.59734 | -2.4078 | -4.5852 | -5.7563 | -6.4844 | 1.1304 | 1.0463 | 0.92611 | 0.78911 | 0.64877 | 0.45534 | 0.22228 | -0.049123 | -0.43424 | -0.76959 | -2.3317 | -4.0543 | -5.0418 | -6.0167 | -1.5862 | -1.6736 | -1.8012 | -1.9464 | -2.1066 | -2.3308 | -2.5986 | -2.9094 | -3.3552 | -3.7634 | -5.6196 | -7.7141 | -8.7645 | -9.3904
|  | GERRARDS CROSS | SP |  |  | 1.5267 | 1.4537 | 1.3741 | 1.2702 | 1.148 | 0.97684 | 0.78681 | 0.546 | 0.20075 | -0.1484 | -1.4471 | -4.1324 | -5.3208 | -5.8456 | 1.128 | 1.0513 | 0.96545 | 0.85662 | 0.75297 | 0.59543 | 0.41748 | 0.18931 | -0.14406 | -0.45953 | -1.639 | -4.042 | -5.3652 | -6.6849 | -1.5763 | -1.6472 | -1.7245 | -1.8259 | -1.9426 | -2.1208 | -2.3209 | -2.575 | -2.9554 | -3.3256 | -4.6751 | -7.3088 | -8.4174 | -8.8827
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM | MINIMUM HEADROOM | ST 80185 25765 | YES | 24.044 | 23.4687 | 22.8647 | 22.273 | 21.5017 | 20.6225 | 19.0167 | 17.976 | 16.7399 | 15.5118 | 11.9762 | 7.4883 | 6.0487 | 5.0329 | 25.6855 | 25.179 | 24.6964 | 24.3214 | 23.8905 | 23.4575 | 22.0031 | 21.3202 | 20.535 | 19.7717 | 17.5393 | 14.4554 | 13.3344 | 12.5059 | 24.4865 | 24.0296 | 23.4492 | 22.9008 | 22.2057 | 21.4671 | 19.7951 | 18.8045 | 17.6295 | 16.4535 | 13.1133 | 8.8272 | 7.4939 | 6.5423
|  | GILLINGHAM | CT |  |  | 24.1868 | 23.6857 | 23.1813 | 22.7069 | 22.0841 | 21.3543 | 19.9097 | 19.0384 | 18.0102 | 16.8474 | 13.4369 | 8.2632 | 6.0487 | 5.0329 | 25.7377 | 25.2647 | 24.8209 | 24.4718 | 24.093 | 23.7161 | 22.3263 | 21.7126 | 21.0189 | 20.2944 | 18.1545 | 14.7519 | 13.3344 | 12.5059 | 24.4865 | 24.0296 | 23.5836 | 23.2452 | 22.7171 | 22.0885 | 20.5581 | 19.7174 | 18.7334 | 17.6202 | 14.3832 | 9.5338 | 7.4939 | 6.5423
|  | GILLINGHAM | LW |  |  | 24.044 | 23.4687 | 22.8647 | 22.273 | 21.5017 | 20.6225 | 19.0167 | 17.976 | 16.7399 | 15.5118 | 11.9762 | 7.4883 | 6.3804 | 5.7971 | 25.6855 | 25.179 | 24.6964 | 24.3214 | 23.8905 | 23.4575 | 22.0031 | 21.3202 | 20.535 | 19.7717 | 17.5393 | 14.4554 | 13.579 | 13.0847 | 24.5006 | 24.03 | 23.4492 | 22.9008 | 22.2057 | 21.4671 | 19.7951 | 18.8045 | 17.6295 | 16.4535 | 13.1133 | 8.8272 | 7.725 | 7.1355
|  | GILLINGHAM | ST |  |  | 24.2884 | 23.8673 | 23.4573 | 23.1319 | 22.7404 | 22.3382 | 21.1836 | 20.5795 | 19.8847 | 19.2072 | 16.9567 | 12.795 | 10.8138 | 10.2479 | 25.793 | 25.3587 | 24.969 | 24.7164 | 24.4428 | 24.1846 | 22.9158 | 22.4171 | 21.8665 | 21.3412 | 19.6435 | 16.096 | 14.4264 | 14.0182 | 24.5622 | 24.1527 | 23.7652 | 23.5048 | 23.2238 | 22.9517 | 21.7237 | 21.1452 | 20.4661 | 19.8041 | 17.5452 | 13.3423 | 11.7339 | 10.9449
|  | GILLINGHAM | SP |  |  | 24.3115 | 23.8972 | 23.5027 | 23.2147 | 22.8208 | 22.4288 | 21.3149 | 20.7319 | 20.0814 | 19.4487 | 17.4698 | 13.642 | 11.6834 | 10.8158 | 25.804 | 25.3742 | 24.9909 | 24.7506 | 24.4857 | 24.2426 | 22.9895 | 22.5076 | 21.9884 | 21.4976 | 19.9888 | 16.9758 | 15.246 | 14.2115 | 24.5686 | 24.1633 | 23.7823 | 23.5312 | 23.2704 | 23.0257 | 21.84 | 21.2858 | 20.6789 | 20.069 | 18.1305 | 14.2131 | 12.26 | 11.429
BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING | MINIMUM HEADROOM | SU 96743 44375 | YES | 11.0298 | 10.2807 | 9.5484 | 8.7779 | 7.6199 | 6.388 | 5.0374 | 3.5784 | 1.8057 | -0.030991 | -4.7354 | -10.0737 | -12.486 | -14.3837 | 17.6485 | 17.1957 | 16.7413 | 16.2477 | 15.6024 | 14.9002 | 14.0872 | 13.2023 | 12.0539 | 10.8609 | 7.9558 | 4.8187 | 2.2147 | -0.0089213 | 13.0686 | 12.3791 | 11.6884 | 10.9503 | 9.8815 | 8.7375 | 7.4608 | 6.09 | 4.4084 | 2.6648 | -1.7519 | -6.6836 | -8.606 | -10.1558
|  | GODALMING | CT |  |  | 11.3166 | 10.7659 | 10.1726 | 9.5441 | 8.7759 | 7.9368 | 7.0581 | 6.108 | 4.9809 | 3.1951 | -1.4219 | -8.2495 | -12.486 | -14.3837 | 17.6759 | 17.265 | 16.8212 | 16.3434 | 15.8302 | 15.2619 | 14.6441 | 13.9673 | 13.1425 | 11.9429 | 8.9258 | 4.8187 | 2.2147 | -0.0089213 | 13.2778 | 12.7514 | 12.1899 | 11.5923 | 10.8692 | 10.0783 | 9.2456 | 8.343 | 7.2652 | 5.5716 | 1.2378 | -4.9849 | -8.606 | -10.1558
|  | GODALMING | LW |  |  | 11.0298 | 10.2807 | 9.5484 | 8.7779 | 7.6199 | 6.388 | 5.0374 | 3.5784 | 1.8057 | -0.030991 | -4.7354 | -10.0737 | -11.6546 | -12.4798 | 17.6485 | 17.1957 | 16.7413 | 16.2477 | 15.6024 | 14.9002 | 14.0872 | 13.2023 | 12.0539 | 10.8609 | 7.9558 | 4.9142 | 4.2307 | 3.895 | 13.0686 | 12.3791 | 11.6884 | 10.9503 | 9.8815 | 8.7375 | 7.4608 | 6.09 | 4.4084 | 2.6648 | -1.7519 | -6.6836 | -8.0766 | -8.7633
|  | GODALMING | ST |  |  | 11.7426 | 11.4783 | 11.2284 | 10.966 | 10.6409 | 10.26 | 9.8286 | 9.342 | 8.7517 | 8.1095 | 5.2066 | -0.91362 | -3.8192 | -5.2719 | 17.9943 | 17.7896 | 17.578 | 17.3462 | 17.0747 | 16.7712 | 16.4222 | 16.0245 | 15.5375 | 15.0414 | 12.7412 | 7.9136 | 5.3662 | 3.2618 | 13.7154 | 13.4792 | 13.2391 | 12.9786 | 12.651 | 12.2868 | 11.8734 | 11.4055 | 10.8355 | 10.2207 | 7.411 | 1.5536 | -1.1136 | -2.3834
|  | GODALMING | SP |  |  | 11.7949 | 11.5587 | 11.3527 | 11.1459 | 10.8555 | 10.5394 | 10.2023 | 9.8097 | 9.3454 | 8.7874 | 6.6875 | 0.97601 | -2.633 | -3.9008 | 18.0096 | 17.8104 | 17.6157 | 17.4085 | 17.1837 | 16.939 | 16.6739 | 16.3568 | 15.9778 | 15.5384 | 13.817 | 8.9632 | 5.0973 | 1.7492 | 13.7593 | 13.5455 | 13.3463 | 13.1394 | 12.8579 | 12.5565 | 12.2393 | 11.8664 | 11.4236 | 10.8946 | 8.8862 | 3.3905 | -0.035575 | -1.1901
WILLESDEN GSP | ACTON LANE | GOLDSMITHS | MINIMUM HEADROOM | TQ 21089 80758 | YES | 7.1416 | 6.9754 | 6.7375 | 6.4456 | 5.9639 | 5.4495 | 4.9299 | 4.4562 | 3.964 | 3.4544 | 1.8345 | -0.76818 | -3.5471 | -5.1579 | 7.0591 | 6.8417 | 6.5789 | 6.2423 | 5.8167 | 5.2553 | 4.5279 | 3.7384 | 2.8319 | 1.821 | -2.0822 | -13.0135 | -33.8464 | -72.5759 | 5.7097 | 5.5667 | 5.3523 | 5.0902 | 4.6893 | 4.2561 | 3.8103 | 3.3955 | 2.948 | 2.4777 | 0.96968 | -1.2872 | -3.1595 | -4.446
|  | GOLDSMITHS | CT |  |  | 7.2165 | 7.0939 | 6.9135 | 6.6567 | 6.2953 | 5.9048 | 5.5257 | 5.1948 | 4.8708 | 4.3359 | 2.658 | -0.76818 | -3.5471 | -5.1579 | 7.0591 | 6.8417 | 6.5789 | 6.2423 | 5.8167 | 5.2668 | 4.67 | 4.024 | 3.3089 | 2.5011 | -0.3453 | -7.7619 | -19.3744 | -38.0544 | 5.7524 | 5.64 | 5.4764 | 5.2326 | 4.9239 | 4.5815 | 4.2438 | 3.9388 | 3.6281 | 3.154 | 1.6607 | -1.0944 | -3.1595 | -4.446
|  | GOLDSMITHS | LW |  |  | 7.1416 | 6.9754 | 6.7375 | 6.4456 | 5.9639 | 5.4495 | 4.9299 | 4.4562 | 3.964 | 3.4544 | 1.8345 | -0.74203 | -2.2926 | -3.2382 | 7.1656 | 7.0773 | 6.9424 | 6.7749 | 6.5453 | 6.2977 | 6.0366 | 5.7958 | 5.5263 | 5.2449 | 4.3354 | 3.0328 | 2.3891 | 1.9184 | 5.7097 | 5.5667 | 5.3523 | 5.0902 | 4.6893 | 4.2561 | 3.8103 | 3.3955 | 2.948 | 2.4777 | 0.96968 | -1.2872 | -2.485 | -3.235
|  | GOLDSMITHS | ST |  |  | 7.3317 | 7.2709 | 7.1778 | 7.0607 | 6.9057 | 6.7372 | 6.5678 | 6.433 | 6.3 | 6.1533 | 5.6038 | 3.7589 | 2.2503 | 1.0875 | 7.1345 | 6.9524 | 6.7377 | 6.4898 | 6.1585 | 5.7194 | 5.2191 | 4.6694 | 4.0536 | 3.433 | 1.1003 | -5.8519 | -17.1217 | -35.5965 | 5.8675 | 5.8119 | 5.7264 | 5.6195 | 5.4682 | 5.304 | 5.1358 | 4.9961 | 4.8514 | 4.7024 | 4.1181 | 2.3508 | 1.009 | 0.094899
|  | GOLDSMITHS | SP |  |  | 7.3456 | 7.2841 | 7.1983 | 7.0888 | 6.9571 | 6.8155 | 6.6707 | 6.5597 | 6.4555 | 6.339 | 5.9272 | 4.6843 | 3.4697 | 2.7714 | 7.1142 | 6.9061 | 6.6529 | 6.3578 | 5.8756 | 5.2553 | 4.5279 | 3.7384 | 2.8319 | 1.821 | -2.0822 | -13.0135 | -33.8464 | -72.5759 | 5.8798 | 5.8181 | 5.7372 | 5.6326 | 5.5123 | 5.3805 | 5.2407 | 5.1291 | 5.019 | 4.9032 | 4.4706 | 3.2219 | 2.0982 | 1.481
NURSLING GSP | WINCHESTER | GORDON ROAD | MINIMUM HEADROOM | SU 48217 29991 | YES | 7.045 | 6.7605 | 6.4565 | 6.0976 | 5.4061 | 4.6296 | 3.7683 | 2.7808 | 1.7202 | 0.65121 | -2.7167 | -6.935 | -9.2198 | -10.7339 | 6.2803 | 6.1219 | 5.9492 | 5.7405 | 5.3874 | 4.9854 | 4.5273 | 4.0449 | 3.5029 | 2.9335 | 0.49902 | -3.9803 | -9.1514 | -20.9378 | 0.92574 | 0.79479 | 0.63848 | 0.43751 | 0.17184 | -0.20684 | -0.95932 | -1.89 | -2.8571 | -3.8411 | -6.9209 | -11.0021 | -12.7129 | -14.0514
|  | GORDON ROAD | CT |  |  | 7.1637 | 7.0212 | 6.8142 | 6.5504 | 6.0662 | 5.5069 | 4.9114 | 4.3005 | 3.6803 | 2.8173 | -0.17496 | -5.747 | -9.2198 | -10.7339 | 6.2901 | 6.1412 | 5.9642 | 5.7457 | 5.4218 | 5.0505 | 4.6441 | 4.2153 | 3.7495 | 2.9964 | 0.5617 | -3.9803 | -8.3552 | -14.0837 | 0.92574 | 0.79479 | 0.63848 | 0.43751 | 0.18062 | -0.15014 | -0.53285 | -0.93597 | -1.5386 | -2.3432 | -4.9947 | -9.649 | -12.7129 | -14.0514
|  | GORDON ROAD | LW |  |  | 7.045 | 6.7605 | 6.4565 | 6.0976 | 5.4061 | 4.6296 | 3.7683 | 2.7808 | 1.7202 | 0.65121 | -2.7167 | -6.935 | -8.3713 | -8.8993 | 6.2803 | 6.1219 | 5.9492 | 5.7405 | 5.3874 | 4.9854 | 4.5273 | 4.0449 | 3.5029 | 2.9335 | 0.49902 | -2.4966 | -2.9238 | -3.157 | 0.95355 | 0.81368 | 0.65657 | 0.45383 | 0.17184 | -0.20684 | -0.95932 | -1.89 | -2.8571 | -3.8411 | -6.9209 | -11.0021 | -12.0155 | -12.4886
|  | GORDON ROAD | ST |  |  | 7.3019 | 7.2444 | 7.179 | 7.0824 | 6.9126 | 6.692 | 6.4017 | 6.0979 | 5.766 | 5.3877 | 3.448 | -2.6114 | -5.5268 | -6.0804 | 6.3926 | 6.3264 | 6.2393 | 6.123 | 5.9422 | 5.7289 | 5.4779 | 5.2057 | 4.8921 | 4.5494 | 3.1184 | -1.3043 | -5.6592 | -11.2454 | 1.053 | 1.0004 | 0.9401 | 0.85164 | 0.69737 | 0.50393 | 0.27112 | 0.023043 | -0.27 | -0.63932 | -2.5557 | -8.3972 | -11.2016 | -11.7301
|  | GORDON ROAD | SP |  |  | 7.3114 | 7.2642 | 7.2067 | 7.1269 | 6.9872 | 6.8147 | 6.603 | 6.3647 | 6.1211 | 5.8464 | 4.9247 | 1.0124 | -3.1384 | -4.2328 | 6.3947 | 6.3316 | 6.2462 | 6.1321 | 5.9525 | 5.743 | 5.4961 | 5.2346 | 4.9442 | 4.6131 | 2.9789 | -1.8437 | -9.1514 | -20.9378 | 1.0617 | 1.0176 | 0.96381 | 0.89032 | 0.76456 | 0.6096 | 0.42221 | 0.23178 | 0.031419 | -0.1715 | -0.97722 | -4.8974 | -8.8931 | -9.9426
BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING | MINIMUM HEADROOM | SU 60305 82895 | YES | 8.5541 | 8.3937 | 8.214 | 8.0314 | 7.7485 | 7.4512 | 7.1411 | 6.8123 | 6.4248 | 6.0003 | 5.0514 | 3.8578 | 3.1887 | 2.6344 | 10.4779 | 10.4018 | 10.3073 | 10.21 | 10.0776 | 9.933 | 9.7734 | 9.5987 | 9.3665 | 9.1206 | 8.688 | 8.2278 | 7.7615 | 7.4021 | 9.4667 | 9.3307 | 9.1721 | 9.0103 | 8.7712 | 8.5162 | 8.2447 | 7.9532 | 7.5926 | 7.2077 | 6.409 | 5.4669 | 4.9945 | 4.5878
|  | GORING | CT |  |  | 8.6856 | 8.5913 | 8.4827 | 8.3605 | 8.1903 | 8.0067 | 7.8187 | 7.6052 | 7.3692 | 6.9648 | 6.0167 | 4.4497 | 3.1887 | 2.6344 | 10.5007 | 10.4358 | 10.3586 | 10.2689 | 10.1696 | 10.059 | 9.943 | 9.8059 | 9.6482 | 9.4004 | 8.891 | 8.2574 | 7.7615 | 7.4021 | 9.5594 | 9.4723 | 9.3707 | 9.2551 | 9.104 | 8.9394 | 8.77 | 8.5751 | 8.357 | 7.9882 | 7.1605 | 5.9211 | 4.9945 | 4.5878
|  | GORING | LW |  |  | 8.5541 | 8.3937 | 8.214 | 8.0314 | 7.7485 | 7.4512 | 7.1411 | 6.8123 | 6.4248 | 6.0003 | 5.0514 | 3.8578 | 3.3948 | 3.1254 | 10.4779 | 10.4018 | 10.3073 | 10.21 | 10.0776 | 9.933 | 9.7734 | 9.5987 | 9.3665 | 9.1206 | 8.688 | 8.2278 | 8.069 | 7.9738 | 9.4667 | 9.3307 | 9.1721 | 9.0103 | 8.7712 | 8.5162 | 8.2447 | 7.9532 | 7.5926 | 7.2077 | 6.409 | 5.4669 | 5.1175 | 4.9149
|  | GORING | ST |  |  | 8.7495 | 8.6969 | 8.6396 | 8.5769 | 8.4799 | 8.3765 | 8.2724 | 8.159 | 8.0329 | 7.9004 | 7.3231 | 6.2822 | 5.7251 | 5.3 | 10.5535 | 10.521 | 10.4833 | 10.4404 | 10.3788 | 10.3116 | 10.242 | 10.1641 | 10.0737 | 9.9891 | 9.5789 | 8.877 | 8.5434 | 8.2079 | 9.6248 | 9.5791 | 9.5278 | 9.4713 | 9.3842 | 9.2907 | 9.1962 | 9.0923 | 8.9753 | 8.855 | 8.3109 | 7.3598 | 6.9018 | 6.5604
|  | GORING | SP |  |  | 8.7645 | 8.7162 | 8.6699 | 8.6157 | 8.4933 | 8.3579 | 8.2165 | 8.0706 | 7.9178 | 7.7431 | 7.1402 | 5.7265 | 5.003 | 4.589 | 10.5566 | 10.5218 | 10.4874 | 10.4452 | 10.3876 | 10.3226 | 10.2502 | 10.1728 | 10.0892 | 9.9981 | 9.6475 | 8.7227 | 8.2577 | 7.913 | 9.6358 | 9.5922 | 9.5506 | 9.501 | 9.399 | 9.2878 | 9.1694 | 9.0461 | 8.9159 | 8.7676 | 8.2345 | 6.9481 | 6.3294 | 5.9981
IVER 132KV | DENHAM | GRASSINGHAM ROAD | MINIMUM HEADROOM | TQ 00165 90988 | YES | 10.2446 | 9.8641 | 9.4681 | 9.0358 | 8.3463 | 7.6192 | 6.8215 | 5.9145 | 4.7483 | 3.7404 | 1.8581 | -0.60505 | -2.3293 | -3.4397 | 8.6168 | 8.3785 | 8.1162 | 7.835 | 7.4535 | 7.0363 | 6.5562 | 5.9899 | 5.1998 | 4.5508 | 3.5662 | 2.1585 | 0.84233 | -0.28855 | 5.991 | 5.6302 | 5.2543 | 4.8424 | 4.2001 | 3.521 | 2.7706 | 1.9124 | 0.794 | -0.16431 | -1.8983 | -4.1395 | -5.6244 | -6.5972
|  | GRASSINGHAM ROAD | CT |  |  | 10.3698 | 10.085 | 9.7464 | 9.4008 | 8.9512 | 8.4715 | 7.9456 | 7.3436 | 6.6307 | 5.5089 | 3.4733 | 0.092828 | -2.3293 | -3.4397 | 8.6168 | 8.3893 | 8.1162 | 7.835 | 7.528 | 7.1959 | 6.8168 | 6.3746 | 5.8362 | 5.0754 | 3.8954 | 2.1585 | 0.84233 | -0.28855 | 6.0941 | 5.8175 | 5.4877 | 5.1509 | 4.7245 | 4.2686 | 3.7655 | 3.1874 | 2.4987 | 1.4287 | -0.45274 | -3.4893 | -5.6244 | -6.5972
|  | GRASSINGHAM ROAD | LW |  |  | 10.2446 | 9.8641 | 9.4681 | 9.0358 | 8.3463 | 7.6192 | 6.8215 | 5.9145 | 4.7483 | 3.7404 | 1.8581 | -0.60505 | -1.592 | -2.0364 | 8.6201 | 8.3785 | 8.1252 | 7.8419 | 7.4535 | 7.0363 | 6.5562 | 5.9899 | 5.1998 | 4.5508 | 3.5662 | 2.3666 | 1.9675 | 1.7834 | 5.991 | 5.6302 | 5.2543 | 4.8424 | 4.2001 | 3.521 | 2.7706 | 1.9124 | 0.794 | -0.16431 | -1.8983 | -4.1395 | -5.0097 | -5.3967
|  | GRASSINGHAM ROAD | ST |  |  | 10.6592 | 10.5475 | 10.4047 | 10.2287 | 10.0213 | 9.8008 | 9.555 | 9.2725 | 8.9468 | 8.6151 | 6.8388 | 4.3958 | 3.0804 | 2.1563 | 8.8345 | 8.7365 | 8.6111 | 8.4558 | 8.287 | 8.1061 | 7.9005 | 7.6619 | 7.383 | 7.1263 | 5.6931 | 3.8211 | 2.7808 | 1.7206 | 6.3768 | 6.2694 | 6.1309 | 5.9594 | 5.7593 | 5.5463 | 5.3081 | 5.0335 | 4.7157 | 4.3965 | 2.6621 | 0.3448 | -0.83781 | -1.648
|  | GRASSINGHAM ROAD | SP |  |  | 10.677 | 10.5822 | 10.4807 | 10.3682 | 10.1821 | 9.9975 | 9.8052 | 9.563 | 9.3076 | 8.9929 | 7.7384 | 4.5028 | 3.2698 | 2.6909 | 8.836 | 8.7433 | 8.6407 | 8.5261 | 8.3879 | 8.2461 | 8.0943 | 7.898 | 7.6844 | 7.4449 | 6.4438 | 3.7555 | 2.5382 | 1.4207 | 6.3923 | 6.3001 | 6.2014 | 6.0917 | 5.9156 | 5.7407 | 5.5579 | 5.3257 | 5.08 | 4.7796 | 3.5705 | 0.43702 | -0.71372 | -1.2342
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET | MINIMUM HEADROOM | SU 64445 00178 | YES | 16.8475 | 16.7442 | 16.6176 | 16.4445 | 16.256 | 16.0243 | 15.6029 | 15.0691 | 14.4472 | 13.8184 | 11.7469 | 8.4923 | 5.8458 | 3.742 | 13.3975 | 13.2954 | 13.1707 | 13.013 | 12.8336 | 12.6306 | 12.3154 | 11.8766 | 11.4097 | 10.8744 | 9.0165 | 3.6866 | -6.476 | -24.3197 | 10.0487 | 9.889 | 9.7082 | 9.4763 | 9.1346 | 8.7339 | 8.2922 | 7.8167 | 7.2508 | 6.6679 | 4.7492 | 1.8849 | -0.19077 | -1.8567
|  | GREETHAM STREET | CT |  |  | 16.8475 | 16.7442 | 16.6176 | 16.4445 | 16.256 | 16.0405 | 15.8246 | 15.588 | 15.3321 | 14.8021 | 12.9376 | 8.9712 | 5.8458 | 3.742 | 13.3975 | 13.2954 | 13.1707 | 13.013 | 12.8336 | 12.6306 | 12.3154 | 11.8766 | 11.4097 | 10.8744 | 9.0165 | 4.5001 | -1.3962 | -10.2676 | 10.1087 | 9.9914 | 9.8505 | 9.6547 | 9.3863 | 9.0838 | 8.7791 | 8.448 | 8.0884 | 7.5682 | 5.8769 | 2.3833 | -0.19077 | -1.8567
|  | GREETHAM STREET | LW |  |  | 16.8654 | 16.7562 | 16.6296 | 16.4584 | 16.2592 | 16.0243 | 15.6029 | 15.0691 | 14.4472 | 13.8184 | 11.7469 | 8.4923 | 6.4818 | 4.9212 | 13.4309 | 13.346 | 13.2455 | 13.1158 | 12.9632 | 12.7853 | 12.587 | 12.3668 | 12.0397 | 11.4724 | 9.5634 | 7.2506 | 6.648 | 6.1697 | 10.0487 | 9.889 | 9.7082 | 9.4763 | 9.1346 | 8.7339 | 8.2922 | 7.8167 | 7.2508 | 6.6679 | 4.7492 | 1.8849 | 0.29591 | -0.89568
|  | GREETHAM STREET | ST |  |  | 16.9277 | 16.8729 | 16.8052 | 16.7055 | 16.5823 | 16.4341 | 16.2861 | 16.1176 | 15.9232 | 15.6899 | 14.7701 | 11.4347 | 9.103 | 8.2784 | 13.4619 | 13.3988 | 13.3213 | 13.2224 | 13.0951 | 12.9362 | 12.7663 | 12.5389 | 12.1671 | 11.7759 | 10.3009 | 6.0749 | 0.42545 | -8.2192 | 10.2189 | 10.1705 | 10.1101 | 10.0242 | 9.9072 | 9.768 | 9.6277 | 9.4687 | 9.277 | 9.0361 | 8.1225 | 4.7545 | 2.5599 | 1.8899
|  | GREETHAM STREET | SP |  |  | 16.9319 | 16.8843 | 16.8212 | 16.729 | 16.6225 | 16.4978 | 16.3755 | 16.2407 | 16.101 | 15.9422 | 15.3688 | 13.5004 | 10.5961 | 9.475 | 13.4609 | 13.4005 | 13.3206 | 13.2205 | 13.0753 | 12.9043 | 12.5963 | 12.1711 | 11.693 | 11.1794 | 9.2307 | 3.6866 | -6.476 | -24.3197 | 10.2306 | 10.1922 | 10.1397 | 10.065 | 9.9722 | 9.8665 | 9.7602 | 9.644 | 9.5221 | 9.3535 | 8.7657 | 6.9808 | 3.999 | 2.9678
COWLEY GSP | DRAYTON BSP | GROVE | MINIMUM HEADROOM | SU 39515 89611 | YES | -0.76463 | -1.5063 | -2.3799 | -3.3203 | -4.4542 | -5.6585 | -6.9755 | -8.4366 | -10.371 | -12.0495 | -15.9377 | -20.8554 | -22.6873 | -23.9319 | 3.6954 | 3.2898 | 2.8117 | 2.2981 | 1.7067 | 1.0743 | 0.37309 | -0.41183 | -1.4757 | -2.4074 | -4.4464 | -7.0997 | -9.1388 | -10.7895 | -0.12968 | -0.75765 | -1.4988 | -2.3017 | -3.296 | -4.3529 | -5.5066 | -6.7858 | -8.468 | -9.9438 | -13.3975 | -17.7435 | -19.3788 | -20.4713
|  | GROVE | CT |  |  | -0.50882 | -1.0964 | -1.7877 | -2.5993 | -3.4724 | -4.401 | -5.4249 | -6.5972 | -8.0939 | -9.7512 | -13.6207 | -19.5357 | -22.6873 | -23.9319 | 3.7698 | 3.4095 | 2.994 | 2.5035 | 2.0024 | 1.4686 | 0.87659 | 0.19396 | -0.66967 | -1.6312 | -3.8129 | -7.0997 | -9.1388 | -10.7895 | 0.078937 | -0.41849 | -1.005 | -1.7051 | -2.4487 | -3.2406 | -4.1161 | -5.126 | -6.4082 | -7.8626 | -11.2049 | -16.5047 | -19.3788 | -20.4713
|  | GROVE | LW |  |  | -0.76463 | -1.5063 | -2.3799 | -3.3203 | -4.4542 | -5.6585 | -6.9755 | -8.4366 | -10.371 | -12.0495 | -15.9377 | -20.8554 | -22.1948 | -22.7335 | 3.6954 | 3.2898 | 2.8117 | 2.2981 | 1.7067 | 1.0743 | 0.37309 | -0.41183 | -1.4757 | -2.4074 | -4.4464 | -6.9533 | -7.5728 | -7.8007 | -0.12968 | -0.75765 | -1.4988 | -2.3017 | -3.296 | -4.3529 | -5.5066 | -6.7858 | -8.468 | -9.9438 | -13.3975 | -17.7435 | -18.9448 | -19.4518
|  | GROVE | ST |  |  | -0.23238 | -0.59292 | -1.0023 | -1.4477 | -1.9601 | -2.5048 | -3.1081 | -3.7751 | -4.6483 | -5.3834 | -7.9937 | -12.2706 | -14.0014 | -14.9135 | 3.9453 | 3.7185 | 3.4631 | 3.1818 | 2.8617 | 2.5201 | 2.1393 | 1.7174 | 1.1705 | 0.70783 | -1.0089 | -3.9467 | -5.5157 | -7.0685 | 0.3449 | 0.057962 | -0.27207 | -0.63727 | -1.0725 | -1.5363 | -2.0515 | -2.6219 | -3.3646 | -3.9946 | -6.3297 | -10.0974 | -11.5451 | -12.2886
|  | GROVE | SP |  |  | -0.18611 | -0.52763 | -0.89632 | -1.28 | -1.7501 | -2.249 | -2.8065 | -3.425 | -4.1968 | -4.9029 | -7.1348 | -11.9321 | -14.034 | -14.9268 | 3.9628 | 3.739 | 3.4986 | 3.2443 | 2.9631 | 2.659 | 2.3115 | 1.9202 | 1.4303 | 0.97397 | -0.54083 | -4.0505 | -6.4989 | -9.3242 | 0.38324 | 0.1091 | -0.18608 | -0.49649 | -0.8783 | -1.2871 | -1.7504 | -2.2694 | -2.9145 | -3.5095 | -5.4419 | -9.7323 | -11.5533 | -12.2856
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL | MINIMUM HEADROOM | ST 98638 11417 | YES | 3.3361 | 3.3039 | 3.2655 | 3.2253 | 3.1733 | 3.1204 | 3.0617 | 2.9948 | 2.9014 | 2.8254 | 2.6544 | 2.4578 | 2.4136 | 2.3786 | 3.7636 | 3.7499 | 3.732 | 3.7128 | 3.6891 | 3.6649 | 3.6366 | 3.6028 | 3.5557 | 3.5191 | 3.4518 | 3.3701 | 3.3538 | 3.3419 | 3.7323 | 3.7025 | 3.6679 | 3.6311 | 3.5833 | 3.5346 | 3.4809 | 3.4187 | 3.3314 | 3.2607 | 3.1056 | 2.9229 | 2.8818 | 2.8491
|  | GUSSAGE ST MICHAEL | CT |  |  | 3.363 | 3.3461 | 3.3257 | 3.2981 | 3.2649 | 3.2284 | 3.1846 | 3.1321 | 3.0723 | 3.0034 | 2.8722 | 2.6492 | 2.5161 | 2.4573 | 3.7709 | 3.7621 | 3.751 | 3.7348 | 3.7178 | 3.6986 | 3.6766 | 3.6487 | 3.6157 | 3.5787 | 3.5229 | 3.4326 | 3.3818 | 3.3539 | 3.7577 | 3.7418 | 3.7225 | 3.6961 | 3.665 | 3.6307 | 3.5898 | 3.5404 | 3.4837 | 3.4185 | 3.2988 | 3.0972 | 2.9772 | 2.922
|  | GUSSAGE ST MICHAEL | LW |  |  | 3.3361 | 3.3039 | 3.2655 | 3.2253 | 3.1733 | 3.1204 | 3.0617 | 2.9948 | 2.9014 | 2.8254 | 2.6544 | 2.4578 | 2.4136 | 2.3786 | 3.7636 | 3.7499 | 3.732 | 3.7128 | 3.6891 | 3.6649 | 3.6366 | 3.6028 | 3.5557 | 3.5191 | 3.4518 | 3.3701 | 3.3538 | 3.3419 | 3.7323 | 3.7025 | 3.6679 | 3.6311 | 3.5833 | 3.5346 | 3.4809 | 3.4187 | 3.3314 | 3.2607 | 3.1056 | 2.9229 | 2.8818 | 2.8491
|  | GUSSAGE ST MICHAEL | ST |  |  | 3.3796 | 3.3719 | 3.3631 | 3.3522 | 3.3336 | 3.3137 | 3.2928 | 3.2706 | 3.241 | 3.209 | 3.0744 | 2.9062 | 2.8133 | 2.7587 | 3.7797 | 3.7757 | 3.7709 | 3.7646 | 3.7548 | 3.7441 | 3.7327 | 3.7204 | 3.7043 | 3.6883 | 3.6141 | 3.5307 | 3.4902 | 3.4636 | 3.7734 | 3.7663 | 3.758 | 3.7477 | 3.7302 | 3.7115 | 3.6918 | 3.6707 | 3.6428 | 3.6129 | 3.4851 | 3.3282 | 3.2443 | 3.1959
|  | GUSSAGE ST MICHAEL | SP |  |  | 3.3835 | 3.377 | 3.3686 | 3.3607 | 3.3445 | 3.3289 | 3.3108 | 3.2923 | 3.2732 | 3.2419 | 3.1289 | 2.8535 | 2.6882 | 2.581 | 3.7811 | 3.777 | 3.7716 | 3.7665 | 3.7584 | 3.7505 | 3.7412 | 3.7315 | 3.7209 | 3.7066 | 3.6503 | 3.5083 | 3.4404 | 3.3979 | 3.7769 | 3.7707 | 3.7626 | 3.755 | 3.7399 | 3.7255 | 3.7086 | 3.6913 | 3.6733 | 3.6446 | 3.5394 | 3.2818 | 3.1325 | 3.0372
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE | MINIMUM HEADROOM | SU 47370 08794 | YES | 12.8904 | 12.6571 | 12.3869 | 12.0896 | 11.592 | 11.0595 | 10.4816 | 9.8583 | 9.0918 | 8.2299 | 6.2025 | 3.6804 | 1.8036 | 0.65134 | 17.713 | 17.6385 | 17.556 | 17.4558 | 17.351 | 17.2376 | 16.9248 | 16.5216 | 15.9806 | 15.3896 | 14.119 | 12.242 | 10.6313 | 8.8524 | 14.7502 | 14.5297 | 14.2653 | 13.9709 | 13.5212 | 13.0342 | 12.4948 | 11.9072 | 11.1492 | 10.3234 | 8.4832 | 6.2794 | 4.884 | 3.9466
|  | HAMBLE | CT |  |  | 12.9701 | 12.7981 | 12.5971 | 12.3402 | 11.995 | 11.6294 | 11.2465 | 10.8346 | 10.3079 | 9.4403 | 7.2984 | 4.0726 | 1.8036 | 0.65134 | 17.713 | 17.6385 | 17.556 | 17.4558 | 17.351 | 17.2376 | 17.0922 | 16.7659 | 16.3569 | 15.7511 | 14.2966 | 12.242 | 10.6313 | 8.9947 | 14.7985 | 14.625 | 14.4179 | 14.1462 | 13.8139 | 13.4599 | 13.081 | 12.6714 | 12.1614 | 11.3504 | 9.4076 | 6.6877 | 4.884 | 3.9466
|  | HAMBLE | LW |  |  | 12.8904 | 12.6571 | 12.3869 | 12.0896 | 11.592 | 11.0595 | 10.4816 | 9.8583 | 9.0918 | 8.2299 | 6.2025 | 3.6804 | 2.6198 | 2.0621 | 17.7304 | 17.6579 | 17.5792 | 17.4885 | 17.3834 | 17.2629 | 16.9248 | 16.5216 | 15.9806 | 15.3896 | 14.119 | 12.6844 | 12.2013 | 11.9386 | 14.7502 | 14.5297 | 14.2653 | 13.9709 | 13.5212 | 13.0342 | 12.4948 | 11.9072 | 11.1492 | 10.3234 | 8.4832 | 6.2794 | 5.4254 | 4.9892
|  | HAMBLE | ST |  |  | 13.1314 | 13.0568 | 12.9698 | 12.8683 | 12.7292 | 12.5771 | 12.4048 | 12.2147 | 11.9849 | 11.7313 | 10.5107 | 7.7962 | 6.4341 | 5.5656 | 17.7703 | 17.7304 | 17.6897 | 17.644 | 17.5858 | 17.5215 | 17.4458 | 17.3606 | 17.2524 | 17.1273 | 16.186 | 13.8983 | 12.4705 | 10.9219 | 14.9641 | 14.8898 | 14.8 | 14.6933 | 14.5485 | 14.3893 | 14.2075 | 14.0063 | 13.7605 | 13.5022 | 12.285 | 9.7224 | 8.549 | 7.837
|  | HAMBLE | SP |  |  | 13.1476 | 13.0731 | 12.9945 | 12.9109 | 12.7931 | 12.6729 | 12.548 | 12.3962 | 12.2241 | 12.0196 | 11.2288 | 8.6893 | 7.2216 | 6.6381 | 17.7701 | 17.7301 | 17.6894 | 17.646 | 17.5979 | 17.5455 | 17.4882 | 17.4197 | 17.3409 | 17.2426 | 16.5764 | 14.0298 | 11.6917 | 8.8524 | 14.9774 | 14.8998 | 14.8168 | 14.7274 | 14.6101 | 14.4887 | 14.362 | 14.2042 | 14.026 | 13.8178 | 13.0012 | 10.5385 | 9.1817 | 8.6836
MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY | MINIMUM HEADROOM | SZ 00104 90800 | YES | 13.5056 | 12.5557 | 11.4041 | 10.4933 | 8.8228 | 7.0016 | 5.125 | 3.1662 | 0.89538 | -1.5497 | -7.5144 | -13.5543 | -17.7828 | -20.3212 | 19.1571 | 18.6207 | 17.9605 | 17.4116 | 16.4925 | 15.4842 | 14.4254 | 13.3135 | 11.98 | 10.4821 | 6.8669 | 2.2085 | -1.6283 | -5.8206 | 14.2105 | 13.4304 | 12.4699 | 11.6793 | 10.2297 | 8.6473 | 7.0066 | 5.2879 | 3.2906 | 1.0924 | -4.3373 | -9.8047 | -13.5656 | -15.8498
|  | HAMWORTHY | CT |  |  | 13.6634 | 12.8296 | 11.8809 | 11.0365 | 9.6481 | 8.121 | 6.5778 | 4.9693 | 3.1773 | 0.79714 | -5.3053 | -12.9036 | -17.7828 | -20.3212 | 19.1785 | 18.6586 | 18.0705 | 17.4948 | 16.6462 | 15.7118 | 14.7514 | 13.741 | 12.5957 | 11.0901 | 7.1235 | 2.2085 | -1.6283 | -5.8206 | 14.3611 | 13.6903 | 12.9134 | 12.189 | 11.005 | 9.6993 | 8.3699 | 6.9774 | 5.3754 | 3.2273 | -2.3221 | -9.1414 | -13.5656 | -15.8498
|  | HAMWORTHY | LW |  |  | 13.5056 | 12.5557 | 11.4041 | 10.4933 | 8.8228 | 7.0016 | 5.125 | 3.1662 | 0.89538 | -1.5497 | -7.5144 | -13.5543 | -15.9936 | -17.4627 | 19.1571 | 18.6207 | 17.9605 | 17.4116 | 16.4925 | 15.4842 | 14.4254 | 13.3135 | 11.98 | 10.4821 | 6.8669 | 3.4434 | 2.307 | 1.6055 | 14.2105 | 13.4304 | 12.4699 | 11.6793 | 10.2297 | 8.6473 | 7.0066 | 5.2879 | 3.2906 | 1.0924 | -4.3373 | -9.8047 | -11.8958 | -13.1304
|  | HAMWORTHY | ST |  |  | 13.9933 | 13.4798 | 12.9178 | 12.5334 | 11.7421 | 10.8661 | 9.9795 | 9.0719 | 8.0597 | 7.0069 | 3.6652 | -2.601 | -5.7894 | -7.6971 | 19.3874 | 19.0546 | 18.6853 | 18.3978 | 17.8559 | 17.2557 | 16.6337 | 15.989 | 15.268 | 14.5261 | 11.983 | 6.7284 | 3.2323 | -0.56796 | 14.6604 | 14.2816 | 13.8594 | 13.5489 | 12.9185 | 12.2163 | 11.4951 | 10.7507 | 9.9121 | 8.9957 | 5.955 | 0.085579 | -2.7509 | -4.3708
|  | HAMWORTHY | SP |  |  | 14.0445 | 13.5384 | 13.0045 | 12.6407 | 11.9821 | 11.2531 | 10.4989 | 9.7294 | 8.9028 | 8.0321 | 5.5208 | 0.37044 | -3.0792 | -4.4734 | 19.4087 | 19.0695 | 18.7021 | 18.4112 | 17.9444 | 17.4207 | 16.8586 | 16.2703 | 15.6315 | 14.9339 | 12.7129 | 7.4313 | 1.6392 | -5.7941 | 14.7073 | 14.3376 | 13.9422 | 13.6521 | 13.1379 | 12.5656 | 11.9632 | 11.3441 | 10.6764 | 9.966 | 7.7429 | 2.8975 | -0.29878 | -1.5035
IVER 132KV | DENHAM | HAREFIELD | MINIMUM HEADROOM | TQ 04001 91227 | YES | 7.9693 | 7.8661 | 7.7382 | 7.5972 | 7.373 | 7.1343 | 6.873 | 6.5898 | 6.2524 | 5.8796 | 4.964 | 3.8906 | 3.229 | 2.7813 | 10.544 | 10.521 | 10.4946 | 10.4578 | 10.4202 | 10.3791 | 10.2445 | 10.0735 | 9.8576 | 9.6141 | 9.0559 | 8.2792 | 7.5818 | 6.7991 | 9.7212 | 9.6271 | 9.5115 | 9.3844 | 9.179 | 8.9607 | 8.7226 | 8.4648 | 8.1599 | 7.8228 | 6.986 | 6.0018 | 5.3911 | 4.9837
|  | HAREFIELD | CT |  |  | 8.0206 | 7.9514 | 7.8719 | 7.7522 | 7.5967 | 7.4342 | 7.2544 | 7.0619 | 6.8421 | 6.4774 | 5.5273 | 4.1479 | 3.229 | 2.7813 | 10.544 | 10.521 | 10.4946 | 10.4578 | 10.4202 | 10.3791 | 10.3292 | 10.1878 | 10.022 | 9.7735 | 9.1413 | 8.2792 | 7.5818 | 6.8679 | 9.7703 | 9.7083 | 9.6371 | 9.5309 | 9.3904 | 9.2435 | 9.0817 | 8.9085 | 8.7117 | 8.3824 | 7.4964 | 6.2412 | 5.3911 | 4.9837
|  | HAREFIELD | LW |  |  | 7.9693 | 7.8661 | 7.7382 | 7.5972 | 7.373 | 7.1343 | 6.873 | 6.5898 | 6.2524 | 5.8796 | 4.964 | 3.8906 | 3.4592 | 3.2549 | 10.5496 | 10.528 | 10.5009 | 10.4693 | 10.4311 | 10.3883 | 10.2445 | 10.0735 | 9.8576 | 9.6141 | 9.0559 | 8.4612 | 8.2656 | 8.1686 | 9.7212 | 9.6271 | 9.5115 | 9.3844 | 9.179 | 8.9607 | 8.7226 | 8.4648 | 8.1599 | 7.8228 | 6.986 | 6.0018 | 5.613 | 5.4362
|  | HAREFIELD | ST |  |  | 8.0861 | 8.0565 | 8.0204 | 7.9786 | 7.9147 | 7.8437 | 7.7639 | 7.6747 | 7.5741 | 7.4647 | 6.9748 | 5.8688 | 5.3226 | 4.9548 | 10.5627 | 10.551 | 10.5376 | 10.5222 | 10.5014 | 10.4779 | 10.4507 | 10.4193 | 10.3828 | 10.3408 | 9.9751 | 9.0395 | 8.4679 | 7.7954 | 9.8295 | 9.8033 | 9.7714 | 9.7346 | 9.6778 | 9.6148 | 9.5439 | 9.4648 | 9.3756 | 9.277 | 8.84 | 7.7985 | 7.3126 | 6.9977
|  | HAREFIELD | SP |  |  | 8.0991 | 8.0671 | 8.0315 | 7.9941 | 7.9386 | 7.8834 | 7.8201 | 7.7508 | 7.6729 | 7.578 | 7.2139 | 6.1756 | 5.5447 | 5.2827 | 10.5633 | 10.5504 | 10.5357 | 10.5197 | 10.5013 | 10.4813 | 10.4586 | 10.4321 | 10.4026 | 10.3664 | 10.0901 | 9.0541 | 8.0641 | 6.7991 | 9.8413 | 9.8134 | 9.7823 | 9.7497 | 9.7 | 9.6507 | 9.594 | 9.5323 | 9.463 | 9.3776 | 9.0527 | 8.0908 | 7.5002 | 7.2704
NURSLING GSP | WINCHESTER | HARESTOCK | MINIMUM HEADROOM | SU 45908 31300 | YES | 11.8778 | 11.2017 | 10.4146 | 9.567 | 8.3344 | 7.025 | 5.6399 | 4.1363 | 2.3181 | 0.44335 | -4.2635 | -9.1897 | -11.5971 | -13.0485 | 18.5333 | 18.1318 | 17.6568 | 17.1435 | 16.4721 | 15.7507 | 14.9605 | 14.0922 | 12.9435 | 11.7702 | 9.1823 | 6.5611 | 4.695 | 3.27 | 14.0845 | 13.4887 | 12.7878 | 12.031 | 10.9754 | 9.848 | 8.6025 | 7.2296 | 5.5076 | 3.7394 | -0.44642 | -4.731 | -6.6045 | -7.7822
|  | HARESTOCK | CT |  |  | 12.124 | 11.6009 | 10.9619 | 10.2554 | 9.3576 | 8.3917 | 7.4081 | 6.3056 | 5.047 | 3.1386 | -1.7128 | -8.0273 | -11.5971 | -13.0485 | 18.5646 | 18.1919 | 17.739 | 17.2381 | 16.6796 | 16.0751 | 15.4421 | 14.7241 | 13.8817 | 12.6607 | 9.8344 | 6.5611 | 4.695 | 3.27 | 14.2369 | 13.7511 | 13.1551 | 12.494 | 11.7004 | 10.844 | 9.9601 | 8.9617 | 7.8022 | 6.0526 | 1.7386 | -3.6705 | -6.6045 | -7.7822
|  | HARESTOCK | LW |  |  | 11.8778 | 11.2017 | 10.4146 | 9.567 | 8.3344 | 7.025 | 5.6399 | 4.1363 | 2.3181 | 0.44335 | -4.2635 | -9.1897 | -10.4915 | -10.9676 | 18.5333 | 18.1318 | 17.6568 | 17.1435 | 16.4721 | 15.7507 | 14.9605 | 14.0922 | 12.9435 | 11.7702 | 9.1823 | 6.699 | 6.2019 | 6.0305 | 14.0845 | 13.4887 | 12.7878 | 12.031 | 10.9754 | 9.848 | 8.6025 | 7.2296 | 5.5076 | 3.7394 | -0.44642 | -4.731 | -5.8064 | -6.1927
|  | HARESTOCK | ST |  |  | 12.459 | 12.1721 | 11.8308 | 11.4537 | 10.9768 | 10.462 | 9.9261 | 9.3243 | 8.639 | 7.9128 | 4.8707 | 0.099209 | -1.7659 | -2.91 | 18.8307 | 18.6297 | 18.3864 | 18.1095 | 17.7674 | 17.3967 | 17.0029 | 16.557 | 16.0423 | 15.5349 | 13.322 | 9.8448 | 8.3645 | 7.0163 | 14.5946 | 14.3486 | 14.0495 | 13.7105 | 13.2741 | 12.802 | 12.3054 | 11.7442 | 11.0992 | 10.4348 | 7.5831 | 3.2053 | 1.606 | 0.67042
|  | HARESTOCK | SP |  |  | 12.5015 | 12.2363 | 11.937 | 11.6239 | 11.1631 | 10.6763 | 10.1593 | 9.5891 | 8.9679 | 8.2767 | 5.8477 | 0.7808 | -1.3769 | -2.2093 | 18.8413 | 18.6434 | 18.4179 | 18.1756 | 17.8851 | 17.5706 | 17.2241 | 16.8259 | 16.3845 | 15.9096 | 14.1402 | 10.2042 | 8.1381 | 6.4796 | 14.626 | 14.3948 | 14.134 | 13.8572 | 13.4674 | 13.0516 | 12.6001 | 12.0897 | 11.5303 | 10.9125 | 8.6659 | 3.895 | 1.9316 | 1.2314
EALING GSP | EALING (D) | HARVARD LANE | MINIMUM HEADROOM | TQ 20021 78030 | YES | 9.0435 | 8.6147 | 8.0371 | 22.8265 | 21.846 | 20.754 | 19.5823 | 18.3202 | 17.004 | 15.6299 | 11.1804 | 4.339 | -0.79873 | -4.5914 | 7.3845 | 7.1717 | 6.8713 | 29.5429 | 29.118 | 28.4354 | 27.6043 | 26.6849 | 25.6724 | 24.443 | 20.2412 | 10.1949 | -9.3915 | -43.1954 | 2.9304 | 2.5435 | 2.0247 | 24.4718 | 23.5879 | 22.6391 | 21.626 | 20.5302 | 19.3504 | 18.1035 | 14.0534 | 8.0125 | 3.776 | 0.60295
|  | HARVARD LANE | CT |  |  | 9.1671 | 8.8191 | 8.3195 | 23.1745 | 22.4495 | 21.6685 | 20.8991 | 20.0607 | 19.1757 | 17.8367 | 13.542 | 5.3551 | -0.79873 | -4.5914 | 7.3845 | 7.1717 | 6.8713 | 29.5429 | 29.118 | 28.4354 | 27.6043 | 26.6849 | 25.6724 | 24.443 | 20.2412 | 10.9187 | -1.2332 | -19.0013 | 3.0298 | 2.7115 | 2.2582 | 24.7585 | 24.1102 | 23.3999 | 22.6947 | 21.9256 | 21.1214 | 19.931 | 16.1027 | 9.0451 | 3.776 | 0.60295
|  | HARVARD LANE | LW |  |  | 9.0435 | 8.6147 | 8.0371 | 22.8265 | 21.846 | 20.754 | 19.5823 | 18.3202 | 17.004 | 15.6299 | 11.1804 | 4.339 | 0.54471 | -2.0102 | 7.4616 | 7.3126 | 7.1142 | 29.9032 | 29.5562 | 29.1891 | 28.7496 | 28.2097 | 27.4232 | 26.5882 | 23.8569 | 19.9412 | 18.1089 | 16.8215 | 2.9304 | 2.5435 | 2.0247 | 24.4718 | 23.5879 | 22.6391 | 21.626 | 20.5302 | 19.3504 | 18.1035 | 14.0534 | 8.0125 | 4.8252 | 2.7348
|  | HARVARD LANE | ST |  |  | 9.4837 | 9.3265 | 9.088 | 24.236 | 23.927 | 23.589 | 23.2313 | 22.8254 | 22.404 | 21.9531 | 20.1804 | 14.7673 | 10.8755 | 8.1041 | 7.4559 | 7.3264 | 7.1311 | 29.9003 | 29.6217 | 29.3172 | 28.9309 | 28.2476 | 27.4922 | 26.7338 | 23.8344 | 15.1662 | 3.7447 | -13.5599 | 3.329 | 3.1886 | 2.9781 | 25.7518 | 25.4691 | 25.1588 | 24.828 | 24.451 | 24.0499 | 23.6231 | 21.9253 | 16.8435 | 13.4251 | 11.2033
|  | HARVARD LANE | SP |  |  | 9.532 | 9.3751 | 9.1482 | 24.3128 | 24.0612 | 23.7893 | 23.4933 | 23.1604 | 22.8389 | 22.4839 | 21.206 | 17.1213 | 13.2238 | 11.0566 | 7.4481 | 7.308 | 7.0853 | 29.824 | 29.4987 | 29.1312 | 28.4626 | 27.6281 | 26.6934 | 25.6503 | 21.6662 | 10.1949 | -9.3915 | -43.1954 | 3.3738 | 3.231 | 3.0292 | 25.8164 | 25.5889 | 25.3423 | 25.0693 | 24.7609 | 24.4556 | 24.1199 | 22.9009 | 19.0121 | 15.383 | 13.49
BRAMLEY (FLEE) | FERNHURST | HASLEMERE | MINIMUM HEADROOM | SU 89300 31710 | YES | 7.9227 | 7.2946 | 6.6229 | 8.9832 | 7.938 | 6.8431 | 5.6651 | 4.375 | 2.8503 | 1.3873 | -1.82 | -5.8094 | -7.5927 | -9.387 | 7.3117 | 6.9546 | 6.5634 | 13.7229 | 13.1651 | 12.5676 | 11.8889 | 11.1188 | 10.1384 | 9.2489 | 7.5388 | 5.5757 | 3.38 | 1.4883 | 3.9516 | 3.3794 | 2.765 | 9.6886 | 8.732 | 7.7276 | 6.6396 | 5.4428 | 4.0234 | 2.6932 | -0.28233 | -3.8891 | -5.4166 | -6.986
|  | HASLEMERE | CT |  |  | 8.3122 | 7.923 | 7.4803 | 10.0341 | 9.368 | 8.665 | 7.9056 | 7.0562 | 6.068 | 4.6036 | 1.4224 | -3.712 | -7.5927 | -9.387 | 7.3893 | 7.0956 | 6.7552 | 13.9422 | 13.5111 | 13.0507 | 12.5352 | 11.9486 | 11.2444 | 10.2919 | 8.386 | 5.5757 | 3.38 | 1.4883 | 4.2863 | 3.9252 | 3.5118 | 10.6158 | 10.0104 | 9.3726 | 8.6866 | 7.9214 | 7.0353 | 5.6857 | 2.7462 | -2.0022 | -5.4166 | -6.986
|  | HASLEMERE | LW |  |  | 7.9227 | 7.2946 | 6.6229 | 8.9832 | 7.938 | 6.8431 | 5.6651 | 4.375 | 2.8503 | 1.3873 | -1.82 | -5.8094 | -7.2752 | -8.154 | 7.3117 | 6.9546 | 6.5634 | 13.7229 | 13.1651 | 12.5676 | 11.8889 | 11.1188 | 10.1384 | 9.2489 | 7.5388 | 5.585 | 4.9774 | 4.6233 | 3.9516 | 3.3794 | 2.765 | 9.6886 | 8.732 | 7.7276 | 6.6396 | 5.4428 | 4.0234 | 2.6932 | -0.28233 | -3.8891 | -5.1777 | -5.942
|  | HASLEMERE | ST |  |  | 8.6262 | 8.4442 | 8.2258 | 11.0589 | 10.7532 | 10.4212 | 10.0651 | 9.6558 | 9.1706 | 8.6676 | 6.3175 | 2.587 | 0.56605 | -0.78023 | 7.625 | 7.4857 | 7.311 | 14.6938 | 14.4606 | 14.2031 | 13.9181 | 13.5922 | 13.2093 | 12.8453 | 11.0538 | 8.2327 | 6.5247 | 4.7548 | 4.588 | 4.4257 | 4.2272 | 11.5844 | 11.2974 | 10.9853 | 10.6491 | 10.2718 | 9.8381 | 9.3818 | 7.2704 | 3.7541 | 1.9407 | 0.72433
|  | HASLEMERE | SP |  |  | 8.6839 | 8.5213 | 8.3526 | 11.2591 | 10.9307 | 10.6133 | 10.2646 | 9.8898 | 9.4899 | 8.9673 | 7.0283 | 2.2109 | -0.22069 | -1.5073 | 7.6414 | 7.4989 | 7.3436 | 14.7654 | 14.5471 | 14.325 | 14.0836 | 13.8007 | 13.488 | 13.1205 | 11.678 | 7.8974 | 5.4594 | 2.9074 | 4.6389 | 4.4923 | 4.3395 | 11.7656 | 11.4638 | 11.1717 | 10.8515 | 10.5033 | 10.1305 | 9.6466 | 7.8787 | 3.4516 | 1.2119 | 0.066604
BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE | MINIMUM HEADROOM | SU 98188 20276 | YES | 2.1466 | 1.7755 | 1.3598 | 0.931 | 0.31467 | -0.31678 | -0.96645 | -1.6624 | -2.4583 | -3.1702 | -4.6139 | -6.0202 | -6.4158 | -7.0584 | 6.1768 | 6.0126 | 5.8153 | 5.6096 | 5.333 | 5.044 | 4.7294 | 4.3714 | 3.917 | 3.5286 | 2.8565 | 2.1995 | 1.8205 | 0.97806 | 3.7289 | 3.4197 | 3.0687 | 2.687 | 2.1449 | 1.586 | 0.99972 | 0.35708 | -0.40855 | -1.0712 | -2.3509 | -3.5659 | -3.8872 | -4.3242
|  | HASLINGBOURNE | CT |  |  | 2.5145 | 2.3354 | 2.1361 | 1.8874 | 1.5312 | 1.1578 | 0.75338 | 0.28773 | -0.21729 | -0.88728 | -2.1249 | -3.751 | -4.8669 | -5.3686 | 6.2824 | 6.1775 | 6.0561 | 5.8925 | 5.6978 | 5.4899 | 5.2631 | 4.9886 | 4.6789 | 4.2805 | 3.6008 | 2.7993 | 2.24 | 1.7726 | 4.0103 | 3.8514 | 3.6721 | 3.4419 | 3.1301 | 2.8016 | 2.4452 | 2.028 | 1.5568 | 0.92923 | -0.2124 | -1.6767 | -2.6295 | -3.0401
|  | HASLINGBOURNE | LW |  |  | 2.1466 | 1.7755 | 1.3598 | 0.931 | 0.31467 | -0.31678 | -0.96645 | -1.6624 | -2.4583 | -3.1702 | -4.6139 | -6.0202 | -6.4158 | -6.6663 | 6.1768 | 6.0126 | 5.8153 | 5.6096 | 5.333 | 5.044 | 4.7294 | 4.3714 | 3.917 | 3.5286 | 2.8565 | 2.1995 | 2.0443 | 1.954 | 3.7289 | 3.4197 | 3.0687 | 2.687 | 2.1449 | 1.586 | 0.99972 | 0.35708 | -0.40855 | -1.0712 | -2.3509 | -3.5659 | -3.8872 | -4.0845
|  | HASLINGBOURNE | ST |  |  | 2.6126 | 2.5013 | 2.3748 | 2.2366 | 2.0216 | 1.7987 | 1.5699 | 1.3231 | 1.0416 | 0.74597 | -0.46944 | -2.3314 | -3.2562 | -3.7171 | 6.356 | 6.2995 | 6.23 | 6.1497 | 6.0327 | 5.9094 | 5.7787 | 5.6336 | 5.4614 | 5.2959 | 4.5279 | 3.4212 | 2.8842 | 2.4461 | 4.1067 | 4.0132 | 3.9041 | 3.7828 | 3.5961 | 3.4018 | 3.2008 | 2.9821 | 2.7296 | 2.4708 | 1.3299 | -0.39448 | -1.2198 | -1.6182
|  | HASLINGBOURNE | SP |  |  | 2.6504 | 2.5553 | 2.4527 | 2.3537 | 2.049 | 1.7448 | 1.4411 | 1.1141 | 0.77798 | 0.34441 | -1.0779 | -4.1027 | -5.8997 | -7.0584 | 6.3659 | 6.3088 | 6.2441 | 6.1813 | 6.0455 | 5.9087 | 5.7723 | 5.615 | 5.4544 | 5.2598 | 4.5429 | 2.8226 | 1.8205 | 0.97806 | 4.1354 | 4.0519 | 3.9607 | 3.8731 | 3.6218 | 3.3709 | 3.1211 | 2.8413 | 2.5439 | 2.1717 | 0.90188 | -1.8976 | -3.4058 | -4.3242
MELKSHAM GSP | FROME BSP | HAWKERIDGE | MINIMUM HEADROOM | ST 86422 53026 | YES | 2.2216 | 2.1718 | 2.1088 | 2.0364 | 1.9433 | 1.8397 | 1.7222 | 1.5904 | 1.447 | 1.2727 | 0.68441 | -0.10702 | -0.44194 | -0.64242 | 2.4995 | 2.4753 | 2.4499 | 2.4216 | 2.3842 | 2.343 | 2.297 | 2.2454 | 2.1879 | 2.1219 | 1.9059 | 1.5925 | 1.4159 | 1.2478 | 2.5839 | 2.5273 | 2.4688 | 2.4013 | 2.315 | 2.2184 | 2.1084 | 1.9846 | 1.8492 | 1.6841 | 1.1258 | 0.37352 | 0.053647 | -0.14291
|  | HAWKERIDGE | CT |  |  | 2.222 | 2.2046 | 2.1681 | 2.1233 | 2.0655 | 1.9996 | 1.9224 | 1.8337 | 1.7377 | 1.6044 | 1.1452 | 0.22001 | -0.32167 | -0.64229 | 2.5156 | 2.5009 | 2.4851 | 2.4663 | 2.4406 | 2.412 | 2.3808 | 2.3452 | 2.3048 | 2.25 | 2.0667 | 1.6831 | 1.4159 | 1.2478 | 2.6136 | 2.5775 | 2.5378 | 2.492 | 2.431 | 2.3629 | 2.2881 | 2.204 | 2.1129 | 1.9865 | 1.5505 | 0.673 | 0.16174 | -0.14291
|  | HAWKERIDGE | LW |  |  | 2.2216 | 2.1718 | 2.1088 | 2.0364 | 1.9433 | 1.8397 | 1.7222 | 1.5904 | 1.447 | 1.2727 | 0.68441 | -0.10702 | -0.44194 | -0.64242 | 2.4995 | 2.4753 | 2.4499 | 2.4216 | 2.3842 | 2.343 | 2.297 | 2.2454 | 2.1879 | 2.1219 | 1.9059 | 1.5925 | 1.4236 | 1.322 | 2.5839 | 2.5273 | 2.4688 | 2.4013 | 2.315 | 2.2184 | 2.1084 | 1.9846 | 1.8492 | 1.6841 | 1.1258 | 0.37352 | 0.053647 | -0.13737
|  | HAWKERIDGE | ST |  |  | 2.2339 | 2.2241 | 2.215 | 2.2039 | 2.1778 | 2.1415 | 2.0987 | 2.0485 | 1.9896 | 1.9109 | 1.5901 | 0.76895 | 0.20409 | -0.1629 | 2.5249 | 2.5161 | 2.5075 | 2.4977 | 2.4828 | 2.4657 | 2.4463 | 2.4241 | 2.399 | 2.3674 | 2.2399 | 1.927 | 1.6794 | 1.4942 | 2.6401 | 2.6205 | 2.6014 | 2.5797 | 2.5467 | 2.5087 | 2.4647 | 2.4137 | 2.3554 | 2.2776 | 1.9715 | 1.1861 | 0.64645 | 0.31296
|  | HAWKERIDGE | SP |  |  | 2.2359 | 2.2285 | 2.2224 | 2.215 | 2.2063 | 2.1804 | 2.1508 | 2.1188 | 2.0802 | 2.0235 | 1.8286 | 1.2473 | 0.63619 | 0.32419 | 2.5282 | 2.5219 | 2.5162 | 2.5098 | 2.4973 | 2.4843 | 2.4696 | 2.4543 | 2.4375 | 2.415 | 2.3352 | 2.1075 | 1.8725 | 1.7184 | 2.646 | 2.6313 | 2.6179 | 2.6025 | 2.5753 | 2.546 | 2.5129 | 2.478 | 2.4399 | 2.387 | 2.2046 | 1.6556 | 1.0749 | 0.77937
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY | MINIMUM HEADROOM | SU 85973 57691 | YES | 18.1056 | 17.5064 | 16.96 | 16.4448 | 15.6553 | 14.8433 | 13.9536 | 12.9847 | 11.7493 | 10.4937 | 7.4419 | 3.1759 | -0.73327 | -3.1899 | 21.9728 | 21.5346 | 21.1431 | 20.7797 | 20.2933 | 19.7965 | 19.2347 | 18.6134 | 17.7923 | 16.9628 | 15.0853 | 11.9831 | 9.1698 | 6.3387 | 19.1129 | 18.5829 | 18.0801 | 17.5981 | 16.8894 | 16.1568 | 15.3435 | 14.4515 | 13.2952 | 12.1157 | 9.3439 | 5.6278 | 2.3381 | 0.27822
|  | HAWLEY | CT |  |  | 18.1908 | 17.6611 | 17.2527 | 16.7638 | 16.1701 | 15.5656 | 14.9059 | 14.1867 | 13.328 | 12.0363 | 8.7743 | 3.3772 | -0.73327 | -3.1899 | 21.9752 | 21.5471 | 21.2186 | 20.8257 | 20.3964 | 19.9628 | 19.4851 | 18.9588 | 18.3156 | 17.4332 | 15.278 | 11.9831 | 9.1698 | 6.3387 | 19.1643 | 18.6952 | 18.3216 | 17.8474 | 17.3041 | 16.7451 | 16.1302 | 15.4562 | 14.6397 | 13.4385 | 10.4953 | 5.8759 | 2.3381 | 0.27822
|  | HAWLEY | LW |  |  | 18.1056 | 17.5064 | 16.96 | 16.4448 | 15.6553 | 14.8433 | 13.9536 | 12.9847 | 11.7493 | 10.4937 | 7.4419 | 3.1759 | 0.82342 | -0.77581 | 21.9728 | 21.5346 | 21.1431 | 20.7797 | 20.2933 | 19.7965 | 19.2347 | 18.6134 | 17.7923 | 16.9628 | 15.0853 | 12.7133 | 11.6019 | 10.8172 | 19.1129 | 18.5829 | 18.0801 | 17.5981 | 16.8894 | 16.1568 | 15.3435 | 14.4515 | 13.2952 | 12.1157 | 9.3439 | 5.6278 | 3.641 | 2.3213
|  | HAWLEY | ST |  |  | 18.4397 | 18.0617 | 17.8059 | 17.6034 | 17.3236 | 17.0444 | 16.7391 | 16.3977 | 16.0097 | 15.6363 | 13.8867 | 9.8879 | 7.4544 | 5.6881 | 22.1493 | 21.8224 | 21.598 | 21.4175 | 21.1766 | 20.9383 | 20.6745 | 20.3778 | 20.0387 | 19.7202 | 18.2365 | 14.9614 | 12.6435 | 10.0792 | 19.4033 | 19.0766 | 18.8464 | 18.6575 | 18.3916 | 18.1221 | 17.8252 | 17.491 | 17.1093 | 16.7479 | 15.0197 | 11.2732 | 9.2448 | 7.8357
|  | HAWLEY | SP |  |  | 18.4641 | 18.0669 | 17.8134 | 17.6138 | 17.3978 | 17.189 | 16.9721 | 16.7209 | 16.4432 | 16.1487 | 14.9776 | 11.337 | 8.986 | 7.7322 | 22.1588 | 21.8116 | 21.5794 | 21.3905 | 21.1921 | 21.0002 | 20.7958 | 20.5581 | 20.2921 | 19.9873 | 18.7702 | 15.0925 | 11.417 | 6.6716 | 19.4243 | 19.0745 | 18.8437 | 18.655 | 18.4522 | 18.2536 | 18.0458 | 17.8019 | 17.5313 | 17.2452 | 16.0947 | 12.53 | 10.3883 | 9.3403
COWLEY GSP | HEADINGTON BSP | HEADINGTON | MINIMUM HEADROOM | SP 54440 08085 | NO | 22.1926 | 22.0211 | 21.7869 | 21.4682 | 21.0127 | 20.3662 | 19.0329 | 17.6183 | 16.018 | 14.3458 | 9.874 | 5.0205 | 1.3011 | -1.2781 | 25.2958 | 25.0348 | 24.6906 | 24.2204 | 23.4677 | 22.7116 | 21.9858 | 21.2062 | 20.2863 | 19.3273 | 16.6981 | 12.882 | 9.2655 | 3.6507 | 22.121 | 21.7129 | 21.2128 | 20.5297 | 19.3174 | 18.0921 | 16.9331 | 15.6992 | 14.2952 | 12.8282 | 8.8519 | 4.5619 | 1.4399 | -0.73314
|  | HEADINGTON | CT |  |  | 22.1926 | 22.0217 | 21.8019 | 21.4895 | 21.0604 | 20.6344 | 20.2582 | 19.5997 | 18.3771 | 16.6918 | 12.24 | 6.0033 | 1.3011 | -1.2781 | 25.3262 | 25.0772 | 24.7685 | 24.2879 | 23.5992 | 22.9 | 22.2552 | 21.556 | 20.768 | 19.7428 | 16.8929 | 12.882 | 9.2655 | 5.1408 | 22.3359 | 22.0564 | 21.7098 | 21.1435 | 20.1948 | 19.2332 | 18.3769 | 17.4556 | 16.4286 | 14.9832 | 11.1164 | 5.475 | 1.4399 | -0.73314
|  | HEADINGTON | LW |  |  | 22.2055 | 22.0211 | 21.7869 | 21.4682 | 21.0127 | 20.3662 | 19.0329 | 17.6183 | 16.018 | 14.3458 | 9.874 | 5.0205 | 2.6768 | 1.1021 | 25.2958 | 25.0348 | 24.6906 | 24.2204 | 23.4677 | 22.7116 | 21.9858 | 21.2062 | 20.2863 | 19.3273 | 16.6981 | 14.1828 | 13.1585 | 12.4359 | 22.121 | 21.7129 | 21.2128 | 20.5297 | 19.3174 | 18.0921 | 16.9331 | 15.6992 | 14.2952 | 12.8282 | 8.8519 | 4.5619 | 2.5909 | 1.2977
|  | HEADINGTON | ST |  |  | 22.2809 | 22.1711 | 22.0248 | 21.8061 | 21.4456 | 21.096 | 20.8039 | 20.4933 | 20.1302 | 19.7304 | 18.5651 | 14.2368 | 11.4785 | 9.7175 | 25.4942 | 25.3469 | 25.1586 | 24.8946 | 24.4373 | 23.982 | 23.5586 | 23.1 | 22.5709 | 22.0184 | 20.217 | 16.2205 | 12.9351 | 9.0769 | 22.551 | 22.4087 | 22.2257 | 21.9624 | 21.4791 | 20.9974 | 20.5637 | 20.0959 | 19.554 | 18.9579 | 17.1518 | 13.3384 | 10.935 | 9.3983
|  | HEADINGTON | SP |  |  | 22.2832 | 22.1731 | 22.0267 | 21.8142 | 21.4837 | 21.1675 | 20.9056 | 20.6297 | 20.317 | 19.9765 | 19.1303 | 15.9965 | 13.1275 | 11.7029 | 25.501 | 25.342 | 25.1433 | 24.8847 | 24.491 | 24.0913 | 23.7061 | 23.2804 | 22.8031 | 22.2333 | 20.4532 | 16.3078 | 11.0255 | 3.6507 | 22.5845 | 22.4495 | 22.2785 | 22.049 | 21.6275 | 21.2047 | 20.8233 | 20.4071 | 19.9561 | 19.4256 | 17.9296 | 14.8581 | 12.463 | 11.2902
NURSLING GSP | VELMORE BSP | HEDGE END | MINIMUM HEADROOM | SU 49035 15685 | YES | 20.725 | 20.2325 | 19.5957 | 18.8797 | 17.9776 | 17.0578 | 16.2454 | 15.4072 | 14.7053 | 14.0869 | 12.662 | 10.726 | 9.2236 | 8.3466 | 23.3662 | 22.9647 | 22.4596 | 21.9209 | 21.357 | 20.7542 | 20.1922 | 19.5911 | 18.966 | 18.4326 | 17.4566 | 15.8559 | 14.5564 | 13.2471 | 21.9006 | 21.3705 | 20.6981 | 19.9479 | 19.0325 | 18.0961 | 17.2467 | 16.3505 | 15.501 | 14.7671 | 13.2915 | 11.3612 | 10.1231 | 9.359
|  | HEDGE END | CT |  |  | 20.7781 | 20.3244 | 19.7156 | 19.033 | 18.2532 | 17.4592 | 16.8005 | 16.1192 | 15.5931 | 14.9559 | 13.5015 | 10.9855 | 9.2236 | 8.3466 | 23.3662 | 22.9647 | 22.4596 | 21.9209 | 21.357 | 20.7846 | 20.2803 | 19.7346 | 19.2458 | 18.6591 | 17.5453 | 15.8559 | 14.5564 | 13.2471 | 21.9308 | 21.4356 | 20.7779 | 20.0513 | 19.2485 | 18.4287 | 17.728 | 16.9825 | 16.3585 | 15.5886 | 14.0516 | 11.6693 | 10.1231 | 9.359
|  | HEDGE END | LW |  |  | 20.725 | 20.2325 | 19.5957 | 18.8797 | 17.9776 | 17.0578 | 16.2454 | 15.4072 | 14.7053 | 14.0869 | 12.662 | 10.726 | 9.8242 | 9.3758 | 23.3812 | 22.9786 | 22.4925 | 21.9664 | 21.3653 | 20.7542 | 20.1922 | 19.5911 | 18.966 | 18.4326 | 17.4566 | 16.236 | 15.8038 | 15.5703 | 21.9006 | 21.3705 | 20.6981 | 19.9479 | 19.0325 | 18.0961 | 17.2467 | 16.3505 | 15.501 | 14.7671 | 13.2915 | 11.3612 | 10.5547 | 10.1504
|  | HEDGE END | ST |  |  | 20.9157 | 20.6232 | 20.2669 | 19.89 | 19.4747 | 19.0583 | 18.7096 | 18.3581 | 18.0939 | 17.8517 | 17.0281 | 15.371 | 14.257 | 13.5303 | 23.5311 | 23.2728 | 22.9547 | 22.6079 | 22.2154 | 21.8233 | 21.4788 | 21.1279 | 20.8297 | 20.5704 | 19.4944 | 17.6982 | 16.5056 | 15.2746 | 22.1343 | 21.8411 | 21.4722 | 21.0689 | 20.6076 | 20.144 | 19.7441 | 19.3381 | 19.0107 | 18.7221 | 17.5769 | 15.6785 | 14.6665 | 14.0866
|  | HEDGE END | SP |  |  | 20.9289 | 20.6544 | 20.3344 | 20.0055 | 19.6555 | 19.3101 | 19.0193 | 18.7269 | 18.5159 | 18.3265 | 17.7785 | 16.399 | 15.2571 | 14.769 | 23.535 | 23.2875 | 23.0029 | 22.6995 | 22.3848 | 22.0649 | 21.7636 | 21.4487 | 21.1931 | 20.9468 | 20.1216 | 17.9339 | 16.1276 | 13.9042 | 22.1465 | 21.8734 | 21.5544 | 21.216 | 20.8547 | 20.4908 | 20.1607 | 19.8199 | 19.5592 | 19.3185 | 18.5575 | 16.6095 | 15.6205 | 15.2149
BRAMLEY (FLEE) | READING BSP | HENLEY | MINIMUM HEADROOM | SU 76070 82422 | YES | -6.1277 | -6.6389 | -7.1976 | -7.8869 | -9.1133 | -10.4897 | -11.9497 | -13.5507 | -15.4076 | -17.2501 | -22.574 | -27.0534 | -28.9149 | -30.4642 | -4.8724 | -5.1451 | -5.4556 | -5.8448 | -6.4697 | -7.1748 | -7.9538 | -8.8242 | -9.8843 | -10.9103 | -13.7013 | -16.4582 | -19.1484 | -21.8818 | -8.9472 | -9.4166 | -9.936 | -10.5665 | -11.6584 | -12.8774 | -14.1836 | -15.621 | -17.3034 | -18.9641 | -23.6847 | -27.7343 | -29.3923 | -30.8471
|  | HENLEY | CT |  |  | -5.8189 | -6.1314 | -6.4916 | -7.003 | -7.8906 | -8.9223 | -10.0002 | -11.1734 | -12.5109 | -14.3025 | -19.523 | -25.2915 | -28.9149 | -30.4642 | -4.8205 | -5.0614 | -5.3429 | -5.7229 | -6.2574 | -6.8725 | -7.5392 | -8.2683 | -9.1172 | -10.1827 | -13.1706 | -16.4582 | -19.1484 | -21.8527 | -8.6742 | -8.973 | -9.3191 | -9.8004 | -10.5903 | -11.5018 | -12.4639 | -13.5121 | -14.7138 | -16.3285 | -20.9586 | -26.1248 | -29.3923 | -30.8471
|  | HENLEY | LW |  |  | -6.1277 | -6.6389 | -7.1976 | -7.8869 | -9.1133 | -10.4897 | -11.9497 | -13.5507 | -15.4076 | -17.2501 | -22.574 | -27.0534 | -28.4041 | -29.0049 | -4.8724 | -5.1451 | -5.4556 | -5.8448 | -6.4697 | -7.1748 | -7.9538 | -8.8242 | -9.8843 | -10.9103 | -13.7013 | -15.9176 | -16.4948 | -16.7469 | -8.9472 | -9.4166 | -9.936 | -10.5665 | -11.6584 | -12.8774 | -14.1836 | -15.621 | -17.3034 | -18.9641 | -23.6847 | -27.7343 | -28.9232 | -29.4473
|  | HENLEY | ST |  |  | -5.5518 | -5.6924 | -5.862 | -6.1162 | -6.6073 | -7.1923 | -7.7943 | -8.4592 | -9.2187 | -10.0213 | -13.2866 | -17.4514 | -19.4948 | -20.767 | -4.6261 | -4.7431 | -4.8862 | -5.0875 | -5.4263 | -5.8225 | -6.242 | -6.7097 | -7.2516 | -7.7948 | -10.1089 | -13.4668 | -15.6382 | -18.1305 | -8.4142 | -8.5461 | -8.7068 | -8.9392 | -9.3683 | -9.8711 | -10.3943 | -10.9744 | -11.6416 | -12.3423 | -15.2504 | -19.1522 | -20.9974 | -22.1115
|  | HENLEY | SP |  |  | -5.5118 | -5.6387 | -5.7803 | -5.9946 | -6.4681 | -7.0279 | -7.6124 | -8.2678 | -8.9619 | -9.7533 | -12.6018 | -17.2008 | -19.764 | -20.9218 | -4.6153 | -4.7358 | -4.8749 | -5.0651 | -5.3738 | -5.7309 | -6.1224 | -6.5705 | -7.0641 | -7.6141 | -9.6985 | -13.7385 | -17.3353 | -21.8818 | -8.3786 | -8.4997 | -8.6352 | -8.8308 | -9.2355 | -9.7058 | -10.2047 | -10.7684 | -11.3664 | -12.0506 | -14.5334 | -18.8505 | -21.2402 | -22.28
AXMINSTER | YEOVIL BSP | HENSTRIDGE | MINIMUM HEADROOM | ST 72676 19263 | YES | 13.0141 | 12.5008 | 11.8568 | 11.2555 | 10.4665 | 9.6409 | 8.7915 | 7.8933 | 6.9074 | 5.9072 | 3.5717 | 1.2227 | 0.68064 | 0.28544 | 16.7284 | 16.5306 | 16.2832 | 16.0513 | 15.748 | 15.4296 | 15.0993 | 14.7234 | 14.3322 | 13.929 | 12.9541 | 11.9639 | 11.7284 | 11.5623 | 14.7276 | 14.2834 | 13.7284 | 13.2029 | 12.5118 | 11.7873 | 11.0381 | 10.2328 | 9.3473 | 8.4464 | 6.3616 | 4.2783 | 3.8014 | 3.4552
|  | HENSTRIDGE | CT |  |  | 13.4903 | 13.2198 | 12.844 | 12.4598 | 11.9455 | 11.3956 | 10.8129 | 10.1828 | 9.5349 | 8.6317 | 6.5651 | 3.6818 | 2.1692 | 1.5448 | 16.899 | 16.7881 | 16.6351 | 16.4814 | 16.2803 | 16.0649 | 15.8364 | 15.5635 | 15.304 | 14.9532 | 14.0949 | 12.8246 | 12.1572 | 11.7978 | 15.1439 | 14.913 | 14.5964 | 14.2646 | 13.8231 | 13.3511 | 12.8492 | 12.2935 | 11.7299 | 10.9346 | 9.0537 | 6.4477 | 5.1109 | 4.5617
|  | HENSTRIDGE | LW |  |  | 13.0141 | 12.5008 | 11.8568 | 11.2555 | 10.4665 | 9.6409 | 8.7915 | 7.8933 | 6.9074 | 5.9072 | 3.5717 | 1.2227 | 0.68064 | 0.28544 | 16.7284 | 16.5306 | 16.2832 | 16.0513 | 15.748 | 15.4296 | 15.0993 | 14.7234 | 14.3322 | 13.929 | 12.9541 | 11.9639 | 11.7284 | 11.5623 | 14.7276 | 14.2834 | 13.7284 | 13.2029 | 12.5118 | 11.7873 | 11.0381 | 10.2328 | 9.3473 | 8.4464 | 6.3616 | 4.2783 | 3.8014 | 3.4552
|  | HENSTRIDGE | ST |  |  | 13.6103 | 13.4246 | 13.1824 | 12.9669 | 12.6354 | 12.2825 | 11.9251 | 11.5245 | 11.135 | 10.7287 | 9.3717 | 7.2138 | 6.0906 | 5.3039 | 16.9484 | 16.8719 | 16.7725 | 16.6834 | 16.5512 | 16.4091 | 16.2642 | 16.079 | 15.9164 | 15.7426 | 15.1728 | 14.1976 | 13.6065 | 13.1623 | 15.2578 | 15.1059 | 14.9131 | 14.7357 | 14.4529 | 14.1509 | 13.8438 | 13.4942 | 13.1619 | 12.8115 | 11.6226 | 9.6513 | 8.6351 | 7.9312
|  | HENSTRIDGE | SP |  |  | 13.679 | 13.5243 | 13.3254 | 13.1532 | 12.7645 | 12.3668 | 11.9624 | 11.5252 | 11.1048 | 10.5766 | 9.0162 | 5.7632 | 3.8892 | 2.6725 | 16.9732 | 16.9082 | 16.824 | 16.7508 | 16.5989 | 16.4421 | 16.2821 | 16.0835 | 15.9088 | 15.6936 | 15.0542 | 13.7253 | 12.8533 | 12.2565 | 15.3184 | 15.193 | 15.0383 | 14.8992 | 14.5703 | 14.233 | 13.8883 | 13.5024 | 13.1367 | 12.6756 | 11.2805 | 8.3558 | 6.6455 | 5.5742
BRAMLEY (FLEE) | ALTON | HERRIARD | MINIMUM HEADROOM | SU 66770 44972 | YES | 5.8083 | 5.725 | 5.6403 | 5.5532 | 5.4388 | 5.3273 | 5.2084 | 5.0697 | 4.9163 | 4.793 | 4.4767 | 4.1242 | 4.0442 | 3.9923 | 6.0594 | 6.0267 | 5.9937 | 5.9593 | 5.9142 | 5.8698 | 5.8217 | 5.7657 | 5.7036 | 5.6507 | 5.508 | 5.3486 | 5.3137 | 5.2915 | 5.3458 | 5.2707 | 5.1942 | 5.1153 | 5.0121 | 4.9114 | 4.8031 | 4.6715 | 4.5256 | 4.4132 | 4.1404 | 3.8262 | 3.7553 | 3.7096
|  | HERRIARD | CT |  |  | 5.8896 | 5.8497 | 5.8037 | 5.7593 | 5.6947 | 5.6296 | 5.555 | 5.4702 | 5.3852 | 5.2722 | 5.0412 | 4.6122 | 4.3392 | 4.2382 | 6.0628 | 6.0504 | 6.0332 | 6.0164 | 5.9964 | 5.9744 | 5.9422 | 5.906 | 5.8693 | 5.8214 | 5.7138 | 5.5131 | 5.3869 | 5.3165 | 5.4108 | 5.3705 | 5.3228 | 5.2772 | 5.2174 | 5.1556 | 5.0838 | 4.9988 | 4.9141 | 4.8008 | 4.6126 | 4.254 | 4.0162 | 3.9271
|  | HERRIARD | LW |  |  | 5.8083 | 5.725 | 5.6403 | 5.5532 | 5.4388 | 5.3273 | 5.2084 | 5.0697 | 4.9163 | 4.793 | 4.4767 | 4.1242 | 4.0442 | 3.9923 | 6.0594 | 6.0267 | 5.9937 | 5.9593 | 5.9142 | 5.8698 | 5.8217 | 5.7657 | 5.7036 | 5.6507 | 5.508 | 5.3486 | 5.3137 | 5.2915 | 5.3458 | 5.2707 | 5.1942 | 5.1153 | 5.0121 | 4.9114 | 4.8031 | 4.6715 | 4.5256 | 4.4132 | 4.1404 | 3.8262 | 3.7553 | 3.7096
|  | HERRIARD | ST |  |  | 5.9232 | 5.9035 | 5.8801 | 5.8544 | 5.8153 | 5.7752 | 5.7327 | 5.6879 | 5.6377 | 5.5822 | 5.3535 | 5.0787 | 4.9079 | 4.7993 | 6.0762 | 6.0706 | 6.0648 | 6.0565 | 6.0472 | 6.036 | 6.0183 | 5.9982 | 5.9756 | 5.9502 | 5.8474 | 5.6692 | 5.577 | 5.5219 | 5.4474 | 5.429 | 5.4056 | 5.3794 | 5.3429 | 5.3054 | 5.2647 | 5.2214 | 5.1719 | 5.1204 | 4.8827 | 4.6393 | 4.5011 | 4.4093
|  | HERRIARD | SP |  |  | 5.934 | 5.9208 | 5.9058 | 5.8912 | 5.8512 | 5.8088 | 5.7677 | 5.7205 | 5.6744 | 5.6053 | 5.3724 | 4.861 | 4.5527 | 4.3574 | 6.0764 | 6.0718 | 6.0659 | 6.0603 | 6.0534 | 6.044 | 6.0317 | 6.0116 | 5.9914 | 5.9627 | 5.8656 | 5.6397 | 5.4893 | 5.3957 | 5.455 | 5.4421 | 5.4268 | 5.412 | 5.3769 | 5.3395 | 5.3035 | 5.2599 | 5.2175 | 5.1551 | 4.9388 | 4.4572 | 4.1958 | 4.0302
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE | MINIMUM HEADROOM | SU 84733 92200 | YES | 10.6263 | 10.4499 | 10.2522 | 10.0135 | 9.7432 | 9.4269 | 9.0474 | 8.5862 | 7.9127 | 7.091 | 4.0785 | 0.42479 | -0.53616 | -1.1983 | 13.5202 | 13.3687 | 13.2106 | 13.0319 | 12.7673 | 12.4808 | 12.1639 | 11.8172 | 11.4015 | 10.9413 | 9.6483 | 7.5663 | 6.6147 | 5.4252 | 11.0108 | 10.8881 | 10.6991 | 10.4679 | 10.2069 | 9.9016 | 9.5055 | 8.9763 | 8.2424 | 7.3483 | 4.498 | 1.0604 | 0.18311 | -0.3159
|  | HIGH WYCOMBE | CT |  |  | 10.6263 | 10.459 | 10.2799 | 10.0608 | 9.828 | 9.5663 | 9.2724 | 8.9456 | 8.58 | 8.0804 | 6.2037 | 1.9427 | -0.091475 | -1.1983 | 13.5589 | 13.4369 | 13.3101 | 13.1521 | 12.9584 | 12.7474 | 12.5206 | 12.2712 | 11.9908 | 11.5509 | 10.2916 | 8.132 | 6.6147 | 5.4252 | 11.0108 | 10.8925 | 10.7253 | 10.5127 | 10.2878 | 10.0348 | 9.7506 | 9.4346 | 9.052 | 8.4738 | 6.517 | 2.5122 | 0.66687 | -0.26581
|  | HIGH WYCOMBE | LW |  |  | 10.6403 | 10.4499 | 10.2522 | 10.0135 | 9.7432 | 9.4269 | 9.0474 | 8.5862 | 7.9127 | 7.091 | 4.0785 | 0.42479 | -0.53616 | -1.0834 | 13.5202 | 13.3687 | 13.2106 | 13.0319 | 12.7673 | 12.4808 | 12.1639 | 11.8172 | 11.4015 | 10.9413 | 9.6483 | 7.5663 | 7.0784 | 6.7753 | 11.0204 | 10.8881 | 10.6991 | 10.4679 | 10.2069 | 9.9016 | 9.5055 | 8.9763 | 8.2424 | 7.3483 | 4.498 | 1.0604 | 0.18311 | -0.3159
|  | HIGH WYCOMBE | ST |  |  | 10.7585 | 10.672 | 10.5923 | 10.4981 | 10.3848 | 10.2481 | 10.0885 | 9.9006 | 9.661 | 9.3539 | 8.0936 | 4.6014 | 2.741 | 2.0593 | 13.6466 | 13.5785 | 13.5145 | 13.4406 | 13.3522 | 13.2516 | 13.1382 | 13.0087 | 12.8516 | 12.6654 | 11.8839 | 9.4971 | 8.0523 | 7.4745 | 11.0975 | 11.032 | 10.9735 | 10.9049 | 10.8258 | 10.694 | 10.5396 | 10.3579 | 10.1262 | 9.8296 | 8.5787 | 4.9929 | 3.2125 | 2.5868
|  | HIGH WYCOMBE | SP |  |  | 10.7631 | 10.6833 | 10.6102 | 10.5288 | 10.4415 | 10.3452 | 10.236 | 10.1099 | 9.9636 | 9.774 | 9.1015 | 6.8366 | 4.316 | 3.5201 | 13.6557 | 13.5903 | 13.53 | 13.4634 | 13.394 | 13.3195 | 13.2363 | 13.1394 | 13.0276 | 12.8786 | 12.3271 | 10.6703 | 8.9871 | 7.3703 | 11.1018 | 11.0402 | 10.9864 | 10.9273 | 10.8675 | 10.788 | 10.6826 | 10.5606 | 10.4191 | 10.236 | 9.5863 | 7.1606 | 4.7314 | 3.9757
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN | MINIMUM HEADROOM | SU 86304 92972 | YES | 38.8347 | 38.5121 | 38.1411 | 37.7385 | 37.0595 | 36.3439 | 35.5876 | 34.7828 | 33.8393 | 32.8593 | 29.9766 | 26.0004 | 23.2149 | 20.991 | 43.8639 | 43.763 | 43.6446 | 43.4741 | 43.1704 | 42.8458 | 42.4933 | 42.1153 | 41.6569 | 41.1673 | 39.5909 | 36.4583 | 33.3884 | 28.7167 | 40.8549 | 40.7403 | 40.4888 | 40.1115 | 39.4955 | 38.8427 | 38.1448 | 37.3976 | 36.5013 | 35.566 | 32.875 | 29.3033 | 27.0456 | 25.1931
|  | HIGH WYCOMBE TOWN | CT |  |  | 39.0315 | 38.8242 | 38.5746 | 38.2733 | 37.8148 | 37.3259 | 36.8427 | 36.3196 | 35.7277 | 34.7988 | 32.0636 | 26.9903 | 23.2149 | 20.991 | 43.8639 | 43.763 | 43.6446 | 43.5045 | 43.3204 | 43.0516 | 42.7743 | 42.473 | 42.0982 | 41.5175 | 39.7712 | 36.4583 | 33.3884 | 29.9351 | 40.8549 | 40.7403 | 40.6051 | 40.4443 | 40.1248 | 39.6668 | 39.2078 | 38.7044 | 38.1147 | 37.2121 | 34.6423 | 30.2272 | 27.0456 | 25.1931
|  | HIGH WYCOMBE TOWN | LW |  |  | 38.8347 | 38.5121 | 38.1411 | 37.7385 | 37.0595 | 36.3439 | 35.5876 | 34.7828 | 33.8393 | 32.8593 | 29.9766 | 26.0004 | 23.9475 | 22.4976 | 43.8913 | 43.796 | 43.6641 | 43.4741 | 43.1704 | 42.8458 | 42.4933 | 42.1153 | 41.6569 | 41.1673 | 39.5909 | 37.5011 | 36.5517 | 35.8625 | 40.8766 | 40.7553 | 40.4888 | 40.1115 | 39.4955 | 38.8427 | 38.1448 | 37.3976 | 36.5013 | 35.566 | 32.875 | 29.3033 | 27.5761 | 26.3712
|  | HIGH WYCOMBE TOWN | ST |  |  | 39.2501 | 39.1711 | 39.0798 | 38.9782 | 38.8116 | 38.6229 | 38.418 | 38.1885 | 37.897 | 37.549 | 36.13 | 31.2924 | 29.1262 | 28.3683 | 43.9506 | 43.9012 | 43.8445 | 43.7799 | 43.6871 | 43.5809 | 43.4579 | 43.3158 | 43.1222 | 42.8614 | 41.7324 | 38.4863 | 35.7256 | 32.4903 | 40.963 | 40.9125 | 40.8541 | 40.7875 | 40.6887 | 40.5749 | 40.4436 | 40.2915 | 40.0818 | 39.8003 | 38.4027 | 33.4298 | 31.3832 | 30.8426
|  | HIGH WYCOMBE TOWN | SP |  |  | 39.2787 | 39.2122 | 39.1371 | 39.0551 | 38.9156 | 38.7739 | 38.6072 | 38.4303 | 38.2234 | 37.943 | 36.9268 | 33.831 | 30.872 | 29.8628 | 43.9509 | 43.9059 | 43.8529 | 43.7926 | 43.7111 | 43.6182 | 43.5142 | 43.3941 | 43.1982 | 42.9593 | 41.8784 | 38.525 | 34.3826 | 28.7167 | 40.9661 | 40.9229 | 40.8729 | 40.8161 | 40.7378 | 40.6491 | 40.5513 | 40.4396 | 40.2936 | 40.126 | 39.2315 | 36.1236 | 33.0654 | 32.1311
LOVEDEAN GSP | WYMERING BSP | HILSEA | MINIMUM HEADROOM | SU 66394 03806 | NO | 17.4229 | 17.3352 | 17.2309 | 17.1326 | 17.0057 | 16.8685 | 16.7186 | 16.5552 | 16.3571 | 16.1416 | 15.4479 | 14.5469 | 14.1771 | 13.8794 | 20.2999 | 20.2355 | 20.1562 | 20.0852 | 19.9912 | 19.8557 | 19.6954 | 19.5139 | 19.2644 | 18.9331 | 17.8235 | 16.5446 | 16.3133 | 16.1631 | 17.2648 | 17.1829 | 17.0862 | 16.9947 | 16.8823 | 16.7587 | 16.5311 | 16.243 | 15.8903 | 15.464 | 14.0441 | 12.4009 | 12.0916 | 11.8909
|  | HILSEA | CT |  |  | 17.4501 | 17.3831 | 17.3 | 17.2204 | 17.128 | 17.0276 | 16.9224 | 16.8068 | 16.6691 | 16.4902 | 15.9029 | 14.8608 | 14.2539 | 13.8794 | 20.2999 | 20.2401 | 20.1641 | 20.0969 | 20.0202 | 19.9039 | 19.7778 | 19.6369 | 19.4683 | 19.2615 | 18.4772 | 17.1301 | 16.7257 | 16.4985 | 17.2812 | 17.2155 | 17.1336 | 17.0574 | 16.9718 | 16.8781 | 16.7493 | 16.544 | 16.3028 | 15.9905 | 14.9555 | 13.2015 | 12.6359 | 12.3339
|  | HILSEA | LW |  |  | 17.4229 | 17.3352 | 17.2309 | 17.1326 | 17.0057 | 16.8685 | 16.7186 | 16.5552 | 16.3571 | 16.1416 | 15.4479 | 14.5469 | 14.1771 | 13.9146 | 20.3003 | 20.2355 | 20.1562 | 20.0852 | 19.9912 | 19.8557 | 19.6954 | 19.5139 | 19.2644 | 18.9331 | 17.8235 | 16.5446 | 16.3133 | 16.1631 | 17.2648 | 17.1829 | 17.0862 | 16.9947 | 16.8823 | 16.7587 | 16.5311 | 16.243 | 15.8903 | 15.464 | 14.0441 | 12.4009 | 12.0916 | 11.8909
|  | HILSEA | ST |  |  | 17.489 | 17.4485 | 17.395 | 17.3542 | 17.3068 | 17.2541 | 17.1978 | 17.1339 | 17.053 | 16.9543 | 16.5677 | 15.5574 | 14.8129 | 14.4948 | 20.3296 | 20.2894 | 20.2363 | 20.1972 | 20.1573 | 20.1125 | 20.0637 | 20.0077 | 19.9092 | 19.7588 | 19.17 | 17.432 | 16.5355 | 16.297 | 17.3204 | 17.2806 | 17.2287 | 17.1891 | 17.1448 | 17.0948 | 17.0395 | 16.9688 | 16.873 | 16.752 | 15.9301 | 13.725 | 12.6111 | 12.3193
|  | HILSEA | SP |  |  | 17.4958 | 17.4589 | 17.4102 | 17.3749 | 17.3428 | 17.3079 | 17.2723 | 17.2333 | 17.1827 | 17.1194 | 16.8971 | 16.1892 | 15.4806 | 15.1619 | 20.3318 | 20.2934 | 20.2425 | 20.2059 | 20.1726 | 20.1359 | 20.0979 | 20.0556 | 20.0029 | 19.9423 | 19.6395 | 18.5386 | 17.3011 | 16.9298 | 17.3256 | 17.2894 | 17.2422 | 17.2077 | 17.1762 | 17.1385 | 17.0962 | 17.0488 | 16.9877 | 16.9162 | 16.6024 | 15.1155 | 13.5941 | 13.1562
MANNINGTON GSP | ARNEWOOD | HINCHELSEA | MINIMUM HEADROOM | SU 27805 00447 | YES | 7.8531 | 7.679 | 7.4823 | 7.2724 | 6.9339 | 6.5795 | 6.2017 | 5.7901 | 5.258 | 4.7351 | 3.7597 | 2.5159 | 1.6067 | 1.0303 | 10.0372 | 9.9352 | 9.8121 | 9.6766 | 9.4919 | 9.294 | 9.0724 | 8.8221 | 8.4718 | 8.1445 | 7.667 | 7.1023 | 6.509 | 6.0308 | 8.631 | 8.4656 | 8.2743 | 8.0683 | 7.7531 | 7.4209 | 7.0615 | 6.6653 | 6.1493 | 5.6542 | 4.7626 | 3.6931 | 2.9696 | 2.5015
|  | HINCHELSEA | CT |  |  | 7.9585 | 7.8502 | 7.7226 | 7.5645 | 7.3552 | 7.127 | 6.8762 | 6.5888 | 6.2584 | 5.7024 | 4.6526 | 2.9346 | 1.6067 | 1.0303 | 10.0501 | 9.9628 | 9.8566 | 9.7196 | 9.5804 | 9.4292 | 9.2582 | 9.0565 | 8.8166 | 8.4499 | 7.8732 | 7.1023 | 6.509 | 6.0308 | 8.7103 | 8.5991 | 8.4663 | 8.2986 | 8.0965 | 7.8803 | 7.6419 | 7.3674 | 7.05 | 6.5215 | 5.5542 | 4.0545 | 2.9696 | 2.5015
|  | HINCHELSEA | LW |  |  | 7.8531 | 7.679 | 7.4823 | 7.2724 | 6.9339 | 6.5795 | 6.2017 | 5.7901 | 5.258 | 4.7351 | 3.7597 | 2.5159 | 2.0478 | 1.8437 | 10.0372 | 9.9352 | 9.8121 | 9.6766 | 9.4919 | 9.294 | 9.0724 | 8.8221 | 8.4718 | 8.1445 | 7.667 | 7.1502 | 6.9934 | 6.9264 | 8.631 | 8.4656 | 8.2743 | 8.0683 | 7.7531 | 7.4209 | 7.0615 | 6.6653 | 6.1493 | 5.6542 | 4.7626 | 3.6931 | 3.309 | 3.1431
|  | HINCHELSEA | ST |  |  | 8.05 | 8.0015 | 7.9415 | 7.8697 | 7.7701 | 7.659 | 7.5426 | 7.41 | 7.258 | 7.0952 | 6.3001 | 5.0997 | 4.492 | 4.057 | 10.1259 | 10.0875 | 10.0376 | 9.9755 | 9.8979 | 9.8091 | 9.7136 | 9.6023 | 9.4766 | 9.359 | 8.7391 | 7.8803 | 7.4534 | 7.0192 | 8.8082 | 8.7607 | 8.7 | 8.6259 | 8.5256 | 8.4125 | 8.2932 | 8.156 | 8.0043 | 7.8488 | 7.0772 | 5.9418 | 5.3983 | 5.0173
|  | HINCHELSEA | SP |  |  | 8.0602 | 8.0144 | 7.9642 | 7.9159 | 7.8106 | 7.6973 | 7.5852 | 7.4561 | 7.3186 | 7.1546 | 6.5353 | 4.9284 | 4.3148 | 4.0225 | 10.1253 | 10.0827 | 10.0349 | 9.9876 | 9.919 | 9.8474 | 9.7714 | 9.6785 | 9.5775 | 9.4647 | 9.0062 | 7.7664 | 7.212 | 6.6929 | 8.8152 | 8.7677 | 8.7156 | 8.6656 | 8.5659 | 8.4602 | 8.3537 | 8.2283 | 8.0943 | 7.9368 | 7.3329 | 5.7905 | 5.2227 | 4.9619
BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD | MINIMUM HEADROOM | SU 88631 36479 | YES | 17.3183 | 16.9022 | 16.4521 | 15.9704 | 15.2282 | 14.4504 | 13.602 | 12.6482 | 11.545 | 10.5495 | 8.3225 | 5.591 | 4.4319 | 3.2766 | 20.4389 | 20.21 | 19.9541 | 19.672 | 19.2896 | 18.8798 | 18.4063 | 17.8492 | 17.1504 | 16.5533 | 15.4366 | 14.1372 | 13.1149 | 12.2188 | 18.7922 | 18.4122 | 18.0024 | 17.5648 | 16.883 | 16.1698 | 15.3951 | 14.5279 | 13.5329 | 12.6277 | 10.5628 | 8.021 | 6.9251 | 5.8415
|  | HINDHEAD | CT |  |  | 17.5561 | 17.2889 | 16.9807 | 16.6342 | 16.1611 | 15.6609 | 15.1203 | 14.5097 | 13.8284 | 12.8056 | 10.61 | 6.9932 | 4.4319 | 3.2766 | 20.4694 | 20.2738 | 20.0429 | 19.7779 | 19.4816 | 19.1629 | 18.7988 | 18.3776 | 17.8928 | 17.2381 | 16.0317 | 14.3416 | 13.1149 | 12.2188 | 19.0213 | 18.7821 | 18.507 | 18.1985 | 17.7691 | 17.3156 | 16.8282 | 16.2793 | 15.6693 | 14.7453 | 12.7232 | 9.3347 | 6.9251 | 5.8415
|  | HINDHEAD | LW |  |  | 17.3183 | 16.9022 | 16.4521 | 15.9704 | 15.2282 | 14.4504 | 13.602 | 12.6482 | 11.545 | 10.5495 | 8.3225 | 5.591 | 4.6379 | 4.0825 | 20.4389 | 20.21 | 19.9541 | 19.672 | 19.2896 | 18.8798 | 18.4063 | 17.8492 | 17.1504 | 16.5533 | 15.4366 | 14.1372 | 13.7552 | 13.5419 | 18.7922 | 18.4122 | 18.0024 | 17.5648 | 16.883 | 16.1698 | 15.3951 | 14.5279 | 13.5329 | 12.6277 | 10.5628 | 8.021 | 7.1332 | 6.6181
|  | HINDHEAD | ST |  |  | 17.8086 | 17.6952 | 17.5515 | 17.3808 | 17.15 | 16.9063 | 16.64 | 16.3366 | 15.9988 | 15.6453 | 13.9531 | 11.4091 | 10.0581 | 9.1377 | 20.6543 | 20.5707 | 20.4598 | 20.3247 | 20.1617 | 19.9878 | 19.7917 | 19.5631 | 19.2997 | 19.052 | 17.7631 | 15.9733 | 15.106 | 14.3142 | 19.2459 | 19.1436 | 19.015 | 18.863 | 18.6554 | 18.4362 | 18.1971 | 17.9257 | 17.6242 | 17.3047 | 15.7963 | 13.4797 | 12.2169 | 11.3537
|  | HINDHEAD | SP |  |  | 17.8426 | 17.7399 | 17.6331 | 17.5136 | 17.2812 | 17.0623 | 16.8161 | 16.5372 | 16.2578 | 15.8849 | 14.5015 | 11.1399 | 9.4968 | 8.6541 | 20.6627 | 20.5762 | 20.4821 | 20.3746 | 20.232 | 20.0927 | 19.9379 | 19.7472 | 19.5505 | 19.3132 | 18.3607 | 15.9031 | 14.7172 | 13.8508 | 19.278 | 19.1865 | 19.0917 | 18.9859 | 18.7739 | 18.5745 | 18.3498 | 18.0976 | 17.845 | 17.5057 | 16.2585 | 13.2414 | 11.7318 | 10.9528
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL | MINIMUM HEADROOM | SU 00702 06030 | YES | 4.3207 | 4.2053 | 4.0896 | 3.9728 | 3.8161 | 3.6547 | 3.4804 | 3.2896 | 3.0851 | 2.9365 | 2.5603 | 2.1347 | 2.0549 | 1.9839 | 3.8411 | 3.7838 | 3.7262 | 3.6661 | 3.588 | 3.5064 | 3.4118 | 3.2989 | 3.1739 | 3.0949 | 2.9109 | 2.6874 | 2.6519 | 2.625 | 3.4345 | 3.3378 | 3.2408 | 3.1413 | 3.0098 | 2.8735 | 2.7215 | 2.5466 | 2.356 | 2.2198 | 1.8785 | 1.49 | 1.4196 | 1.3579
|  | HINTON MARTELL | CT |  |  | 4.4245 | 4.368 | 4.3052 | 4.2396 | 4.1492 | 4.0554 | 3.9462 | 3.8266 | 3.7077 | 3.5682 | 3.2976 | 2.8303 | 2.5665 | 2.4544 | 3.8703 | 3.8323 | 3.7886 | 3.7413 | 3.6871 | 3.63 | 3.5593 | 3.4786 | 3.3973 | 3.3064 | 3.1635 | 2.9129 | 2.7735 | 2.6724 | 3.5058 | 3.4524 | 3.3919 | 3.3276 | 3.2467 | 3.162 | 3.06 | 2.9457 | 2.8314 | 2.6999 | 2.4765 | 2.0952 | 1.8767 | 1.7789
|  | HINTON MARTELL | LW |  |  | 4.3207 | 4.2053 | 4.0896 | 3.9728 | 3.8161 | 3.6547 | 3.4804 | 3.2896 | 3.0851 | 2.9365 | 2.5603 | 2.1347 | 2.0549 | 1.9839 | 3.8411 | 3.7838 | 3.7262 | 3.6661 | 3.588 | 3.5064 | 3.4118 | 3.2989 | 3.1739 | 3.0949 | 2.9109 | 2.6874 | 2.6519 | 2.625 | 3.4345 | 3.3378 | 3.2408 | 3.1413 | 3.0098 | 2.8735 | 2.7215 | 2.5466 | 2.356 | 2.2198 | 1.8785 | 1.49 | 1.4196 | 1.3579
|  | HINTON MARTELL | ST |  |  | 4.4703 | 4.4431 | 4.4072 | 4.3706 | 4.3149 | 4.255 | 4.1934 | 4.1253 | 4.054 | 3.9772 | 3.6436 | 3.246 | 3.0294 | 2.9254 | 3.9011 | 3.8838 | 3.8583 | 3.832 | 3.7995 | 3.7634 | 3.7252 | 3.6813 | 3.6317 | 3.5834 | 3.3437 | 3.0846 | 2.9432 | 2.8451 | 3.5502 | 3.5261 | 3.4918 | 3.4567 | 3.408 | 3.3548 | 3.2995 | 3.2372 | 3.1693 | 3.0993 | 2.7698 | 2.4164 | 2.2404 | 2.1643
|  | HINTON MARTELL | SP |  |  | 4.4917 | 4.4734 | 4.4522 | 4.4291 | 4.376 | 4.3217 | 4.2683 | 4.209 | 4.1471 | 4.0546 | 3.7343 | 3.0244 | 2.5868 | 2.3247 | 3.908 | 3.8937 | 3.8765 | 3.857 | 3.8268 | 3.7963 | 3.7654 | 3.7291 | 3.6889 | 3.6385 | 3.4467 | 3.0028 | 2.7667 | 2.6271 | 3.5656 | 3.5482 | 3.5273 | 3.5042 | 3.4583 | 3.4119 | 3.3661 | 3.3136 | 3.2572 | 3.1782 | 2.8915 | 2.2478 | 1.8883 | 1.6567
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE | MINIMUM HEADROOM | SU 79461 54769 | YES | 16.423 | 15.4726 | 14.5797 | 13.6 | 12.1272 | 10.5422 | 8.8592 | 6.9469 | 4.6793 | 2.5311 | -2.5198 | -8.0267 | -9.845 | -11.5648 | 23.7946 | 23.2251 | 22.6908 | 22.0899 | 21.2792 | 20.3964 | 19.4237 | 18.2929 | 16.85 | 15.5118 | 12.5872 | 9.4775 | 7.3899 | 5.5691 | 18.4877 | 17.6357 | 16.8239 | 15.927 | 14.5926 | 13.1554 | 11.6137 | 9.8559 | 7.7402 | 5.7466 | 1.1293 | -3.9457 | -5.4551 | -6.9653
|  | HITCHES LANE | CT |  |  | 16.7079 | 15.9594 | 15.1947 | 14.3922 | 13.342 | 12.2 | 11.0758 | 9.726 | 8.2324 | 6.0351 | 1.0988 | -5.7562 | -9.845 | -11.5648 | 23.8308 | 23.3087 | 22.7589 | 22.1779 | 21.5164 | 20.795 | 20.0488 | 19.1395 | 18.1209 | 16.7025 | 13.7204 | 9.7723 | 7.3899 | 5.5691 | 18.7262 | 18.052 | 17.3447 | 16.6011 | 15.6445 | 14.6054 | 13.5707 | 12.3228 | 10.938 | 8.8945 | 4.389 | -1.8346 | -5.4551 | -6.9653
|  | HITCHES LANE | LW |  |  | 16.423 | 15.4726 | 14.5797 | 13.6 | 12.1272 | 10.5422 | 8.8592 | 6.9469 | 4.6793 | 2.5311 | -2.5198 | -8.0267 | -9.599 | -10.2576 | 23.7946 | 23.2251 | 22.6908 | 22.0899 | 21.2792 | 20.3964 | 19.4237 | 18.2929 | 16.85 | 15.5118 | 12.5872 | 9.4775 | 8.786 | 8.5134 | 18.4877 | 17.6357 | 16.8239 | 15.927 | 14.5926 | 13.1554 | 11.6137 | 9.8559 | 7.7402 | 5.7466 | 1.1293 | -3.9457 | -5.3421 | -5.9197
|  | HITCHES LANE | ST |  |  | 17.2814 | 16.9064 | 16.5334 | 16.1041 | 15.5929 | 15.0211 | 14.4202 | 13.7388 | 12.9378 | 12.0836 | 8.5206 | 3.103 | 0.46652 | -0.95663 | 24.2343 | 23.9648 | 23.681 | 23.346 | 22.9767 | 22.5638 | 22.1171 | 21.611 | 21.0059 | 20.4005 | 17.7293 | 13.5835 | 11.4524 | 9.7398 | 19.2806 | 18.9648 | 18.6336 | 18.246 | 17.7869 | 17.274 | 16.7264 | 16.1068 | 15.372 | 14.5929 | 11.2374 | 6.0852 | 3.6686 | 2.4175
|  | HITCHES LANE | SP |  |  | 17.3346 | 16.997 | 16.6988 | 16.3681 | 15.9355 | 15.4526 | 14.9679 | 14.3796 | 13.7194 | 12.9528 | 10.3128 | 4.3168 | 1.101 | -0.16107 | 24.2514 | 23.9945 | 23.75 | 23.472 | 23.1699 | 22.8293 | 22.4756 | 22.0394 | 21.5417 | 20.9938 | 19.0155 | 14.1699 | 11.1716 | 8.9654 | 19.3282 | 19.046 | 18.7858 | 18.493 | 18.1127 | 17.6883 | 17.2563 | 16.7279 | 16.1319 | 15.4386 | 12.9986 | 7.2285 | 4.1703 | 3.0081
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD | MINIMUM HEADROOM | SU 57855 04433 | YES | 7.2391 | 6.7455 | 6.218 | 5.7012 | 4.9893 | 4.2707 | 3.4877 | 2.6659 | 1.714 | 0.69195 | -2.4659 | -6.7084 | -10.8675 | -13.6863 | 6.8005 | 6.6428 | 6.4886 | 6.2892 | 6.0642 | 5.743 | 5.2484 | 4.723 | 4.0941 | 3.3975 | 1.3516 | -1.4056 | -4.0423 | -6.5733 | 4.8257 | 4.4865 | 4.0859 | 3.673 | 3.0721 | 2.4432 | 1.7066 | 0.92864 | 0.016389 | -0.97348 | -3.9562 | -7.7081 | -11.1695 | -13.5198
|  | HOEFORD | CT |  |  | 7.3686 | 6.9579 | 6.5692 | 6.1112 | 5.5962 | 5.0821 | 4.5108 | 3.9123 | 3.2643 | 2.2739 | -0.98857 | -6.4573 | -10.8675 | -13.6863 | 6.8005 | 6.6428 | 6.4938 | 6.2904 | 6.0727 | 5.8702 | 5.5692 | 5.1302 | 4.6391 | 3.9577 | 1.7482 | -1.4056 | -4.0423 | -6.5733 | 4.8257 | 4.6092 | 4.3787 | 4.0224 | 3.5959 | 3.1459 | 2.5976 | 2.0202 | 1.3867 | 0.43776 | -2.6738 | -7.4464 | -11.1695 | -13.5198
|  | HOEFORD | LW |  |  | 7.2391 | 6.7455 | 6.218 | 5.7012 | 4.9893 | 4.2707 | 3.4877 | 2.6659 | 1.714 | 0.69195 | -2.4659 | -6.7084 | -9.3822 | -11.3422 | 6.8127 | 6.6516 | 6.4886 | 6.2892 | 6.0642 | 5.743 | 5.2484 | 4.723 | 4.0941 | 3.3975 | 1.3516 | -0.94499 | -2.2383 | -3.2285 | 4.8367 | 4.4865 | 4.0859 | 3.673 | 3.0721 | 2.4432 | 1.7066 | 0.92864 | 0.016389 | -0.97348 | -3.9562 | -7.7081 | -9.9547 | -11.5719
|  | HOEFORD | ST |  |  | 7.5547 | 7.3127 | 7.1004 | 6.8984 | 6.651 | 6.4143 | 6.143 | 5.8629 | 5.5437 | 5.1981 | 3.7802 | -0.42737 | -3.2074 | -5.2407 | 6.8711 | 6.7598 | 6.6629 | 6.54 | 6.388 | 6.2542 | 6.0991 | 5.9452 | 5.7645 | 5.5606 | 4.5279 | 1.1492 | -1.1115 | -3.3584 | 4.9135 | 4.7546 | 4.6201 | 4.4764 | 4.3119 | 4.1608 | 3.9851 | 3.8061 | 3.576 | 3.2406 | 1.7115 | -2.2819 | -4.5905 | -6.2453
|  | HOEFORD | SP |  |  | 7.5825 | 7.3446 | 7.1433 | 6.9522 | 6.7599 | 6.5849 | 6.3921 | 6.1917 | 5.9794 | 5.7233 | 4.7592 | 1.7325 | -0.97005 | -2.4904 | 6.8748 | 6.7633 | 6.6674 | 6.5472 | 6.4135 | 6.3021 | 6.1782 | 6.058 | 5.9296 | 5.7796 | 5.078 | 2.0417 | -1.4374 | -5.4745 | 4.9191 | 4.7608 | 4.6291 | 4.4904 | 4.35 | 4.2289 | 4.0942 | 3.9599 | 3.815 | 3.6563 | 2.8123 | -0.17436 | -2.7125 | -3.9118
MANNINGTON GSP | LYTCHETT | HOLES BAY | MINIMUM HEADROOM | SZ 00725 91955 | YES | 11.0073 | 10.8504 | 10.6697 | 10.4749 | 10.2255 | 9.9591 | 9.672 | 9.3644 | 8.9988 | 8.6063 | 7.3884 | 5.7865 | 4.9823 | 4.2954 | 16.5081 | 16.3888 | 16.2438 | 16.0882 | 15.9407 | 15.7809 | 15.6035 | 15.4126 | 15.1767 | 14.9202 | 14.118 | 13.191 | 12.9232 | 12.5467 | 12.2677 | 12.1302 | 11.9701 | 11.7959 | 11.6126 | 11.4128 | 11.1903 | 10.9488 | 10.6486 | 10.3204 | 9.2855 | 8.0302 | 7.6349 | 7.3597
|  | HOLES BAY | CT |  |  | 11.0399 | 10.9118 | 10.7595 | 10.5892 | 10.4047 | 10.2089 | 10.0014 | 9.7813 | 9.5298 | 9.1791 | 8.104 | 6.1699 | 4.9823 | 4.2954 | 16.5081 | 16.3916 | 16.252 | 16.0993 | 15.9653 | 15.8236 | 15.6733 | 15.5156 | 15.3342 | 15.1177 | 14.4511 | 13.4068 | 12.9232 | 12.5467 | 12.2704 | 12.1469 | 11.9992 | 11.8347 | 11.6788 | 11.5124 | 11.3346 | 11.1459 | 10.9256 | 10.6511 | 9.8008 | 8.4185 | 7.7794 | 7.3979
|  | HOLES BAY | LW |  |  | 11.0073 | 10.8504 | 10.6697 | 10.4749 | 10.2255 | 9.9591 | 9.672 | 9.3644 | 8.9988 | 8.6063 | 7.3884 | 5.7865 | 5.1218 | 4.6807 | 16.5123 | 16.3888 | 16.2438 | 16.0882 | 15.9407 | 15.7809 | 15.6035 | 15.4126 | 15.1767 | 14.9202 | 14.118 | 13.191 | 12.9393 | 12.7646 | 12.2677 | 12.1302 | 11.9701 | 11.7959 | 11.6126 | 11.4128 | 11.1903 | 10.9488 | 10.6486 | 10.3204 | 9.2855 | 8.0302 | 7.6349 | 7.3597
|  | HOLES BAY | ST |  |  | 11.1071 | 11.0208 | 10.9215 | 10.8163 | 10.7175 | 10.6111 | 10.4968 | 10.3752 | 10.2305 | 10.0576 | 9.3724 | 7.6582 | 6.5716 | 5.9893 | 16.5544 | 16.4662 | 16.3635 | 16.2564 | 16.1673 | 16.0727 | 15.9719 | 15.8663 | 15.7419 | 15.6021 | 15.0507 | 13.7681 | 13.0377 | 12.6585 | 12.3299 | 12.2429 | 12.1426 | 12.0363 | 11.9415 | 11.839 | 11.7284 | 11.6104 | 11.467 | 11.3012 | 10.6365 | 9.0382 | 8.1502 | 7.7781
|  | HOLES BAY | SP |  |  | 11.117 | 11.0355 | 10.9413 | 10.8453 | 10.7638 | 10.679 | 10.5931 | 10.5026 | 10.4029 | 10.2881 | 9.8876 | 8.7273 | 7.6499 | 7.1962 | 16.5583 | 16.4719 | 16.3706 | 16.2682 | 16.1905 | 16.1106 | 16.0299 | 15.9467 | 15.8574 | 15.7599 | 15.4223 | 14.473 | 13.5073 | 12.9204 | 12.3362 | 12.2522 | 12.1548 | 12.0557 | 11.9757 | 11.8925 | 11.8079 | 11.7187 | 11.6202 | 11.5121 | 11.1332 | 10.0187 | 8.9753 | 8.5898
MELKSHAM GSP | FROME BSP | HOLWELL | MINIMUM HEADROOM | ST 72191 44633 | YES | 3.7457 | 3.5214 | 3.3156 | 3.1993 | 3.0592 | 2.9187 | 2.775 | 2.5669 | 2.3633 | 2.1775 | 1.678 | 0.17802 | -0.22245 | -0.44803 | 6.3164 | 6.2581 | 6.2025 | 6.1646 | 6.1187 | 6.0709 | 6.0186 | 5.9097 | 5.8296 | 5.7418 | 5.4874 | 4.9683 | 4.751 | 4.6336 | 4.3245 | 4.1248 | 3.9412 | 3.8356 | 3.7082 | 3.5802 | 3.4486 | 3.2563 | 3.0669 | 2.8937 | 2.4802 | 1.1307 | 0.76849 | 0.56875
|  | HOLWELL | CT |  |  | 4.0186 | 3.9283 | 3.8405 | 3.7771 | 3.6965 | 3.615 | 3.5256 | 3.3725 | 3.2483 | 3.0921 | 2.7391 | 2.2817 | 2.0195 | 1.9038 | 6.3747 | 6.3461 | 6.3159 | 6.292 | 6.2608 | 6.2307 | 6.1944 | 6.1047 | 6.0525 | 5.9834 | 5.7938 | 5.533 | 5.4439 | 5.3623 | 4.5631 | 4.481 | 4.4011 | 4.3416 | 4.2669 | 4.1913 | 4.1082 | 3.9651 | 3.8485 | 3.6996 | 3.3648 | 2.9613 | 2.7313 | 2.6295
|  | HOLWELL | LW |  |  | 3.7457 | 3.5214 | 3.3156 | 3.1993 | 3.0592 | 2.9187 | 2.775 | 2.5669 | 2.3633 | 2.1775 | 1.751 | 1.3434 | 1.262 | 1.1866 | 6.3164 | 6.2581 | 6.2025 | 6.1646 | 6.1187 | 6.0709 | 6.0186 | 5.9097 | 5.8296 | 5.7418 | 5.4874 | 5.2427 | 5.2089 | 5.1828 | 4.3245 | 4.1248 | 3.9412 | 3.8356 | 3.7082 | 3.5802 | 3.4486 | 3.2563 | 3.0669 | 2.8937 | 2.5055 | 2.1365 | 2.0641 | 1.9979
|  | HOLWELL | ST |  |  | 4.0422 | 3.97 | 3.8953 | 3.8128 | 3.6918 | 3.5691 | 3.4445 | 3.2683 | 3.1538 | 3.0723 | 2.7481 | 2.3245 | 2.1292 | 2.0202 | 6.3876 | 6.368 | 6.3489 | 6.3271 | 6.2951 | 6.2618 | 6.2262 | 6.1394 | 6.0932 | 6.0467 | 5.8815 | 5.5908 | 5.4627 | 5.4211 | 4.5861 | 4.5218 | 4.4551 | 4.3806 | 4.2725 | 4.1627 | 4.0508 | 3.8907 | 3.7859 | 3.7103 | 3.4048 | 3.0081 | 2.8325 | 2.7363
|  | HOLWELL | SP |  |  | 4.0833 | 4.0318 | 3.9776 | 3.9244 | 3.7198 | 3.5143 | 3.31 | 3.05 | 2.827 | 2.5471 | 1.678 | 0.17802 | -0.22245 | -0.44803 | 6.396 | 6.3816 | 6.3671 | 6.3514 | 6.3025 | 6.2522 | 6.2022 | 6.0998 | 6.0347 | 5.9534 | 5.6983 | 4.9683 | 4.751 | 4.6336 | 4.6224 | 4.5762 | 4.5274 | 4.4795 | 4.2985 | 4.1166 | 3.9359 | 3.7031 | 3.5048 | 3.2561 | 2.4802 | 1.1307 | 0.76849 | 0.56875
MANNINGTON GSP | SALISBURY | HOMINGTON | MINIMUM HEADROOM | SU 11742 26037 | YES | 9.3264 | 9.2287 | 9.0039 | 8.756 | 8.4279 | 8.0914 | 7.7485 | 7.3716 | 6.86 | 6.4027 | 5.3341 | 4.1545 | 3.9404 | 3.8111 | 11.1617 | 11.1116 | 11.0527 | 10.9813 | 10.896 | 10.797 | 10.6794 | 10.543 | 10.352 | 10.1409 | 9.469 | 8.5667 | 8.4789 | 8.4263 | 9.766 | 9.5618 | 9.3427 | 9.1164 | 8.8179 | 8.5113 | 8.1969 | 7.8518 | 7.3903 | 6.9742 | 5.9761 | 4.9024 | 4.7117 | 4.5971
|  | HOMINGTON | CT |  |  | 9.3372 | 9.2604 | 9.1712 | 9.0648 | 8.9426 | 8.8082 | 8.613 | 8.3377 | 8.0134 | 7.6037 | 6.765 | 5.4474 | 4.7205 | 4.4185 | 11.1617 | 11.1116 | 11.0527 | 10.9815 | 10.9036 | 10.8174 | 10.7212 | 10.6129 | 10.4706 | 10.3034 | 9.7966 | 9.0352 | 8.8781 | 8.7736 | 9.9465 | 9.8447 | 9.7278 | 9.5934 | 9.411 | 9.2189 | 9.0053 | 8.7623 | 8.4791 | 8.1218 | 7.3285 | 6.0698 | 5.4052 | 5.1382
|  | HOMINGTON | LW |  |  | 9.3264 | 9.2287 | 9.0039 | 8.756 | 8.4279 | 8.0914 | 7.7485 | 7.3716 | 6.86 | 6.4027 | 5.3341 | 4.1545 | 3.9404 | 3.8111 | 11.172 | 11.1164 | 11.0535 | 10.9813 | 10.896 | 10.797 | 10.6794 | 10.543 | 10.352 | 10.1409 | 9.469 | 8.5667 | 8.4789 | 8.4263 | 9.766 | 9.5618 | 9.3427 | 9.1164 | 8.8179 | 8.5113 | 8.1969 | 7.8518 | 7.3903 | 6.9742 | 5.9761 | 4.9024 | 4.7117 | 4.5971
|  | HOMINGTON | ST |  |  | 9.4091 | 9.3741 | 9.3363 | 9.2914 | 9.2288 | 9.1549 | 9.0717 | 8.9779 | 8.8389 | 8.6465 | 7.8052 | 6.3128 | 5.5663 | 5.4527 | 11.2101 | 11.1881 | 11.1639 | 11.1345 | 11.0955 | 11.0485 | 10.9948 | 10.9336 | 10.8408 | 10.73 | 10.2561 | 9.1356 | 8.638 | 8.5669 | 10.0292 | 9.974 | 9.9141 | 9.8445 | 9.7366 | 9.6196 | 9.4989 | 9.3662 | 9.2016 | 9.0225 | 8.2828 | 7.0942 | 6.5009 | 6.2488
|  | HOMINGTON | SP |  |  | 9.4175 | 9.3865 | 9.3565 | 9.3206 | 9.2666 | 9.2134 | 9.1524 | 9.0818 | 8.9721 | 8.7609 | 8.0265 | 6.273 | 5.1907 | 4.6286 | 11.2133 | 11.1929 | 11.1728 | 11.1488 | 11.1178 | 11.0872 | 11.051 | 11.0084 | 10.9519 | 10.8855 | 10.6342 | 9.8409 | 9.1461 | 8.9534 | 10.0624 | 10.0202 | 9.9748 | 9.9308 | 9.8123 | 9.6973 | 9.5787 | 9.4471 | 9.3095 | 9.1166 | 8.4495 | 6.8558 | 5.8431 | 5.3261
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK | MINIMUM HEADROOM | SU 72602 53780 | YES | 15.7381 | 15.2049 | 14.6588 | 14.0746 | 13.1904 | 12.271 | 11.266 | 10.1397 | 8.7247 | 7.407 | 4.3127 | 0.44758 | -0.93516 | -2.2954 | 20.458 | 20.1201 | 19.7808 | 19.41 | 18.8978 | 18.3672 | 17.764 | 17.0687 | 16.137 | 15.2959 | 13.4955 | 11.3278 | 9.4142 | 7.7846 | 15.7147 | 15.199 | 14.6789 | 14.1205 | 13.2911 | 12.4335 | 11.4897 | 10.4269 | 9.0772 | 7.8283 | 4.9541 | 1.39 | 0.13028 | -1.1544
|  | HOOK | CT |  |  | 15.9862 | 15.6154 | 15.1942 | 14.7545 | 14.1597 | 13.5386 | 12.8838 | 12.1164 | 11.2273 | 9.9368 | 7.0511 | 2.1469 | -0.93516 | -2.2954 | 20.4995 | 20.2014 | 19.8693 | 19.5196 | 19.1079 | 18.6814 | 18.2163 | 17.6602 | 17.0029 | 16.1309 | 14.3111 | 11.3829 | 9.4142 | 7.7846 | 15.9215 | 15.5514 | 15.137 | 14.704 | 14.1339 | 13.5442 | 12.9188 | 12.1826 | 11.3267 | 10.0987 | 7.4115 | 2.9404 | 0.13028 | -1.1544
|  | HOOK | LW |  |  | 15.7381 | 15.2049 | 14.6588 | 14.0746 | 13.1904 | 12.271 | 11.266 | 10.1397 | 8.7247 | 7.407 | 4.3127 | 0.44758 | -0.74279 | -1.3171 | 20.458 | 20.1201 | 19.7808 | 19.41 | 18.8978 | 18.3672 | 17.764 | 17.0687 | 16.137 | 15.2959 | 13.4955 | 11.3278 | 10.7485 | 10.4648 | 15.7147 | 15.199 | 14.6789 | 14.1205 | 13.2911 | 12.4335 | 11.4897 | 10.4269 | 9.0772 | 7.8283 | 4.9541 | 1.39 | 0.31191 | -0.22707
|  | HOOK | ST |  |  | 16.3472 | 16.1651 | 15.9625 | 15.7295 | 15.4189 | 15.0932 | 14.7443 | 14.3477 | 13.8805 | 13.3815 | 11.0398 | 7.0883 | 4.9666 | 3.7679 | 20.7677 | 20.608 | 20.4377 | 20.2405 | 19.9975 | 19.7468 | 19.4719 | 19.1556 | 18.7792 | 18.404 | 16.5882 | 13.5298 | 11.7027 | 10.1206 | 16.2765 | 16.0874 | 15.8861 | 15.6542 | 15.3498 | 15.0364 | 14.6993 | 14.3154 | 13.8626 | 13.3836 | 11.1168 | 7.3559 | 5.3993 | 4.3265
|  | HOOK | SP |  |  | 16.3874 | 16.2324 | 16.0703 | 15.9046 | 15.5781 | 15.2586 | 14.929 | 14.5467 | 14.1294 | 13.6331 | 11.8213 | 7.2768 | 4.776 | 3.6267 | 20.7801 | 20.6302 | 20.4766 | 20.3172 | 20.0885 | 19.8687 | 19.6344 | 19.3533 | 19.0387 | 18.6868 | 17.3431 | 13.7599 | 11.3507 | 9.2223 | 16.306 | 16.1467 | 15.9839 | 15.8164 | 15.504 | 15.2047 | 14.8946 | 14.5324 | 14.1367 | 13.6684 | 11.9514 | 7.6106 | 5.2633 | 4.2137
LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR | MINIMUM HEADROOM | TQ 12710 72057 | YES | 9.4978 | 9.3858 | 9.248 | 9.0948 | 8.8848 | 8.6596 | 8.4293 | 8.1828 | 7.9008 | 7.6185 | 6.6043 | 4.0357 | 0.82444 | -1.9126 | 10.9133 | 10.8525 | 10.7733 | 10.6853 | 10.5746 | 10.4529 | 10.3254 | 10.1869 | 10.0274 | 9.8624 | 9.2763 | 7.6692 | 5.7605 | 3.7838 | 9.9578 | 9.8648 | 9.7477 | 9.6164 | 9.4346 | 9.2393 | 9.0377 | 8.8209 | 8.5711 | 8.3187 | 7.4223 | 5.2719 | 2.6528 | 0.42703
|  | HOPE AND ANCHOR | CT |  |  | 9.5326 | 9.439 | 9.3323 | 9.1933 | 9.0246 | 8.8419 | 8.6522 | 8.4503 | 8.2341 | 7.9536 | 6.933 | 4.0447 | 0.82444 | -1.9126 | 10.9202 | 10.8606 | 10.7945 | 10.7025 | 10.6005 | 10.489 | 10.3702 | 10.2429 | 10.103 | 9.9286 | 9.2951 | 7.6692 | 5.7605 | 3.7838 | 9.9884 | 9.9115 | 9.8233 | 9.704 | 9.5587 | 9.401 | 9.2359 | 9.0597 | 8.8694 | 8.62 | 7.7216 | 5.2965 | 2.6528 | 0.42703
|  | HOPE AND ANCHOR | LW |  |  | 9.4978 | 9.3858 | 9.248 | 9.0948 | 8.8848 | 8.6596 | 8.4293 | 8.1828 | 7.9008 | 7.6185 | 6.6043 | 4.0357 | 1.3144 | -1.1122 | 10.9133 | 10.8525 | 10.7733 | 10.6853 | 10.5746 | 10.4529 | 10.3254 | 10.1869 | 10.0274 | 9.8624 | 9.2763 | 7.9214 | 6.5382 | 5.2778 | 9.9578 | 9.8648 | 9.7477 | 9.6164 | 9.4346 | 9.2393 | 9.0377 | 8.8209 | 8.5711 | 8.3187 | 7.4223 | 5.2719 | 3.0648 | 1.1085
|  | HOPE AND ANCHOR | ST |  |  | 9.58 | 9.5247 | 9.465 | 9.401 | 9.315 | 9.2208 | 9.1287 | 9.0288 | 8.9219 | 8.8155 | 8.3534 | 6.5319 | 4.5094 | 2.7314 | 10.9516 | 10.9147 | 10.8745 | 10.8306 | 10.7679 | 10.6991 | 10.6302 | 10.5545 | 10.4725 | 10.3892 | 10.0301 | 8.7211 | 7.2136 | 5.5958 | 10.033 | 9.9919 | 9.947 | 9.898 | 9.828 | 9.7507 | 9.6743 | 9.5908 | 9.5005 | 9.41 | 9.018 | 7.5113 | 5.8584 | 4.3936
|  | HOPE AND ANCHOR | SP |  |  | 9.5877 | 9.5327 | 9.4759 | 9.4142 | 9.3487 | 9.2795 | 9.2053 | 9.1295 | 9.0491 | 8.9637 | 8.6039 | 7.1532 | 5.3081 | 3.6119 | 10.9548 | 10.9152 | 10.8737 | 10.8272 | 10.778 | 10.7245 | 10.6631 | 10.5994 | 10.5291 | 10.4411 | 10.0737 | 8.7629 | 6.8621 | 4.4177 | 10.0402 | 9.9988 | 9.9563 | 9.909 | 9.8585 | 9.8049 | 9.7452 | 9.684 | 9.6183 | 9.5471 | 9.2497 | 8.055 | 6.4612 | 5.0775
LOVEDEAN GSP | HAVANT | HORNDEAN | MINIMUM HEADROOM | SU 70271 12802 | YES | 7.602 | 6.6701 | 5.5457 | 4.466 | 2.8486 | 1.1419 | -0.70435 | -2.7576 | -5.2512 | -7.6405 | -13.1148 | -20.0916 | -26.0636 | -29.8858 | 8.548 | 7.943 | 7.2061 | 6.4799 | 5.5382 | 4.5303 | 3.3938 | 2.0923 | 0.3867 | -1.2039 | -4.2767 | -8.5738 | -12.641 | -16.3776 | 2.4452 | 1.6479 | 0.64731 | -0.3414 | -1.8125 | -3.3683 | -5.063 | -6.9563 | -9.2865 | -11.5106 | -16.4416 | -22.653 | -27.7071 | -30.9477
|  | HORNDEAN | CT |  |  | 7.8877 | 7.1588 | 6.2802 | 5.336 | 4.2061 | 3.0078 | 1.7288 | 0.25605 | -1.4223 | -4.0807 | -10.0146 | -19.0805 | -26.0636 | -29.8858 | 8.5801 | 8.0248 | 7.3739 | 6.6271 | 5.8488 | 5.0179 | 4.1086 | 3.0371 | 1.7802 | 0.018054 | -3.5772 | -8.5738 | -12.641 | -16.3776 | 2.7121 | 2.0811 | 1.2935 | 0.41789 | -0.61849 | -1.719 | -2.8995 | -4.266 | -5.8339 | -8.2016 | -13.5266 | -21.6787 | -27.7071 | -30.9477
|  | HORNDEAN | LW |  |  | 7.602 | 6.6701 | 5.5457 | 4.466 | 2.8486 | 1.1419 | -0.70435 | -2.7576 | -5.2512 | -7.6405 | -13.1148 | -20.0916 | -23.6935 | -25.8443 | 8.548 | 7.943 | 7.2061 | 6.4799 | 5.5382 | 4.5303 | 3.3938 | 2.0923 | 0.3867 | -1.2039 | -4.2767 | -7.869 | -9.4583 | -10.4755 | 2.4452 | 1.6479 | 0.64731 | -0.3414 | -1.8125 | -3.3683 | -5.063 | -6.9563 | -9.2865 | -11.5106 | -16.4416 | -22.653 | -25.7068 | -27.4834
|  | HORNDEAN | ST |  |  | 8.3403 | 7.9355 | 7.4574 | 7.0213 | 6.4898 | 5.9213 | 5.3025 | 4.6031 | 3.8211 | 3.0062 | -0.8899 | -7.4541 | -11.2383 | -14.02 | 8.9299 | 8.6112 | 8.2408 | 7.8799 | 7.4477 | 6.9832 | 6.4681 | 5.8814 | 5.2157 | 4.5643 | 1.4016 | -3.6472 | -6.8434 | -10.2399 | 3.1065 | 2.7786 | 2.4057 | 2.0339 | 1.5513 | 1.0339 | 0.46664 | -0.17674 | -0.90065 | -1.6483 | -5.1643 | -11.0846 | -14.362 | -16.7199
|  | HORNDEAN | SP |  |  | 8.3933 | 7.9972 | 7.5674 | 7.2024 | 6.7669 | 6.3209 | 5.8306 | 5.2662 | 4.6583 | 3.9518 | 1.2506 | -5.8844 | -9.4169 | -11.3531 | 8.9462 | 8.6145 | 8.263 | 7.939 | 7.596 | 7.2377 | 6.8395 | 6.362 | 5.8387 | 5.2222 | 2.7677 | -3.6508 | -8.4667 | -14.4275 | 3.1546 | 2.8365 | 2.5068 | 2.1984 | 1.8119 | 1.4162 | 0.97789 | 0.4674 | -0.084552 | -0.72806 | -3.2122 | -9.6634 | -12.8369 | -14.4626
NURSLING GSP | WINCHESTER | HOUGHTON | MINIMUM HEADROOM | SU 33784 31741 | YES | 7.2327 | 6.8481 | 6.4588 | 6.0646 | 5.5477 | 5.017 | 4.4779 | 3.8893 | 3.2137 | 2.5906 | 0.98497 | -0.57825 | -0.74945 | -0.78585 | 10.3275 | 10.2583 | 10.1928 | 10.1257 | 10.0447 | 9.9552 | 9.7873 | 9.4866 | 9.116 | 8.791 | 8.0815 | 7.389 | 7.3004 | 7.1977 | 9.0488 | 8.7229 | 8.3993 | 8.076 | 7.6464 | 7.2077 | 6.7707 | 6.2986 | 5.7683 | 5.26 | 3.8195 | 2.3826 | 2.2253 | 2.1916
|  | HOUGHTON | CT |  |  | 7.6426 | 7.4575 | 7.2621 | 7.0632 | 6.7702 | 6.465 | 6.1389 | 5.78 | 5.4083 | 4.8725 | 3.626 | 1.8057 | 1.4163 | 1.3115 | 10.3389 | 10.2771 | 10.2192 | 10.1596 | 10.0952 | 10.0239 | 9.9474 | 9.8615 | 9.7731 | 9.5694 | 8.9494 | 8.1208 | 7.8572 | 7.6605 | 9.334 | 9.2369 | 9.1413 | 8.9979 | 8.7657 | 8.526 | 8.2764 | 8.0096 | 7.7346 | 7.2715 | 6.1705 | 4.5612 | 4.2112 | 4.1159
|  | HOUGHTON | LW |  |  | 7.2327 | 6.8481 | 6.4588 | 6.0646 | 5.5477 | 5.017 | 4.4779 | 3.8893 | 3.2137 | 2.5906 | 0.98497 | -0.57825 | -0.74945 | -0.78585 | 10.3275 | 10.2583 | 10.1928 | 10.1257 | 10.0447 | 9.9552 | 9.7873 | 9.4866 | 9.116 | 8.791 | 8.0815 | 7.389 | 7.3004 | 7.2746 | 9.0488 | 8.7229 | 8.3993 | 8.076 | 7.6464 | 7.2077 | 6.7707 | 6.2986 | 5.7683 | 5.26 | 3.8195 | 2.3826 | 2.2253 | 2.1916
|  | HOUGHTON | ST |  |  | 7.751 | 7.6303 | 7.511 | 7.3845 | 7.1941 | 7.0008 | 6.8038 | 6.5924 | 6.3662 | 6.1183 | 5.1515 | 3.7308 | 2.9233 | 2.3911 | 10.3774 | 10.339 | 10.3091 | 10.2791 | 10.2431 | 10.2046 | 10.1612 | 10.1121 | 10.0537 | 9.9804 | 9.6863 | 8.8855 | 8.4525 | 8.1079 | 9.3826 | 9.3154 | 9.2552 | 9.1946 | 9.0474 | 8.8941 | 8.7401 | 8.5778 | 8.4066 | 8.2088 | 7.5121 | 6.2445 | 5.5487 | 5.0783
|  | HOUGHTON | SP |  |  | 7.7974 | 7.707 | 7.621 | 7.5358 | 7.2818 | 7.0306 | 6.772 | 6.5017 | 6.2247 | 5.8619 | 4.6769 | 2.1717 | 0.66701 | -0.28082 | 10.3795 | 10.3436 | 10.3176 | 10.2923 | 10.2584 | 10.2262 | 10.189 | 10.1496 | 10.1074 | 10.0504 | 9.7531 | 8.3784 | 7.656 | 7.1977 | 9.4047 | 9.3519 | 9.3075 | 9.2646 | 9.1138 | 8.8984 | 8.6796 | 8.4558 | 8.2276 | 7.9235 | 6.9656 | 4.9125 | 3.5376 | 2.6666
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS | MINIMUM HEADROOM | SU 62187 52886 | YES | 23.1919 | 22.9742 | 22.3353 | 21.4234 | 20.1867 | 19.1447 | 18.0717 | 16.8916 | 15.5101 | 14.0576 | 9.5983 | 6.7216 | 5.3212 | 4.5591 | 24.6722 | 24.5564 | 24.229 | 23.8118 | 23.2466 | 22.6468 | 22.0267 | 21.3501 | 20.5431 | 19.6829 | 17.3234 | 15.4811 | 14.1127 | 12.8512 | 24.2314 | 24.1188 | 23.7385 | 22.9991 | 21.8368 | 20.8483 | 19.8221 | 18.6837 | 17.3206 | 15.8764 | 11.9579 | 9.3568 | 8.0562 | 7.3438
|  | HOUNDMILLS | CT |  |  | 23.2824 | 23.122 | 22.5509 | 21.6859 | 20.5858 | 19.6845 | 18.7611 | 17.7428 | 16.5699 | 15.1474 | 10.6008 | 7.1105 | 5.3212 | 4.5591 | 24.6866 | 24.5826 | 24.2703 | 23.8578 | 23.3413 | 22.7865 | 22.2184 | 21.6018 | 20.889 | 20.0349 | 17.5967 | 15.4811 | 14.1127 | 12.8512 | 24.2314 | 24.1188 | 23.7443 | 23.2227 | 22.1812 | 21.3172 | 20.4274 | 19.4416 | 18.2917 | 16.8812 | 12.9128 | 9.7234 | 8.0562 | 7.3438
|  | HOUNDMILLS | LW |  |  | 23.1919 | 22.9742 | 22.3353 | 21.4234 | 20.1867 | 19.1447 | 18.0717 | 16.8916 | 15.5101 | 14.0576 | 9.5983 | 6.7216 | 5.8883 | 5.5968 | 24.6722 | 24.5564 | 24.229 | 23.8118 | 23.2466 | 22.6468 | 22.0267 | 21.3501 | 20.5431 | 19.6829 | 17.3234 | 15.7741 | 15.3662 | 15.2137 | 24.2416 | 24.1221 | 23.7385 | 22.9991 | 21.8368 | 20.8483 | 19.8221 | 18.6837 | 17.3206 | 15.8764 | 11.9579 | 9.3568 | 8.5956 | 8.3295
|  | HOUNDMILLS | ST |  |  | 23.3757 | 23.2911 | 22.9402 | 22.4469 | 21.805 | 21.2877 | 20.7644 | 20.1995 | 19.5467 | 18.8417 | 16.211 | 13.3519 | 12.1027 | 11.4319 | 24.7432 | 24.6811 | 24.452 | 24.1797 | 23.8445 | 23.5611 | 23.2283 | 22.8209 | 22.3528 | 21.858 | 20.1788 | 18.1968 | 16.9448 | 15.7075 | 24.2949 | 24.2243 | 23.9082 | 23.5158 | 23.0456 | 22.662 | 22.2806 | 21.8317 | 21.1784 | 20.49 | 18.1369 | 15.5473 | 14.4108 | 13.7956
|  | HOUNDMILLS | SP |  |  | 23.3933 | 23.3176 | 22.9897 | 22.5417 | 21.9991 | 21.565 | 21.1184 | 20.6473 | 20.1287 | 19.5689 | 17.6684 | 15.2093 | 13.8685 | 13.4151 | 24.7484 | 24.6883 | 24.4665 | 24.209 | 23.9168 | 23.6695 | 23.4156 | 23.077 | 22.6796 | 22.2388 | 20.8173 | 18.915 | 17.0457 | 14.7959 | 24.2981 | 24.23 | 23.9195 | 23.5375 | 23.1041 | 22.7526 | 22.3981 | 22.0404 | 21.6482 | 21.2375 | 19.4267 | 17.1314 | 15.9302 | 15.5535
BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD | MINIMUM HEADROOM | SU 34066 68957 | YES | 2.5128 | 2.313 | 2.1192 | 1.8338 | 1.3801 | 0.82685 | 0.22634 | -0.40138 | -1.1049 | -1.8641 | -4.0079 | -6.574 | -7.2965 | -7.6295 | 3.5479 | 3.3829 | 3.2178 | 3.045 | 2.7926 | 2.5134 | 2.2169 | 1.9001 | 1.5194 | 1.1137 | 0.085638 | -1.0623 | -1.6102 | -2.0497 | 1.3283 | 1.0181 | 0.71316 | 0.40097 | -0.081331 | -0.5823 | -1.093 | -1.6324 | -2.2384 | -2.9093 | -4.8589 | -7.1554 | -7.7933 | -8.0856
|  | HUNGERFORD | CT |  |  | 2.6719 | 2.5928 | 2.4974 | 2.3898 | 2.212 | 2.0248 | 1.8311 | 1.5143 | 1.1182 | 0.45988 | -1.4116 | -4.8223 | -6.8742 | -7.0833 | 3.6186 | 3.5709 | 3.4751 | 3.3565 | 3.1875 | 2.9981 | 2.7975 | 2.5765 | 2.3328 | 1.9564 | 0.97778 | -0.60068 | -1.6102 | -2.0497 | 1.6357 | 1.5048 | 1.3665 | 1.2102 | 0.93739 | 0.65233 | 0.35671 | 0.034803 | -0.30461 | -0.87589 | -2.6135 | -5.603 | -7.4104 | -7.5954
|  | HUNGERFORD | LW |  |  | 2.5128 | 2.313 | 2.1192 | 1.8338 | 1.3801 | 0.82685 | 0.22634 | -0.40138 | -1.1049 | -1.8641 | -4.0079 | -6.574 | -7.2965 | -7.6295 | 3.5479 | 3.3829 | 3.2178 | 3.045 | 2.7926 | 2.5134 | 2.2169 | 1.9001 | 1.5194 | 1.1137 | 0.085638 | -1.0623 | -1.3626 | -1.5012 | 1.3283 | 1.0181 | 0.71316 | 0.40097 | -0.081331 | -0.5823 | -1.093 | -1.6324 | -2.2384 | -2.9093 | -4.8589 | -7.1554 | -7.7933 | -8.0856
|  | HUNGERFORD | ST |  |  | 2.7175 | 2.6727 | 2.6108 | 2.5454 | 2.4459 | 2.3406 | 2.2307 | 2.1156 | 1.9883 | 1.8328 | 0.93003 | -1.0227 | -2.2511 | -3.1516 | 3.6519 | 3.6287 | 3.6018 | 3.5355 | 3.4386 | 3.3354 | 3.2258 | 3.1093 | 2.9678 | 2.8138 | 2.1862 | 0.93178 | 0.18724 | -0.50082 | 1.686 | 1.6021 | 1.5117 | 1.4107 | 1.2558 | 1.0942 | 0.92915 | 0.75689 | 0.56904 | 0.34581 | -0.47635 | -2.2956 | -3.3517 | -4.1011
|  | HUNGERFORD | SP |  |  | 2.7193 | 2.6872 | 2.6586 | 2.608 | 2.4474 | 2.2822 | 2.1152 | 1.8567 | 1.5855 | 1.2641 | 0.019356 | -2.6884 | -4.3944 | -5.4077 | 3.6525 | 3.6293 | 3.6125 | 3.5735 | 3.4374 | 3.2982 | 3.1543 | 3.0024 | 2.8425 | 2.6498 | 1.965 | 0.33672 | -0.84588 | -1.9266 | 1.7122 | 1.6454 | 1.5877 | 1.5135 | 1.2496 | 0.98054 | 0.70953 | 0.43188 | 0.14711 | -0.18862 | -1.2678 | -3.67 | -5.2133 | -6.1099
LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON | MINIMUM HEADROOM | SU 86949 02632 | YES | 9.819 | 9.5652 | 9.3526 | 9.1403 | 8.9213 | 8.6798 | 8.3187 | 7.8683 | 7.1486 | 6.3376 | 3.6628 | 0.97344 | 0.061322 | -0.75298 | 17.0877 | 16.8752 | 16.7195 | 16.5466 | 16.3248 | 16.043 | 15.7397 | 15.4128 | 14.9889 | 14.5356 | 13.0793 | 11.6458 | 10.4694 | 9.3723 | 10.8181 | 10.5811 | 10.3928 | 10.2065 | 10.0193 | 9.8145 | 9.2664 | 8.6576 | 7.8711 | 7.0383 | 4.5854 | 2.264 | 1.4073 | 0.69479
|  | HUNSTON | CT |  |  | 9.819 | 9.5661 | 9.3636 | 9.1586 | 8.958 | 8.742 | 8.5103 | 8.2175 | 7.7897 | 7.2656 | 5.0907 | 1.8354 | 0.061322 | -0.75298 | 17.0877 | 16.8752 | 16.7195 | 16.566 | 16.4246 | 16.2625 | 16.0456 | 15.7884 | 15.4604 | 15.0341 | 13.5455 | 11.6458 | 10.4694 | 9.3723 | 10.8181 | 10.5811 | 10.3996 | 10.2169 | 10.0435 | 9.8581 | 9.6596 | 9.4443 | 9.0279 | 8.2458 | 5.8702 | 2.9712 | 1.4073 | 0.69479
|  | HUNSTON | LW |  |  | 9.8272 | 9.5652 | 9.3526 | 9.1403 | 8.9213 | 8.6798 | 8.3187 | 7.8683 | 7.1486 | 6.3376 | 3.6628 | 0.97344 | 0.3457 | -0.025932 | 17.0977 | 16.881 | 16.7202 | 16.5466 | 16.3248 | 16.043 | 15.7397 | 15.4128 | 14.9889 | 14.5356 | 13.0793 | 11.6625 | 11.3373 | 11.1678 | 10.8278 | 10.5836 | 10.3928 | 10.2065 | 10.0193 | 9.8145 | 9.2664 | 8.6576 | 7.8711 | 7.0383 | 4.5854 | 2.264 | 1.6298 | 1.3075
|  | HUNSTON | ST |  |  | 9.8957 | 9.6888 | 9.5488 | 9.4236 | 9.2964 | 9.158 | 9.0041 | 8.8306 | 8.5878 | 8.3125 | 7.0943 | 4.1605 | 2.8895 | 2.6501 | 17.1463 | 16.9684 | 16.8547 | 16.7556 | 16.6601 | 16.5598 | 16.4513 | 16.3303 | 16.1653 | 15.9832 | 15.2263 | 13.2282 | 12.2526 | 11.2323 | 10.89 | 10.6958 | 10.5656 | 10.4498 | 10.3326 | 10.206 | 10.0702 | 9.9189 | 9.7084 | 9.4752 | 8.5149 | 5.7011 | 4.4814 | 4.2553
|  | HUNSTON | SP |  |  | 9.9001 | 9.6974 | 9.5607 | 9.4403 | 9.3321 | 9.2172 | 9.0954 | 8.9614 | 8.7742 | 8.573 | 7.8499 | 5.9065 | 4.0743 | 3.6139 | 17.149 | 16.9737 | 16.8617 | 16.7653 | 16.6842 | 16.6016 | 16.5127 | 16.4164 | 16.288 | 16.1501 | 15.6117 | 13.9018 | 12.0592 | 9.9495 | 10.8939 | 10.703 | 10.5756 | 10.4638 | 10.3648 | 10.2604 | 10.1491 | 10.0287 | 9.8637 | 9.6895 | 9.0618 | 7.3849 | 5.6242 | 5.1859
BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT | MINIMUM HEADROOM | SU 39384 52476 | YES | 1.5138 | 1.2918 | 1.058 | 0.82133 | 0.49684 | 0.16723 | -0.17231 | -0.54854 | -1.0041 | -1.3901 | -2.2661 | -3.2508 | -3.455 | -3.5323 | 1.2352 | 1.1334 | 1.0209 | 0.9056 | 0.7509 | 0.59325 | 0.42436 | 0.22459 | -0.02782 | -0.23268 | -0.60792 | -1.0158 | -1.0948 | -1.1893 | 0.54483 | 0.35146 | 0.14249 | -0.07021 | -0.35844 | -0.65171 | -0.95961 | -1.3129 | -1.7462 | -2.1042 | -2.8386 | -3.6415 | -3.8039 | -3.8649
|  | HURSTBOURNE TARRANT | CT |  |  | 1.7259 | 1.6172 | 1.493 | 1.3611 | 1.1706 | 0.97512 | 0.7644 | 0.51345 | 0.23832 | -0.12063 | -0.77741 | -1.9182 | -2.6616 | -2.8222 | 1.3039 | 1.2393 | 1.1635 | 1.0817 | 0.976 | 0.86709 | 0.7489 | 0.60324 | 0.43914 | 0.22975 | -0.10698 | -0.64113 | -0.99877 | -1.1893 | 0.7118 | 0.61012 | 0.49312 | 0.36839 | 0.19201 | 0.01094 | -0.18437 | -0.41928 | -0.6785 | -1.0168 | -1.6121 | -2.5802 | -3.1748 | -3.3004
|  | HURSTBOURNE TARRANT | LW |  |  | 1.5138 | 1.2918 | 1.058 | 0.82133 | 0.49684 | 0.16723 | -0.17231 | -0.54854 | -1.0041 | -1.3901 | -2.2661 | -3.2508 | -3.455 | -3.5323 | 1.2352 | 1.1334 | 1.0209 | 0.9056 | 0.7509 | 0.59325 | 0.42436 | 0.22459 | -0.02782 | -0.23268 | -0.60792 | -1.0158 | -1.0948 | -1.1253 | 0.54483 | 0.35146 | 0.14249 | -0.07021 | -0.35844 | -0.65171 | -0.95961 | -1.3129 | -1.7462 | -2.1042 | -2.8386 | -3.6415 | -3.8039 | -3.8649
|  | HURSTBOURNE TARRANT | ST |  |  | 1.8184 | 1.7614 | 1.6989 | 1.6334 | 1.5182 | 1.4009 | 1.284 | 1.1544 | 1.0028 | 0.84796 | 0.17358 | -0.65257 | -1.0673 | -1.3363 | 1.3586 | 1.3251 | 1.2869 | 1.2461 | 1.1805 | 1.1132 | 1.0449 | 0.96733 | 0.87459 | 0.78686 | 0.37525 | -0.12906 | -0.39656 | -0.63107 | 0.79961 | 0.74751 | 0.68926 | 0.62827 | 0.52165 | 0.41301 | 0.30469 | 0.18386 | 0.041585 | -0.1019 | -0.7402 | -1.5049 | -1.8737 | -2.0967
|  | HURSTBOURNE TARRANT | SP |  |  | 1.8666 | 1.8222 | 1.7757 | 1.7309 | 1.6079 | 1.4856 | 1.3582 | 1.2223 | 1.0796 | 0.88391 | 0.21664 | -1.2829 | -2.1165 | -2.6701 | 1.3767 | 1.347 | 1.3148 | 1.2828 | 1.2182 | 1.1546 | 1.0886 | 1.0144 | 0.93598 | 0.83765 | 0.47798 | -0.38792 | -0.79585 | -1.0805 | 0.84156 | 0.80023 | 0.7565 | 0.71453 | 0.6025 | 0.49174 | 0.3784 | 0.25551 | 0.12683 | -0.047058 | -0.65738 | -2.0598 | -2.7645 | -3.219
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE | MINIMUM HEADROOM | SU 63055 50105 | YES | 19.2226 | 18.8455 | 18.3598 | 17.8405 | 17.0098 | 16.2049 | 15.347 | 14.4348 | 13.3813 | 12.2354 | 9.057 | 5.4512 | 3.2788 | 1.9573 | 22.5363 | 22.3027 | 21.9948 | 21.6657 | 21.1934 | 20.7704 | 20.3206 | 19.8463 | 19.3018 | 18.7025 | 17.009 | 15.0712 | 13.3346 | 11.9619 | 20.3071 | 19.9597 | 19.5152 | 19.0404 | 18.2794 | 17.5469 | 16.7681 | 15.9417 | 14.9484 | 13.8202 | 10.7828 | 7.441 | 5.747 | 4.5993
|  | JAYS CLOSE | CT |  |  | 19.3707 | 19.0898 | 18.7374 | 18.2869 | 17.6861 | 17.1223 | 16.5386 | 15.9272 | 15.2398 | 14.0915 | 10.882 | 6.235 | 3.2788 | 1.9573 | 22.5755 | 22.3675 | 22.0975 | 21.7776 | 21.3828 | 21.0429 | 20.6924 | 20.3292 | 19.9319 | 19.3508 | 17.6624 | 15.0712 | 13.3346 | 11.9619 | 20.4441 | 20.1858 | 19.8607 | 19.4516 | 18.9015 | 18.3904 | 17.8501 | 17.2459 | 16.5585 | 15.4701 | 12.4464 | 8.2198 | 5.747 | 4.5993
|  | JAYS CLOSE | LW |  |  | 19.2226 | 18.8455 | 18.3598 | 17.8405 | 17.0098 | 16.2049 | 15.347 | 14.4348 | 13.3813 | 12.2354 | 9.057 | 5.4512 | 4.188 | 3.7194 | 22.5363 | 22.3027 | 21.9948 | 21.6657 | 21.1934 | 20.7704 | 20.3206 | 19.8463 | 19.3018 | 18.7025 | 17.009 | 15.139 | 14.5734 | 14.3481 | 20.3071 | 19.9597 | 19.5152 | 19.0404 | 18.2794 | 17.5469 | 16.7681 | 15.9417 | 14.9484 | 13.8202 | 10.7828 | 7.441 | 6.3701 | 5.9771
|  | JAYS CLOSE | ST |  |  | 19.5817 | 19.4246 | 19.2094 | 18.9803 | 18.6668 | 18.4031 | 18.124 | 17.8253 | 17.4848 | 17.1113 | 15.5246 | 11.7128 | 9.853 | 8.7629 | 22.6857 | 22.5425 | 22.3466 | 22.1409 | 21.8818 | 21.6837 | 21.4787 | 21.2645 | 21.0264 | 20.7716 | 19.7641 | 17.3751 | 15.8478 | 14.494 | 20.6339 | 20.4871 | 20.286 | 20.0727 | 19.7826 | 19.5425 | 19.2896 | 19.0201 | 18.714 | 18.3728 | 16.7883 | 13.1288 | 11.4241 | 10.464
|  | JAYS CLOSE | SP |  |  | 19.6136 | 19.4552 | 19.2457 | 19.027 | 18.7563 | 18.541 | 18.3333 | 18.1038 | 17.858 | 17.5625 | 16.4881 | 13.3751 | 11.301 | 10.6049 | 22.6964 | 22.5515 | 22.3541 | 22.1491 | 21.9098 | 21.7342 | 21.5629 | 21.3823 | 21.1922 | 20.9781 | 20.2122 | 18.1725 | 16.2064 | 14.37 | 20.6624 | 20.5159 | 20.3208 | 20.1176 | 19.8651 | 19.6678 | 19.4779 | 19.2699 | 19.0485 | 18.781 | 17.7381 | 14.706 | 12.7183 | 12.0792
COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON | MINIMUM HEADROOM | SP 52881 01094 | NO | 11.2408 | 11.2232 | 11.2046 | 11.1821 | 11.1541 | 11.1209 | 11.0807 | 11.0333 | 10.9779 | 10.9079 | 10.6615 | 10.3195 | 10.1602 | 10.0297 | 9.2635 | 9.2546 | 9.245 | 9.2332 | 9.2185 | 9.2008 | 9.179 | 9.1531 | 9.1224 | 9.0839 | 8.9459 | 8.7147 | 8.6075 | 8.5065 | 8.8633 | 8.8447 | 8.8248 | 8.8012 | 8.7718 | 8.7373 | 8.6962 | 8.6483 | 8.5932 | 8.5238 | 8.2824 | 7.9576 | 7.8189 | 7.6994
|  | KENNINGTON | CT |  |  | 11.2414 | 11.2265 | 11.2101 | 11.1908 | 11.1678 | 11.1407 | 11.1086 | 11.0724 | 11.0324 | 10.9794 | 10.7853 | 10.3929 | 10.1727 | 10.0297 | 9.2635 | 9.2553 | 9.2464 | 9.236 | 9.2235 | 9.2086 | 9.1907 | 9.1702 | 9.1473 | 9.1173 | 9.0052 | 8.7719 | 8.6162 | 8.5065 | 8.8661 | 8.8512 | 8.8346 | 8.8153 | 8.792 | 8.7648 | 8.7331 | 8.6976 | 8.6589 | 8.6072 | 8.4207 | 8.0504 | 7.8377 | 7.6994
|  | KENNINGTON | LW |  |  | 11.2408 | 11.2232 | 11.2046 | 11.1821 | 11.1541 | 11.1209 | 11.0807 | 11.0333 | 10.9779 | 10.9079 | 10.6615 | 10.3195 | 10.1602 | 10.0675 | 9.2638 | 9.2546 | 9.245 | 9.2332 | 9.2185 | 9.2008 | 9.179 | 9.1531 | 9.1224 | 9.0839 | 8.9459 | 8.7147 | 8.6075 | 8.5364 | 8.8633 | 8.8447 | 8.8248 | 8.8012 | 8.7718 | 8.7373 | 8.6962 | 8.6483 | 8.5932 | 8.5238 | 8.2824 | 7.9576 | 7.8189 | 7.7372
|  | KENNINGTON | ST |  |  | 11.2526 | 11.245 | 11.2375 | 11.2291 | 11.2177 | 11.2035 | 11.1855 | 11.1653 | 11.1389 | 11.1044 | 10.9621 | 10.5855 | 10.3219 | 10.1556 | 9.2693 | 9.265 | 9.2608 | 9.256 | 9.2497 | 9.2418 | 9.2317 | 9.2202 | 9.2052 | 9.1857 | 9.1043 | 8.8886 | 8.7282 | 8.6015 | 8.8776 | 8.87 | 8.8625 | 8.8543 | 8.8428 | 8.8286 | 8.8108 | 8.7911 | 8.7655 | 8.7319 | 8.5947 | 8.2339 | 7.9817 | 7.821
|  | KENNINGTON | SP |  |  | 11.2537 | 11.2479 | 11.2425 | 11.2365 | 11.2292 | 11.2197 | 11.2093 | 11.1974 | 11.1838 | 11.166 | 11.0995 | 10.8752 | 10.6129 | 10.479 | 9.27 | 9.2667 | 9.2639 | 9.2607 | 9.2569 | 9.252 | 9.2465 | 9.2401 | 9.2328 | 9.2234 | 9.1871 | 9.064 | 8.9148 | 8.8315 | 8.8787 | 8.8729 | 8.8675 | 8.8614 | 8.8537 | 8.8436 | 8.8327 | 8.8203 | 8.8065 | 8.788 | 8.7205 | 8.4969 | 8.2427 | 8.1191
BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL | MINIMUM HEADROOM | SU 67102 74048 | YES | 9.4441 | 9.1661 | 8.8418 | 8.5152 | 8.1932 | 7.8736 | 7.5268 | 7.1541 | 6.7137 | 6.2268 | 5.1761 | 4.099 | 3.2613 | 2.7248 | 11.9848 | 11.8266 | 11.6382 | 11.4464 | 11.2686 | 11.0888 | 10.8865 | 10.6657 | 10.3891 | 10.0742 | 9.4605 | 8.786 | 8.1522 | 7.6052 | 10.5905 | 10.3539 | 10.073 | 9.7858 | 9.4919 | 9.1973 | 8.8758 | 8.5298 | 8.1156 | 7.6541 | 6.6771 | 5.7116 | 4.9874 | 4.5417
|  | KENTWOOD HILL | CT |  |  | 9.5107 | 9.2755 | 9.0132 | 8.7239 | 8.5044 | 8.2908 | 8.0573 | 7.8038 | 7.5267 | 7.0459 | 5.8453 | 4.3435 | 3.2613 | 2.7248 | 11.9952 | 11.8453 | 11.6796 | 11.4896 | 11.3472 | 11.2045 | 11.0461 | 10.8728 | 10.6783 | 10.3598 | 9.5916 | 8.786 | 8.1522 | 7.6052 | 10.6402 | 10.4401 | 10.2161 | 9.9608 | 9.7629 | 9.5657 | 9.3471 | 9.1098 | 8.8483 | 8.3936 | 7.2696 | 5.9332 | 4.9874 | 4.5417
|  | KENTWOOD HILL | LW |  |  | 9.4441 | 9.1661 | 8.8418 | 8.5152 | 8.1932 | 7.8736 | 7.5268 | 7.1541 | 6.7137 | 6.2268 | 5.1761 | 4.099 | 3.6443 | 3.4035 | 11.9848 | 11.8266 | 11.6382 | 11.4464 | 11.2686 | 11.0888 | 10.8865 | 10.6657 | 10.3891 | 10.0742 | 9.4605 | 8.936 | 8.7447 | 8.6416 | 10.5905 | 10.3539 | 10.073 | 9.7858 | 9.4919 | 9.1973 | 8.8758 | 8.5298 | 8.1156 | 7.6541 | 6.6771 | 5.7116 | 5.3174 | 5.112
|  | KENTWOOD HILL | ST |  |  | 9.6462 | 9.5111 | 9.3641 | 9.2171 | 9.1107 | 9.0068 | 8.8866 | 8.7549 | 8.6108 | 8.4684 | 7.8384 | 6.5019 | 5.9523 | 5.5489 | 12.0903 | 12.0045 | 11.9097 | 11.81 | 11.7313 | 11.6513 | 11.5575 | 11.4544 | 11.3388 | 11.2323 | 10.74 | 9.7054 | 9.248 | 8.7438 | 10.7712 | 10.6645 | 10.5462 | 10.4231 | 10.3257 | 10.2279 | 10.1141 | 9.9895 | 9.8516 | 9.7179 | 9.107 | 7.8342 | 7.3715 | 7.0269
|  | KENTWOOD HILL | SP |  |  | 9.6587 | 9.5274 | 9.3901 | 9.263 | 9.178 | 9.0997 | 9.0112 | 8.906 | 8.7948 | 8.6625 | 8.174 | 6.8305 | 6.167 | 5.9105 | 12.0937 | 12.0067 | 11.9133 | 11.8229 | 11.7619 | 11.7034 | 11.6357 | 11.5536 | 11.464 | 11.3618 | 10.9657 | 9.8319 | 9.0744 | 8.322 | 10.7813 | 10.6766 | 10.5658 | 10.4608 | 10.3854 | 10.3145 | 10.2337 | 10.1364 | 10.0323 | 9.9103 | 9.4487 | 8.1559 | 7.5487 | 7.3299
COWLEY GSP | YARNTON BSP | KIDDINGTON | MINIMUM HEADROOM | SP 43362 24301 | NO | 15.5549 | 14.8849 | 14.0482 | 13.2023 | 11.8056 | 10.3293 | 8.7447 | 7.0398 | 4.9382 | 2.7338 | -2.3978 | -9.3645 | -16.6436 | -20.9702 | 13.38 | 12.9911 | 12.4723 | 11.9345 | 11.165 | 10.3393 | 9.4221 | 8.4175 | 7.0866 | 5.5941 | 2.587 | -1.9688 | -6.4695 | -10.814 | 8.9202 | 8.346 | 7.5988 | 6.8069 | 5.5223 | 4.1616 | 2.6918 | 1.1048 | -0.87534 | -2.952 | -7.6765 | -13.8558 | -20.0601 | -23.7276
|  | KIDDINGTON | CT |  |  | 15.8457 | 15.3628 | 14.8159 | 14.1003 | 13.1714 | 12.1768 | 11.1093 | 9.9393 | 8.5763 | 6.2938 | 0.60741 | -8.9165 | -16.6436 | -20.9702 | 13.4383 | 13.0926 | 12.6962 | 12.1485 | 11.5371 | 10.8758 | 10.1542 | 9.3514 | 8.3861 | 6.7919 | 3.1311 | -1.9688 | -6.4695 | -10.814 | 9.1907 | 8.7859 | 8.2817 | 7.5987 | 6.7307 | 5.8003 | 4.7981 | 3.696 | 2.4013 | 0.25656 | -4.9908 | -13.3968 | -20.0601 | -23.7276
|  | KIDDINGTON | LW |  |  | 15.5549 | 14.8849 | 14.0482 | 13.2023 | 11.8056 | 10.3293 | 8.7447 | 7.0398 | 4.9382 | 2.7338 | -2.3978 | -9.3645 | -13.4007 | -15.8732 | 13.38 | 12.9911 | 12.4723 | 11.9345 | 11.165 | 10.3393 | 9.4221 | 8.4175 | 7.0866 | 5.5941 | 2.587 | -0.87371 | -2.6651 | -3.8499 | 8.9202 | 8.346 | 7.5988 | 6.8069 | 5.5223 | 4.1616 | 2.6918 | 1.1048 | -0.87534 | -2.952 | -7.6765 | -13.8558 | -17.2747 | -19.3173
|  | KIDDINGTON | ST |  |  | 16.2088 | 15.9766 | 15.6963 | 15.4225 | 15.0209 | 14.5759 | 14.0909 | 13.5529 | 12.9442 | 12.3161 | 9.3759 | 2.7289 | -1.286 | -4.5307 | 13.6956 | 13.5167 | 13.2983 | 13.0733 | 12.759 | 12.4085 | 12.0189 | 11.5825 | 11.0803 | 10.5817 | 8.1715 | 2.8086 | -0.61853 | -4.4314 | 9.5102 | 9.3233 | 9.0977 | 8.8704 | 8.4985 | 8.0791 | 7.6194 | 7.1076 | 6.5245 | 5.9309 | 3.1148 | -2.9421 | -6.4654 | -9.1931
|  | KIDDINGTON | SP |  |  | 16.2504 | 16.0002 | 15.74 | 15.4909 | 15.1188 | 14.7219 | 14.3152 | 13.8458 | 13.3456 | 12.7681 | 10.5028 | 4.0642 | 0.29345 | -1.7812 | 13.7042 | 13.4979 | 13.2759 | 13.0499 | 12.7888 | 12.5007 | 12.1944 | 11.8361 | 11.4399 | 10.9383 | 8.9049 | 2.7812 | -2.6196 | -9.5126 | 9.5466 | 9.3482 | 9.1416 | 8.9312 | 8.5907 | 8.2264 | 7.8509 | 7.4147 | 6.9463 | 6.406 | 4.2702 | -1.6913 | -5.0535 | -6.7763
BRAMLEY (FLEE) | READING BSP | KIDMORE END | MINIMUM HEADROOM | SU 69953 78205 | YES | 12.9712 | 12.7812 | 12.5882 | 12.3857 | 12.1026 | 11.7204 | 11.2711 | 10.7875 | 10.2549 | 9.713 | 8.3104 | 6.7719 | 6.4468 | 6.2621 | 15.4367 | 15.3172 | 15.1815 | 15.0402 | 14.8532 | 14.6586 | 14.4487 | 14.2013 | 13.9009 | 13.63 | 13.1067 | 12.5671 | 12.4623 | 12.3014 | 13.2709 | 13.0409 | 12.7876 | 12.5257 | 12.1705 | 11.8038 | 11.4152 | 10.9652 | 10.393 | 9.8546 | 8.6324 | 7.3365 | 7.071 | 6.9239
|  | KIDMORE END | CT |  |  | 13.165 | 13.0761 | 12.9788 | 12.8754 | 12.7098 | 12.5381 | 12.3571 | 12.1622 | 11.97 | 11.4607 | 10.3054 | 8.5934 | 7.8592 | 7.6486 | 15.5189 | 15.4425 | 15.3576 | 15.2528 | 15.1266 | 14.9919 | 14.8451 | 14.673 | 14.4872 | 14.2069 | 13.7128 | 13.0719 | 12.7868 | 12.6492 | 13.4646 | 13.3352 | 13.1932 | 13.0221 | 12.799 | 12.5631 | 12.3085 | 12.015 | 11.7031 | 11.2244 | 10.3034 | 8.8244 | 8.1935 | 8.024
|  | KIDMORE END | LW |  |  | 12.9712 | 12.7812 | 12.5882 | 12.3857 | 12.1026 | 11.7204 | 11.2711 | 10.7875 | 10.2549 | 9.713 | 8.3104 | 6.7719 | 6.4468 | 6.2621 | 15.4367 | 15.3172 | 15.1815 | 15.0402 | 14.8532 | 14.6586 | 14.4487 | 14.2013 | 13.9009 | 13.63 | 13.1067 | 12.5671 | 12.4623 | 12.4051 | 13.2709 | 13.0409 | 12.7876 | 12.5257 | 12.1705 | 11.8038 | 11.4152 | 10.9652 | 10.393 | 9.8546 | 8.6324 | 7.3365 | 7.071 | 6.9239
|  | KIDMORE END | ST |  |  | 13.2124 | 13.1522 | 13.0912 | 13.0267 | 12.9261 | 12.8223 | 12.7149 | 12.6016 | 12.4771 | 12.317 | 11.722 | 10.3389 | 9.5792 | 9.0656 | 15.5703 | 15.5302 | 15.4822 | 15.4271 | 15.3479 | 15.2632 | 15.1768 | 15.0823 | 14.9724 | 14.864 | 14.3582 | 13.6926 | 13.3812 | 13.1439 | 13.5459 | 13.4735 | 13.3899 | 13.2959 | 13.156 | 13.0081 | 12.8589 | 12.6977 | 12.513 | 12.3214 | 11.4778 | 10.3166 | 9.7012 | 9.25
|  | KIDMORE END | SP |  |  | 13.2344 | 13.1893 | 13.1429 | 13.0945 | 12.9368 | 12.7753 | 12.6128 | 12.4452 | 12.2754 | 12.0524 | 10.9742 | 8.7507 | 7.4135 | 6.5205 | 15.5813 | 15.5439 | 15.5025 | 15.4596 | 15.3631 | 15.2632 | 15.1628 | 15.0504 | 14.9371 | 14.7986 | 14.3044 | 13.1661 | 12.6381 | 12.3014 | 13.5709 | 13.508 | 13.4401 | 13.3705 | 13.1827 | 12.9898 | 12.7974 | 12.5872 | 12.3765 | 12.1118 | 11.2049 | 8.9863 | 7.8243 | 7.1107
BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE | MINIMUM HEADROOM | SU 87551 61530 | YES | 15.4124 | 15.1024 | 14.7772 | 14.4215 | 13.8905 | 13.3363 | 12.7341 | 12.0327 | 11.1722 | 10.4472 | 9.0298 | 6.7947 | 4.9488 | 3.3531 | 18.4062 | 18.3533 | 18.2928 | 18.2269 | 18.163 | 18.0935 | 17.8351 | 17.4043 | 16.8423 | 16.3908 | 15.6737 | 14.4822 | 13.076 | 11.8421 | 16.5209 | 16.2443 | 15.9543 | 15.6377 | 15.1569 | 14.6555 | 14.1123 | 13.4825 | 12.7154 | 12.0637 | 10.7616 | 8.7579 | 7.1403 | 5.7583
|  | KINGS RIDE | CT |  |  | 15.5332 | 15.307 | 15.0437 | 14.7637 | 14.416 | 14.0476 | 13.6433 | 13.1816 | 12.6534 | 11.8456 | 10.3295 | 7.4694 | 4.9488 | 3.3531 | 18.4062 | 18.3533 | 18.2928 | 18.2269 | 18.163 | 18.0935 | 18.0139 | 17.7628 | 17.382 | 16.8432 | 15.9764 | 14.4822 | 13.076 | 11.8421 | 16.6391 | 16.4419 | 16.2124 | 15.968 | 15.658 | 15.3298 | 14.9703 | 14.5606 | 14.0933 | 13.3718 | 11.9901 | 9.3908 | 7.1403 | 5.7583
|  | KINGS RIDE | LW |  |  | 15.4124 | 15.1024 | 14.7772 | 14.4215 | 13.8905 | 13.3363 | 12.7341 | 12.0327 | 11.1722 | 10.4472 | 9.0298 | 6.7947 | 5.2776 | 4.1624 | 18.4203 | 18.3721 | 18.321 | 18.2631 | 18.1949 | 18.1202 | 17.8351 | 17.4043 | 16.8423 | 16.3908 | 15.6737 | 14.5897 | 13.8596 | 13.2971 | 16.5209 | 16.2443 | 15.9543 | 15.6377 | 15.1569 | 14.6555 | 14.1123 | 13.4825 | 12.7154 | 12.0637 | 10.7616 | 8.7579 | 7.4582 | 6.5326
|  | KINGS RIDE | ST |  |  | 15.742 | 15.6486 | 15.5225 | 15.3805 | 15.2029 | 15.0168 | 14.8134 | 14.5827 | 14.3249 | 14.0704 | 12.7261 | 10.6974 | 9.2452 | 8.0501 | 18.4488 | 18.4225 | 18.3894 | 18.3516 | 18.3094 | 18.2646 | 18.214 | 18.1559 | 18.0893 | 18.0254 | 17.2329 | 15.7985 | 14.7696 | 13.6925 | 16.8232 | 16.7434 | 16.6355 | 16.5138 | 16.3592 | 16.1974 | 16.0203 | 15.8192 | 15.5945 | 15.3695 | 14.195 | 12.428 | 11.1896 | 10.1837
|  | KINGS RIDE | SP |  |  | 15.7525 | 15.6707 | 15.581 | 15.477 | 15.3205 | 15.1593 | 14.9968 | 14.7956 | 14.5903 | 14.3354 | 13.3481 | 10.6529 | 9.2795 | 8.2635 | 18.4467 | 18.4203 | 18.3917 | 18.3585 | 18.3265 | 18.2909 | 18.2537 | 18.2076 | 18.1585 | 18.1041 | 17.7492 | 15.6616 | 14.5305 | 13.3645 | 16.8339 | 16.7649 | 16.6893 | 16.6015 | 16.4639 | 16.3225 | 16.1797 | 16.0032 | 15.8233 | 15.5972 | 14.7313 | 12.378 | 11.2068 | 10.3738
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE | MINIMUM HEADROOM | SU 51982 59358 | YES | 16.7082 | 16.3909 | 16.0524 | 15.6784 | 14.875 | 14.0313 | 13.1281 | 12.0931 | 10.9329 | 9.9301 | 7.3145 | 4.3225 | 2.6803 | 1.4589 | 21.4449 | 21.2541 | 21.048 | 20.8139 | 20.3792 | 19.9185 | 19.4076 | 18.8024 | 18.0973 | 17.4912 | 16.0044 | 14.1791 | 12.5715 | 11.0876 | 17.8338 | 17.5266 | 17.1962 | 16.8268 | 16.1021 | 15.3376 | 14.5035 | 13.5295 | 12.4184 | 11.4606 | 9.0577 | 6.3538 | 5.1123 | 4.1205
|  | KINGSCLERE | CT |  |  | 16.8363 | 16.6109 | 16.3459 | 16.0484 | 15.4537 | 14.8222 | 14.1702 | 13.4333 | 12.6319 | 11.5638 | 8.9346 | 5.1531 | 2.6803 | 1.4589 | 21.459 | 21.2865 | 21.0816 | 20.8486 | 20.4822 | 20.0899 | 19.667 | 19.1827 | 18.6525 | 17.9857 | 16.4118 | 14.1791 | 12.5715 | 11.0876 | 17.9251 | 17.6938 | 17.4185 | 17.107 | 16.5611 | 15.9785 | 15.3633 | 14.6608 | 13.8955 | 12.8853 | 10.4897 | 7.1558 | 5.1123 | 4.1205
|  | KINGSCLERE | LW |  |  | 16.7082 | 16.3909 | 16.0524 | 15.6784 | 14.875 | 14.0313 | 13.1281 | 12.0931 | 10.9329 | 9.9301 | 7.3145 | 4.3225 | 3.1815 | 2.5649 | 21.4449 | 21.2541 | 21.048 | 20.8139 | 20.3792 | 19.9185 | 19.4076 | 18.8024 | 18.0973 | 17.4912 | 16.0044 | 14.3844 | 13.8762 | 13.5957 | 17.8338 | 17.5266 | 17.1962 | 16.8268 | 16.1021 | 15.3376 | 14.5035 | 13.5295 | 12.4184 | 11.4606 | 9.0577 | 6.3538 | 5.4066 | 4.9055
|  | KINGSCLERE | ST |  |  | 17.0805 | 17.003 | 16.9048 | 16.7805 | 16.5008 | 16.199 | 15.8833 | 15.5236 | 15.1108 | 14.7252 | 12.9709 | 10.1077 | 8.642 | 7.7428 | 21.6217 | 21.5479 | 21.4561 | 21.3409 | 21.1359 | 20.9134 | 20.6757 | 20.4031 | 20.089 | 19.8028 | 18.4993 | 16.3087 | 14.9322 | 13.5528 | 18.1734 | 18.0924 | 17.9871 | 17.8514 | 17.5889 | 17.304 | 17.0019 | 16.6545 | 16.255 | 15.887 | 14.1738 | 11.509 | 10.2095 | 9.4415
|  | KINGSCLERE | SP |  |  | 17.1062 | 17.0364 | 16.9612 | 16.8696 | 16.6658 | 16.4492 | 16.2152 | 15.9461 | 15.6402 | 15.3193 | 14.1399 | 11.2205 | 9.5524 | 8.8455 | 21.6302 | 21.5557 | 21.473 | 21.3737 | 21.2148 | 21.0428 | 20.8508 | 20.6281 | 20.3719 | 20.1071 | 19.1049 | 16.6241 | 14.569 | 12.3476 | 18.1952 | 18.1179 | 18.0349 | 17.9325 | 17.7458 | 17.5461 | 17.3232 | 17.0626 | 16.7644 | 16.4531 | 15.2807 | 12.4784 | 10.9504 | 10.3497
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY | MINIMUM HEADROOM | SU 37657 67143 | YES | 3.1128 | 2.6266 | 2.1363 | 1.6336 | 0.93845 | 0.23217 | -0.49246 | -1.1961 | -1.9008 | -2.5489 | -3.7673 | -4.8875 | -6.9888 | -8.3484 | 3.0826 | 2.888 | 2.6904 | 2.4789 | 2.2012 | 1.9165 | 1.5861 | 1.2265 | 0.83685 | 0.49136 | -0.11011 | -0.70455 | -1.7367 | -2.4854 | 1.4744 | 1.0127 | 0.54791 | 0.074769 | -0.5859 | -1.2564 | -1.9349 | -2.5807 | -3.2108 | -3.801 | -4.9233 | -5.9462 | -7.8713 | -9.1185
|  | KINTBURY | CT |  |  | 3.6252 | 3.3968 | 3.1469 | 2.8933 | 2.4974 | 2.0914 | 1.6837 | 1.2477 | 0.83682 | 0.24383 | -0.61311 | -1.3678 | -1.7199 | -1.8587 | 3.2149 | 3.0896 | 2.9465 | 2.7981 | 2.6117 | 2.4179 | 2.2079 | 1.9657 | 1.7213 | 1.3856 | 0.90468 | 0.42194 | 0.15702 | -0.12303 | 1.9843 | 1.7744 | 1.5457 | 1.3137 | 0.94645 | 0.56998 | 0.19371 | -0.20594 | -0.5806 | -1.1227 | -1.9141 | -2.6173 | -2.9473 | -3.0777
|  | KINTBURY | LW |  |  | 3.1128 | 2.6266 | 2.1363 | 1.6336 | 0.93845 | 0.23217 | -0.49246 | -1.1961 | -1.9008 | -2.5489 | -3.7673 | -4.5349 | -4.6893 | -4.7434 | 3.0826 | 2.888 | 2.6904 | 2.4789 | 2.2012 | 1.9165 | 1.5861 | 1.2265 | 0.83685 | 0.49136 | -0.11011 | -0.55551 | -0.62712 | -0.65056 | 1.4744 | 1.0127 | 0.54791 | 0.074769 | -0.5859 | -1.2564 | -1.9349 | -2.5807 | -3.2108 | -3.801 | -4.9233 | -5.6215 | -5.7608 | -5.8094
|  | KINTBURY | ST |  |  | 3.7199 | 3.5613 | 3.3858 | 3.1988 | 2.945 | 2.6838 | 2.4155 | 2.1284 | 1.8295 | 1.5094 | 0.24616 | -1.7313 | -2.6962 | -2.9692 | 3.2955 | 3.2238 | 3.137 | 3.039 | 2.9229 | 2.801 | 2.6691 | 2.5225 | 2.3612 | 2.203 | 1.4707 | 0.42214 | -0.1375 | -0.47389 | 2.0612 | 1.9113 | 1.7489 | 1.5782 | 1.3402 | 1.0962 | 0.84789 | 0.58428 | 0.31317 | 0.016834 | -1.1365 | -2.9754 | -3.8858 | -4.1438
|  | KINTBURY | SP |  |  | 3.7748 | 3.653 | 3.5263 | 3.3957 | 2.9552 | 2.5134 | 2.0742 | 1.6075 | 1.1395 | 0.5938 | -1.2075 | -4.8875 | -6.9888 | -8.3484 | 3.3106 | 3.2495 | 3.1827 | 3.1109 | 2.9473 | 2.7847 | 2.6193 | 2.4316 | 2.2404 | 2.0208 | 1.1728 | -0.70455 | -1.7367 | -2.4854 | 2.1157 | 2.0022 | 1.8848 | 1.7649 | 1.3384 | 0.90922 | 0.48352 | 0.036561 | -0.4114 | -0.93334 | -2.612 | -5.9462 | -7.8713 | -9.1185
BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL | MINIMUM HEADROOM | SU 82849 79105 | YES | 4.0641 | 3.7889 | 3.5006 | 3.2078 | 2.8171 | 2.4181 | 2.0048 | 1.5653 | 1.0496 | 0.5801 | -0.49212 | -1.6 | -1.708 | -1.734 | 4.0052 | 3.8825 | 3.7489 | 3.6099 | 3.4303 | 3.2446 | 3.0435 | 2.8237 | 2.55 | 2.3063 | 1.8378 | 1.3694 | 1.3238 | 1.0138 | 2.5571 | 2.3182 | 2.0643 | 1.8042 | 1.4613 | 1.1096 | 0.73889 | 0.34016 | -0.14013 | -0.57188 | -1.4976 | -2.4825 | -2.5768 | -2.5985
|  | KNOWL HILL | CT |  |  | 4.3611 | 4.2366 | 4.0986 | 3.9433 | 3.722 | 3.4919 | 3.2408 | 2.9643 | 2.6625 | 2.2572 | 1.4277 | 0.15347 | -0.14487 | -0.23035 | 4.1053 | 4.0345 | 3.954 | 3.8602 | 3.742 | 3.6178 | 3.4799 | 3.325 | 3.1503 | 2.9209 | 2.4945 | 1.9127 | 1.7076 | 1.5327 | 2.7941 | 2.6785 | 2.5497 | 2.4035 | 2.2 | 1.988 | 1.7558 | 1.499 | 1.2163 | 0.83691 | 0.082255 | -0.98093 | -1.2272 | -1.2964
|  | KNOWL HILL | LW |  |  | 4.0641 | 3.7889 | 3.5006 | 3.2078 | 2.8171 | 2.4181 | 2.0048 | 1.5653 | 1.0496 | 0.5801 | -0.49212 | -1.6 | -1.708 | -1.734 | 4.0052 | 3.8825 | 3.7489 | 3.6099 | 3.4303 | 3.2446 | 3.0435 | 2.8237 | 2.55 | 2.3063 | 1.8378 | 1.3694 | 1.3238 | 1.3118 | 2.5571 | 2.3182 | 2.0643 | 1.8042 | 1.4613 | 1.1096 | 0.73889 | 0.34016 | -0.14013 | -0.57188 | -1.4976 | -2.4825 | -2.5768 | -2.5985
|  | KNOWL HILL | ST |  |  | 4.442 | 4.3652 | 4.2789 | 4.1882 | 4.0469 | 3.9009 | 3.7516 | 3.5912 | 3.4174 | 3.2342 | 2.4789 | 1.4649 | 0.93385 | 0.5947 | 4.1588 | 4.1184 | 4.0699 | 4.0172 | 3.9435 | 3.8653 | 3.7823 | 3.6907 | 3.5883 | 3.4899 | 3.038 | 2.4407 | 2.1357 | 1.868 | 2.8764 | 2.8086 | 2.7297 | 2.6459 | 2.519 | 2.3866 | 2.2494 | 2.1006 | 1.9371 | 1.7706 | 1.0506 | 0.11541 | -0.32599 | -0.60074
|  | KNOWL HILL | SP |  |  | 4.4819 | 4.4236 | 4.3627 | 4.2988 | 4.1058 | 3.9174 | 3.7225 | 3.5141 | 3.3046 | 3.0306 | 2.1182 | 0.19009 | -0.88787 | -1.5914 | 4.1725 | 4.137 | 4.0986 | 4.057 | 3.9684 | 3.8831 | 3.7923 | 3.69 | 3.5857 | 3.4574 | 2.9991 | 1.9503 | 1.4146 | 1.0138 | 2.9086 | 2.8548 | 2.7981 | 2.7379 | 2.5721 | 2.4117 | 2.2443 | 2.0617 | 1.8779 | 1.6404 | 0.82785 | -0.9335 | -1.8556 | -2.4736
BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD | MINIMUM HEADROOM | SU 86017 50475 | YES | 2.3452 | 2.2286 | 2.1123 | 1.9851 | 1.8157 | 1.6422 | 1.4444 | 1.2035 | 0.93638 | 0.73613 | 0.24921 | -0.34486 | -0.55579 | -0.66605 | 2.3152 | 2.2472 | 2.1802 | 2.1044 | 2.0089 | 1.9108 | 1.7928 | 1.6411 | 1.4702 | 1.3515 | 1.1182 | 0.82061 | 0.67312 | 0.47412 | 1.666 | 1.5527 | 1.4406 | 1.32 | 1.1561 | 0.98785 | 0.80136 | 0.58219 | 0.34132 | 0.15128 | -0.32582 | -0.90251 | -1.1031 | -1.2069
|  | LABURNAM ROAD | CT |  |  | 2.4094 | 2.3377 | 2.2612 | 2.1706 | 2.0596 | 1.9445 | 1.8062 | 1.6447 | 1.4778 | 1.2662 | 0.89294 | 0.19093 | -0.27937 | -0.511 | 2.3292 | 2.2767 | 2.2209 | 2.1533 | 2.0805 | 2.0045 | 1.9102 | 1.7976 | 1.6803 | 1.5373 | 1.3211 | 0.93841 | 0.67312 | 0.47412 | 1.7442 | 1.6794 | 1.6122 | 1.5343 | 1.4321 | 1.3261 | 1.202 | 1.0601 | 0.91394 | 0.72502 | 0.33551 | -0.37344 | -0.83063 | -1.0539
|  | LABURNAM ROAD | LW |  |  | 2.3452 | 2.2286 | 2.1123 | 1.9851 | 1.8157 | 1.6422 | 1.4444 | 1.2035 | 0.93638 | 0.73613 | 0.24921 | -0.34486 | -0.55579 | -0.66605 | 2.3152 | 2.2472 | 2.1802 | 2.1044 | 2.0089 | 1.9108 | 1.7928 | 1.6411 | 1.4702 | 1.3515 | 1.1182 | 0.82061 | 0.70738 | 0.64606 | 1.666 | 1.5527 | 1.4406 | 1.32 | 1.1561 | 0.98785 | 0.80136 | 0.58219 | 0.34132 | 0.15128 | -0.32582 | -0.90251 | -1.1031 | -1.2069
|  | LABURNAM ROAD | ST |  |  | 2.475 | 2.4452 | 2.4127 | 2.3651 | 2.3056 | 2.2469 | 2.1779 | 2.0967 | 2.0093 | 1.9195 | 1.4693 | 0.96328 | 0.65052 | 0.43072 | 2.3731 | 2.3493 | 2.3236 | 2.2855 | 2.244 | 2.203 | 2.1531 | 2.0932 | 2.0279 | 1.9659 | 1.6344 | 1.2711 | 1.0389 | 0.83358 | 1.8016 | 1.7732 | 1.744 | 1.7037 | 1.65 | 1.5962 | 1.5347 | 1.4638 | 1.3871 | 1.3039 | 0.91899 | 0.41855 | 0.090186 | -0.13498
|  | LABURNAM ROAD | SP |  |  | 2.4884 | 2.4618 | 2.4379 | 2.4066 | 2.3672 | 2.3265 | 2.2836 | 2.2308 | 2.1775 | 2.0947 | 1.7748 | 1.0242 | 0.62906 | 0.36845 | 2.3769 | 2.3531 | 2.3311 | 2.3026 | 2.2747 | 2.2454 | 2.2134 | 2.1727 | 2.1312 | 2.0766 | 1.8531 | 1.316 | 1.0553 | 0.86197 | 1.8172 | 1.7935 | 1.7729 | 1.747 | 1.711 | 1.6735 | 1.6346 | 1.5887 | 1.542 | 1.4647 | 1.1808 | 0.50874 | 0.091626 | -0.17285
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN | MINIMUM HEADROOM | SU 33280 78217 | YES | 24.6696 | 24.0846 | 23.3317 | 22.1389 | 20.5199 | 19.4091 | 18.2201 | 16.8986 | 15.317 | 13.6153 | 8.9915 | 3.1302 | -0.63675 | -3.3148 | 11.2802 | 10.9556 | 10.4991 | 9.7965 | 8.9396 | 8.3244 | 7.645 | 6.8564 | 5.852 | 4.7145 | 1.4505 | -4.1977 | -9.5651 | -22.2284 | 5.7393 | 5.2183 | 4.5143 | 3.4534 | 2.0337 | 1.0036 | -0.11254 | -1.3771 | -2.9026 | -4.5551 | -8.9677 | -14.3514 | -17.3544 | -19.5718
|  | LAMBOURN | CT |  |  | 24.9208 | 24.484 | 23.9359 | 22.8486 | 21.5395 | 20.7483 | 19.9466 | 19.0425 | 17.948 | 16.268 | 11.6518 | 4.3821 | -0.63675 | -3.3148 | 11.3028 | 10.9706 | 10.5452 | 9.7965 | 8.9569 | 8.3667 | 7.7401 | 7.0109 | 6.118 | 4.8945 | 1.4505 | -4.1977 | -9.5651 | -16.3685 | 5.9342 | 5.5344 | 5.0175 | 4.0291 | 2.8669 | 2.1042 | 1.3212 | 0.42154 | -0.65118 | -2.2291 | -6.5606 | -13.1475 | -17.3544 | -19.5718
|  | LAMBOURN | LW |  |  | 24.6696 | 24.0846 | 23.3317 | 22.1389 | 20.5199 | 19.4091 | 18.2201 | 16.8986 | 15.317 | 13.6153 | 8.9915 | 3.1302 | 0.56416 | -0.95809 | 11.2802 | 10.9556 | 10.4991 | 9.8069 | 8.9396 | 8.3244 | 7.645 | 6.8564 | 5.852 | 4.7145 | 1.7578 | -1.6807 | -2.9368 | -3.693 | 5.7393 | 5.2183 | 4.5143 | 3.4534 | 2.0337 | 1.0036 | -0.11254 | -1.3771 | -2.9026 | -4.5551 | -8.9677 | -14.3514 | -16.5359 | -17.8007
|  | LAMBOURN | ST |  |  | 25.2831 | 25.0762 | 24.8061 | 24.2764 | 23.6099 | 23.2993 | 22.959 | 22.5341 | 22.0124 | 21.3883 | 19.0092 | 13.3636 | 10.1256 | 8.067 | 11.5244 | 11.3293 | 11.0692 | 10.6521 | 10.1306 | 9.8053 | 9.4431 | 8.9848 | 8.4531 | 7.8543 | 5.6008 | -0.037565 | -5.0249 | -11.5721 | 6.2852 | 6.105 | 5.8539 | 5.4062 | 4.8195 | 4.5056 | 4.1607 | 3.7142 | 3.1909 | 2.584 | 0.27182 | -5.059 | -7.964 | -9.7421
|  | LAMBOURN | SP |  |  | 25.34 | 25.1383 | 24.8897 | 24.4092 | 23.8992 | 23.6944 | 23.4754 | 23.1897 | 22.8434 | 22.3633 | 20.7877 | 16.1623 | 12.6906 | 11.0559 | 11.5426 | 11.3341 | 11.0637 | 10.6502 | 10.1881 | 9.8803 | 9.5379 | 9.1041 | 8.6059 | 7.9765 | 5.75 | -0.53203 | -9.1015 | -22.2284 | 6.3377 | 6.1558 | 5.9203 | 5.5154 | 5.0854 | 4.8769 | 4.653 | 4.3459 | 3.9973 | 3.5307 | 1.9742 | -2.4217 | -5.6422 | -7.0785
FAWLEY GSP | LANGLEY BSP | LANGLEY | MINIMUM HEADROOM | SU 45158 01418 | NO | 2.1716 | 1.8269 | 1.4731 | 1.1187 | 0.61458 | 0.10026 | -0.43929 | -1.0091 | -1.679 | -2.3414 | -3.9182 | -5.7445 | -6.1873 | -6.3898 | 2.9911 | 2.8099 | 2.6278 | 2.4477 | 2.2017 | 1.9507 | 1.6797 | 1.3879 | 1.01 | 0.64239 | -0.11148 | -0.89618 | -1.0867 | -1.2982 | 0.24583 | -0.080151 | -0.41078 | -0.74026 | -1.2103 | -1.689 | -2.1896 | -2.7171 | -3.3315 | -3.9405 | -5.4066 | -7.0395 | -7.4318 | -7.6101
|  | LANGLEY | CT |  |  | 2.4791 | 2.2948 | 2.1078 | 1.8979 | 1.5928 | 1.2771 | 0.95443 | 0.59194 | 0.198 | -0.40387 | -1.799 | -3.9863 | -5.1908 | -5.3858 | 3.1044 | 2.9829 | 2.8609 | 2.7208 | 2.549 | 2.3701 | 2.1823 | 1.964 | 1.7179 | 1.3585 | 0.61327 | -0.40889 | -0.98835 | -1.2749 | 0.5382 | 0.36388 | 0.19038 | -0.00131 | -0.28382 | -0.5751 | -0.87219 | -1.2044 | -1.5635 | -2.1122 | -3.4066 | -5.4719 | -6.5507 | -6.7237
|  | LANGLEY | LW |  |  | 2.1716 | 1.8269 | 1.4731 | 1.1187 | 0.61458 | 0.10026 | -0.43929 | -1.0091 | -1.679 | -2.3414 | -3.9182 | -5.7445 | -6.1873 | -6.3898 | 2.9911 | 2.8099 | 2.6278 | 2.4477 | 2.2017 | 1.9507 | 1.6797 | 1.3879 | 1.01 | 0.64239 | -0.11148 | -0.89618 | -1.0867 | -1.1748 | 0.24583 | -0.080151 | -0.41078 | -0.74026 | -1.2103 | -1.689 | -2.1896 | -2.7171 | -3.3315 | -3.9405 | -5.4066 | -7.0395 | -7.4318 | -7.6101
|  | LANGLEY | ST |  |  | 2.5641 | 2.4397 | 2.3233 | 2.1972 | 2.02 | 1.8399 | 1.6512 | 1.453 | 1.2273 | 0.9911 | 0.023566 | -1.5913 | -2.4478 | -3.0466 | 3.1596 | 3.0762 | 3.0033 | 2.9254 | 2.8245 | 2.7227 | 2.611 | 2.4903 | 2.3472 | 2.2094 | 1.5875 | 0.57638 | 0.078487 | -0.35674 | 0.61431 | 0.49371 | 0.38364 | 0.26691 | 0.10228 | -0.064233 | -0.23813 | -0.42061 | -0.62733 | -0.84523 | -1.7255 | -3.2154 | -4.0252 | -4.5908
|  | LANGLEY | SP |  |  | 2.5986 | 2.4896 | 2.3963 | 2.305 | 2.047 | 1.7915 | 1.535 | 1.2611 | 0.98146 | 0.64881 | -0.46491 | -2.9285 | -4.2831 | -5.1584 | 3.1728 | 3.0934 | 3.0292 | 2.9681 | 2.8407 | 2.7147 | 2.5875 | 2.4476 | 2.302 | 2.1353 | 1.5467 | 0.10433 | -0.69392 | -1.2982 | 0.64686 | 0.54132 | 0.4529 | 0.36793 | 0.12557 | -0.11367 | -0.35395 | -0.60962 | -0.87009 | -1.1802 | -2.2107 | -4.4754 | -5.7447 | -6.5184
BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT | MINIMUM HEADROOM | SU 80847 29056 | YES | 3.5574 | 3.5042 | 3.4288 | 3.2948 | 3.0281 | 2.6797 | 1.8987 | 0.90582 | -0.38726 | -1.7903 | -5.4838 | -8.8851 | -10.5054 | -11.3252 | -2.1149 | -2.1589 | -2.211 | -2.3466 | -2.5957 | -2.9092 | -3.1983 | -3.6599 | -4.2387 | -4.891 | -6.8313 | -8.4893 | -9.2522 | -9.7648 | -1.4827 | -1.5611 | -1.6608 | -1.8175 | -2.1471 | -2.5926 | -3.1051 | -3.7596 | -4.565 | -5.512 | -8.5288 | -11.4504 | -12.9014 | -13.6567
|  | LANGLEY COURT | CT |  |  | 3.5574 | 3.5042 | 3.4412 | 3.3002 | 3.0452 | 2.7124 | 2.4085 | 1.8874 | 0.86304 | -0.54603 | -4.4337 | -8.5841 | -10.5054 | -11.3252 | -2.1149 | -2.1589 | -2.211 | -2.3466 | -2.5957 | -2.9081 | -3.182 | -3.5328 | -3.94 | -4.5266 | -6.4857 | -8.4591 | -9.2522 | -9.7648 | -1.4637 | -1.5225 | -1.5911 | -1.7404 | -2.0286 | -2.3987 | -2.7405 | -3.1645 | -3.7191 | -4.6008 | -7.4789 | -11.1429 | -12.9014 | -13.6567
|  | LANGLEY COURT | LW |  |  | 3.5668 | 3.5082 | 3.4288 | 3.2948 | 3.0281 | 2.6797 | 1.8987 | 0.90582 | -0.38726 | -1.7903 | -5.4838 | -8.8851 | -9.6545 | -9.9125 | -2.1038 | -2.1489 | -2.2106 | -2.3368 | -2.5899 | -2.9092 | -3.1983 | -3.6599 | -4.2387 | -4.891 | -6.8313 | -8.4893 | -8.7911 | -8.9048 | -1.4827 | -1.5611 | -1.6608 | -1.8175 | -2.1471 | -2.5926 | -3.1051 | -3.7596 | -4.565 | -5.512 | -8.5288 | -11.4504 | -12.1714 | -12.4181
|  | LANGLEY COURT | ST |  |  | 3.6082 | 3.5858 | 3.5592 | 3.4852 | 3.2782 | 2.9989 | 2.7511 | 2.4297 | 2.0473 | 1.5984 | -0.5474 | -3.9426 | -4.9789 | -5.6456 | -2.0752 | -2.0953 | -2.119 | -2.2017 | -2.414 | -2.6857 | -2.9171 | -3.2213 | -3.5691 | -3.9736 | -5.4502 | -7.033 | -7.7056 | -8.2208 | -1.407 | -1.4317 | -1.4606 | -1.5396 | -1.7554 | -2.0399 | -2.2897 | -2.6134 | -2.9952 | -3.4475 | -5.1259 | -7.195 | -8.1337 | -8.7441
|  | LANGLEY COURT | SP |  |  | 3.609 | 3.5853 | 3.5573 | 3.4837 | 3.2936 | 3.037 | 2.8128 | 2.5149 | 2.1683 | 1.7547 | 0.27558 | -3.0414 | -4.1234 | -4.5256 | -2.0754 | -2.0972 | -2.1229 | -2.2064 | -2.4053 | -2.6593 | -2.8724 | -3.1585 | -3.4791 | -3.8601 | -5.196 | -6.718 | -7.4154 | -8.0764 | -1.4022 | -1.4269 | -1.4553 | -1.5322 | -1.7318 | -1.9927 | -2.2154 | -2.5138 | -2.8555 | -3.2666 | -4.7191 | -6.4938 | -7.1492 | -7.4292
AXMINSTER | YEOVIL BSP | LARKHILL | MINIMUM HEADROOM | ST 53677 16914 | YES | 14.0562 | 13.622 | 13.1541 | 12.6943 | 12.1154 | 11.5124 | 10.8462 | 10.0779 | 9.1553 | 8.3595 | 6.5627 | 4.3974 | 3.7966 | 3.3812 | 3.1696 | 2.9389 | 2.6837 | 2.4266 | 2.1214 | 1.7996 | 1.4384 | 1.0008 | 0.43248 | -0.038515 | -0.96475 | -2.0511 | -2.638 | -3.3565 | 1.6852 | 1.2728 | 0.83074 | 0.39296 | -0.17633 | -0.76746 | -1.3903 | -2.09 | -2.9255 | -3.6535 | -5.3345 | -7.3639 | -7.9255 | -8.314
|  | LARKHILL | CT |  |  | 14.3027 | 14.016 | 13.6907 | 13.3564 | 12.9906 | 12.6001 | 12.1802 | 11.6602 | 11.1206 | 10.3478 | 8.816 | 6.065 | 4.256 | 3.4717 | 3.2249 | 3.0367 | 2.8196 | 2.5855 | 2.3567 | 2.1093 | 1.8377 | 1.4828 | 1.1084 | 0.60015 | -0.24729 | -1.6682 | -2.638 | -3.3565 | 1.9565 | 1.7005 | 1.4101 | 1.1096 | 0.76034 | 0.38899 | -0.0076366 | -0.48894 | -0.98707 | -1.7083 | -3.2015 | -5.7901 | -7.4958 | -8.234
|  | LARKHILL | LW |  |  | 14.0562 | 13.622 | 13.1541 | 12.6943 | 12.1154 | 11.5124 | 10.8462 | 10.0779 | 9.1553 | 8.3595 | 6.5627 | 4.3974 | 3.7966 | 3.3812 | 3.1696 | 2.9389 | 2.6837 | 2.4266 | 2.1214 | 1.7996 | 1.4384 | 1.0008 | 0.43248 | -0.038515 | -0.96475 | -2.0511 | -2.3059 | -2.4733 | 1.6852 | 1.2728 | 0.83074 | 0.39296 | -0.17633 | -0.76746 | -1.3903 | -2.09 | -2.9255 | -3.6535 | -5.3345 | -7.3639 | -7.9255 | -8.314
|  | LARKHILL | ST |  |  | 14.5014 | 14.345 | 14.1672 | 13.9904 | 13.7876 | 13.5686 | 13.3291 | 13.0668 | 12.768 | 12.4636 | 11.0582 | 9.0392 | 8.0059 | 7.3727 | 3.3691 | 3.2711 | 3.1551 | 3.0328 | 2.901 | 2.7564 | 2.5937 | 2.4111 | 2.1965 | 1.9957 | 0.97975 | -0.4145 | -1.1522 | -1.8154 | 2.1349 | 1.9977 | 1.8427 | 1.6852 | 1.4921 | 1.285 | 1.0606 | 0.81661 | 0.54021 | 0.25096 | -1.0343 | -2.9751 | -3.9708 | -4.5667
|  | LARKHILL | SP |  |  | 14.5436 | 14.4048 | 14.2619 | 14.128 | 13.9058 | 13.679 | 13.4452 | 13.1752 | 12.8956 | 12.5417 | 11.3147 | 8.2191 | 6.6075 | 5.7597 | 3.3818 | 3.2871 | 3.187 | 3.0869 | 2.9634 | 2.8365 | 2.7025 | 2.5384 | 2.3634 | 2.1569 | 1.3829 | -0.7004 | -1.8415 | -2.7379 | 2.1797 | 2.0621 | 1.941 | 1.8245 | 1.6045 | 1.3801 | 1.1501 | 0.88905 | 0.61909 | 0.2722 | -0.90397 | -3.755 | -5.2625 | -6.057
COWLEY GSP | WITNEY BSP | LEAFIELD | MINIMUM HEADROOM | SP 30282 15270 | NO | 19.4326 | 19.0942 | 18.7258 | 18.3427 | 17.7372 | 17.1143 | 16.4474 | 15.7433 | 14.9341 | 14.019 | 11.6105 | 8.3988 | 4.9551 | 2.8093 | 22.6162 | 22.3892 | 22.1476 | 21.8896 | 21.5451 | 21.1883 | 20.7883 | 20.3606 | 19.8422 | 19.2436 | 17.802 | 15.4317 | 13.0175 | 9.4964 | 20.3521 | 20.0436 | 19.7051 | 19.3481 | 18.7947 | 18.2243 | 17.6092 | 16.9584 | 16.2043 | 15.3471 | 13.125 | 10.2926 | 7.3742 | 5.5671
|  | LEAFIELD | CT |  |  | 19.5691 | 19.3112 | 19.08 | 18.7575 | 18.346 | 17.919 | 17.4688 | 16.989 | 16.461 | 15.5509 | 12.9537 | 8.6016 | 4.9551 | 2.8093 | 22.648 | 22.4356 | 22.2522 | 21.9855 | 21.6937 | 21.3883 | 21.0577 | 20.7013 | 20.2962 | 19.671 | 17.9254 | 15.4317 | 13.0175 | 10.4557 | 20.4754 | 20.2369 | 20.0227 | 19.717 | 19.3357 | 18.9394 | 18.5195 | 18.0714 | 17.5753 | 16.7269 | 14.3282 | 10.5005 | 7.3742 | 5.5671
|  | LEAFIELD | LW |  |  | 19.4326 | 19.0942 | 18.7258 | 18.3427 | 17.7372 | 17.1143 | 16.4474 | 15.7433 | 14.9341 | 14.019 | 11.6105 | 8.3988 | 6.4263 | 5.0037 | 22.6162 | 22.3892 | 22.1476 | 21.8896 | 21.5451 | 21.1883 | 20.7883 | 20.3606 | 19.8422 | 19.2436 | 17.802 | 16.2175 | 15.3355 | 14.6651 | 20.3521 | 20.0436 | 19.7051 | 19.3481 | 18.7947 | 18.2243 | 17.6092 | 16.9584 | 16.2043 | 15.3471 | 13.125 | 10.2926 | 8.6365 | 7.4623
|  | LEAFIELD | ST |  |  | 19.6851 | 19.5054 | 19.3658 | 19.2248 | 19.0382 | 18.845 | 18.6362 | 18.4034 | 18.1487 | 17.888 | 16.7817 | 13.7556 | 11.8069 | 10.2792 | 22.7263 | 22.5658 | 22.4434 | 22.3202 | 22.1653 | 22.0049 | 21.8206 | 21.6079 | 21.3706 | 21.1384 | 20.1246 | 17.5057 | 15.5863 | 13.2812 | 20.581 | 20.4161 | 20.2922 | 20.167 | 19.9937 | 19.814 | 19.6181 | 19.3988 | 19.1575 | 18.9135 | 17.8674 | 15.0832 | 13.4262 | 12.1635
|  | LEAFIELD | SP |  |  | 19.7044 | 19.5169 | 19.3723 | 19.2354 | 19.0545 | 18.8715 | 18.6735 | 18.4644 | 18.2409 | 17.9893 | 17.0584 | 14.4335 | 12.5811 | 11.5192 | 22.7317 | 22.5579 | 22.4218 | 22.2914 | 22.1488 | 21.9995 | 21.8375 | 21.6569 | 21.4514 | 21.1992 | 20.2147 | 17.3534 | 14.0668 | 9.4964 | 20.5984 | 20.4277 | 20.298 | 20.1718 | 20.0084 | 19.8421 | 19.662 | 19.4698 | 19.2633 | 19.0308 | 18.1659 | 15.7422 | 14.1117 | 13.2477
WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK | MINIMUM HEADROOM | TQ 20539 81536 | YES | 1.8952 | 1.6264 | 1.3621 | 1.0898 | 0.69188 | 0.28047 | -0.14856 | -0.60992 | -1.1757 | -1.7271 | -2.8866 | -4.2145 | -4.6002 | -4.799 | 1.563 | 1.4324 | 1.2986 | 1.1563 | 0.95949 | 0.75361 | 0.5308 | 0.28455 | -0.045896 | -0.3541 | -0.89388 | -1.497 | -1.6622 | -2.065 | 0.88686 | 0.64007 | 0.39594 | 0.14487 | -0.22353 | -0.60383 | -0.99943 | -1.4238 | -1.9388 | -2.4442 | -3.5321 | -4.769 | -5.116 | -5.2903
|  | LEAMINGTON PARK | CT |  |  | 2.1422 | 1.9963 | 1.8551 | 1.6911 | 1.4513 | 1.1979 | 0.93923 | 0.64151 | 0.3039 | -0.20676 | -1.2602 | -2.9572 | -3.8155 | -3.9251 | 1.6447 | 1.5544 | 1.4628 | 1.3517 | 1.2144 | 1.0675 | 0.91437 | 0.73125 | 0.5137 | 0.20723 | -0.34043 | -1.1349 | -1.5718 | -1.7764 | 1.1141 | 0.98004 | 0.84704 | 0.69121 | 0.46949 | 0.23518 | -0.0049395 | -0.2834 | -0.60209 | -1.0801 | -2.0394 | -3.5907 | -4.401 | -4.5036
|  | LEAMINGTON PARK | LW |  |  | 1.8952 | 1.6264 | 1.3621 | 1.0898 | 0.69188 | 0.28047 | -0.14856 | -0.60992 | -1.1757 | -1.7271 | -2.8866 | -4.2145 | -4.6002 | -4.7792 | 1.563 | 1.4324 | 1.2986 | 1.1563 | 0.95949 | 0.75361 | 0.5308 | 0.28455 | -0.045896 | -0.3541 | -0.89388 | -1.497 | -1.6482 | -1.7172 | 0.88686 | 0.64007 | 0.39594 | 0.14487 | -0.22353 | -0.60383 | -0.99943 | -1.4238 | -1.9388 | -2.4442 | -3.5321 | -4.769 | -5.116 | -5.2794
|  | LEAMINGTON PARK | ST |  |  | 2.229 | 2.1281 | 2.0272 | 1.9178 | 1.7582 | 1.5995 | 1.433 | 1.2585 | 1.0676 | 0.86738 | 0.018995 | -1.2794 | -2.0115 | -2.4985 | 1.7125 | 1.6582 | 1.6014 | 1.5365 | 1.4471 | 1.356 | 1.2564 | 1.1492 | 1.0268 | 0.9085 | 0.35345 | -0.43993 | -0.8549 | -1.1992 | 1.1982 | 1.107 | 1.014 | 0.91353 | 0.76694 | 0.62182 | 0.46978 | 0.30896 | 0.13004 | -0.055639 | -0.85833 | -2.0612 | -2.7145 | -3.1637
|  | LEAMINGTON PARK | SP |  |  | 2.2578 | 2.171 | 2.0907 | 2.0084 | 1.7547 | 1.4912 | 1.2331 | 0.95789 | 0.67767 | 0.34385 | -0.75312 | -2.9862 | -4.0779 | -4.799 | 1.7236 | 1.6719 | 1.6215 | 1.5687 | 1.453 | 1.3291 | 1.2062 | 1.0708 | 0.93011 | 0.76771 | 0.20881 | -1.0789 | -1.6622 | -2.065 | 1.2252 | 1.1479 | 1.0738 | 0.99761 | 0.7617 | 0.51618 | 0.27224 | 0.012965 | -0.24993 | -0.56463 | -1.5798 | -3.618 | -4.6422 | -5.2903
MINETY GSP | STRATTON (2 X 60) | LECHLADE | MINIMUM HEADROOM | SP 22074 00496 | NO | 4.281 | 4.1969 | 14.3784 | 14.2586 | 13.9958 | 13.6079 | 13.1974 | 12.7596 | 12.2303 | 11.6853 | 9.7836 | 6.7497 | 4.3582 | 2.3821 | 3.3691 | 3.3512 | 15.4105 | 15.3826 | 15.3535 | 15.3221 | 15.288 | 15.251 | 15.2017 | 14.9971 | 13.8944 | 11.7993 | 9.8589 | 7.3237 | 2.0322 | 1.962 | 13.8625 | 13.6634 | 13.3458 | 13.0051 | 12.6439 | 12.2585 | 11.7878 | 11.2843 | 9.5283 | 6.8344 | 4.8639 | 3.2221
|  | LECHLADE | CT |  |  | 4.281 | 4.1969 | 14.3784 | 14.2598 | 14.1312 | 13.9884 | 13.7484 | 13.4362 | 13.0743 | 12.5644 | 10.8244 | 7.209 | 4.3582 | 2.3821 | 3.3691 | 3.3512 | 15.4105 | 15.3826 | 15.3535 | 15.3221 | 15.288 | 15.251 | 15.2064 | 15.0673 | 13.9612 | 11.7993 | 9.8589 | 7.5126 | 2.0322 | 2.0046 | 13.9832 | 13.8098 | 13.6125 | 13.3748 | 13.1184 | 12.842 | 12.5168 | 12.073 | 10.48 | 7.2808 | 4.8639 | 3.2221
|  | LECHLADE | LW |  |  | 4.2933 | 4.2021 | 14.3794 | 14.2586 | 13.9958 | 13.6079 | 13.1974 | 12.7596 | 12.2303 | 11.6853 | 9.7836 | 6.7497 | 4.8192 | 3.3215 | 3.3722 | 3.355 | 15.4127 | 15.3876 | 15.3594 | 15.3276 | 15.2919 | 15.2529 | 15.2017 | 14.9971 | 13.8944 | 12.2945 | 11.4197 | 10.7017 | 2.0353 | 1.962 | 13.8625 | 13.6634 | 13.3458 | 13.0051 | 12.6439 | 12.2585 | 11.7878 | 11.2843 | 9.5283 | 6.8344 | 5.2332 | 4.0117
|  | LECHLADE | ST |  |  | 4.3443 | 4.2969 | 14.5267 | 14.4683 | 14.3943 | 14.3083 | 14.2129 | 14.1031 | 13.9501 | 13.7734 | 13.028 | 10.3653 | 8.4063 | 7.0039 | 3.3808 | 3.3694 | 15.4373 | 15.4229 | 15.4041 | 15.383 | 15.3607 | 15.3348 | 15.3041 | 15.2724 | 15.1229 | 12.9719 | 11.0173 | 9.0042 | 2.0522 | 2.0368 | 14.0997 | 14.0789 | 14.0507 | 13.9426 | 13.8072 | 13.65 | 13.4223 | 13.1475 | 12.0093 | 8.9261 | 7.2194 | 6.6389
|  | LECHLADE | SP |  |  | 4.3496 | 4.3074 | 14.5399 | 14.4878 | 14.4287 | 14.3638 | 14.2934 | 14.2163 | 14.1145 | 14.0035 | 13.5764 | 11.8833 | 9.8531 | 8.5972 | 3.3811 | 3.3692 | 15.4357 | 15.4213 | 15.4053 | 15.3879 | 15.3686 | 15.3477 | 15.3228 | 15.2958 | 15.1876 | 13.3225 | 10.6595 | 7.3237 | 2.053 | 2.037 | 14.0979 | 14.0779 | 14.0559 | 14.0323 | 13.9372 | 13.8313 | 13.6871 | 13.5203 | 12.9027 | 10.8162 | 8.6534 | 7.8478
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD | MINIMUM HEADROOM | SU 43962 77635 | YES | 3.8653 | 3.6042 | 3.3223 | 7.7786 | 7.3565 | 6.9244 | 6.4733 | 5.9772 | 5.3685 | 4.7799 | 3.4231 | 1.8075 | 1.3642 | 1.0402 | 2.9935 | 2.8698 | 2.7343 | 8.8914 | 8.6913 | 8.4845 | 8.2649 | 8.0195 | 7.7102 | 7.4144 | 6.789 | 6.0699 | 5.8278 | 5.5431 | 2.3222 | 2.0803 | 1.8227 | 7.8558 | 7.4653 | 7.0677 | 6.6517 | 6.1961 | 5.6415 | 5.1018 | 3.8631 | 2.4172 | 2.0143 | 1.7199
|  | LECKHAMPSTEAD | CT |  |  | 4.0975 | 3.9612 | 3.8106 | 8.3814 | 8.1264 | 7.8612 | 7.5809 | 7.2598 | 6.8877 | 6.3527 | 5.1735 | 3.1422 | 1.7844 | 1.4874 | 3.0823 | 3.006 | 2.9207 | 9.1175 | 8.9842 | 8.8441 | 8.6945 | 8.5206 | 8.3157 | 8.0363 | 7.445 | 6.4708 | 5.8278 | 5.5431 | 2.5523 | 2.4284 | 2.2918 | 8.4305 | 8.1967 | 7.954 | 7.6978 | 7.4056 | 7.0696 | 6.5825 | 5.4882 | 3.6015 | 2.3984 | 2.1287
|  | LECKHAMPSTEAD | LW |  |  | 3.8653 | 3.6042 | 3.3223 | 7.7786 | 7.3565 | 6.9244 | 6.4733 | 5.9772 | 5.3685 | 4.7799 | 3.4231 | 1.8075 | 1.3642 | 1.0402 | 2.9935 | 2.8698 | 2.7343 | 8.8914 | 8.6913 | 8.4845 | 8.2649 | 8.0195 | 7.7102 | 7.4144 | 6.789 | 6.0699 | 5.886 | 5.7548 | 2.3222 | 2.0803 | 1.8227 | 7.8558 | 7.4653 | 7.0677 | 6.6517 | 6.1961 | 5.6415 | 5.1018 | 3.8631 | 2.4172 | 2.0143 | 1.7199
|  | LECKHAMPSTEAD | ST |  |  | 4.1789 | 4.0971 | 4.0066 | 8.6533 | 8.5043 | 8.3455 | 8.1801 | 8.0041 | 7.8021 | 7.588 | 6.6922 | 5.3266 | 4.5541 | 4.0345 | 3.1305 | 3.0857 | 3.0355 | 9.2767 | 9.1972 | 9.1112 | 9.02 | 8.9217 | 8.8071 | 8.6919 | 8.1904 | 7.4128 | 6.9563 | 6.5704 | 2.6211 | 2.5458 | 2.4644 | 8.6713 | 8.5346 | 8.3893 | 8.2383 | 8.0778 | 7.8943 | 7.6979 | 6.8883 | 5.6322 | 4.9063 | 4.4168
|  | LECKHAMPSTEAD | SP |  |  | 4.2061 | 4.138 | 4.0636 | 8.737 | 8.5137 | 8.2852 | 8.0616 | 7.8202 | 7.5732 | 7.2678 | 6.2525 | 3.9973 | 2.7843 | 2.0205 | 3.1411 | 3.101 | 3.0559 | 9.3085 | 9.2011 | 9.0895 | 8.9798 | 8.8585 | 8.7323 | 8.5824 | 8.0659 | 6.8598 | 6.2112 | 5.7469 | 2.6476 | 2.5868 | 2.5197 | 8.7499 | 8.5417 | 8.3276 | 8.1159 | 7.8912 | 7.6622 | 7.3766 | 6.4472 | 4.3816 | 3.2838 | 2.61
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT | MINIMUM HEADROOM | SU 56858 00293 | YES | 1.0149 | 0.61955 | 0.2247 | -0.17579 | -0.71779 | -1.2713 | -1.8112 | -2.354 | -2.7802 | -3.0234 | -3.4011 | -5.0135 | -6.6584 | -7.7815 | 1.4078 | 1.2506 | 1.0953 | 0.93345 | 0.71861 | 0.48035 | 0.23837 | -0.028874 | -0.27742 | -0.44356 | -0.64906 | -1.3667 | -2.0752 | -2.5696 | 0.19586 | -0.15124 | -0.49722 | -0.84972 | -1.3237 | -1.8093 | -2.2875 | -2.7818 | -3.1909 | -3.4324 | -3.7758 | -5.1356 | -6.5673 | -7.5547
|  | LEE-ON-SOLENT | CT |  |  | 1.4594 | 1.2902 | 1.1013 | 0.9183 | 0.62878 | 0.32748 | 0.025972 | -0.30661 | -0.57399 | -0.83817 | -1.1428 | -1.5683 | -1.7063 | -1.7594 | 1.5197 | 1.4263 | 1.3168 | 1.2113 | 1.0757 | 0.93295 | 0.78352 | 0.60183 | 0.43006 | 0.22792 | 0.025049 | -0.24706 | -0.38877 | -0.54756 | 0.56645 | 0.41033 | 0.23463 | 0.064824 | -0.19357 | -0.46623 | -0.74018 | -1.0454 | -1.2951 | -1.5624 | -1.8489 | -2.233 | -2.3509 | -2.3945
|  | LEE-ON-SOLENT | LW |  |  | 1.0149 | 0.61955 | 0.2247 | -0.17579 | -0.71779 | -1.2713 | -1.8112 | -2.354 | -2.7802 | -3.0234 | -3.4011 | -3.825 | -3.8711 | -3.8814 | 1.4078 | 1.2506 | 1.0953 | 0.93345 | 0.71861 | 0.48035 | 0.23837 | -0.028874 | -0.27742 | -0.44356 | -0.64906 | -0.88254 | -0.90638 | -0.91227 | 0.19586 | -0.15124 | -0.49722 | -0.84972 | -1.3237 | -1.8093 | -2.2875 | -2.7818 | -3.1909 | -3.4324 | -3.7758 | -4.1628 | -4.2042 | -4.213
|  | LEE-ON-SOLENT | ST |  |  | 1.531 | 1.4067 | 1.2774 | 1.1401 | 0.94291 | 0.7389 | 0.53369 | 0.31835 | 0.091321 | -0.15857 | -1.1022 | -2.4993 | -2.9435 | -3.043 | 1.5855 | 1.5289 | 1.4661 | 1.3933 | 1.3054 | 1.2118 | 1.1128 | 1.005 | 0.88404 | 0.76598 | 0.21412 | -0.48635 | -0.75836 | -0.93823 | 0.63979 | 0.52967 | 0.41366 | 0.28809 | 0.11325 | -0.068539 | -0.25289 | -0.44772 | -0.65585 | -0.88002 | -1.7639 | -3.0173 | -3.4005 | -3.484
|  | LEE-ON-SOLENT | SP |  |  | 1.576 | 1.4843 | 1.394 | 1.3014 | 0.958 | 0.61357 | 0.27388 | -0.080594 | -0.44187 | -0.87212 | -2.2505 | -5.0135 | -6.6584 | -7.7815 | 1.5963 | 1.5499 | 1.5035 | 1.4537 | 1.3294 | 1.2047 | 1.08 | 0.9406 | 0.79039 | 0.60596 | -0.014411 | -1.3667 | -2.0752 | -2.5696 | 0.67685 | 0.5945 | 0.51369 | 0.43019 | 0.13537 | -0.15998 | -0.45154 | -0.7593 | -1.0735 | -1.4466 | -2.6608 | -5.1356 | -6.5673 | -7.5547
LOVEDEAN GSP | HAVANT | LEIGH PARK | MINIMUM HEADROOM | SU 72144 07875 | YES | 10.957 | 10.5983 | 10.1478 | 9.6309 | 8.7762 | 7.8638 | 6.8812 | 5.8362 | 4.5714 | 3.2152 | 0.041831 | -4.1153 | -8.1122 | -10.8177 | 15.2931 | 15.0811 | 14.8024 | 14.482 | 14.0206 | 13.5208 | 12.9412 | 12.3085 | 11.4642 | 10.5516 | 8.6695 | 6.0054 | 3.3772 | 0.88285 | 12.2963 | 11.9835 | 11.5946 | 11.1515 | 10.3986 | 9.5965 | 8.7343 | 7.8179 | 6.645 | 5.3812 | 2.4882 | -1.1893 | -4.5668 | -6.8441
|  | LEIGH PARK | CT |  |  | 11.1084 | 10.8594 | 10.5479 | 10.1019 | 9.5233 | 8.893 | 8.2387 | 7.533 | 6.6591 | 5.2935 | 1.8159 | -3.6526 | -8.1122 | -10.8177 | 15.3186 | 15.1345 | 14.9051 | 14.5766 | 14.2074 | 13.7954 | 13.3299 | 12.8242 | 12.1741 | 11.2413 | 9.0166 | 6.0054 | 3.3772 | 0.88285 | 12.4372 | 12.2245 | 11.9599 | 11.5839 | 11.0826 | 10.5378 | 9.9735 | 9.3333 | 8.518 | 7.251 | 4.0737 | -0.74317 | -4.5668 | -6.8441
|  | LEIGH PARK | LW |  |  | 10.957 | 10.5983 | 10.1478 | 9.6309 | 8.7762 | 7.8638 | 6.8812 | 5.8362 | 4.5714 | 3.2152 | 0.041831 | -4.1153 | -6.6666 | -8.4492 | 15.2931 | 15.0811 | 14.8024 | 14.482 | 14.0206 | 13.5208 | 12.9412 | 12.3085 | 11.4642 | 10.5516 | 8.6695 | 6.5048 | 5.3289 | 4.4643 | 12.2963 | 11.9835 | 11.5946 | 11.1515 | 10.3986 | 9.5965 | 8.7343 | 7.8179 | 6.645 | 5.3812 | 2.4882 | -1.1893 | -3.334 | -4.8025
|  | LEIGH PARK | ST |  |  | 11.3528 | 11.2512 | 11.113 | 10.932 | 10.6862 | 10.4095 | 10.1046 | 9.7688 | 9.3693 | 8.9363 | 7.0669 | 3.0777 | 0.49394 | -1.4604 | 15.4816 | 15.3945 | 15.2793 | 15.132 | 14.9412 | 14.7266 | 14.4868 | 14.2209 | 13.9008 | 13.5534 | 11.9637 | 8.7331 | 6.6155 | 4.3961 | 12.6521 | 12.5694 | 12.4576 | 12.313 | 12.1102 | 11.882 | 11.6295 | 11.3507 | 11.0186 | 10.6542 | 8.913 | 5.2429 | 3.0348 | 1.4188
|  | LEIGH PARK | SP |  |  | 11.3831 | 11.2796 | 11.1582 | 11.01 | 10.837 | 10.6477 | 10.4339 | 10.1888 | 9.9037 | 9.5589 | 8.25 | 4.6698 | 2.339 | 0.96293 | 15.4919 | 15.3952 | 15.2822 | 15.1493 | 15.0072 | 14.8507 | 14.6708 | 14.4619 | 14.2187 | 13.915 | 12.6634 | 9.0983 | 6.0079 | 2.3591 | 12.6795 | 12.5966 | 12.5003 | 12.3848 | 12.2454 | 12.0934 | 11.9206 | 11.7216 | 11.4899 | 11.2058 | 10.0472 | 6.7002 | 4.6448 | 3.5277
BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD | MINIMUM HEADROOM | SU 75372 72019 | YES | 15.7082 | 15.5392 | 15.1769 | 14.7852 | 14.3167 | 13.7228 | 13.0885 | 12.4151 | 11.5343 | 10.6119 | 7.6483 | 3.5607 | 0.11493 | -1.9964 | 19.6117 | 19.5006 | 19.2913 | 19.0342 | 18.7773 | 18.3856 | 17.959 | 17.514 | 16.9107 | 16.2793 | 14.105 | 10.4852 | 7.3739 | 0.88842 | 18.0714 | 17.938 | 17.6801 | 17.3465 | 16.9126 | 16.3532 | 15.7461 | 15.108 | 14.2709 | 13.3935 | 10.5981 | 6.9543 | 4.215 | 2.491
|  | LITTLE HUNGERFORD | CT |  |  | 15.7564 | 15.6236 | 15.3356 | 14.9613 | 14.619 | 14.1533 | 13.6581 | 13.1316 | 12.4654 | 11.5296 | 8.5437 | 3.5607 | 0.11493 | -1.9964 | 19.6117 | 19.5006 | 19.3009 | 19.0342 | 18.7796 | 18.4052 | 18.0051 | 17.5871 | 17.0433 | 16.3523 | 14.105 | 10.4852 | 7.3739 | 3.7493 | 18.1169 | 18.0169 | 17.8122 | 17.4965 | 17.169 | 16.7178 | 16.2343 | 15.728 | 15.086 | 14.2061 | 11.4214 | 7.0559 | 4.215 | 2.491
|  | LITTLE HUNGERFORD | LW |  |  | 15.7082 | 15.5392 | 15.1769 | 14.7852 | 14.3167 | 13.7228 | 13.0885 | 12.4151 | 11.5343 | 10.6119 | 7.6483 | 3.5939 | 1.4851 | 0.090966 | 19.6173 | 19.5129 | 19.2913 | 19.0511 | 18.7773 | 18.3856 | 17.959 | 17.514 | 16.9107 | 16.2793 | 14.2484 | 11.7533 | 10.6765 | 9.9206 | 18.0714 | 17.938 | 17.6801 | 17.3465 | 16.9126 | 16.3532 | 15.7461 | 15.108 | 14.2709 | 13.3935 | 10.5981 | 6.9543 | 5.2136 | 4.0703
|  | LITTLE HUNGERFORD | ST |  |  | 15.8744 | 15.8152 | 15.6617 | 15.4984 | 15.3507 | 15.0912 | 14.8206 | 14.5391 | 14.1376 | 13.718 | 12.0663 | 8.4721 | 6.1611 | 4.5729 | 19.6912 | 19.6295 | 19.5106 | 19.3806 | 19.2351 | 18.9775 | 18.7037 | 18.4243 | 18.0346 | 17.6222 | 16.0202 | 12.6515 | 9.7897 | 6.3722 | 18.2082 | 18.166 | 18.0695 | 17.9649 | 17.8541 | 17.6203 | 17.3566 | 17.0819 | 16.6936 | 16.2965 | 14.7045 | 11.3043 | 9.2949 | 8.0036
|  | LITTLE HUNGERFORD | SP |  |  | 15.8859 | 15.8209 | 15.6729 | 15.5185 | 15.3988 | 15.1731 | 14.9442 | 14.7046 | 14.3702 | 14.0149 | 12.7095 | 10.0389 | 8.0144 | 6.9015 | 19.693 | 19.6216 | 19.4974 | 19.3633 | 19.2302 | 18.9857 | 18.7286 | 18.4651 | 18.1043 | 17.6686 | 16.0441 | 12.483 | 7.8569 | 0.88842 | 18.2188 | 18.1764 | 18.0868 | 17.9925 | 17.8998 | 17.6884 | 17.4696 | 17.251 | 16.9357 | 16.6006 | 15.3563 | 12.785 | 10.9647 | 10.0383
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW | MINIMUM HEADROOM | SU 86037 87794 | YES | 28.0687 | 27.3455 | 26.5579 | 25.6878 | 24.2249 | 22.6604 | 20.9404 | 19.0725 | 16.6247 | 14.1211 | 9.12 | 2.8725 | -1.5726 | -4.0589 | 21.835 | 21.3517 | 20.7764 | 20.1416 | 19.389 | 18.4539 | 17.3879 | 16.2107 | 14.5316 | 12.8294 | 9.779 | 4.9553 | 0.90485 | -3.1414 | 18.1249 | 17.4121 | 16.6578 | 15.8216 | 14.4551 | 12.9901 | 11.3684 | 9.6015 | 7.2478 | 4.8445 | 0.14962 | -5.6006 | -9.3954 | -11.5523
|  | LITTLE MARLOW | CT |  |  | 28.2316 | 27.6346 | 26.937 | 26.1731 | 25.1781 | 24.1033 | 22.9815 | 21.7445 | 20.2153 | 17.5943 | 12.033 | 3.8682 | -1.5726 | -4.0589 | 21.835 | 21.3517 | 20.7764 | 20.1416 | 19.433 | 18.6597 | 17.8172 | 16.8774 | 15.6917 | 13.8387 | 10.1009 | 4.9553 | 0.90485 | -3.1414 | 18.2279 | 17.6536 | 16.9728 | 16.2263 | 15.2807 | 14.2581 | 13.1822 | 11.9928 | 10.5128 | 8.0031 | 2.7826 | -4.6097 | -9.3954 | -11.5523
|  | LITTLE MARLOW | LW |  |  | 28.0687 | 27.3455 | 26.5579 | 25.6878 | 24.2249 | 22.6604 | 20.9404 | 19.0725 | 16.6247 | 14.1211 | 9.12 | 2.8725 | 0.49958 | -0.4511 | 21.882 | 21.3826 | 20.8492 | 20.2492 | 19.389 | 18.4539 | 17.3879 | 16.2107 | 14.5316 | 12.8294 | 9.779 | 6.2964 | 5.2566 | 4.8239 | 18.1249 | 17.4121 | 16.6578 | 15.8216 | 14.4551 | 12.9901 | 11.3684 | 9.6015 | 7.2478 | 4.8445 | 0.14962 | -5.6006 | -7.6766 | -8.4858
|  | LITTLE MARLOW | ST |  |  | 28.8176 | 28.6095 | 28.3565 | 28.0136 | 27.6007 | 27.134 | 26.6096 | 26.0162 | 25.3008 | 24.5597 | 20.7912 | 13.8972 | 10.6276 | 8.5667 | 22.2976 | 22.0835 | 21.8158 | 21.49 | 21.1209 | 20.7049 | 20.2317 | 19.6939 | 19.0452 | 18.407 | 15.1832 | 9.29 | 5.7613 | 1.8806 | 18.8463 | 18.6327 | 18.3588 | 18.0211 | 17.6195 | 17.1658 | 16.6539 | 16.0733 | 15.3711 | 14.6521 | 10.915 | 4.3076 | 1.4026 | -0.38117
|  | LITTLE MARLOW | SP |  |  | 28.8619 | 28.6608 | 28.457 | 28.2044 | 27.8853 | 27.5307 | 27.1642 | 26.6971 | 26.1565 | 25.536 | 23.0325 | 15.7492 | 12.4426 | 11.2438 | 22.3089 | 22.084 | 21.837 | 21.5621 | 21.2701 | 20.943 | 20.5938 | 20.1546 | 19.639 | 19.0333 | 16.5686 | 9.3607 | 3.7593 | -3.1195 | 18.8854 | 18.6736 | 18.4498 | 18.2017 | 17.8945 | 17.5537 | 17.2002 | 16.7467 | 16.2198 | 15.6181 | 13.1777 | 5.9636 | 2.8291 | 1.7704
NURSLING GSP | ROWNHAMS | LORDSHILL | MINIMUM HEADROOM | SU 38746 16055 | YES | 11.6615 | 11.2566 | 10.8163 | 10.3012 | 9.4581 | 8.5635 | 7.5951 | 6.5113 | 5.1341 | 3.7705 | 0.79327 | -3.0162 | -5.4569 | -7.0945 | 17.9211 | 17.6653 | 17.3614 | 17.0332 | 16.6122 | 16.1185 | 15.5692 | 14.9422 | 14.0427 | 13.1544 | 11.4113 | 8.1178 | 5.1748 | 0.36528 | 13.7183 | 13.3044 | 12.852 | 12.3632 | 11.5802 | 10.7469 | 9.8396 | 8.8186 | 7.5045 | 6.207 | 3.4336 | -0.051947 | -2.1226 | -3.4916
|  | LORDSHILL | CT |  |  | 11.8526 | 11.549 | 11.156 | 10.7369 | 10.1758 | 9.5729 | 8.9365 | 8.202 | 7.3619 | 5.947 | 2.8501 | -2.093 | -5.4569 | -7.0945 | 17.9211 | 17.6653 | 17.3614 | 17.0332 | 16.6449 | 16.223 | 15.7645 | 15.2261 | 14.5598 | 13.5593 | 11.4473 | 8.1178 | 5.1748 | 1.7651 | 13.8364 | 13.5189 | 13.1383 | 12.732 | 12.2021 | 11.6314 | 11.0258 | 10.3235 | 9.5163 | 8.1701 | 5.2847 | 0.8266 | -2.1226 | -3.4916
|  | LORDSHILL | LW |  |  | 11.6615 | 11.2566 | 10.8163 | 10.3012 | 9.4581 | 8.5635 | 7.5951 | 6.5113 | 5.1341 | 3.7705 | 0.79327 | -3.0162 | -4.4909 | -5.1722 | 17.9227 | 17.6654 | 17.382 | 17.0716 | 16.6122 | 16.1185 | 15.5692 | 14.9422 | 14.0427 | 13.1544 | 11.4113 | 9.3413 | 8.6905 | 8.3788 | 13.7183 | 13.3044 | 12.852 | 12.3632 | 11.5802 | 10.7469 | 9.8396 | 8.8186 | 7.5045 | 6.207 | 3.4336 | -0.051947 | -1.3348 | -1.9115
|  | LORDSHILL | ST |  |  | 12.1293 | 12.0214 | 11.8839 | 11.7231 | 11.4792 | 11.209 | 10.9091 | 10.573 | 10.1716 | 9.7416 | 7.6631 | 3.8603 | 1.8809 | 0.59644 | 18.1384 | 18.0168 | 17.864 | 17.6832 | 17.4671 | 17.2298 | 16.9617 | 16.6591 | 16.2988 | 15.9354 | 14.1642 | 10.6758 | 8.092 | 4.9175 | 14.1588 | 14.0406 | 13.8835 | 13.6952 | 13.4573 | 13.1973 | 12.9075 | 12.582 | 12.1919 | 11.7786 | 9.7579 | 6.1456 | 4.3724 | 3.2668
|  | LORDSHILL | SP |  |  | 12.1607 | 12.0656 | 11.9578 | 11.8395 | 11.6321 | 11.3967 | 11.1553 | 10.8728 | 10.5459 | 10.1569 | 8.6644 | 4.5192 | 2.3754 | 1.4562 | 18.1436 | 18.0188 | 17.8716 | 17.7094 | 17.5082 | 17.2857 | 17.0448 | 16.7609 | 16.4304 | 16.0512 | 14.5672 | 10.1783 | 6.0324 | 0.36528 | 14.1854 | 14.0747 | 13.9471 | 13.808 | 13.604 | 13.3817 | 13.1529 | 12.8825 | 12.5691 | 12.1982 | 10.7647 | 6.7674 | 4.7592 | 3.9433
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE | MINIMUM HEADROOM | SU 47334 68495 | YES | 17.7706 | 17.6465 | 17.5046 | 17.3469 | 17.081 | 16.795 | 16.4908 | 16.165 | 15.7704 | 15.0316 | 12.7792 | 9.2435 | 5.6603 | 3.2297 | 20.374 | 20.254 | 20.1055 | 19.938 | 19.6701 | 19.3777 | 19.0556 | 18.7051 | 18.256 | 17.7683 | 16.4803 | 14.2676 | 12.073 | 10.0037 | 19.8569 | 19.7443 | 19.6145 | 19.4696 | 19.2288 | 18.9691 | 18.6908 | 18.3918 | 17.868 | 17.2945 | 15.2371 | 12.1135 | 9.1089 | 7.0802
|  | LOVE LANE | CT |  |  | 17.8154 | 17.7242 | 17.6203 | 17.4888 | 17.3075 | 17.1104 | 16.8965 | 16.6657 | 16.4105 | 15.9959 | 13.8373 | 9.401 | 5.6603 | 3.2297 | 20.3932 | 20.2898 | 20.1692 | 20.0027 | 19.7865 | 19.5498 | 19.2903 | 19.0042 | 18.6725 | 18.1724 | 16.7397 | 14.2676 | 12.073 | 10.0037 | 19.8953 | 19.812 | 19.7168 | 19.5947 | 19.429 | 19.2484 | 19.0518 | 18.839 | 18.6021 | 18.2197 | 16.1663 | 12.2946 | 9.1089 | 7.0802
|  | LOVE LANE | LW |  |  | 17.7706 | 17.6465 | 17.5046 | 17.3469 | 17.081 | 16.795 | 16.4908 | 16.165 | 15.7704 | 15.0316 | 12.7792 | 9.2435 | 6.8793 | 5.1749 | 20.374 | 20.254 | 20.1055 | 19.938 | 19.6701 | 19.3777 | 19.0556 | 18.7051 | 18.256 | 17.7683 | 16.4803 | 14.5637 | 13.4287 | 12.5668 | 19.8569 | 19.7443 | 19.6145 | 19.4696 | 19.2288 | 18.9691 | 18.6908 | 18.3918 | 17.868 | 17.2945 | 15.2371 | 12.1135 | 10.1405 | 8.7484
|  | LOVE LANE | ST |  |  | 17.89 | 17.8417 | 17.7898 | 17.7323 | 17.6552 | 17.57 | 17.4787 | 17.3781 | 17.2575 | 17.1119 | 16.5018 | 14.4455 | 12.233 | 10.4845 | 20.4809 | 20.4241 | 20.3608 | 20.2878 | 20.1909 | 20.0839 | 19.9658 | 19.8219 | 19.6498 | 19.467 | 18.6432 | 16.4877 | 14.7712 | 13.0042 | 19.9664 | 19.9237 | 19.8777 | 19.8264 | 19.7564 | 19.679 | 19.5951 | 19.5022 | 19.3901 | 19.2553 | 18.6871 | 16.6352 | 14.8068 | 13.4204
|  | LOVE LANE | SP |  |  | 17.8992 | 17.8542 | 17.8069 | 17.7559 | 17.6891 | 17.6177 | 17.537 | 17.4538 | 17.3627 | 17.2518 | 16.8337 | 15.4222 | 13.4031 | 12.0781 | 20.4882 | 20.4287 | 20.3639 | 20.2927 | 20.2122 | 20.1259 | 20.0269 | 19.917 | 19.783 | 19.6057 | 18.8998 | 16.6913 | 14.1222 | 10.9756 | 19.9748 | 19.9348 | 19.8928 | 19.8474 | 19.7879 | 19.7244 | 19.6518 | 19.5763 | 19.4931 | 19.3913 | 19.008 | 17.5216 | 15.6887 | 14.5954
COWLEY GSP | YARNTON BSP | LOVELACE ROAD | MINIMUM HEADROOM | SP 50395 10376 | NO | 19.3076 | 18.5413 | 17.8038 | 17.0438 | 15.8673 | 14.5568 | 13.2798 | 11.8584 | 10.4425 | 9.0525 | 5.599 | 1.74 | 0.63935 | 0.13644 | 14.9731 | 14.5024 | 14.0876 | 13.6703 | 13.087 | 12.4391 | 11.7938 | 11.0584 | 10.2993 | 9.5377 | 7.6215 | 4.171 | -0.44092 | -8.9009 | 10.3388 | 9.6634 | 8.9848 | 8.2882 | 7.2351 | 6.0687 | 4.9164 | 3.6282 | 2.3171 | 1.0211 | -2.1807 | -5.708 | -6.68 | -7.0659
|  | LOVELACE ROAD | CT |  |  | 19.7182 | 19.1879 | 18.6761 | 18.116 | 17.2853 | 16.3253 | 15.4524 | 14.4431 | 13.5236 | 12.219 | 8.8805 | 4.038 | 1.305 | 0.13644 | 15.0781 | 14.6541 | 14.2785 | 13.8799 | 13.3737 | 12.8017 | 12.255 | 11.6146 | 10.9983 | 10.1928 | 7.9244 | 4.171 | 0.83631 | -3.3838 | 10.5235 | 10.1419 | 9.7453 | 9.2241 | 8.4773 | 7.6224 | 6.833 | 5.9162 | 5.0634 | 3.847 | 0.71854 | -3.6258 | -6.0411 | -7.0659
|  | LOVELACE ROAD | LW |  |  | 19.3076 | 18.5413 | 17.8038 | 17.0438 | 15.8673 | 14.5568 | 13.2798 | 11.8584 | 10.4425 | 9.0525 | 5.599 | 1.74 | 0.63935 | 0.24751 | 14.9731 | 14.5024 | 14.0876 | 13.6703 | 13.087 | 12.4391 | 11.7938 | 11.0584 | 10.2993 | 9.5377 | 7.6215 | 5.5079 | 5.0203 | 4.8431 | 10.3388 | 9.6634 | 8.9848 | 8.2882 | 7.2351 | 6.0687 | 4.9164 | 3.6282 | 2.3171 | 1.0211 | -2.1807 | -5.708 | -6.68 | -7.0216
|  | LOVELACE ROAD | ST |  |  | 20.0115 | 19.6553 | 19.3486 | 19.0451 | 18.5999 | 18.075 | 17.589 | 17.014 | 16.474 | 15.9033 | 13.7286 | 9.1635 | 7.1696 | 6.1431 | 15.2464 | 14.9202 | 14.6602 | 14.4068 | 14.0871 | 13.723 | 13.3651 | 12.9344 | 12.5074 | 12.0654 | 10.3757 | 6.3332 | 3.0703 | -1.0901 | 10.6877 | 10.4081 | 10.2035 | 10.0126 | 9.7156 | 9.2586 | 8.8249 | 8.3078 | 7.8088 | 7.282 | 5.2377 | -0.0014276 | -2.5033 | -3.0804
|  | LOVELACE ROAD | SP |  |  | 20.0656 | 19.7338 | 19.466 | 19.2119 | 18.7495 | 18.2241 | 17.7323 | 17.1635 | 16.6549 | 16.0616 | 14.1066 | 9.3534 | 6.4436 | 5.1831 | 15.2534 | 14.9366 | 14.6814 | 14.4366 | 14.1057 | 13.7339 | 13.3629 | 12.922 | 12.4947 | 11.9981 | 10.254 | 5.4497 | -0.44092 | -8.9009 | 10.7118 | 10.4515 | 10.2694 | 10.1058 | 9.8463 | 9.4058 | 8.9741 | 8.47 | 8.0084 | 7.4692 | 5.6735 | 1.2259 | -1.5296 | -2.6736
MANNINGTON GSP | ARNEWOOD | LYMINGTON | MINIMUM HEADROOM | SZ 31720 96856 | YES | 17.4411 | 17.2621 | 17.0128 | 16.723 | 16.1803 | 15.7055 | 15.2883 | 14.8522 | 14.3455 | 13.7336 | 11.7253 | 9.4005 | 7.6945 | 6.5001 | 19.4309 | 19.3224 | 19.1685 | 18.9862 | 18.7224 | 18.4724 | 18.2351 | 17.9828 | 17.6709 | 17.2902 | 16.1237 | 14.43 | 12.9187 | 11.3452 | 18.013 | 17.8491 | 17.623 | 17.3604 | 16.8798 | 16.4521 | 16.0666 | 15.6616 | 15.1864 | 14.6139 | 12.8169 | 10.7236 | 9.2983 | 8.2898
|  | LYMINGTON | CT |  |  | 17.4953 | 17.3561 | 17.1465 | 16.8945 | 16.4594 | 16.0978 | 15.8224 | 15.53 | 15.1985 | 14.6266 | 12.6707 | 9.7726 | 7.6945 | 6.5001 | 19.4309 | 19.3224 | 19.1685 | 18.9862 | 18.7224 | 18.4916 | 18.2939 | 18.0788 | 17.8306 | 17.46 | 16.1896 | 14.43 | 12.9187 | 11.3452 | 18.0576 | 17.9284 | 17.7369 | 17.507 | 17.1225 | 16.7964 | 16.5396 | 16.2651 | 15.9529 | 15.4218 | 13.6204 | 11.0876 | 9.2983 | 8.2898
|  | LYMINGTON | LW |  |  | 17.4411 | 17.2621 | 17.0128 | 16.723 | 16.1803 | 15.7055 | 15.2883 | 14.8522 | 14.3455 | 13.7336 | 11.7253 | 9.4005 | 8.2732 | 7.4939 | 19.4392 | 19.3344 | 19.1862 | 19.0131 | 18.7273 | 18.4724 | 18.2351 | 17.9828 | 17.6709 | 17.2902 | 16.1237 | 14.8937 | 14.3697 | 13.995 | 18.013 | 17.8491 | 17.623 | 17.3604 | 16.8798 | 16.4521 | 16.0666 | 15.6616 | 15.1864 | 14.6139 | 12.8169 | 10.7236 | 9.7725 | 9.1273
|  | LYMINGTON | ST |  |  | 17.6399 | 17.58 | 17.4842 | 17.3617 | 17.1197 | 16.9304 | 16.791 | 16.6467 | 16.4685 | 16.2504 | 15.2862 | 13.0117 | 11.6825 | 10.8632 | 19.5336 | 19.4795 | 19.4026 | 19.3049 | 19.133 | 18.9874 | 18.8634 | 18.7314 | 18.5694 | 18.3947 | 17.6253 | 15.7442 | 14.4478 | 13.0201 | 18.1974 | 18.1444 | 18.0621 | 17.9557 | 17.747 | 17.5786 | 17.4479 | 17.3113 | 17.1419 | 16.9397 | 16.0443 | 13.9052 | 12.7211 | 12.0277
|  | LYMINGTON | SP |  |  | 17.646 | 17.587 | 17.4924 | 17.3829 | 17.183 | 17.0285 | 16.911 | 16.7882 | 16.6479 | 16.4604 | 15.711 | 13.9361 | 12.5106 | 11.8485 | 19.5311 | 19.4727 | 19.3889 | 19.2927 | 19.1517 | 19.0326 | 18.9248 | 18.8071 | 18.67 | 18.5023 | 17.8264 | 16.0795 | 14.1943 | 11.9561 | 18.2025 | 18.1497 | 18.0678 | 17.9733 | 17.8063 | 17.6732 | 17.565 | 17.4507 | 17.3195 | 17.1473 | 16.4619 | 14.7933 | 13.4768 | 12.9057
MELKSHAM GSP | CHIPPENHAM | LYNEHAM | MINIMUM HEADROOM | ST 99348 80481 | YES | 11.162 | 10.6785 | 9.9575 | 9.2098 | 8.0318 | 6.787 | 5.4369 | 3.9745 | 2.4266 | 0.78871 | -3.1727 | -7.4561 | -10.2849 | -12.0551 | 17.7561 | 17.4942 | 17.0245 | 16.539 | 15.9098 | 15.2327 | 14.4679 | 13.609 | 12.6173 | 11.5899 | 9.3783 | 7.1574 | 4.9857 | 3.084 | 13.5262 | 13.076 | 12.3891 | 11.6724 | 10.5963 | 9.4544 | 8.2012 | 6.8273 | 5.3222 | 3.7666 | 0.077884 | -3.7524 | -6.0031 | -7.4545
|  | LYNEHAM | CT |  |  | 11.4755 | 11.1879 | 10.7107 | 10.1154 | 9.3135 | 8.4452 | 7.4805 | 6.4182 | 5.39 | 3.7237 | -0.37294 | -6.1924 | -10.2849 | -12.0551 | 17.7965 | 17.5807 | 17.2053 | 16.7207 | 16.2014 | 15.6389 | 15.0197 | 14.3254 | 13.6106 | 12.5331 | 10.0704 | 7.1574 | 4.9857 | 3.084 | 13.7664 | 13.4792 | 13.0117 | 12.4088 | 11.6499 | 10.8337 | 9.9414 | 8.9546 | 7.9789 | 6.4056 | 2.5822 | -2.6255 | -6.0031 | -7.4545
|  | LYNEHAM | LW |  |  | 11.162 | 10.6785 | 9.9575 | 9.2098 | 8.0318 | 6.787 | 5.4369 | 3.9745 | 2.4266 | 0.78871 | -3.1727 | -7.4561 | -9.0087 | -9.575 | 17.7561 | 17.4942 | 17.0245 | 16.539 | 15.9098 | 15.2327 | 14.4679 | 13.609 | 12.6173 | 11.5899 | 9.3783 | 7.3239 | 6.7516 | 6.5391 | 13.5262 | 13.076 | 12.3891 | 11.6724 | 10.5963 | 9.4544 | 8.2012 | 6.8273 | 5.3222 | 3.7666 | 0.077884 | -3.7524 | -5.0468 | -5.516
|  | LYNEHAM | ST |  |  | 11.7443 | 11.6166 | 11.3237 | 11.0375 | 10.6311 | 10.1875 | 9.701 | 9.1803 | 8.6545 | 8.0986 | 5.7147 | 1.0136 | -1.2212 | -2.6464 | 17.9964 | 17.8984 | 17.6632 | 17.4329 | 17.1297 | 16.7953 | 16.4243 | 16.0229 | 15.6043 | 15.1988 | 13.3513 | 9.8402 | 8.1228 | 6.3801 | 14.0415 | 13.9174 | 13.64 | 13.3658 | 12.9767 | 12.5505 | 12.0806 | 11.5748 | 11.062 | 10.5354 | 8.237 | 3.7509 | 1.7221 | 0.46545
|  | LYNEHAM | SP |  |  | 11.801 | 11.6788 | 11.4031 | 11.1471 | 10.7792 | 10.3682 | 9.95 | 9.487 | 9.0591 | 8.554 | 6.7095 | 2.0297 | -0.50814 | -1.4682 | 18.0101 | 17.8952 | 17.6535 | 17.4275 | 17.1832 | 16.9129 | 16.6218 | 16.2904 | 15.9714 | 15.5956 | 14.1463 | 10.2753 | 7.4333 | 4.4838 | 14.088 | 13.9605 | 13.6937 | 13.4444 | 13.1092 | 12.7359 | 12.3506 | 11.9175 | 11.5051 | 11.0223 | 9.2484 | 4.7519 | 2.3554 | 1.4845
BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E | MINIMUM HEADROOM | SU 98120 65945 | YES | 4.3954 | 4.0687 | 10.898 | 10.5324 | 10.0108 | 9.4788 | 8.913 | 8.2806 | 7.5604 | 6.9224 | 5.4142 | 3.7384 | 3.2909 | 3.0774 | 3.7868 | 3.6231 | 14.0179 | 13.8189 | 13.552 | 13.2788 | 12.9717 | 12.6073 | 12.1711 | 11.7988 | 11.0734 | 10.3036 | 10.0925 | 9.6238 | 1.2099 | 0.91364 | 11.1738 | 10.839 | 10.365 | 9.8811 | 9.3632 | 8.7801 | 8.1118 | 7.5223 | 6.1593 | 4.6529 | 4.2568 | 4.0688
|  | M V E E | CT |  |  | 4.7002 | 4.5402 | 11.5426 | 11.3291 | 11.0217 | 10.7028 | 10.3528 | 9.9544 | 9.514 | 8.8856 | 7.5998 | 5.5062 | 4.1123 | 3.5311 | 3.8757 | 3.7662 | 14.2203 | 14.0596 | 13.871 | 13.673 | 13.4501 | 13.1844 | 12.8839 | 12.4673 | 11.759 | 10.7744 | 10.0925 | 9.6238 | 1.4747 | 1.3254 | 11.7386 | 11.5361 | 11.2521 | 10.9572 | 10.6324 | 10.2604 | 9.8272 | 9.2235 | 8.0599 | 6.2142 | 4.992 | 4.4808
|  | M V E E | LW |  |  | 4.3954 | 4.0687 | 10.898 | 10.5324 | 10.0108 | 9.4788 | 8.913 | 8.2806 | 7.5604 | 6.9224 | 5.4142 | 3.7384 | 3.2909 | 3.0774 | 3.7868 | 3.6231 | 14.0179 | 13.8189 | 13.552 | 13.2788 | 12.9717 | 12.6073 | 12.1711 | 11.7988 | 11.0734 | 10.3036 | 10.1201 | 10.0339 | 1.2099 | 0.91364 | 11.1738 | 10.839 | 10.365 | 9.8811 | 9.3632 | 8.7801 | 8.1118 | 7.5223 | 6.1593 | 4.6529 | 4.2568 | 4.0688
|  | M V E E | ST |  |  | 4.8366 | 4.7551 | 11.8447 | 11.742 | 11.5752 | 11.4034 | 11.2198 | 11.0202 | 10.8012 | 10.5636 | 9.5263 | 8.0252 | 7.229 | 6.7258 | 3.9717 | 3.9159 | 14.4309 | 14.353 | 14.246 | 14.1345 | 14.0094 | 13.8695 | 13.7097 | 13.5561 | 12.806 | 11.7752 | 11.2788 | 10.8424 | 1.6041 | 1.5288 | 12.0247 | 11.9282 | 11.774 | 11.6151 | 11.4441 | 11.2577 | 11.0518 | 10.831 | 9.8293 | 8.407 | 7.7128 | 7.2692
|  | M V E E | SP |  |  | 4.8846 | 4.8226 | 11.9387 | 11.8728 | 11.7135 | 11.5508 | 11.3931 | 11.2138 | 11.0237 | 10.7523 | 9.819 | 7.5854 | 6.3564 | 5.6237 | 3.9876 | 3.9353 | 14.4602 | 14.4007 | 14.3087 | 14.2121 | 14.1179 | 14.001 | 13.8762 | 13.7192 | 13.1317 | 11.6121 | 10.8878 | 10.3861 | 1.6463 | 1.5876 | 12.1073 | 12.0447 | 11.8995 | 11.7509 | 11.6071 | 11.4415 | 11.2662 | 11.018 | 10.1558 | 8.0369 | 6.9309 | 6.2843
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON | MINIMUM HEADROOM | SY 59138 97747 | YES | 25.2188 | 25.0662 | 24.946 | 24.6908 | 24.2774 | 24.0531 | 23.828 | 23.6071 | 23.4216 | 23.2627 | 22.8488 | 22.5367 | 22.4963 | 22.4681 | 26.4481 | 26.3172 | 26.2051 | 25.9479 | 25.5088 | 25.2748 | 25.0424 | 24.8181 | 24.6345 | 24.4792 | 24.057 | 23.7271 | 23.654 | 23.601 | 26.8918 | 26.6197 | 26.3953 | 26.0369 | 25.5178 | 25.1456 | 24.7699 | 24.3715 | 23.9959 | 23.7273 | 23.1433 | 22.5696 | 22.3922 | 22.2651
|  | MAIDEN NEWTON | CT |  |  | 25.2284 | 25.0828 | 24.9684 | 24.7153 | 24.3118 | 24.1041 | 23.8964 | 23.6957 | 23.5371 | 23.3935 | 23.0407 | 22.71 | 22.6162 | 22.5889 | 26.4832 | 26.3669 | 26.269 | 26.0261 | 25.607 | 25.3939 | 25.1838 | 24.9836 | 24.8281 | 24.687 | 24.3132 | 23.9176 | 23.7245 | 23.6748 | 26.9714 | 26.732 | 26.5396 | 26.2129 | 25.7422 | 25.4192 | 25.0965 | 24.7583 | 24.4559 | 24.1852 | 23.6415 | 22.9118 | 22.4604 | 22.3419
|  | MAIDEN NEWTON | LW |  |  | 25.2188 | 25.0662 | 24.946 | 24.6908 | 24.2774 | 24.0531 | 23.828 | 23.6071 | 23.4216 | 23.2627 | 22.8488 | 22.5367 | 22.4963 | 22.4681 | 26.4481 | 26.3172 | 26.2051 | 25.9479 | 25.5088 | 25.2748 | 25.0424 | 24.8181 | 24.6345 | 24.4792 | 24.057 | 23.7271 | 23.654 | 23.601 | 26.8918 | 26.6197 | 26.3953 | 26.0369 | 25.5178 | 25.1456 | 24.7699 | 24.3715 | 23.9959 | 23.7273 | 23.1433 | 22.5696 | 22.3922 | 22.2651
|  | MAIDEN NEWTON | ST |  |  | 25.2574 | 25.129 | 25.0224 | 24.7815 | 24.3864 | 24.1877 | 23.9955 | 23.8158 | 23.6798 | 23.58 | 23.2848 | 22.954 | 22.8211 | 22.7923 | 26.496 | 26.4003 | 26.3236 | 26.1086 | 25.7244 | 25.5483 | 25.3754 | 25.2168 | 25.0979 | 24.9961 | 24.6898 | 24.3465 | 24.2028 | 24.1549 | 27.0488 | 26.8865 | 26.7601 | 26.5146 | 26.1282 | 25.895 | 25.6656 | 25.4381 | 25.2457 | 25.1035 | 24.6152 | 24.1642 | 23.914 | 23.7418
|  | MAIDEN NEWTON | SP |  |  | 25.2584 | 25.1297 | 25.0253 | 24.7861 | 24.3966 | 24.2034 | 24.015 | 23.8384 | 23.7081 | 23.6118 | 23.3376 | 22.984 | 22.7603 | 22.6953 | 26.5009 | 26.406 | 26.3277 | 26.1117 | 25.6972 | 25.4921 | 25.2912 | 25.1057 | 24.962 | 24.8357 | 24.5321 | 24.2147 | 24.0152 | 23.9204 | 27.0612 | 26.902 | 26.7779 | 26.5346 | 26.0899 | 25.7922 | 25.494 | 25.2048 | 24.9601 | 24.7481 | 24.2634 | 23.5421 | 23.2204 | 23.0159
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD | MINIMUM HEADROOM | SU 86485 79800 | YES | 2.0708 | 1.7446 | 1.386 | 1.0119 | 0.52522 | 0.017549 | -0.50558 | -1.0636 | -1.7281 | -2.3915 | -3.9963 | -5.6282 | -5.7854 | -6.1035 | 3.3992 | 3.3235 | 3.2195 | 3.0616 | 2.8652 | 2.6553 | 2.4324 | 2.1911 | 1.8673 | 1.5312 | 0.91876 | 0.33219 | 0.27579 | 0.045192 | 0.095818 | -0.20925 | -0.54261 | -0.8897 | -1.3429 | -1.8149 | -2.3 | -2.8133 | -3.4268 | -4.0364 | -5.4571 | -6.8743 | -7.0107 | -7.2685
|  | MAIDENHEAD | CT |  |  | 2.4779 | 2.3355 | 2.1783 | 1.9753 | 1.6955 | 1.3977 | 1.0756 | 0.72755 | 0.33138 | -0.22129 | -1.4516 | -3.2233 | -3.634 | -3.7173 | 3.4527 | 3.4058 | 3.3507 | 3.2672 | 3.179 | 3.0809 | 2.9423 | 2.776 | 2.5608 | 2.2517 | 1.674 | 0.98789 | 0.79272 | 0.68472 | 0.48252 | 0.35126 | 0.20697 | 0.023026 | -0.23506 | -0.50904 | -0.80548 | -1.1251 | -1.4858 | -1.9888 | -3.1299 | -4.8018 | -5.1884 | -5.2666
|  | MAIDENHEAD | LW |  |  | 2.0708 | 1.7446 | 1.386 | 1.0119 | 0.52522 | 0.017549 | -0.50558 | -1.0636 | -1.7281 | -2.3915 | -3.9963 | -5.6282 | -5.7854 | -5.9053 | 3.3992 | 3.3235 | 3.2195 | 3.0616 | 2.8652 | 2.6553 | 2.4324 | 2.1911 | 1.8673 | 1.5312 | 0.91876 | 0.33219 | 0.27579 | 0.24016 | 0.095818 | -0.20925 | -0.54261 | -0.8897 | -1.3429 | -1.8149 | -2.3 | -2.8133 | -3.4268 | -4.0364 | -5.4571 | -6.8743 | -7.0107 | -7.1115
|  | MAIDENHEAD | ST |  |  | 2.5555 | 2.4482 | 2.3336 | 2.2065 | 2.0063 | 1.8156 | 1.6163 | 1.411 | 1.1841 | 0.93451 | -0.038709 | -1.5122 | -2.2531 | -2.7106 | 3.4901 | 3.4635 | 3.4321 | 3.393 | 3.3367 | 3.278 | 3.2134 | 3.1464 | 3.0364 | 2.9222 | 2.4024 | 1.6252 | 1.3084 | 1.0826 | 0.55205 | 0.45189 | 0.34543 | 0.22798 | 0.042434 | -0.13361 | -0.31712 | -0.50619 | -0.71422 | -0.94492 | -1.8331 | -3.1944 | -3.895 | -4.3278
|  | MAIDENHEAD | SP |  |  | 2.6057 | 2.5234 | 2.4334 | 2.3426 | 2.0633 | 1.7727 | 1.4842 | 1.1798 | 0.86757 | 0.46006 | -0.86625 | -3.4139 | -5.0351 | -6.1035 | 3.498 | 3.4718 | 3.441 | 3.4096 | 3.3509 | 3.285 | 3.2209 | 3.1041 | 2.9775 | 2.8212 | 2.2847 | 1.0276 | 0.41677 | 0.045192 | 0.59949 | 0.52361 | 0.44095 | 0.35751 | 0.095363 | -0.17652 | -0.4468 | -0.73121 | -1.0223 | -1.4038 | -2.6151 | -4.9598 | -6.366 | -7.2685
MELKSHAM GSP | CHIPPENHAM | MALMESBURY | MINIMUM HEADROOM | ST 92288 87493 | YES | 24.6806 | 24.0895 | 23.4263 | 22.6976 | 21.5478 | 20.1804 | 18.6803 | 16.8614 | 14.6003 | 12.3753 | 7.8734 | 3.1519 | 0.20413 | -1.5299 | 22.8723 | 22.5023 | 22.0774 | 21.6021 | 20.943 | 20.1581 | 19.2685 | 18.1757 | 16.749 | 15.3621 | 12.782 | 9.7622 | 7.1764 | 4.8837 | 15.4192 | 14.8916 | 14.3009 | 13.6523 | 12.6091 | 11.3857 | 10.0461 | 8.3918 | 6.2994 | 4.2454 | 0.13931 | -4.1768 | -6.7141 | -8.34
|  | MALMESBURY | CT |  |  | 24.8678 | 24.4191 | 23.8892 | 23.2748 | 22.4828 | 21.4883 | 20.4202 | 19.086 | 17.4929 | 15.1767 | 10.4358 | 4.219 | 0.20413 | -1.5299 | 22.8817 | 22.537 | 22.1269 | 21.6475 | 21.1106 | 20.4556 | 19.7335 | 18.8433 | 17.7709 | 16.2768 | 13.3657 | 9.7622 | 7.1764 | 4.8837 | 15.6024 | 15.2095 | 14.7455 | 14.2074 | 13.4993 | 12.5895 | 11.6031 | 10.3812 | 8.9192 | 6.779 | 2.4487 | -3.1553 | -6.7141 | -8.34
|  | MALMESBURY | LW |  |  | 24.6806 | 24.0895 | 23.4263 | 22.6976 | 21.5478 | 20.1804 | 18.6803 | 16.8614 | 14.6003 | 12.3753 | 7.8734 | 3.1519 | 1.5379 | 0.95688 | 22.8723 | 22.5023 | 22.0774 | 21.6021 | 20.943 | 20.1581 | 19.2685 | 18.1757 | 16.749 | 15.3621 | 12.782 | 10.2399 | 9.5493 | 9.3006 | 15.4192 | 14.8916 | 14.3009 | 13.6523 | 12.6091 | 11.3857 | 10.0461 | 8.3918 | 6.2994 | 4.2454 | 0.13931 | -4.1768 | -5.5994 | -6.1033
|  | MALMESBURY | ST |  |  | 25.2778 | 25.085 | 24.8534 | 24.5687 | 24.2115 | 23.7179 | 23.1763 | 22.4861 | 21.65 | 20.7991 | 17.5977 | 12.8254 | 10.5904 | 9.1317 | 23.1785 | 23.0164 | 22.8209 | 22.5792 | 22.2935 | 21.9198 | 21.5036 | 20.9874 | 20.3635 | 19.7558 | 17.2765 | 13.4556 | 11.3696 | 9.1807 | 15.9666 | 15.8017 | 15.6029 | 15.3583 | 15.0479 | 14.6328 | 14.1757 | 13.6005 | 12.8502 | 12.0891 | 9.07 | 4.5292 | 2.5087 | 1.2335
|  | MALMESBURY | SP |  |  | 25.3148 | 25.1347 | 24.9358 | 24.717 | 24.4116 | 23.9925 | 23.5528 | 22.9538 | 22.2762 | 21.5225 | 19.1717 | 13.9003 | 11.5279 | 10.6318 | 23.1893 | 23.0249 | 22.8399 | 22.6335 | 22.3992 | 22.097 | 21.7658 | 21.3216 | 20.8138 | 20.2484 | 18.3382 | 13.6562 | 10.5552 | 7.2641 | 16.0011 | 15.8489 | 15.68 | 15.4939 | 15.2271 | 14.8744 | 14.5055 | 14.0103 | 13.454 | 12.8013 | 10.6245 | 5.5257 | 3.2703 | 2.454
MINETY GSP | SWINDON BSP | MANCHESTER ROAD | MINIMUM HEADROOM | SU 15254 85130 | NO | 1.8266 | 1.2544 | 0.64541 | 0.092882 | -0.68867 | -1.5011 | -2.3441 | -3.2661 | -4.2612 | -5.2554 | -7.6954 | -10.5546 | -11.3197 | -11.6944 | 1.5391 | 1.295 | 1.0367 | 0.80112 | 0.47412 | 0.13168 | -0.22919 | -0.62702 | -1.2011 | -1.7891 | -3.0313 | -4.4002 | -5.0266 | -5.8812 | -0.38739 | -0.89435 | -1.434 | -1.9346 | -2.63 | -3.3557 | -4.121 | -4.9733 | -5.9227 | -6.864 | -9.0524 | -11.5671 | -12.2038 | -12.5088
|  | MANCHESTER ROAD | CT |  |  | 2.2258 | 1.8718 | 1.4698 | 1.13 | 0.6728 | 0.18718 | -0.30989 | -0.88127 | -1.4872 | -2.4174 | -4.5823 | -8.1162 | -10.5482 | -11.465 | 1.6956 | 1.5317 | 1.346 | 1.1852 | 0.97555 | 0.7522 | 0.52119 | 0.19921 | -0.1999 | -0.77943 | -2.0235 | -3.8192 | -5.0266 | -5.8812 | -0.042132 | -0.36055 | -0.72551 | -1.0444 | -1.4676 | -1.9173 | -2.38 | -2.9157 | -3.4873 | -4.361 | -6.3579 | -9.5065 | -11.5067 | -12.252
|  | MANCHESTER ROAD | LW |  |  | 1.8266 | 1.2544 | 0.64541 | 0.092882 | -0.68867 | -1.5011 | -2.3441 | -3.2661 | -4.2612 | -5.2554 | -7.6954 | -10.5546 | -11.3197 | -11.6944 | 1.5391 | 1.295 | 1.0367 | 0.80112 | 0.47412 | 0.13168 | -0.22919 | -0.62702 | -1.2011 | -1.7891 | -3.0313 | -4.4002 | -4.6979 | -4.8342 | -0.38739 | -0.89435 | -1.434 | -1.9346 | -2.63 | -3.3557 | -4.121 | -4.9733 | -5.9227 | -6.864 | -9.0524 | -11.5671 | -12.2038 | -12.5088
|  | MANCHESTER ROAD | ST |  |  | 2.443 | 2.2437 | 2.0152 | 1.8232 | 1.5678 | 1.3015 | 1.0161 | 0.70549 | 0.36659 | 0.0045621 | -1.5464 | -4.1217 | -5.4072 | -6.1983 | 1.7903 | 1.6931 | 1.5831 | 1.4884 | 1.3674 | 1.2401 | 1.1015 | 0.95043 | 0.78442 | 0.60537 | -0.35505 | -2.1427 | -3.067 | -3.8984 | 0.16812 | -0.001828 | -0.20077 | -0.37737 | -0.61421 | -0.86054 | -1.1258 | -1.4154 | -1.7347 | -2.0727 | -3.5486 | -5.9704 | -7.1282 | -7.8209
|  | MANCHESTER ROAD | SP |  |  | 2.5062 | 2.3346 | 2.1585 | 2.0184 | 1.7037 | 1.3794 | 1.0588 | 0.69996 | 0.3299 | -0.12523 | -1.6882 | -5.3256 | -7.3431 | -8.4076 | 1.8144 | 1.7277 | 1.6366 | 1.5601 | 1.4154 | 1.2639 | 1.1115 | 0.94124 | 0.76347 | 0.54629 | -0.20419 | -2.6078 | -4.1197 | -5.3777 | 0.22451 | 0.078279 | -0.072179 | -0.20074 | -0.48621 | -0.77994 | -1.0701 | -1.3975 | -1.7368 | -2.1531 | -3.5974 | -7.0021 | -8.8553 | -9.801
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON | MINIMUM HEADROOM | SU 07592 05256 | YES | 34.8588 | 33.8373 | 32.8237 | 31.8492 | 30.6169 | 29.3355 | 27.9654 | 26.5025 | 24.8515 | 23.0252 | 17.4503 | 10.5461 | 5.821 | 2.5894 | 40.9354 | 40.2827 | 39.7128 | 39.0222 | 38.3283 | 37.599 | 36.8111 | 35.9526 | 34.987 | 33.7278 | 29.6924 | 22.2796 | 11.9213 | -8.9098 | 35.7523 | 34.7753 | 33.836 | 32.9356 | 31.816 | 30.6536 | 29.4001 | 28.0586 | 26.5235 | 24.8343 | 19.6515 | 13.3606 | 9.5589 | 6.8591
|  | MANNINGTON | CT |  |  | 35.1524 | 34.3001 | 33.4869 | 32.6408 | 31.737 | 30.8027 | 29.8391 | 28.8021 | 27.6769 | 25.9387 | 20.6371 | 11.7551 | 5.821 | 2.5894 | 40.9354 | 40.2827 | 39.7128 | 39.0222 | 38.3283 | 37.599 | 36.8111 | 35.9526 | 34.987 | 33.7278 | 29.6924 | 22.2796 | 14.5728 | 4.243 | 35.7713 | 35.0841 | 34.3935 | 33.5884 | 32.7449 | 31.877 | 30.9757 | 30.0047 | 28.9386 | 27.344 | 22.4563 | 14.5758 | 9.5589 | 6.8591
|  | MANNINGTON | LW |  |  | 34.8588 | 33.8373 | 32.8237 | 31.8492 | 30.6169 | 29.3355 | 27.9654 | 26.5025 | 24.8515 | 23.0252 | 17.4503 | 10.5461 | 7.4672 | 5.6774 | 41.0216 | 40.3955 | 39.7544 | 39.148 | 38.4734 | 37.7771 | 37.0106 | 36.1872 | 35.2099 | 34.1169 | 30.7552 | 26.2379 | 25.251 | 24.5096 | 35.7523 | 34.7753 | 33.836 | 32.9356 | 31.816 | 30.6536 | 29.4001 | 28.0586 | 26.5235 | 24.8343 | 19.6515 | 13.3606 | 10.76 | 9.268
|  | MANNINGTON | ST |  |  | 35.5538 | 35.0071 | 34.5465 | 34.1411 | 33.7473 | 33.3357 | 32.882 | 32.3765 | 31.7784 | 31.015 | 27.8156 | 19.029 | 14.8889 | 14.0031 | 41.1251 | 40.5931 | 40.2216 | 39.9007 | 39.4848 | 39.0379 | 38.5364 | 37.9759 | 37.3051 | 36.5356 | 33.7928 | 26.7627 | 19.2492 | 9.2047 | 36.021 | 35.5021 | 35.1208 | 34.7955 | 34.5022 | 34.1994 | 33.8142 | 33.3329 | 32.7595 | 32.0578 | 28.8897 | 20.4618 | 16.5235 | 15.4262
|  | MANNINGTON | SP |  |  | 35.603 | 35.0829 | 34.6584 | 34.2925 | 33.9594 | 33.6263 | 33.2625 | 32.8598 | 32.4219 | 31.8263 | 29.9184 | 23.6173 | 17.4319 | 15.6944 | 41.1205 | 40.5996 | 40.2348 | 39.8956 | 39.4463 | 38.975 | 38.4416 | 37.8457 | 37.1504 | 36.2885 | 33.1916 | 24.9543 | 11.9213 | -8.9098 | 36.0241 | 35.5254 | 35.1647 | 34.8644 | 34.6127 | 34.3649 | 34.0876 | 33.7818 | 33.3795 | 32.8369 | 31.0731 | 24.8878 | 18.9789 | 17.3523
LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET | MINIMUM HEADROOM | SU 86479 04732 | NO | 7.424 | 7.2195 | 7.0605 | 6.8251 | 6.5198 | 6.2882 | 6.0211 | 5.6746 | 5.3882 | 5.1267 | 4.4504 | 3.7489 | 3.4852 | 3.2688 | 10.4885 | 10.3559 | 10.2767 | 10.0929 | 9.903 | 9.7828 | 9.6176 | 9.3801 | 9.2194 | 9.054 | 8.548 | 8.0872 | 7.9157 | 7.7834 | 8.9918 | 8.8266 | 8.6955 | 8.503 | 8.2563 | 8.0685 | 7.8469 | 7.5536 | 7.3021 | 7.0761 | 6.5396 | 5.9884 | 5.7858 | 5.6369
|  | MARKET | CT |  |  | 7.4987 | 7.3391 | 7.2265 | 7.031 | 6.7899 | 6.6247 | 6.4204 | 6.1399 | 5.9371 | 5.6791 | 5.0579 | 4.1705 | 3.5691 | 3.2688 | 10.4885 | 10.3559 | 10.2767 | 10.0929 | 9.9064 | 9.7933 | 9.641 | 9.4179 | 9.2816 | 9.1348 | 8.6953 | 8.184 | 7.9404 | 7.7834 | 9.0368 | 8.9015 | 8.8023 | 8.6333 | 8.4312 | 8.2901 | 8.1144 | 7.8704 | 7.6885 | 7.4566 | 6.9542 | 6.2863 | 5.855 | 5.6369
|  | MARKET | LW |  |  | 7.424 | 7.2195 | 7.0605 | 6.8251 | 6.5198 | 6.2882 | 6.0211 | 5.6746 | 5.3882 | 5.1267 | 4.4504 | 3.7489 | 3.4852 | 3.3209 | 10.4919 | 10.3576 | 10.2785 | 10.0949 | 9.903 | 9.7828 | 9.6176 | 9.3801 | 9.2194 | 9.054 | 8.548 | 8.0872 | 7.9157 | 7.8156 | 8.9918 | 8.8266 | 8.6955 | 8.503 | 8.2563 | 8.0685 | 7.8469 | 7.5536 | 7.3021 | 7.0761 | 6.5396 | 5.9884 | 5.7858 | 5.6628
|  | MARKET | ST |  |  | 7.5395 | 7.4013 | 7.3142 | 7.1525 | 6.9551 | 6.8357 | 6.6837 | 6.4632 | 6.3223 | 6.1784 | 5.6467 | 4.9925 | 4.5962 | 4.325 | 10.5047 | 10.3816 | 10.3149 | 10.1455 | 9.9753 | 9.887 | 9.7639 | 9.5707 | 9.4566 | 9.3415 | 8.9448 | 8.4009 | 8.0912 | 7.9113 | 9.0763 | 8.9615 | 8.887 | 8.7529 | 8.5881 | 8.4869 | 8.3587 | 8.1714 | 8.0484 | 7.9245 | 7.4377 | 6.8717 | 6.5605 | 6.3532
|  | MARKET | SP |  |  | 7.5618 | 7.4299 | 7.353 | 7.2006 | 7.0027 | 6.8809 | 6.7317 | 6.517 | 6.3812 | 6.2362 | 5.7562 | 4.9621 | 4.4665 | 4.1777 | 10.5061 | 10.3842 | 10.3199 | 10.153 | 9.9876 | 9.9056 | 9.7901 | 9.6144 | 9.5171 | 9.4242 | 9.1309 | 8.7475 | 8.4057 | 8.2505 | 9.0923 | 8.9812 | 8.9151 | 8.7882 | 8.6274 | 8.5267 | 8.4059 | 8.2284 | 8.1142 | 7.9962 | 7.5883 | 6.8785 | 6.4859 | 6.2686
MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH | MINIMUM HEADROOM | SU 19293 68264 | YES | 11.1583 | 11.0248 | 10.8745 | 10.6761 | 10.1843 | 9.2946 | 8.3675 | 7.3839 | 6.3256 | 5.2406 | 1.7651 | -2.5209 | -4.7118 | -6.9242 | 9.5635 | 9.4656 | 9.3567 | 9.2123 | 9.0671 | 8.7692 | 8.3739 | 7.9516 | 7.4889 | 7.0024 | 5.2609 | 2.9959 | 0.69659 | -1.5559 | 6.6036 | 6.291 | 5.9525 | 5.4545 | 4.689 | 3.9162 | 3.1098 | 2.2542 | 1.3474 | 0.41779 | -2.5527 | -6.2308 | -8.029 | -9.8754
|  | MARLBOROUGH SOUTH | CT |  |  | 11.1583 | 11.0248 | 10.8783 | 10.6803 | 10.4905 | 10.3004 | 10.0984 | 9.4919 | 8.7857 | 7.7717 | 4.5167 | -0.75917 | -4.607 | -6.9242 | 9.5635 | 9.4656 | 9.3567 | 9.2123 | 9.0671 | 8.917 | 8.7555 | 8.5772 | 8.3511 | 7.8933 | 6.1338 | 3.1134 | 0.69659 | -1.5559 | 6.815 | 6.6225 | 6.4078 | 6.1251 | 5.7003 | 5.1909 | 4.7127 | 4.1922 | 3.6035 | 2.7418 | -0.014238 | -4.6231 | -7.9442 | -9.8754
|  | MARLBOROUGH SOUTH | LW |  |  | 11.1708 | 11.029 | 10.8745 | 10.6761 | 10.1843 | 9.2946 | 8.3675 | 7.3839 | 6.3256 | 5.2406 | 1.7651 | -2.5209 | -4.7118 | -6.2865 | 9.5778 | 9.4791 | 9.37 | 9.2327 | 9.0831 | 8.7692 | 8.3739 | 7.9516 | 7.4889 | 7.0024 | 5.2609 | 2.9959 | 1.9446 | 1.1673 | 6.6036 | 6.291 | 5.9525 | 5.4545 | 4.689 | 3.9162 | 3.1098 | 2.2542 | 1.3474 | 0.41779 | -2.5527 | -6.2308 | -8.029 | -9.2748
|  | MARLBOROUGH SOUTH | ST |  |  | 11.2404 | 11.1565 | 11.0691 | 10.9503 | 10.8241 | 10.701 | 10.566 | 10.4114 | 10.2083 | 9.9751 | 9.0505 | 5.3757 | 2.9615 | 1.2504 | 9.6287 | 9.5708 | 9.5095 | 9.4292 | 9.3367 | 9.2425 | 9.137 | 9.0142 | 8.8536 | 8.6694 | 7.9377 | 5.7564 | 3.6237 | 1.6127 | 6.9873 | 6.9061 | 6.8192 | 6.7057 | 6.5493 | 6.3921 | 6.2233 | 6.0342 | 5.8046 | 5.4959 | 4.2035 | 0.98959 | -1.2413 | -2.6557
|  | MARLBOROUGH SOUTH | SP |  |  | 11.2425 | 11.1633 | 11.0792 | 10.9677 | 10.8598 | 10.7577 | 10.6488 | 10.5261 | 10.3714 | 10.1992 | 9.5737 | 7.4205 | 4.3062 | 3.1523 | 9.629 | 9.5735 | 9.513 | 9.4362 | 9.3567 | 9.2769 | 9.1895 | 9.09 | 8.9641 | 8.8179 | 8.2824 | 6.458 | 3.5313 | 0.32537 | 6.9997 | 6.9294 | 6.8546 | 6.7563 | 6.6589 | 6.5655 | 6.4651 | 6.3515 | 6.208 | 6.0077 | 5.1964 | 2.7612 | 0.35642 | -0.82481
NURSLING GSP | ROWNHAMS | MAYBUSH | MINIMUM HEADROOM | SU 38426 14930 | YES | 2.1347 | 1.767 | 1.3736 | 0.96424 | 0.3442 | -0.30626 | -0.99075 | -1.7144 | -2.6061 | -3.5188 | -5.7375 | -8.2386 | -8.9514 | -9.7557 | 6.4363 | 6.2519 | 6.0484 | 5.833 | 5.5236 | 5.1944 | 4.8381 | 4.457 | 3.9607 | 3.4522 | 2.296 | 1.0704 | -0.35129 | -1.6647 | 3.4343 | 3.1165 | 2.7545 | 2.3765 | 1.8105 | 1.2153 | 0.58532 | -0.082565 | -0.91647 | -1.7693 | -3.8049 | -6.0714 | -6.7031 | -7.4873
|  | MAYBUSH | CT |  |  | 2.4332 | 2.2231 | 1.9935 | 1.7279 | 1.345 | 0.94119 | 0.51646 | 0.056862 | -0.46477 | -1.3115 | -3.3874 | -6.66 | -8.8529 | -9.7557 | 6.5316 | 6.3933 | 6.2382 | 6.0554 | 5.8264 | 5.5821 | 5.3187 | 5.0295 | 4.6929 | 4.1637 | 2.9186 | 1.1155 | -0.35129 | -1.6647 | 3.5865 | 3.4867 | 3.2951 | 3.0414 | 2.6858 | 2.3104 | 1.9137 | 1.4831 | 0.99054 | 0.19555 | -1.7225 | -4.6584 | -6.6115 | -7.4873
|  | MAYBUSH | LW |  |  | 2.1347 | 1.767 | 1.3736 | 0.96424 | 0.3442 | -0.30626 | -0.99075 | -1.7144 | -2.6061 | -3.5188 | -5.7375 | -8.2386 | -8.9514 | -9.2964 | 6.4363 | 6.2519 | 6.0484 | 5.833 | 5.5236 | 5.1944 | 4.8381 | 4.457 | 3.9607 | 3.4522 | 2.296 | 1.0704 | 0.76605 | 0.62244 | 3.4343 | 3.1165 | 2.7545 | 2.3765 | 1.8105 | 1.2153 | 0.58532 | -0.082565 | -0.91647 | -1.7693 | -3.8049 | -6.0714 | -6.7031 | -7.0286
|  | MAYBUSH | ST |  |  | 2.6057 | 2.4947 | 2.3756 | 2.2451 | 2.0434 | 1.8336 | 1.6099 | 1.3689 | 1.0948 | 0.79725 | -0.46273 | -2.7974 | -3.9845 | -4.7501 | 6.6422 | 6.5664 | 6.4826 | 6.3887 | 6.2565 | 6.1167 | 5.9623 | 5.793 | 5.5964 | 5.3956 | 4.5147 | 2.7369 | 1.6368 | 0.39304 | 3.6639 | 3.6093 | 3.5539 | 3.4957 | 3.3534 | 3.1578 | 2.9479 | 2.7209 | 2.4613 | 2.1825 | 0.98224 | -1.2204 | -2.2906 | -2.963
|  | MAYBUSH | SP |  |  | 2.6503 | 2.5569 | 2.4604 | 2.3631 | 2.1184 | 1.8695 | 1.6122 | 1.3393 | 1.0529 | 0.69168 | -0.55945 | -3.5173 | -5.1579 | -6.0039 | 6.6579 | 6.5852 | 6.5065 | 6.4238 | 6.2803 | 6.1299 | 5.9697 | 5.7931 | 5.6008 | 5.3691 | 4.5187 | 2.3138 | 0.5206 | -1.5717 | 3.6855 | 3.6429 | 3.6003 | 3.5568 | 3.4238 | 3.1977 | 2.9633 | 2.7128 | 2.4488 | 2.1178 | 0.95892 | -1.819 | -3.3306 | -4.086
MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN | MINIMUM HEADROOM | ST 90170 64096 | NO | 9.9283 | 9.4349 | 8.9486 | 8.4611 | 7.6334 | 6.7785 | 5.8457 | 4.9432 | 3.863 | 2.7859 | -0.64153 | -5.6531 | -10.2869 | -13.1871 | 7.5554 | 7.1867 | 6.8303 | 6.4782 | 5.9924 | 5.4896 | 4.9109 | 4.3518 | 3.6951 | 3.0627 | 0.75998 | -3.6827 | -8.3366 | -19.2194 | 5.6128 | 5.135 | 4.6428 | 4.1455 | 3.3469 | 2.5182 | 1.5989 | 0.70451 | -0.36976 | -1.4378 | -4.8245 | -9.1917 | -13.0367 | -15.4281
|  | MELKSHAM TOWN | CT |  |  | 10.1338 | 9.7571 | 9.4219 | 9.0376 | 8.456 | 7.8569 | 7.1514 | 6.4851 | 5.7889 | 4.7379 | 1.3948 | -5.2117 | -10.2869 | -13.1871 | 7.5973 | 7.2397 | 6.9246 | 6.5624 | 6.1155 | 5.6535 | 5.1048 | 4.5732 | 3.9933 | 3.233 | 0.75998 | -3.6827 | -8.3366 | -14.1349 | 5.7916 | 5.4177 | 5.0827 | 4.6684 | 4.085 | 3.4825 | 2.7688 | 2.0894 | 1.3672 | 0.32633 | -2.9691 | -8.7349 | -13.0367 | -15.4281
|  | MELKSHAM TOWN | LW |  |  | 9.9283 | 9.4349 | 8.9486 | 8.4611 | 7.6334 | 6.7785 | 5.8457 | 4.9432 | 3.863 | 2.7859 | -0.64153 | -5.6531 | -8.3821 | -10.0721 | 7.5554 | 7.1867 | 6.8303 | 6.4782 | 5.9924 | 5.4896 | 4.9109 | 4.3518 | 3.6951 | 3.0627 | 0.93704 | -1.5736 | -2.7817 | -3.5779 | 5.6128 | 5.135 | 4.6428 | 4.1455 | 3.3469 | 2.5182 | 1.5989 | 0.70451 | -0.36976 | -1.4378 | -4.8245 | -9.1917 | -11.4372 | -12.769
|  | MELKSHAM TOWN | ST |  |  | 10.2818 | 9.9975 | 9.7664 | 9.5549 | 9.2682 | 8.9748 | 8.6315 | 8.3162 | 7.9635 | 7.6048 | 6.3561 | 2.9447 | 0.12654 | -2.0317 | 7.6862 | 7.3822 | 7.1277 | 6.8891 | 6.591 | 6.2835 | 5.9151 | 5.5601 | 5.1673 | 4.8008 | 3.4439 | -0.22393 | -4.1968 | -9.5653 | 5.9432 | 5.662 | 5.4307 | 5.2177 | 4.923 | 4.62 | 4.2599 | 3.9251 | 3.5502 | 3.1908 | 1.9059 | -1.4555 | -3.8991 | -5.6874
|  | MELKSHAM TOWN | SP |  |  | 10.3104 | 10.0276 | 9.8012 | 9.5957 | 9.3287 | 9.0612 | 8.7366 | 8.4517 | 8.1545 | 7.846 | 6.8388 | 4.5155 | 2.2575 | 0.80476 | 7.6917 | 7.3748 | 7.106 | 6.8522 | 6.5511 | 6.2384 | 5.8592 | 5.4946 | 5.0972 | 4.6712 | 3.0343 | -1.2006 | -7.9747 | -19.2194 | 5.9698 | 5.6807 | 5.4471 | 5.2328 | 4.9673 | 4.7001 | 4.3712 | 4.0785 | 3.7701 | 3.4592 | 2.4169 | 0.026446 | -2.0285 | -3.1478
LOVEDEAN GSP | HAVANT | MEYRICK ROAD | MINIMUM HEADROOM | SU 70849 06469 | YES | 7.8192 | 7.3852 | 6.9061 | 6.4685 | 5.8128 | 5.0263 | 4.0691 | 3.0476 | 1.8387 | 0.55281 | -3.659 | -8.8145 | -11.671 | -13.6954 | 4.9853 | 4.5489 | 4.0085 | 3.4905 | 2.8099 | 2.0672 | 1.2179 | 0.25627 | -1.028 | -2.3827 | -5.0828 | -7.8358 | -10.365 | -12.3951 | 1.5211 | 0.81817 | -0.039339 | -0.86014 | -2.0218 | -3.2725 | -4.6295 | -6.1107 | -8.0036 | -9.9878 | -14.2771 | -18.9999 | -21.4128 | -23.0761
|  | MEYRICK ROAD | CT |  |  | 8.0163 | 7.7056 | 7.3674 | 7.0337 | 6.6115 | 6.1554 | 5.6584 | 5.1172 | 4.4937 | 3.3561 | -0.39362 | -7.224 | -11.671 | -13.6954 | 5.0868 | 4.7243 | 4.3163 | 3.8233 | 3.2954 | 2.7085 | 2.031 | 1.2728 | 0.34385 | -1.0195 | -4.0509 | -7.8198 | -10.365 | -12.3951 | 1.8095 | 1.2983 | 0.72035 | 0.027137 | -0.77452 | -1.6388 | -2.5873 | -3.6373 | -4.8925 | -6.8397 | -11.3573 | -17.5338 | -21.4128 | -23.0761
|  | MEYRICK ROAD | LW |  |  | 7.8192 | 7.3852 | 6.9061 | 6.4685 | 5.8128 | 5.0263 | 4.0691 | 3.0476 | 1.8387 | 0.55281 | -3.659 | -8.8145 | -10.5019 | -11.1252 | 4.9853 | 4.5489 | 4.0085 | 3.4905 | 2.8099 | 2.0672 | 1.2179 | 0.25627 | -1.028 | -2.3827 | -5.0828 | -7.8358 | -8.5664 | -8.8415 | 1.5211 | 0.81817 | -0.039339 | -0.86014 | -2.0218 | -3.2725 | -4.6295 | -6.1107 | -8.0036 | -9.9878 | -14.2771 | -18.9999 | -20.4981 | -21.0484
|  | MEYRICK ROAD | ST |  |  | 8.2198 | 8.0423 | 7.8592 | 7.7144 | 7.5256 | 7.3135 | 7.0771 | 6.8128 | 6.4952 | 6.107 | 4.5261 | -0.28127 | -2.5098 | -3.7085 | 5.3568 | 5.1596 | 4.9394 | 4.7341 | 4.4658 | 4.1642 | 3.8239 | 3.4409 | 2.9935 | 2.5111 | 0.2023 | -4.1583 | -6.3074 | -8.2537 | 2.2177 | 1.9635 | 1.677 | 1.4092 | 1.0352 | 0.61729 | 0.15222 | -0.36781 | -0.96836 | -1.596 | -4.4937 | -9.9909 | -12.4378 | -13.8929
|  | MEYRICK ROAD | SP |  |  | 8.2593 | 8.0986 | 7.9402 | 7.8214 | 7.651 | 7.4713 | 7.2793 | 7.0595 | 6.8169 | 6.5048 | 5.4036 | 2.2271 | -0.91289 | -1.78 | 5.3827 | 5.178 | 4.9642 | 4.7728 | 4.5569 | 4.3216 | 4.0729 | 3.7682 | 3.4304 | 3.011 | 1.3073 | -3.624 | -7.0707 | -10.4897 | 2.2768 | 2.0235 | 1.7628 | 1.532 | 1.2221 | 0.89419 | 0.55185 | 0.13582 | -0.31626 | -0.86746 | -2.9733 | -8.7288 | -11.6106 | -12.682
BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP | MINIMUM HEADROOM | SU 30984 40155 | YES | 4.5485 | 3.9659 | 3.2557 | 2.4196 | 1.0014 | -0.62629 | -2.2852 | -3.9724 | -6.0199 | -8.1657 | -13.6477 | -19.9327 | -25.612 | -29.2265 | 11.1482 | 10.8113 | 10.3876 | 9.8839 | 9.1069 | 8.2156 | 7.289 | 6.3378 | 5.1443 | 3.8376 | 0.59856 | -3.2592 | -6.6461 | -9.6041 | 6.6212 | 6.1025 | 5.4556 | 4.6951 | 3.4321 | 1.9883 | 0.49878 | -1.0286 | -2.9064 | -4.8806 | -9.853 | -15.4388 | -20.2503 | -23.3069
|  | MIDDLE WALLOP | CT |  |  | 4.6944 | 4.2231 | 3.7006 | 2.9293 | 1.815 | 0.51409 | -0.77972 | -2.0879 | -3.6091 | -5.7793 | -11.6123 | -19.6322 | -25.612 | -29.2265 | 11.1747 | 10.8654 | 10.5199 | 10.0064 | 9.3377 | 8.5683 | 7.7907 | 6.9937 | 6.0527 | 4.7301 | 1.1833 | -3.2592 | -6.6461 | -9.6041 | 6.7442 | 6.3245 | 5.8527 | 5.1449 | 4.1528 | 3.0023 | 1.8453 | 0.66381 | -0.72257 | -2.712 | -8.0053 | -15.1031 | -20.2503 | -23.3069
|  | MIDDLE WALLOP | LW |  |  | 4.5485 | 3.9659 | 3.2557 | 2.4196 | 1.0014 | -0.62629 | -2.2852 | -3.9724 | -6.0199 | -8.1657 | -13.6477 | -19.9327 | -23.4934 | -25.8337 | 11.1482 | 10.8113 | 10.3876 | 9.8839 | 9.1069 | 8.2156 | 7.289 | 6.3378 | 5.1443 | 3.8376 | 0.59856 | -2.8055 | -4.53 | -5.7212 | 6.6212 | 6.1025 | 5.4556 | 4.6951 | 3.4321 | 1.9883 | 0.49878 | -1.0286 | -2.9064 | -4.8806 | -9.853 | -15.4388 | -18.4512 | -20.3879
|  | MIDDLE WALLOP | ST |  |  | 5.0609 | 4.8296 | 4.5677 | 4.236 | 3.6524 | 2.9517 | 2.2571 | 1.5614 | 0.78059 | -0.036464 | -3.2199 | -9.4849 | -13.216 | -15.9491 | 11.4085 | 11.2466 | 11.0596 | 10.8214 | 10.4304 | 9.9712 | 9.5063 | 9.0324 | 8.4959 | 7.9482 | 5.7525 | 1.132 | -1.6131 | -4.1451 | 7.0978 | 6.9073 | 6.681 | 6.3912 | 5.8801 | 5.2719 | 4.6584 | 4.0353 | 3.3317 | 2.6041 | -0.32391 | -6.0857 | -9.256 | -11.5369
|  | MIDDLE WALLOP | SP |  |  | 5.0926 | 4.8504 | 4.6002 | 4.3031 | 3.8666 | 3.3426 | 2.8183 | 2.2768 | 1.6931 | 1.0485 | -1.2282 | -6.515 | -10.0019 | -11.894 | 11.419 | 11.2424 | 11.0532 | 10.827 | 10.5292 | 10.1789 | 9.8176 | 9.4373 | 9.0207 | 8.554 | 6.854 | 2.4737 | -1.0841 | -4.4813 | 7.1263 | 6.92 | 6.6997 | 6.4403 | 6.0712 | 5.6313 | 5.1786 | 4.7 | 4.1814 | 3.6104 | 1.5417 | -3.4417 | -6.5445 | -8.098
BRAMLEY (FLEE) | FERNHURST | MIDHURST | MINIMUM HEADROOM | SU 88127 19555 | YES | 4.8686 | 4.6595 | 4.4442 | 4.2229 | 3.9158 | 3.6101 | 3.2975 | 2.9617 | 2.5621 | 2.1829 | 1.3523 | 0.49449 | 0.31669 | 0.25164 | 7.4596 | 7.3625 | 7.2607 | 7.1539 | 7.0099 | 6.8653 | 6.7116 | 6.5415 | 6.321 | 6.1182 | 5.7538 | 5.3803 | 5.3013 | 5.1448 | 5.6027 | 5.4191 | 5.2288 | 5.0318 | 4.7613 | 4.4913 | 4.2113 | 3.9069 | 3.5304 | 3.1798 | 2.4803 | 1.7631 | 1.6133 | 1.558
|  | MIDHURST | CT |  |  | 5.0766 | 4.9763 | 4.8699 | 4.7539 | 4.5753 | 4.3963 | 4.2141 | 4.011 | 3.7816 | 3.447 | 2.7457 | 1.6578 | 1.1915 | 1.0837 | 7.518 | 7.4691 | 7.4042 | 7.331 | 7.2351 | 7.1379 | 7.035 | 6.9163 | 6.7759 | 6.5794 | 6.2302 | 5.7246 | 5.4623 | 5.2952 | 5.7682 | 5.6732 | 5.5715 | 5.4589 | 5.2958 | 5.132 | 4.9628 | 4.7712 | 4.5494 | 4.2287 | 3.6154 | 2.7128 | 2.3268 | 2.2354
|  | MIDHURST | LW |  |  | 4.8686 | 4.6595 | 4.4442 | 4.2229 | 3.9158 | 3.6101 | 3.2975 | 2.9617 | 2.5621 | 2.1829 | 1.3523 | 0.49449 | 0.31669 | 0.25164 | 7.4596 | 7.3625 | 7.2607 | 7.1539 | 7.0099 | 6.8653 | 6.7116 | 6.5415 | 6.321 | 6.1182 | 5.7538 | 5.3803 | 5.3013 | 5.2699 | 5.6027 | 5.4191 | 5.2288 | 5.0318 | 4.7613 | 4.4913 | 4.2113 | 3.9069 | 3.5304 | 3.1798 | 2.4803 | 1.7631 | 1.6133 | 1.558
|  | MIDHURST | ST |  |  | 5.1398 | 5.0811 | 5.018 | 4.9461 | 4.8405 | 4.7287 | 4.6166 | 4.4943 | 4.3628 | 4.2227 | 3.6479 | 2.8467 | 2.3773 | 2.0528 | 7.5397 | 7.5305 | 7.5032 | 7.4596 | 7.4027 | 7.3408 | 7.2774 | 7.2057 | 7.1258 | 7.0477 | 6.6866 | 6.2004 | 5.9243 | 5.6763 | 5.8331 | 5.7807 | 5.7232 | 5.6556 | 5.56 | 5.4577 | 5.3548 | 5.2408 | 5.1166 | 4.9886 | 4.4297 | 3.6977 | 3.3064 | 3.0388
|  | MIDHURST | SP |  |  | 5.1712 | 5.1278 | 5.0823 | 5.0353 | 4.8921 | 4.7455 | 4.6006 | 4.4464 | 4.289 | 4.0903 | 3.4192 | 1.9622 | 1.1857 | 0.6949 | 7.5392 | 7.5314 | 7.5218 | 7.4943 | 7.4281 | 7.3589 | 7.2894 | 7.2124 | 7.1321 | 7.0363 | 6.6877 | 5.8661 | 5.458 | 5.1448 | 5.8582 | 5.8182 | 5.7759 | 5.7318 | 5.6088 | 5.4823 | 5.3571 | 5.2218 | 5.083 | 4.9099 | 4.3078 | 2.967 | 2.3156 | 1.9111
AXMINSTER | YEOVIL BSP | MILBORNE PORT | MINIMUM HEADROOM | ST 67929 19741 | YES | 16.4713 | 15.9917 | 15.439 | 14.8647 | 14.0265 | 13.1693 | 12.2652 | 11.284 | 10.0901 | 8.953 | 6.2661 | 3.2343 | 2.3433 | 1.6022 | 13.7393 | 13.5012 | 13.1981 | 12.8757 | 12.4392 | 11.9848 | 11.4796 | 10.9036 | 10.1682 | 9.4933 | 8.098 | 6.6658 | 5.9446 | 5.0399 | 10.6608 | 10.26 | 9.7745 | 9.2647 | 8.5463 | 7.8057 | 7.0052 | 6.1146 | 5.0035 | 3.9513 | 1.515 | -1.138 | -1.8803 | -2.4218
|  | MILBORNE PORT | CT |  |  | 16.8885 | 16.6382 | 16.3464 | 15.9629 | 15.441 | 14.8963 | 14.2913 | 13.5912 | 12.8481 | 11.7514 | 9.2813 | 5.493 | 2.7824 | 1.6022 | 13.8593 | 13.6955 | 13.4984 | 13.2258 | 12.9055 | 12.566 | 12.1874 | 11.7321 | 11.2384 | 10.544 | 9.123 | 7.2282 | 5.9446 | 5.0399 | 10.956 | 10.7277 | 10.4576 | 10.0931 | 9.6228 | 9.1295 | 8.5809 | 7.9356 | 7.2454 | 6.2387 | 4.0728 | 0.77158 | -1.4591 | -2.4218
|  | MILBORNE PORT | LW |  |  | 16.4713 | 15.9917 | 15.439 | 14.8647 | 14.0265 | 13.1693 | 12.2652 | 11.284 | 10.0901 | 8.953 | 6.2661 | 3.2343 | 2.3433 | 1.7823 | 13.7393 | 13.5012 | 13.1981 | 12.8757 | 12.4392 | 11.9848 | 11.4796 | 10.9036 | 10.1682 | 9.4933 | 8.098 | 6.6658 | 6.3182 | 6.1141 | 10.6608 | 10.26 | 9.7745 | 9.2647 | 8.5463 | 7.8057 | 7.0052 | 6.1146 | 5.0035 | 3.9513 | 1.515 | -1.138 | -1.8803 | -2.3389
|  | MILBORNE PORT | ST |  |  | 17.1049 | 16.9789 | 16.8371 | 16.6762 | 16.3943 | 16.1038 | 15.792 | 15.4502 | 15.0518 | 14.6311 | 12.838 | 9.9839 | 8.5841 | 7.6925 | 14.0056 | 13.9237 | 13.8288 | 13.7172 | 13.5369 | 13.3495 | 13.1424 | 12.9107 | 12.6347 | 12.3647 | 11.1157 | 9.1599 | 8.2196 | 7.3893 | 11.1611 | 11.049 | 10.9211 | 10.7737 | 10.5185 | 10.2551 | 9.9698 | 9.6546 | 9.2839 | 8.9031 | 7.2167 | 4.6077 | 3.4403 | 2.7195
|  | MILBORNE PORT | SP |  |  | 17.1702 | 17.0579 | 16.9358 | 16.813 | 16.5332 | 16.2436 | 15.9519 | 15.6318 | 15.2928 | 14.8309 | 13.1929 | 9.2316 | 7.0687 | 5.9632 | 14.0318 | 13.947 | 13.8524 | 13.7548 | 13.5955 | 13.4262 | 13.2573 | 13.0603 | 12.8465 | 12.5752 | 11.5419 | 8.8676 | 7.2723 | 5.9454 | 11.214 | 11.1089 | 10.9941 | 10.8781 | 10.6357 | 10.3831 | 10.1309 | 9.8476 | 9.5462 | 9.145 | 7.6847 | 4.0843 | 2.1567 | 1.173
BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD | MINIMUM HEADROOM | SU 94719 43018 | YES | 1.4666 | 1.3215 | 1.1519 | 0.97383 | 0.70665 | 0.43191 | 0.14421 | -0.15823 | -0.52507 | -0.91077 | -1.7786 | -2.793 | -3.1798 | -3.6194 | 2.8665 | 2.7997 | 2.7105 | 2.6134 | 2.4836 | 2.3476 | 2.197 | 2.0347 | 1.8147 | 1.5847 | 1.1772 | 0.76685 | 0.51631 | 0.26268 | 2.0393 | 1.9081 | 1.7526 | 1.5886 | 1.3456 | 1.0952 | 0.8314 | 0.55337 | 0.20578 | -0.16279 | -0.93702 | -1.8404 | -2.1729 | -2.5561
|  | MILFORD | CT |  |  | 1.5969 | 1.5255 | 1.4398 | 1.3204 | 1.1599 | 0.98741 | 0.80641 | 0.6084 | 0.37257 | 0.003142 | -0.81875 | -2.1452 | -3.1798 | -3.6194 | 2.8996 | 2.8553 | 2.7993 | 2.715 | 2.6216 | 2.5186 | 2.4093 | 2.287 | 2.1324 | 1.9049 | 1.4635 | 0.91592 | 0.51631 | 0.26268 | 2.1516 | 2.0847 | 2.0038 | 1.8893 | 1.7397 | 1.5784 | 1.4088 | 1.2227 | 0.99883 | 0.65068 | -0.10694 | -1.266 | -2.1729 | -2.5561
|  | MILFORD | LW |  |  | 1.4666 | 1.3215 | 1.1519 | 0.97383 | 0.70665 | 0.43191 | 0.14421 | -0.15823 | -0.52507 | -0.91077 | -1.7786 | -2.793 | -3.1286 | -3.3646 | 2.8665 | 2.7997 | 2.7105 | 2.6134 | 2.4836 | 2.3476 | 2.197 | 2.0347 | 1.8147 | 1.5847 | 1.1772 | 0.76685 | 0.65175 | 0.56756 | 2.0393 | 1.9081 | 1.7526 | 1.5886 | 1.3456 | 1.0952 | 0.8314 | 0.55337 | 0.20578 | -0.16279 | -0.93702 | -1.8404 | -2.1336 | -2.3384
|  | MILFORD | ST |  |  | 1.6476 | 1.6049 | 1.555 | 1.5005 | 1.4116 | 1.3151 | 1.2132 | 1.1037 | 0.98424 | 0.85595 | 0.31234 | -0.63468 | -1.1065 | -1.4316 | 2.9363 | 2.9127 | 2.882 | 2.8474 | 2.7943 | 2.7352 | 2.6706 | 2.6 | 2.5206 | 2.4423 | 2.0753 | 1.4687 | 1.2176 | 1.0084 | 2.2011 | 2.1624 | 2.1157 | 2.0646 | 1.9817 | 1.8915 | 1.7958 | 1.6926 | 1.5795 | 1.4595 | 0.94185 | 0.053764 | -0.36491 | -0.64776
|  | MILFORD | SP |  |  | 1.6666 | 1.6275 | 1.5856 | 1.5408 | 1.4301 | 1.317 | 1.1986 | 1.0748 | 0.94252 | 0.77796 | 0.22254 | -1.1086 | -1.7898 | -2.1913 | 2.9414 | 2.9154 | 2.8862 | 2.8541 | 2.8009 | 2.7454 | 2.6869 | 2.6217 | 2.5499 | 2.4657 | 2.1525 | 1.3192 | 0.91695 | 0.63813 | 2.2173 | 2.1807 | 2.1413 | 2.0989 | 1.9986 | 1.8961 | 1.7906 | 1.6784 | 1.5575 | 1.4078 | 0.89554 | -0.35709 | -0.97579 | -1.311
MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA | MINIMUM HEADROOM | SZ 28252 93347 | YES | 11.5823 | 11.0227 | 10.3704 | 9.6759 | 8.8463 | 8.0314 | 7.134 | 6.1355 | 4.9062 | 3.7411 | 1.2014 | -1.9395 | -3.8101 | -5.188 | 15.199 | 14.8959 | 14.5329 | 14.1415 | 13.7131 | 13.2818 | 12.7805 | 12.2026 | 11.4325 | 10.7333 | 9.4732 | 8.0569 | 6.8318 | 5.8901 | 13.098 | 12.6008 | 12.0187 | 11.3951 | 10.6365 | 9.8832 | 9.0488 | 8.1166 | 6.9557 | 5.861 | 3.5302 | 0.68385 | -0.99774 | -2.2952
|  | MILFORD-ON-SEA | CT |  |  | 11.8155 | 11.4028 | 10.9105 | 10.3451 | 9.7856 | 9.2513 | 8.6639 | 7.9914 | 7.225 | 6.034 | 3.4793 | -0.75855 | -3.8101 | -5.188 | 15.226 | 14.9541 | 14.6311 | 14.251 | 13.9065 | 13.5662 | 13.1802 | 12.7274 | 12.1914 | 11.4354 | 10.0426 | 8.1486 | 6.8318 | 5.8901 | 13.2962 | 12.9282 | 12.4883 | 11.9761 | 11.4584 | 10.9565 | 10.4032 | 9.7678 | 9.0389 | 7.9149 | 5.5581 | 1.7585 | -0.99774 | -2.2952
|  | MILFORD-ON-SEA | LW |  |  | 11.5823 | 11.0227 | 10.3704 | 9.6759 | 8.8463 | 8.0314 | 7.134 | 6.1355 | 4.9062 | 3.7411 | 1.2014 | -1.9395 | -3.0637 | -3.7287 | 15.199 | 14.8959 | 14.5329 | 14.1415 | 13.7131 | 13.2818 | 12.7805 | 12.2026 | 11.4325 | 10.7333 | 9.4732 | 8.0569 | 7.6363 | 7.4012 | 13.098 | 12.6008 | 12.0187 | 11.3951 | 10.6365 | 9.8832 | 9.0488 | 8.1166 | 6.9557 | 5.861 | 3.5302 | 0.68385 | -0.31101 | -0.90169
|  | MILFORD-ON-SEA | ST |  |  | 12.0688 | 11.8399 | 11.5643 | 11.266 | 10.9782 | 10.7118 | 10.4115 | 10.0739 | 9.6916 | 9.3008 | 7.4758 | 4.5719 | 3.0212 | 1.9404 | 15.4167 | 15.2731 | 15.0946 | 14.8948 | 14.6974 | 14.5078 | 14.2881 | 14.0373 | 13.7474 | 13.4801 | 12.1101 | 10.0952 | 9.1253 | 8.2499 | 13.543 | 13.3519 | 13.1192 | 12.8603 | 12.5976 | 12.3459 | 12.0618 | 11.7419 | 11.3779 | 11.0092 | 9.2515 | 6.5139 | 5.1197 | 4.1678
|  | MILFORD-ON-SEA | SP |  |  | 12.1044 | 11.8888 | 11.6507 | 11.4024 | 11.095 | 10.8034 | 10.5031 | 10.1593 | 9.7921 | 9.3586 | 7.7902 | 3.9872 | 2.1839 | 1.2451 | 15.4278 | 15.2815 | 15.1177 | 14.9416 | 14.7687 | 14.6015 | 14.4229 | 14.2059 | 13.9672 | 13.7075 | 12.68 | 9.9784 | 8.7183 | 7.8203 | 13.5749 | 13.3922 | 13.1867 | 12.9695 | 12.7106 | 12.4431 | 12.1679 | 11.8502 | 11.5098 | 11.1086 | 9.6361 | 6.0254 | 4.3588 | 3.518
MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood | MINIMUM HEADROOM | SU 14691 05633 | YES | 2.7299 | 2.4241 | 2.0212 | 11.7849 | 10.8318 | 9.8795 | 8.8915 | 7.92 | 6.7251 | 5.548 | 3.0126 | 0.25112 | -1.8519 | -3.0328 | 3.6688 | 3.4932 | 3.2329 | 14.9862 | 14.4665 | 13.9386 | 13.3689 | 12.7895 | 12.0354 | 11.2851 | 9.8438 | 8.4336 | 7.1311 | 6.1309 | 1.1217 | 0.8453 | 0.48178 | 12.107 | 11.2691 | 10.4266 | 9.5498 | 8.6804 | 7.6158 | 6.5606 | 4.239 | 1.6801 | -0.30261 | -1.411
|  | Mill Lane, Ringwood | CT |  |  | 2.887 | 2.6856 | 2.4475 | 12.2798 | 11.5517 | 10.8357 | 10.1008 | 9.3939 | 8.5749 | 7.3873 | 4.5858 | 0.79056 | -1.8519 | -3.0328 | 3.6984 | 3.5539 | 3.3732 | 15.123 | 14.685 | 14.2421 | 13.7778 | 13.3107 | 12.755 | 11.989 | 10.2911 | 8.4336 | 7.1311 | 6.1309 | 1.2723 | 1.094 | 0.88046 | 12.5729 | 11.9461 | 11.3249 | 10.6829 | 10.0589 | 9.3371 | 8.2564 | 5.6428 | 2.1812 | -0.30261 | -1.411
|  | Mill Lane, Ringwood | LW |  |  | 2.7299 | 2.4241 | 2.0212 | 11.7849 | 10.8318 | 9.8795 | 8.8915 | 7.92 | 6.7251 | 5.548 | 3.0126 | 0.25112 | -0.83649 | -1.274 | 3.6688 | 3.4932 | 3.2329 | 14.9862 | 14.4665 | 13.9386 | 13.3689 | 12.7895 | 12.0354 | 11.2851 | 9.8438 | 8.4816 | 8.035 | 7.8496 | 1.1217 | 0.8453 | 0.48178 | 12.107 | 11.2691 | 10.4266 | 9.5498 | 8.6804 | 7.6158 | 6.5606 | 4.239 | 1.6801 | 0.66759 | 0.26388
|  | Mill Lane, Ringwood | ST |  |  | 3.0526 | 2.9588 | 2.8381 | 12.9377 | 12.5366 | 12.1464 | 11.7563 | 11.4022 | 10.9886 | 10.6078 | 8.9749 | 5.9106 | 4.4669 | 3.4577 | 3.8182 | 3.7494 | 3.6542 | 15.6036 | 15.3356 | 15.0695 | 14.7958 | 14.5361 | 14.2269 | 13.9541 | 12.692 | 10.4556 | 9.4805 | 8.5825 | 1.4202 | 1.3381 | 1.2295 | 13.1585 | 12.8317 | 12.5091 | 12.1825 | 11.8789 | 11.5237 | 11.1879 | 9.7207 | 6.8013 | 5.5033 | 4.6149
|  | Mill Lane, Ringwood | SP |  |  | 3.0831 | 2.9799 | 2.86 | 12.9771 | 12.6487 | 12.3196 | 12.0107 | 11.7134 | 11.3902 | 11.0542 | 9.8412 | 6.7137 | 5.2156 | 4.6176 | 3.8304 | 3.745 | 3.641 | 15.5942 | 15.3892 | 15.1811 | 14.975 | 14.7659 | 14.5368 | 14.2939 | 13.3612 | 10.8221 | 9.2744 | 7.8562 | 1.4486 | 1.3598 | 1.2531 | 13.1987 | 12.9348 | 12.6643 | 12.4084 | 12.1542 | 11.8773 | 11.5818 | 10.5069 | 7.566 | 6.1543 | 5.6151
COWLEY GSP | DRAYTON BSP | MILTON | MINIMUM HEADROOM | SU 49992 92060 | NO | 9.0759 | 17.2759 | 16.4898 | 15.7378 | 14.5098 | 13.1189 | 11.5085 | 9.6598 | 7.4735 | 5.2685 | -0.6546 | -6.8006 | -9.3833 | -11.5957 | 17.7804 | 24.4289 | 24.1269 | 23.8749 | 23.3323 | 22.6087 | 21.7394 | 20.659 | 19.2611 | 17.8645 | 14.3591 | 10.8721 | 8.4125 | 6.1624 | 13.8124 | 20.062 | 19.3314 | 18.6319 | 17.5049 | 16.2452 | 14.7899 | 13.1141 | 11.1556 | 9.1218 | 3.7509 | -1.8713 | -4.1193 | -6.0722
|  | MILTON | CT |  |  | 9.5047 | 17.9517 | 17.4441 | 16.9082 | 16.1005 | 15.1275 | 13.9321 | 12.5349 | 10.9694 | 8.8415 | 3.2641 | -4.5583 | -9.3833 | -11.5957 | 17.7804 | 24.4289 | 24.1269 | 23.8749 | 23.5437 | 23.1994 | 22.5283 | 21.6051 | 20.4781 | 19.072 | 15.6047 | 11.182 | 8.4125 | 6.1624 | 14.1202 | 20.6507 | 20.1692 | 19.6562 | 18.9016 | 18.03 | 16.9712 | 15.6604 | 14.17 | 12.1685 | 7.1118 | 0.18482 | -4.1193 | -6.0722
|  | MILTON | LW |  |  | 9.0759 | 17.2759 | 16.4898 | 15.7378 | 14.5098 | 13.1189 | 11.5085 | 9.6598 | 7.4735 | 5.2685 | -0.6546 | -6.8006 | -8.5636 | -9.5871 | 17.8153 | 24.4609 | 24.1567 | 23.9156 | 23.3323 | 22.6087 | 21.7394 | 20.659 | 19.2611 | 17.8645 | 14.3591 | 10.8721 | 10.1662 | 9.7345 | 13.8124 | 20.062 | 19.3314 | 18.6319 | 17.5049 | 16.2452 | 14.7899 | 13.1141 | 11.1556 | 9.1218 | 3.7509 | -1.8713 | -3.4415 | -4.3592
|  | MILTON | ST |  |  | 9.7735 | 18.392 | 18.0801 | 17.8194 | 17.3887 | 16.8749 | 16.2408 | 15.4631 | 14.5305 | 13.5284 | 9.7057 | 3.5904 | 0.44842 | -1.2779 | 17.9118 | 24.6433 | 24.4413 | 24.3162 | 24.0935 | 23.8662 | 23.5583 | 23.1247 | 22.5447 | 21.8791 | 19.1086 | 13.0516 | 10.6461 | 9.9202 | 14.2978 | 20.9882 | 20.7561 | 20.5344 | 20.1296 | 19.665 | 19.0994 | 18.3985 | 17.5602 | 16.6749 | 13.0181 | 6.1367 | 3.1318 | 2.1453
|  | MILTON | SP |  |  | 9.8465 | 18.4929 | 18.2168 | 18.0072 | 17.5234 | 16.9911 | 16.3594 | 15.5967 | 14.7449 | 13.7919 | 10.6314 | 4.4595 | 0.74716 | -0.89964 | 17.921 | 24.6585 | 24.4635 | 24.3515 | 24.1608 | 23.9747 | 23.7221 | 23.3508 | 22.7716 | 22.1212 | 19.9492 | 15.0894 | 11.3435 | 7.8588 | 14.3353 | 21.0476 | 20.8395 | 20.7023 | 20.2571 | 19.7854 | 19.2322 | 18.5548 | 17.7859 | 16.9345 | 14.1329 | 8.1499 | 4.6682 | 3.2182
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON | MINIMUM HEADROOM | ST 96164 14520 | YES | 26.9113 | 21.1631 | 15.0514 | 8.6729 | 5.8169 | 2.5556 | -0.87619 | -4.4895 | -8.4428 | -12.1251 | -19.3279 | -25.2303 | -27.8989 | -29.7359 | 29.6462 | 23.3496 | 16.8014 | 10.1633 | 8.3546 | 6.3617 | 4.2999 | 2.2284 | -0.0090697 | -2.1343 | -6.4841 | -9.8633 | -11.776 | -13.2748 | 28.8301 | 22.2372 | 15.3329 | 8.2205 | 5.7075 | 2.8732 | -0.11914 | -3.2627 | -6.7293 | -9.9796 | -16.4265 | -21.7651 | -24.0343 | -25.6419
|  | MINCHINGTON | CT |  |  | 27.1377 | 21.5479 | 15.6142 | 9.3708 | 6.8552 | 3.945 | 0.93611 | -2.2316 | -5.6116 | -9.2476 | -16.428 | -23.7762 | -27.8989 | -29.7359 | 29.7068 | 23.4614 | 16.9711 | 10.3666 | 8.6852 | 6.8255 | 4.9359 | 3.0484 | 1.082 | -1.0099 | -5.3922 | -9.5641 | -11.776 | -13.2748 | 29.0225 | 22.5698 | 15.8252 | 8.8296 | 6.6202 | 4.1 | 1.4899 | -1.2494 | -4.18 | -7.3833 | -13.8066 | -20.4053 | -24.0343 | -25.6419
|  | MINCHINGTON | LW |  |  | 26.9113 | 21.1631 | 15.0514 | 8.6729 | 5.8169 | 2.5556 | -0.87619 | -4.4895 | -8.4428 | -12.1251 | -19.3279 | -25.2303 | -27.0254 | -27.9072 | 29.6462 | 23.3496 | 16.8014 | 10.1633 | 8.3546 | 6.3617 | 4.2999 | 2.2284 | -0.0090697 | -2.1343 | -6.4841 | -9.8633 | -10.6907 | -11.095 | 28.8301 | 22.2372 | 15.3329 | 8.2205 | 5.7075 | 2.8732 | -0.11914 | -3.2627 | -6.7293 | -9.9796 | -16.4265 | -21.7651 | -23.3319 | -24.0972
|  | MINCHINGTON | ST |  |  | 27.5416 | 22.3144 | 16.8599 | 11.3113 | 9.5383 | 7.5415 | 5.4832 | 3.3913 | 1.2179 | -0.80482 | -5.6298 | -11.8822 | -14.8176 | -16.3039 | 29.938 | 23.8831 | 17.6371 | 11.3759 | 10.0325 | 8.5806 | 7.116 | 5.7068 | 4.2786 | 2.9298 | -0.3779 | -4.7215 | -6.8405 | -8.2161 | 29.4104 | 23.2991 | 17.0017 | 10.6508 | 9.113 | 7.4157 | 5.6629 | 3.8938 | 2.0271 | 0.2795 | -4.1937 | -10.2006 | -12.7981 | -14.0282
|  | MINCHINGTON | SP |  |  | 27.5962 | 22.4003 | 17.0118 | 11.566 | 9.9727 | 8.2223 | 6.3602 | 4.498 | 2.6471 | 0.8899 | -2.9187 | -8.5501 | -11.8675 | -13.085 | 29.9601 | 23.9178 | 17.6998 | 11.4851 | 10.2422 | 8.9224 | 7.5588 | 6.2643 | 5.0023 | 3.7924 | 1.1014 | -2.8321 | -5.6961 | -7.5176 | 29.4599 | 23.3763 | 17.1399 | 10.8852 | 9.522 | 8.0611 | 6.491 | 4.9339 | 3.3938 | 1.8969 | -1.5518 | -7.1346 | -10.2951 | -11.3825
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE | MINIMUM HEADROOM | SU 01647 91932 | NO | 2.1437 | 2.0196 | 1.8779 | 1.7319 | 1.5387 | 1.3396 | 1.1348 | 0.90656 | 0.61196 | 0.36475 | -0.15749 | -0.67899 | -0.79053 | -0.87326 | 3.3353 | 3.277 | 3.2049 | 3.1294 | 3.0326 | 2.931 | 2.8223 | 2.696 | 2.5276 | 2.3901 | 2.1489 | 1.9152 | 1.8683 | 1.8351 | 2.707 | 2.5914 | 2.4604 | 2.3256 | 2.1467 | 1.9625 | 1.7737 | 1.5643 | 1.2952 | 1.0679 | 0.57608 | 0.083759 | -0.020333 | -0.097538
|  | MINETY VILLAGE | CT |  |  | 2.2654 | 2.2049 | 2.1362 | 2.0482 | 1.9312 | 1.8096 | 1.6707 | 1.5151 | 1.3407 | 1.1067 | 0.67898 | 0.057118 | -0.33742 | -0.50281 | 3.3757 | 3.339 | 3.2958 | 3.2367 | 3.1689 | 3.0975 | 3.0162 | 2.9224 | 2.813 | 2.6675 | 2.4408 | 2.1509 | 1.9636 | 1.8452 | 2.8227 | 2.7673 | 2.7047 | 2.6253 | 2.5181 | 2.4068 | 2.2797 | 2.1378 | 1.9796 | 1.7675 | 1.3698 | 0.78168 | 0.40942 | 0.25386
|  | MINETY VILLAGE | LW |  |  | 2.1437 | 2.0196 | 1.8779 | 1.7319 | 1.5387 | 1.3396 | 1.1348 | 0.90656 | 0.61196 | 0.36475 | -0.15749 | -0.67899 | -0.79053 | -0.87326 | 3.3353 | 3.277 | 3.2049 | 3.1294 | 3.0326 | 2.931 | 2.8223 | 2.696 | 2.5276 | 2.3901 | 2.1489 | 1.9152 | 1.8683 | 1.8351 | 2.707 | 2.5914 | 2.4604 | 2.3256 | 2.1467 | 1.9625 | 1.7737 | 1.5643 | 1.2952 | 1.0679 | 0.57608 | 0.083759 | -0.020333 | -0.097538
|  | MINETY VILLAGE | ST |  |  | 2.3106 | 2.277 | 2.2403 | 2.199 | 2.1278 | 2.0532 | 1.9768 | 1.8924 | 1.796 | 1.6954 | 1.2667 | 0.72936 | 0.46238 | 0.31266 | 3.405 | 3.3855 | 3.3634 | 3.3373 | 3.2962 | 3.2524 | 3.2065 | 3.1543 | 3.0939 | 3.0362 | 2.7617 | 2.4323 | 2.2839 | 2.1711 | 2.8636 | 2.8327 | 2.799 | 2.7613 | 2.696 | 2.6276 | 2.5577 | 2.4808 | 2.393 | 2.3003 | 1.9114 | 1.4141 | 1.1616 | 1.0208
|  | MINETY VILLAGE | SP |  |  | 2.3308 | 2.3028 | 2.2739 | 2.2447 | 2.1702 | 2.0937 | 2.0206 | 1.934 | 1.8526 | 1.7315 | 1.3107 | 0.34347 | -0.18128 | -0.50896 | 3.4119 | 3.3927 | 3.3725 | 3.3515 | 3.3135 | 3.2734 | 3.2355 | 3.1871 | 3.1415 | 3.0801 | 2.8489 | 2.2839 | 2.0313 | 1.8734 | 2.8828 | 2.8574 | 2.8313 | 2.8049 | 2.7356 | 2.6649 | 2.5969 | 2.5171 | 2.442 | 2.3294 | 1.9419 | 1.0551 | 0.56 | 0.25099
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER | MINIMUM HEADROOM | SU 62236 64103 | YES | 9.35 | 8.8518 | 8.375 | 7.7675 | 6.9879 | 6.137 | 5.2509 | 4.214 | 3.0695 | 2.0363 | -0.79188 | -2.6463 | -2.8664 | -2.949 | 10.9021 | 10.5972 | 10.3329 | 10.0079 | 9.6085 | 9.177 | 8.7239 | 8.1842 | 7.5751 | 7.046 | 5.6838 | 4.7761 | 4.6717 | 4.6336 | 10.3692 | 9.9797 | 9.561 | 9.0467 | 8.3751 | 7.6458 | 6.8829 | 5.9844 | 4.988 | 4.1074 | 1.7694 | 0.18706 | -0.0045394 | -0.077219
|  | MORTIMER | CT |  |  | 9.6286 | 9.2856 | 8.9269 | 8.4689 | 7.8735 | 7.205 | 6.5092 | 5.6956 | 4.8013 | 3.7961 | 1.2194 | -0.83385 | -1.4649 | -1.633 | 11.0026 | 10.7573 | 10.5257 | 10.255 | 9.9302 | 9.5721 | 9.1937 | 8.7503 | 8.268 | 7.7312 | 6.4282 | 5.3769 | 5.0312 | 4.8237 | 10.3979 | 10.1898 | 10.019 | 9.6559 | 9.1482 | 8.581 | 7.9866 | 7.2891 | 6.5254 | 5.6609 | 3.505 | 1.7566 | 1.2348 | 1.0898
|  | MORTIMER | LW |  |  | 9.35 | 8.8518 | 8.375 | 7.7675 | 6.9879 | 6.137 | 5.2509 | 4.214 | 3.0695 | 2.0363 | -0.79188 | -2.6463 | -2.8664 | -2.949 | 10.9021 | 10.5972 | 10.3329 | 10.0079 | 9.6085 | 9.177 | 8.7239 | 8.1842 | 7.5751 | 7.046 | 5.6838 | 4.7761 | 4.6717 | 4.6336 | 10.3692 | 9.9797 | 9.561 | 9.0467 | 8.3751 | 7.6458 | 6.8829 | 5.9844 | 4.988 | 4.1074 | 1.7694 | 0.18706 | -0.0045394 | -0.077219
|  | MORTIMER | ST |  |  | 9.7799 | 9.5347 | 9.3056 | 9.0031 | 8.6061 | 8.1653 | 7.7094 | 7.1937 | 6.6223 | 6.0339 | 3.9816 | 2.4205 | 1.8607 | 1.5404 | 11.0933 | 10.905 | 10.7477 | 10.5553 | 10.3226 | 10.069 | 9.8055 | 9.508 | 9.1754 | 8.8445 | 7.6419 | 6.7107 | 6.3689 | 6.1073 | 10.4489 | 10.2695 | 10.1424 | 9.9967 | 9.8284 | 9.4658 | 9.089 | 8.6631 | 8.1905 | 7.7068 | 5.9715 | 4.6226 | 4.125 | 3.8429
|  | MORTIMER | SP |  |  | 9.8208 | 9.6067 | 9.4232 | 9.1856 | 8.8341 | 8.4576 | 8.0439 | 7.5778 | 7.068 | 6.4908 | 4.6647 | 2.384 | 1.3944 | 0.78873 | 11.1087 | 10.9349 | 10.8011 | 10.6443 | 10.4419 | 10.2286 | 9.9888 | 9.7158 | 9.4165 | 9.093 | 8.0567 | 6.7132 | 6.2048 | 5.883 | 10.4536 | 10.2802 | 10.1595 | 10.0263 | 9.8765 | 9.7179 | 9.4034 | 9.0227 | 8.6074 | 8.1343 | 6.6206 | 4.5945 | 3.7095 | 3.1733
MANNINGTON GSP | SALISBURY | NETHERHAMPTON | MINIMUM HEADROOM | SU 12478 29102 | YES | 5.4164 | 4.873 | 4.3187 | 3.8518 | 3.1711 | 2.4741 | 1.7305 | 0.90199 | -0.032587 | -0.92339 | -2.9353 | -5.427 | -6.2809 | -7.091 | 5.8262 | 5.5059 | 5.1714 | 4.8974 | 4.5364 | 4.1664 | 3.7579 | 3.2851 | 2.7233 | 2.1841 | 1.1925 | 0.04839 | -1.0613 | -1.989 | 3.8171 | 3.3371 | 2.8355 | 2.4024 | 1.7793 | 1.141 | 0.45601 | -0.33004 | -1.24 | -2.0908 | -3.8686 | -6.0797 | -6.8311 | -7.5226
|  | NETHERHAMPTON | CT |  |  | 5.6993 | 5.3139 | 4.9195 | 4.5993 | 4.1695 | 3.7184 | 3.2348 | 2.6884 | 2.0814 | 1.1759 | -0.71629 | -3.985 | -6.2809 | -7.091 | 5.9039 | 5.6301 | 5.3422 | 5.1027 | 4.832 | 4.5517 | 4.248 | 3.8998 | 3.4923 | 2.9096 | 1.8273 | 0.20341 | -1.0613 | -1.989 | 4.0571 | 3.6991 | 3.3236 | 3 | 2.5918 | 2.1678 | 1.7133 | 1.197 | 0.61962 | -0.23466 | -1.9725 | -4.8012 | -6.8127 | -7.5226
|  | NETHERHAMPTON | LW |  |  | 5.4164 | 4.873 | 4.3187 | 3.8518 | 3.1711 | 2.4741 | 1.7305 | 0.90199 | -0.032587 | -0.92339 | -2.9353 | -5.427 | -6.2803 | -6.698 | 5.8262 | 5.5059 | 5.1714 | 4.8974 | 4.5364 | 4.1664 | 3.7579 | 3.2851 | 2.7233 | 2.1841 | 1.1925 | 0.04839 | -0.3198 | -0.50352 | 3.8171 | 3.3371 | 2.8355 | 2.4024 | 1.7793 | 1.141 | 0.45601 | -0.33004 | -1.24 | -2.0908 | -3.8686 | -6.0797 | -6.8311 | -7.1949
|  | NETHERHAMPTON | ST |  |  | 5.8715 | 5.6152 | 5.3522 | 5.1667 | 4.9239 | 4.6809 | 4.4234 | 4.1448 | 3.8396 | 3.5273 | 2.062 | -0.088364 | -1.2634 | -2.111 | 6.0279 | 5.8417 | 5.6431 | 5.5016 | 5.334 | 5.1668 | 4.9856 | 4.786 | 4.5611 | 4.3491 | 3.332 | 1.7931 | 0.89947 | -0.024087 | 4.2297 | 4.0081 | 3.776 | 3.5981 | 3.3654 | 3.1323 | 2.8813 | 2.6072 | 2.3018 | 1.9993 | 0.59177 | -1.4241 | -2.4741 | -3.2178
|  | NETHERHAMPTON | SP |  |  | 5.9086 | 5.6714 | 5.4447 | 5.2988 | 5.0048 | 4.7253 | 4.4444 | 4.1302 | 3.8136 | 3.4388 | 2.1348 | -0.91801 | -2.3688 | -3.19 | 6.0395 | 5.8569 | 5.674 | 5.551 | 5.3778 | 5.2122 | 5.0446 | 4.8491 | 4.6469 | 4.4154 | 3.5581 | 1.3746 | 0.061257 | -1.309 | 4.2637 | 4.0602 | 3.8555 | 3.7144 | 3.4497 | 3.198 | 2.9425 | 2.6542 | 2.3606 | 2.0146 | 0.77205 | -2.1449 | -3.4699 | -4.1987
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV | MINIMUM HEADROOM | SU 47615 12025 | YES | 8.8937 | 8.7888 | 8.6083 | 8.3762 | 8.0112 | 7.5725 | 7.0997 | 6.5137 | 5.8071 | 5.1254 | 3.8824 | 2.7493 | 1.7632 | 1.2551 | 7.0929 | 7.0742 | 7.0394 | 6.9901 | 6.9318 | 6.8005 | 6.5377 | 6.2151 | 5.8155 | 5.4141 | 4.6165 | 3.5523 | 2.5467 | 0.89096 | 6.2965 | 6.2015 | 6.0458 | 5.8475 | 5.529 | 5.1496 | 4.7402 | 4.2364 | 3.6298 | 3.0401 | 1.9358 | 0.89911 | -0.024768 | -0.49701
|  | NETLEY COMMON 11kV | CT |  |  | 8.9404 | 8.867 | 8.729 | 8.5207 | 8.2365 | 7.8804 | 7.5015 | 7.0151 | 6.4391 | 5.756 | 4.3951 | 2.8398 | 1.7632 | 1.2551 | 7.0929 | 7.0742 | 7.0394 | 6.9901 | 6.9318 | 6.8353 | 6.5956 | 6.2972 | 5.9449 | 5.5203 | 4.6165 | 3.5523 | 2.5467 | 1.3979 | 6.3416 | 6.2762 | 6.1597 | 5.9844 | 5.7416 | 5.4395 | 5.1174 | 4.706 | 4.2184 | 3.6269 | 2.4187 | 0.98086 | -0.024768 | -0.49701
|  | NETLEY COMMON 11kV | LW |  |  | 8.8937 | 8.7888 | 8.6083 | 8.3762 | 8.0112 | 7.5725 | 7.0997 | 6.5137 | 5.8071 | 5.1254 | 3.8824 | 2.7493 | 2.2499 | 2.0429 | 7.0972 | 7.0796 | 7.0449 | 6.9985 | 6.939 | 6.8005 | 6.5377 | 6.2151 | 5.8155 | 5.4141 | 4.692 | 4.1036 | 3.8682 | 3.7638 | 6.2965 | 6.2015 | 6.0458 | 5.8475 | 5.529 | 5.1496 | 4.7402 | 4.2364 | 3.6298 | 3.0401 | 1.9358 | 0.89911 | 0.43971 | 0.2531
|  | NETLEY COMMON 11kV | ST |  |  | 9.0158 | 8.9883 | 8.9179 | 8.819 | 8.6645 | 8.4638 | 8.2485 | 7.9609 | 7.6214 | 7.3256 | 6.6294 | 5.3616 | 4.7721 | 4.3315 | 7.1085 | 7.0994 | 7.0767 | 7.0447 | 6.9995 | 6.9399 | 6.8759 | 6.7908 | 6.5791 | 6.3703 | 5.7894 | 4.611 | 3.7674 | 2.6428 | 6.4087 | 6.3843 | 6.3285 | 6.2514 | 6.1286 | 5.9703 | 5.7995 | 5.5728 | 5.3044 | 5.0664 | 4.4748 | 3.3515 | 2.809 | 2.3995
|  | NETLEY COMMON 11kV | SP |  |  | 9.0216 | 8.9913 | 8.9284 | 8.8403 | 8.7176 | 8.5571 | 8.3822 | 8.1374 | 7.861 | 7.6081 | 7.081 | 5.9791 | 5.3794 | 5.1417 | 7.1087 | 7.0996 | 7.0782 | 7.048 | 7.0092 | 6.9574 | 6.9008 | 6.8236 | 6.6712 | 6.4647 | 5.9223 | 4.5976 | 3.1049 | 0.89096 | 6.4143 | 6.3879 | 6.3391 | 6.2719 | 6.1769 | 6.0541 | 5.9197 | 5.7318 | 5.5211 | 5.323 | 4.8831 | 3.9227 | 3.3905 | 3.1776
MANNINGTON GSP | ARNEWOOD | NEW MILTON | MINIMUM HEADROOM | SZ 23049 94942 | YES | 0.62166 | -0.33398 | -1.2906 | -2.2237 | -3.7833 | -5.4276 | -7.2049 | -9.0299 | -11.2941 | -13.6476 | -19.6301 | -27.6793 | -34.4697 | -38.7753 | 3.6346 | 3.0344 | 2.4294 | 1.844 | 0.99483 | 0.1096 | -0.87196 | -1.8928 | -3.261 | -4.8526 | -8.5165 | -13.7713 | -18.5658 | -23.1643 | -1.9957 | -2.8405 | -3.7077 | -4.5568 | -5.9501 | -7.4064 | -8.9794 | -10.6017 | -12.6164 | -14.8334 | -20.3797 | -27.6101 | -33.3432 | -36.9886
|  | NEW MILTON | CT |  |  | 0.92544 | 0.16583 | -0.51764 | -1.3464 | -2.4483 | -3.6167 | -4.8815 | -6.165 | -7.6534 | -10.0149 | -16.2904 | -26.7403 | -34.4697 | -38.7753 | 3.7036 | 3.1433 | 2.642 | 2.0494 | 1.3473 | 0.61716 | -0.17995 | -1.0041 | -2.0247 | -3.667 | -7.7961 | -13.7713 | -18.5658 | -23.1643 | -1.7342 | -2.4054 | -3.0219 | -3.7524 | -4.727 | -5.748 | -6.855 | -7.9853 | -9.3359 | -11.5519 | -17.3637 | -26.6704 | -33.3432 | -36.9886
|  | NEW MILTON | LW |  |  | 0.62166 | -0.33398 | -1.2906 | -2.2237 | -3.7833 | -5.4276 | -7.2049 | -9.0299 | -11.2941 | -13.6476 | -19.6301 | -27.6793 | -31.7997 | -34.2462 | 3.6346 | 3.0344 | 2.4294 | 1.844 | 0.99483 | 0.1096 | -0.87196 | -1.8928 | -3.261 | -4.8526 | -8.5165 | -12.8763 | -14.7311 | -15.9233 | -1.9957 | -2.8405 | -3.7077 | -4.5568 | -5.9501 | -7.4064 | -8.9794 | -10.6017 | -12.6164 | -14.8334 | -20.3797 | -27.6101 | -31.1011 | -33.1168
|  | NEW MILTON | ST |  |  | 1.3515 | 0.89058 | 0.52441 | 0.20014 | -0.26921 | -0.77366 | -1.3491 | -1.9379 | -2.6192 | -3.3415 | -6.5458 | -14.0961 | -18.7819 | -22.0815 | 3.9539 | 3.5821 | 3.2926 | 3.0267 | 2.6378 | 2.2436 | 1.8113 | 1.3576 | 0.83054 | 0.28963 | -2.207 | -8.4155 | -12.5322 | -16.7593 | -1.3472 | -1.7277 | -2.0355 | -2.3266 | -2.7649 | -3.2143 | -3.7026 | -4.2105 | -4.8009 | -5.4377 | -8.3561 | -15.448 | -19.4978 | -22.2157
|  | NEW MILTON | SP |  |  | 1.4128 | 0.96003 | 0.61228 | 0.32439 | -0.045837 | -0.421 | -0.83898 | -1.2816 | -1.766 | -2.3369 | -4.5397 | -11.0776 | -15.5901 | -17.8408 | 3.9752 | 3.5966 | 3.3026 | 3.0376 | 2.7128 | 2.3945 | 2.0492 | 1.6766 | 1.2619 | 0.75902 | -1.2082 | -7.6738 | -13.9447 | -21.4804 | -1.2925 | -1.6639 | -1.9604 | -2.2187 | -2.5607 | -2.896 | -3.2506 | -3.6301 | -4.0465 | -4.5446 | -6.4491 | -12.6285 | -16.7196 | -18.6091
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT | MINIMUM HEADROOM | SZ 50076 89544 | NO | 10.2531 | 10.0924 | 9.8851 | 9.3781 | 8.2854 | 7.0819 | 5.728 | 4.2723 | 2.5186 | 0.66204 | -3.833 | -8.9506 | -13.0962 | -15.7212 | 15.6872 | 15.4132 | 14.9993 | 14.5273 | 13.8738 | 13.1493 | 12.3093 | 11.3965 | 10.2614 | 9.0406 | 6.2093 | 3.0322 | 0.052529 | -2.5709 | 11.5342 | 11.3226 | 11.0693 | 10.3912 | 9.3256 | 8.1584 | 6.8477 | 5.4383 | 3.7386 | 1.9357 | -2.4527 | -7.1981 | -10.6632 | -12.8016
|  | NEWPORT | CT |  |  | 10.2531 | 10.0924 | 9.9031 | 9.6421 | 9.3487 | 8.549 | 7.5859 | 6.5295 | 5.3299 | 3.4969 | -1.3259 | -8.0385 | -13.0962 | -15.7212 | 15.7498 | 15.5281 | 15.2662 | 14.7985 | 14.2659 | 13.6851 | 13.0183 | 12.2807 | 11.4286 | 10.1948 | 6.9814 | 3.0322 | 0.052529 | -2.5709 | 11.5356 | 11.3574 | 11.1485 | 10.8665 | 10.4086 | 9.5976 | 8.669 | 7.6502 | 6.4919 | 4.7109 | 0.0068469 | -6.3335 | -10.6632 | -12.8016
|  | NEWPORT | LW |  |  | 10.2801 | 10.1032 | 9.8851 | 9.3781 | 8.2854 | 7.0819 | 5.728 | 4.2723 | 2.5186 | 0.66204 | -3.833 | -8.9506 | -11.1775 | -12.4316 | 15.6872 | 15.4132 | 14.9993 | 14.5273 | 13.8738 | 13.1493 | 12.3093 | 11.3965 | 10.2614 | 9.0406 | 6.2093 | 3.4402 | 2.4553 | 1.8806 | 11.5342 | 11.3226 | 11.0693 | 10.3912 | 9.3256 | 8.1584 | 6.8477 | 5.4383 | 3.7386 | 1.9357 | -2.4527 | -7.1981 | -9.1255 | -10.19
|  | NEWPORT | ST |  |  | 10.3992 | 10.3293 | 10.2495 | 10.1524 | 9.9968 | 9.8129 | 9.5905 | 9.3385 | 8.8495 | 8.2523 | 5.691 | -0.066459 | -2.8496 | -4.6801 | 15.9402 | 15.8388 | 15.7057 | 15.5479 | 15.2763 | 14.9638 | 14.5951 | 14.1883 | 13.7183 | 13.257 | 11.2256 | 6.7285 | 4.28 | 1.8622 | 11.7001 | 11.624 | 11.5378 | 11.4335 | 11.2659 | 11.0703 | 10.8358 | 10.4816 | 9.9136 | 9.3456 | 6.8701 | 1.342 | -1.2662 | -2.9279
|  | NEWPORT | SP |  |  | 10.4081 | 10.3378 | 10.2592 | 10.1706 | 10.0532 | 9.9177 | 9.7615 | 9.579 | 9.3565 | 9.0148 | 7.1924 | 2.0934 | -0.91121 | -2.087 | 15.9609 | 15.8296 | 15.6762 | 15.5073 | 15.3014 | 15.0715 | 14.8052 | 14.486 | 14.1362 | 13.7195 | 12.1132 | 7.5166 | 3.5177 | -0.88533 | 11.7122 | 11.6381 | 11.5553 | 11.462 | 11.3346 | 11.1907 | 11.0247 | 10.833 | 10.5499 | 10.0869 | 8.3408 | 3.4193 | 0.53016 | -0.5594
BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY | MINIMUM HEADROOM | SU 93221 52894 | YES | 1.6333 | 0.84036 | -0.20302 | -1.3602 | -3.0717 | -4.8388 | -6.6401 | -8.4499 | -10.4974 | -12.6812 | -19.2407 | -26.8697 | -29.8955 | -32.7786 | 9.9207 | 9.7641 | 9.5445 | 9.1748 | 8.4175 | 7.5346 | 6.5868 | 5.6206 | 4.4607 | 3.2133 | -0.44436 | -4.5076 | -8.9195 | -14.8272 | 5.1317 | 4.597 | 3.7077 | 2.7236 | 1.2551 | -0.29917 | -1.9655 | -3.655 | -5.5957 | -7.6678 | -13.8103 | -20.729 | -23.3299 | -25.8681
|  | NORMANDY | CT |  |  | 2.3985 | 2.014 | 1.4432 | 0.66886 | -0.44074 | -1.5927 | -2.7546 | -3.9082 | -5.1854 | -7.1396 | -13.0224 | -23.1783 | -29.8955 | -32.7786 | 9.9207 | 9.7641 | 9.5445 | 9.2493 | 8.9371 | 8.544 | 7.8076 | 7.0568 | 6.1896 | 4.981 | 1.1899 | -4.5076 | -8.9195 | -13.1304 | 5.2583 | 5.0795 | 4.81 | 4.3865 | 3.5433 | 2.5616 | 1.4701 | 0.36945 | -0.86474 | -2.7307 | -8.2714 | -17.4032 | -23.3299 | -25.8681
|  | NORMANDY | LW |  |  | 1.6333 | 0.84036 | -0.20302 | -1.3602 | -3.0717 | -4.8388 | -6.6401 | -8.4499 | -10.4974 | -12.6812 | -19.2407 | -26.8697 | -29.1607 | -30.5957 | 9.9492 | 9.7892 | 9.5553 | 9.1748 | 8.4175 | 7.5346 | 6.5868 | 5.6206 | 4.4607 | 3.2133 | -0.44436 | -4.3169 | -5.2712 | -5.8617 | 5.1317 | 4.597 | 3.7077 | 2.7236 | 1.2551 | -0.29917 | -1.9655 | -3.655 | -5.5957 | -7.6678 | -13.8103 | -20.729 | -22.7526 | -24.0154
|  | NORMANDY | ST |  |  | 2.6383 | 2.4044 | 2.0652 | 1.6766 | 1.0845 | 0.47175 | -0.15238 | -0.76958 | -1.4652 | -2.2682 | -5.2727 | -12.1472 | -16.3491 | -18.7907 | 10.0437 | 9.9626 | 9.84 | 9.6927 | 9.4962 | 9.2831 | 9.0498 | 8.8047 | 8.3652 | 7.7906 | 5.499 | -0.12622 | -4.0216 | -8.0537 | 5.4157 | 5.3338 | 5.1877 | 5.0095 | 4.7239 | 4.3678 | 3.8484 | 3.3185 | 2.714 | 1.9685 | -0.93863 | -7.5429 | -11.3136 | -13.3965
|  | NORMANDY | SP |  |  | 2.7362 | 2.5423 | 2.2585 | 1.9366 | 1.2369 | 0.53586 | -0.17737 | -0.87496 | -1.6028 | -2.5093 | -5.4981 | -12.2572 | -17.1541 | -19.567 | 10.0515 | 9.9694 | 9.8477 | 9.7043 | 9.5373 | 9.3592 | 9.1689 | 8.8852 | 8.3695 | 7.7427 | 5.489 | -0.32445 | -6.8193 | -14.8272 | 5.429 | 5.3499 | 5.2109 | 5.0443 | 4.834 | 4.4356 | 3.8327 | 3.2343 | 2.6058 | 1.8179 | -0.93646 | -7.4156 | -12.0102 | -14.1672
NURSLING GSP | ROWNHAMS | NORTH BADDESLEY | MINIMUM HEADROOM | SU 38080 20568 | YES | 3.9174 | 3.845 | 3.6731 | 3.453 | 3.1865 | 2.9076 | 2.615 | 2.2869 | 1.8928 | 1.519 | 0.61345 | -0.038326 | -0.3732 | -0.60134 | 3.1934 | 3.1547 | 3.0616 | 2.944 | 2.8088 | 2.6667 | 2.5141 | 2.3415 | 2.1219 | 1.9235 | 1.4896 | 1.1694 | 0.90078 | 0.71722 | 2.9636 | 2.8968 | 2.7499 | 2.5631 | 2.335 | 2.0953 | 1.8418 | 1.5568 | 1.2096 | 0.88402 | 0.11465 | -0.45886 | -0.75179 | -0.95362
|  | NORTH BADDESLEY | CT |  |  | 3.9632 | 3.9176 | 3.7743 | 3.5806 | 3.3603 | 3.1289 | 2.8914 | 2.6149 | 2.2969 | 1.9187 | 1.0132 | 0.17105 | -0.3732 | -0.60134 | 3.2023 | 3.1698 | 3.0839 | 2.9714 | 2.8511 | 2.7246 | 2.5933 | 2.4386 | 2.2579 | 2.0492 | 1.5996 | 1.1851 | 0.90078 | 0.71722 | 3.0028 | 2.9595 | 2.8379 | 2.674 | 2.4869 | 2.2897 | 2.0859 | 1.8474 | 1.5712 | 1.2404 | 0.46888 | -0.27163 | -0.75179 | -0.95362
|  | NORTH BADDESLEY | LW |  |  | 3.9174 | 3.845 | 3.6731 | 3.453 | 3.1865 | 2.9076 | 2.615 | 2.2869 | 1.8928 | 1.519 | 0.61345 | -0.038326 | -0.2731 | -0.4175 | 3.1934 | 3.1547 | 3.0616 | 2.944 | 2.8088 | 2.6667 | 2.5141 | 2.3415 | 2.1219 | 1.9235 | 1.4896 | 1.1694 | 1.0541 | 0.98509 | 2.9636 | 2.8968 | 2.7499 | 2.5631 | 2.335 | 2.0953 | 1.8418 | 1.5568 | 1.2096 | 0.88402 | 0.11465 | -0.45886 | -0.66597 | -0.79306
|  | NORTH BADDESLEY | ST |  |  | 3.9975 | 3.9742 | 3.8855 | 3.7707 | 3.6292 | 3.4838 | 3.3365 | 3.1669 | 2.9817 | 2.7884 | 2.1179 | 1.5698 | 1.2699 | 1.0516 | 3.2283 | 3.2126 | 3.1596 | 3.0911 | 3.0055 | 2.9178 | 2.8285 | 2.7247 | 2.6115 | 2.4977 | 2.0741 | 1.7217 | 1.5325 | 1.3597 | 3.0364 | 3.0148 | 2.9446 | 2.8542 | 2.7384 | 2.619 | 2.4973 | 2.3562 | 2.2022 | 2.0415 | 1.4639 | 0.96869 | 0.70134 | 0.50766
|  | NORTH BADDESLEY | SP |  |  | 4.0046 | 3.9847 | 3.9088 | 3.8095 | 3.6792 | 3.5444 | 3.3999 | 3.2409 | 3.0681 | 2.8816 | 2.2959 | 1.5579 | 1.2377 | 1.0395 | 3.23 | 3.2149 | 3.1687 | 3.1083 | 3.0378 | 2.9636 | 2.88 | 2.7863 | 2.6835 | 2.5753 | 2.2205 | 1.729 | 1.5119 | 1.3229 | 3.0425 | 3.0239 | 2.9657 | 2.8898 | 2.7865 | 2.6788 | 2.5607 | 2.4304 | 2.2888 | 2.1351 | 1.6422 | 0.96371 | 0.67554 | 0.49921
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM | MINIMUM HEADROOM | SU 56427 07430 | YES | 4.3377 | 3.7067 | 3.1271 | 2.7272 | 2.0835 | 1.3959 | 0.63193 | -0.17864 | -1.1998 | -2.1823 | -4.1288 | -6.4822 | -7.8643 | -8.8353 | 4.6773 | 4.3123 | 3.9593 | 3.7189 | 3.3727 | 2.9712 | 2.5129 | 2.0192 | 1.345 | 0.70619 | -0.3894 | -1.6721 | -2.9158 | -3.9644 | 1.6699 | 1.125 | 0.59602 | 0.21507 | -0.38142 | -1.017 | -1.7113 | -2.4476 | -3.3853 | -4.3202 | -6.1228 | -8.263 | -9.4763 | -10.3239
|  | NORTH FAREHAM | CT |  |  | 4.5097 | 3.9853 | 3.5236 | 3.1859 | 2.7557 | 2.2809 | 1.7716 | 1.2129 | 0.59862 | -0.45273 | -2.5631 | -5.6987 | -7.8643 | -8.8353 | 4.7244 | 4.39 | 4.0767 | 3.8493 | 3.56 | 3.2382 | 2.8868 | 2.4943 | 2.0506 | 1.338 | 0.038537 | -1.6721 | -2.9158 | -3.9644 | 1.8173 | 1.3665 | 0.94721 | 0.6419 | 0.24917 | -0.18082 | -0.63815 | -1.169 | -1.7583 | -2.7609 | -4.724 | -7.5378 | -9.4763 | -10.3239
|  | NORTH FAREHAM | LW |  |  | 4.3377 | 3.7067 | 3.1271 | 2.7272 | 2.0835 | 1.3959 | 0.63193 | -0.17864 | -1.1998 | -2.1823 | -4.1288 | -6.4822 | -7.2928 | -7.6021 | 4.6773 | 4.3123 | 3.9593 | 3.7189 | 3.3727 | 2.9712 | 2.5129 | 2.0192 | 1.345 | 0.70619 | -0.3894 | -1.5959 | -1.9293 | -2.0505 | 1.6699 | 1.125 | 0.59602 | 0.21507 | -0.38142 | -1.017 | -1.7113 | -2.4476 | -3.3853 | -4.3202 | -6.1228 | -8.263 | -9.0018 | -9.2734
|  | NORTH FAREHAM | ST |  |  | 4.7649 | 4.4397 | 4.168 | 4.0215 | 3.8271 | 3.6032 | 3.3492 | 3.0724 | 2.7647 | 2.4516 | 0.95418 | -1.4528 | -2.6015 | -3.3778 | 4.8814 | 4.6604 | 4.4537 | 4.3349 | 4.1949 | 4.0357 | 3.8662 | 3.6803 | 3.4379 | 3.1987 | 2.018 | 0.16621 | -0.80464 | -1.8044 | 2.0635 | 1.8012 | 1.5577 | 1.4134 | 1.2259 | 1.0124 | 0.7859 | 0.53995 | 0.26577 | -0.017376 | -1.4559 | -3.7413 | -4.7738 | -5.4509
|  | NORTH FAREHAM | SP |  |  | 4.7907 | 4.4809 | 4.2357 | 4.1176 | 3.9377 | 3.7424 | 3.5343 | 3.2976 | 3.044 | 2.7477 | 1.6302 | -1.302 | -2.5038 | -3.005 | 4.8881 | 4.6705 | 4.4733 | 4.3658 | 4.2432 | 4.1099 | 3.9674 | 3.8057 | 3.634 | 3.4237 | 2.5296 | 0.057728 | -1.4574 | -3.151 | 2.0857 | 1.8366 | 1.6174 | 1.4998 | 1.3295 | 1.147 | 0.9538 | 0.73628 | 0.50816 | 0.23976 | -0.7709 | -3.5997 | -4.7277 | -5.1791
LALEHAM | EAST BEDFONT A | NORTH FELTHAM | MINIMUM HEADROOM | TQ 10987 74875 | YES | 2.2658 | 1.9251 | 1.4934 | 1.0254 | 0.24594 | -0.58248 | -1.4974 | -2.4937 | -3.707 | -5.013 | -8.0753 | -11.5569 | -14.3876 | -16.1481 | 6.4952 | 6.4203 | 6.3252 | 6.1983 | 5.8685 | 5.3831 | 4.8169 | 4.184 | 3.3777 | 2.5143 | 0.63691 | -1.9008 | -4.2606 | -6.961 | 3.7269 | 3.4188 | 3.0075 | 2.5564 | 1.8643 | 1.0989 | 0.23145 | -0.72149 | -1.8839 | -3.1215 | -5.9758 | -9.1402 | -11.433 | -12.8778
|  | NORTH FELTHAM | CT |  |  | 2.4584 | 2.2341 | 1.9689 | 1.5938 | 1.0854 | 0.51599 | -0.12024 | -0.83293 | -1.648 | -2.9625 | -6.2517 | -10.9109 | -14.3876 | -16.1481 | 6.4952 | 6.4203 | 6.3252 | 6.1983 | 6.0609 | 5.6609 | 5.2005 | 4.6775 | 4.0655 | 3.1572 | 0.94673 | -1.9008 | -4.2606 | -6.6218 | 3.8536 | 3.6302 | 3.3632 | 2.9682 | 2.4849 | 1.96 | 1.3715 | 0.70849 | -0.057705 | -1.2725 | -4.3449 | -8.535 | -11.433 | -12.8778
|  | NORTH FELTHAM | LW |  |  | 2.2658 | 1.9251 | 1.4934 | 1.0254 | 0.24594 | -0.58248 | -1.4974 | -2.4937 | -3.707 | -5.013 | -8.0753 | -11.5569 | -13.1043 | -13.9996 | 6.5127 | 6.4437 | 6.3463 | 6.2331 | 5.8685 | 5.3831 | 4.8169 | 4.184 | 3.3777 | 2.5143 | 0.63691 | -1.2431 | -1.9376 | -2.344 | 3.7269 | 3.4188 | 3.0075 | 2.5564 | 1.8643 | 1.0989 | 0.23145 | -0.72149 | -1.8839 | -3.1215 | -5.9758 | -9.1402 | -10.454 | -11.1915
|  | NORTH FELTHAM | ST |  |  | 2.661 | 2.5613 | 2.4347 | 2.2877 | 2.0606 | 1.8013 | 1.4943 | 1.1446 | 0.72064 | 0.26322 | -1.6565 | -5.3735 | -7.2693 | -8.5909 | 6.5491 | 6.507 | 6.4503 | 6.3848 | 6.2995 | 6.1922 | 6.0417 | 5.8675 | 5.5691 | 5.1876 | 3.5756 | 0.49336 | -1.456 | -3.6898 | 4.0607 | 3.9644 | 3.8393 | 3.691 | 3.4626 | 3.2018 | 2.8949 | 2.5424 | 2.1327 | 1.705 | -0.137 | -3.6275 | -5.2788 | -6.424
|  | NORTH FELTHAM | SP |  |  | 2.6938 | 2.5921 | 2.477 | 2.3528 | 2.1531 | 1.9395 | 1.6906 | 1.3987 | 1.08 | 0.68338 | -0.77368 | -4.3486 | -6.3014 | -7.1798 | 6.5504 | 6.5055 | 6.4485 | 6.3854 | 6.3133 | 6.2224 | 6.0949 | 5.9433 | 5.7683 | 5.4377 | 4.048 | 0.54167 | -2.7023 | -6.961 | 4.0873 | 3.9812 | 3.8621 | 3.7331 | 3.5446 | 3.3394 | 3.1058 | 2.8236 | 2.5144 | 2.1397 | 0.76598 | -2.6493 | -4.4238 | -5.1939
COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY | MINIMUM HEADROOM | SP 48645 04403 | YES | 12.7608 | 12.3274 | 11.8053 | 11.2662 | 10.6145 | 9.9107 | 9.0135 | 7.994 | 6.8313 | 5.7464 | 1.7608 | -2.5866 | -3.844 | -5.3566 | 7.3356 | 6.9567 | 6.508 | 6.0413 | 5.5474 | 4.9964 | 4.4029 | 3.7498 | 2.9189 | 1.9818 | -1.1387 | -4.1706 | -6.3883 | -14.1159 | 6.4298 | 6.0158 | 5.5115 | 4.9813 | 4.3077 | 3.5456 | 2.6831 | 1.7189 | 0.47389 | -0.73107 | -4.7039 | -8.8126 | -9.743 | -10.408
|  | NORTH HINKSEY | CT |  |  | 12.7736 | 12.3716 | 11.883 | 11.3683 | 10.8198 | 10.2116 | 9.5518 | 8.8101 | 7.9286 | 6.9043 | 3.5791 | -1.3159 | -3.844 | -5.3566 | 7.3356 | 6.9567 | 6.508 | 6.0413 | 5.5474 | 4.9964 | 4.4029 | 3.7504 | 3.0208 | 2.4028 | 0.037035 | -3.2082 | -6.3883 | -10.384 | 6.4298 | 6.0158 | 5.5207 | 5.0008 | 4.408 | 3.7083 | 2.9494 | 2.1107 | 1.1463 | 0.22634 | -2.8895 | -7.5746 | -9.4555 | -10.408
|  | NORTH HINKSEY | LW |  |  | 12.7608 | 12.3274 | 11.8053 | 11.2662 | 10.6145 | 9.9107 | 9.0135 | 7.994 | 6.8313 | 5.7464 | 1.7608 | -2.5866 | -3.615 | -4.1905 | 7.3615 | 6.9866 | 6.5428 | 6.0878 | 5.5844 | 5.0315 | 4.4225 | 3.7498 | 2.9189 | 1.9818 | -1.1387 | -4.1706 | -4.6768 | -5.0101 | 6.4498 | 6.0198 | 5.5115 | 4.9813 | 4.3077 | 3.5456 | 2.6831 | 1.7189 | 0.47389 | -0.73107 | -4.7039 | -8.8126 | -9.743 | -10.263
|  | NORTH HINKSEY | ST |  |  | 12.8828 | 12.5456 | 12.1349 | 11.728 | 11.2879 | 10.8068 | 10.2881 | 9.7027 | 9.0298 | 8.4858 | 6.2295 | 0.89987 | -1.6528 | -2.308 | 7.4145 | 7.0841 | 6.6971 | 6.3128 | 5.8953 | 5.441 | 4.9416 | 4.3858 | 3.7565 | 3.2653 | 1.5752 | -2.4518 | -4.499 | -8.237 | 6.549 | 6.2085 | 5.8069 | 5.4064 | 4.9694 | 4.4895 | 3.9696 | 3.3854 | 2.6647 | 1.9711 | -0.57227 | -5.7018 | -8.1435 | -8.7553
|  | NORTH HINKSEY | SP |  |  | 12.8948 | 12.5622 | 12.1564 | 11.7581 | 11.3444 | 10.902 | 10.4278 | 9.8986 | 9.3152 | 8.8886 | 7.5172 | 4.2213 | 0.82206 | -0.17934 | 7.4188 | 7.0911 | 6.7032 | 6.3201 | 5.9123 | 5.4709 | 4.984 | 4.4489 | 3.8593 | 3.4162 | 1.9732 | -1.0988 | -6.2861 | -14.1159 | 6.5596 | 6.2278 | 5.8321 | 5.442 | 5.0341 | 4.5971 | 4.1267 | 3.6057 | 3.0246 | 2.5869 | 0.95372 | -2.4959 | -5.7553 | -6.7015
MINETY GSP | CIRENCESTER BSP | NORTHLEACH | MINIMUM HEADROOM | SP 10557 14251 | NO | 2.2643 | 2.049 | 1.81 | 1.5471 | 1.116 | 0.65374 | 0.1599 | -0.38038 | -1.0724 | -1.7481 | -3.2195 | -4.8398 | -6.0865 | -6.8434 | 2.7691 | 2.6339 | 2.481 | 2.3092 | 2.0662 | 1.8056 | 1.5177 | 1.1953 | 0.74431 | 0.31468 | -0.51861 | -1.4916 | -2.4229 | -3.1701 | 0.8677 | 0.65798 | 0.42535 | 0.16954 | -0.23683 | -0.66623 | -1.1275 | -1.6342 | -2.2938 | -2.9348 | -4.3013 | -5.7686 | -6.8486 | -7.5092
|  | NORTHLEACH | CT |  |  | 2.3324 | 2.1812 | 1.9973 | 1.786 | 1.5133 | 1.2243 | 0.92022 | 0.57069 | 0.16964 | -0.522 | -2.1393 | -4.4171 | -6.0865 | -6.8434 | 2.7713 | 2.653 | 2.5085 | 2.341 | 2.1534 | 1.9525 | 1.7345 | 1.4805 | 1.1837 | 0.7213 | -0.28247 | -1.4916 | -2.4229 | -3.1701 | 0.93581 | 0.78917 | 0.61099 | 0.40549 | 0.1407 | -0.14069 | -0.4366 | -0.77647 | -1.166 | -1.8308 | -3.3411 | -5.3813 | -6.8486 | -7.5092
|  | NORTHLEACH | LW |  |  | 2.2643 | 2.049 | 1.81 | 1.5471 | 1.116 | 0.65374 | 0.1599 | -0.38038 | -1.0724 | -1.7481 | -3.2195 | -4.8398 | -5.48 | -5.8194 | 2.7691 | 2.6339 | 2.481 | 2.3092 | 2.0662 | 1.8056 | 1.5177 | 1.1953 | 0.74431 | 0.31468 | -0.51861 | -1.3149 | -1.5802 | -1.7192 | 0.8677 | 0.65798 | 0.42535 | 0.16954 | -0.23683 | -0.66623 | -1.1275 | -1.6342 | -2.2938 | -2.9348 | -4.3013 | -5.7686 | -6.3303 | -6.6246
|  | NORTHLEACH | ST |  |  | 2.4952 | 2.4323 | 2.3536 | 2.257 | 2.1282 | 1.9906 | 1.8345 | 1.6624 | 1.4685 | 1.2591 | 0.25744 | -1.5506 | -2.3548 | -2.954 | 2.89 | 2.8356 | 2.7679 | 2.6846 | 2.5822 | 2.4718 | 2.3445 | 2.2027 | 2.0412 | 1.8812 | 1.0988 | -0.29491 | -0.95478 | -1.6429 | 1.0936 | 1.0328 | 0.95665 | 0.86324 | 0.73854 | 0.60522 | 0.45408 | 0.28727 | 0.099434 | -0.10305 | -1.0756 | -2.809 | -3.5523 | -4.0747
|  | NORTHLEACH | SP |  |  | 2.5068 | 2.4445 | 2.3776 | 2.3058 | 2.1832 | 2.0516 | 1.9223 | 1.7642 | 1.593 | 1.3934 | 0.61891 | -1.4693 | -2.4123 | -2.813 | 2.891 | 2.8328 | 2.7682 | 2.6974 | 2.6086 | 2.5122 | 2.4147 | 2.2927 | 2.1567 | 2.0072 | 1.4035 | -0.28811 | -1.2492 | -2.1219 | 1.105 | 1.0447 | 0.98005 | 0.91039 | 0.79148 | 0.66363 | 0.53784 | 0.38428 | 0.21805 | 0.023811 | -0.72827 | -2.7425 | -3.6267 | -3.9842
BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE | MINIMUM HEADROOM | SU 72207 71092 | YES | 6.1595 | 5.8199 | 5.4115 | 4.9781 | 4.406 | 3.8186 | 3.2201 | 2.575 | 1.8168 | 1.0925 | -0.62588 | -2.0785 | -2.174 | -2.8183 | 5.8308 | 5.6828 | 5.5048 | 5.3207 | 5.0867 | 4.8409 | 4.5802 | 4.281 | 3.8847 | 3.5095 | 2.7948 | 2.1663 | 2.0897 | 1.4667 | 4.163 | 3.8077 | 3.4219 | 3.0291 | 2.5098 | 1.977 | 1.4351 | 0.85304 | 0.17198 | -0.48122 | -2.0576 | -3.3936 | -3.4813 | -4.0639
|  | NORTHUMBERLAND AVENUE | CT |  |  | 6.5053 | 6.3496 | 6.1705 | 5.9554 | 5.6529 | 5.3372 | 4.9968 | 4.6176 | 4.1831 | 3.5882 | 2.2777 | 0.86456 | 0.63586 | 0.52661 | 5.9393 | 5.8519 | 5.7457 | 5.6088 | 5.4468 | 5.2742 | 5.0867 | 4.8689 | 4.6036 | 4.2576 | 3.6824 | 3.0787 | 2.8687 | 2.6508 | 4.5534 | 4.4006 | 4.2274 | 4.0241 | 3.7257 | 3.4156 | 3.0818 | 2.714 | 2.3003 | 1.7418 | 0.54739 | -0.71313 | -0.91947 | -1.0175
|  | NORTHUMBERLAND AVENUE | LW |  |  | 6.1595 | 5.8199 | 5.4115 | 4.9781 | 4.406 | 3.8186 | 3.2201 | 2.575 | 1.8168 | 1.0925 | -0.62588 | -2.0785 | -2.174 | -2.2986 | 5.8308 | 5.6828 | 5.5048 | 5.3207 | 5.0867 | 4.8409 | 4.5802 | 4.281 | 3.8847 | 3.5095 | 2.7948 | 2.1663 | 2.1133 | 2.0591 | 4.163 | 3.8077 | 3.4219 | 3.0291 | 2.5098 | 1.977 | 1.4351 | 0.85304 | 0.17198 | -0.48122 | -2.0576 | -3.3936 | -3.4813 | -3.596
|  | NORTHUMBERLAND AVENUE | ST |  |  | 6.605 | 6.5085 | 6.3971 | 6.2818 | 6.0837 | 5.8798 | 5.6712 | 5.4453 | 5.1966 | 4.9252 | 3.8324 | 2.2305 | 1.3088 | 0.71672 | 6.0067 | 5.9591 | 5.8987 | 5.8344 | 5.7297 | 5.6204 | 5.5057 | 5.3776 | 5.2331 | 5.0866 | 4.4399 | 3.5965 | 3.1671 | 2.7832 | 4.6428 | 4.5429 | 4.4327 | 4.3195 | 4.1243 | 3.9233 | 3.7177 | 3.4966 | 3.2544 | 2.9859 | 1.9675 | 0.50269 | -0.31564 | -0.8373
|  | NORTHUMBERLAND AVENUE | SP |  |  | 6.6534 | 6.5743 | 6.4914 | 6.4042 | 6.1477 | 5.8755 | 5.6141 | 5.3219 | 4.9968 | 4.5701 | 3.1732 | 0.17001 | -1.6235 | -2.8183 | 6.0217 | 5.9745 | 5.9238 | 5.8678 | 5.7567 | 5.6332 | 5.5172 | 5.3877 | 5.2478 | 5.0816 | 4.47 | 2.915 | 2.0897 | 1.4667 | 4.697 | 4.6193 | 4.5384 | 4.4541 | 4.1887 | 3.9053 | 3.63 | 3.3449 | 3.0498 | 2.6609 | 1.3947 | -1.3176 | -2.9655 | -4.0639
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD | MINIMUM HEADROOM | SU 68329 86784 | YES | 13.4812 | 13.275 | 13.0868 | 12.8133 | 12.4597 | 12.0515 | 11.4834 | 10.6036 | 9.5365 | 8.4233 | 4.7435 | 0.55809 | -3.0781 | -5.3941 | 2.5753 | 2.3786 | 2.2137 | 2.0259 | 1.8268 | 1.5967 | 1.3377 | 1.0163 | 0.45491 | -0.13205 | -2.0582 | -5.0615 | -7.8048 | -11.5858 | -0.71944 | -1.0401 | -1.3889 | -1.7703 | -2.3783 | -3.0613 | -3.7828 | -4.5676 | -5.5229 | -6.5256 | -9.8233 | -13.4719 | -16.5012 | -18.4439
|  | NUFFIELD | CT |  |  | 13.4812 | 13.2763 | 13.1037 | 12.8738 | 12.5588 | 12.2007 | 11.8213 | 11.4002 | 10.667 | 9.5716 | 5.9132 | 0.66935 | -3.0781 | -5.3941 | 2.5753 | 2.3786 | 2.2201 | 2.0333 | 1.8455 | 1.6329 | 1.4084 | 1.1574 | 0.7695 | 0.15609 | -1.8945 | -5.0615 | -7.8048 | -10.763 | -0.66102 | -0.89905 | -1.1435 | -1.4943 | -1.9836 | -2.5372 | -3.1243 | -3.7656 | -4.5037 | -5.4849 | -8.7491 | -13.2986 | -16.5012 | -18.4439
|  | NUFFIELD | LW |  |  | 13.49 | 13.275 | 13.0868 | 12.8133 | 12.4597 | 12.0515 | 11.4834 | 10.6036 | 9.5365 | 8.4233 | 4.7435 | 0.55809 | -1.6701 | -3.2044 | 2.5869 | 2.3823 | 2.2137 | 2.0259 | 1.8268 | 1.5967 | 1.3377 | 1.0163 | 0.45491 | -0.13205 | -2.0582 | -4.201 | -5.2294 | -5.9645 | -0.71944 | -1.0401 | -1.3889 | -1.7703 | -2.3783 | -3.0613 | -3.7828 | -4.5676 | -5.5229 | -6.5256 | -9.8233 | -13.4719 | -15.3089 | -16.5661
|  | NUFFIELD | ST |  |  | 13.5531 | 13.3933 | 13.2758 | 13.15 | 12.9826 | 12.7853 | 12.5813 | 12.3424 | 11.9619 | 11.5371 | 9.9131 | 6.1375 | 4.1552 | 2.5221 | 2.6453 | 2.4926 | 2.3878 | 2.2747 | 2.148 | 2.0001 | 1.8424 | 1.655 | 1.403 | 1.1376 | 0.14119 | -2.6027 | -5.0233 | -7.7177 | -0.53321 | -0.68568 | -0.825 | -0.97926 | -1.2321 | -1.5331 | -1.8419 | -2.1965 | -2.6064 | -3.0226 | -4.6312 | -8.1101 | -10.1982 | -11.544
|  | NUFFIELD | SP |  |  | 13.5566 | 13.3989 | 13.2812 | 13.161 | 13.0158 | 12.8446 | 12.6694 | 12.4677 | 12.2112 | 11.9332 | 10.868 | 8.1061 | 5.4728 | 4.5641 | 2.6479 | 2.4979 | 2.3933 | 2.2856 | 2.178 | 2.0527 | 1.9209 | 1.7675 | 1.5658 | 1.3609 | 0.39529 | -2.3544 | -6.1317 | -11.5858 | -0.52654 | -0.67715 | -0.82889 | -0.98282 | -1.1861 | -1.4253 | -1.6788 | -1.9728 | -2.3006 | -2.6501 | -3.9021 | -6.4386 | -8.4591 | -9.5038
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE | MINIMUM HEADROOM | SU 63496 53664 | YES | 9.7713 | 9.5911 | 9.401 | 9.2026 | 8.9413 | 8.6735 | 8.3839 | 8.0405 | 7.6627 | 7.3757 | 6.7123 | 5.9716 | 5.7793 | 5.6668 | 12.3067 | 12.2153 | 12.1165 | 12.011 | 11.8769 | 11.7387 | 11.5819 | 11.3824 | 11.1584 | 10.9995 | 10.6902 | 10.3346 | 10.2408 | 10.0944 | 11.1136 | 10.949 | 10.7746 | 10.5921 | 10.3529 | 10.1076 | 9.8404 | 9.5198 | 9.1658 | 8.9002 | 8.303 | 7.6344 | 7.4679 | 7.3741
|  | OAKRIDGE | CT |  |  | 9.9207 | 9.8235 | 9.7191 | 9.6003 | 9.4417 | 9.2763 | 9.0869 | 8.8687 | 8.6404 | 8.3565 | 7.8443 | 6.9677 | 6.423 | 6.197 | 12.3513 | 12.2871 | 12.217 | 12.1347 | 12.0397 | 11.9394 | 11.8214 | 11.6801 | 11.5293 | 11.3473 | 11.077 | 10.6227 | 10.3151 | 10.0944 | 11.2427 | 11.1508 | 11.0521 | 10.9388 | 10.7912 | 10.637 | 10.4595 | 10.2535 | 10.0373 | 9.7689 | 9.3036 | 8.5163 | 8.0315 | 7.8297
|  | OAKRIDGE | LW |  |  | 9.7713 | 9.5911 | 9.401 | 9.2026 | 8.9413 | 8.6735 | 8.3839 | 8.0405 | 7.6627 | 7.3757 | 6.7123 | 5.9716 | 5.7793 | 5.6668 | 12.3067 | 12.2153 | 12.1165 | 12.011 | 11.8769 | 11.7387 | 11.5819 | 11.3824 | 11.1584 | 10.9995 | 10.6902 | 10.3346 | 10.2408 | 10.1882 | 11.1136 | 10.949 | 10.7746 | 10.5921 | 10.3529 | 10.1076 | 9.8404 | 9.5198 | 9.1658 | 8.9002 | 8.303 | 7.6344 | 7.4679 | 7.3741
|  | OAKRIDGE | ST |  |  | 10.0086 | 9.9655 | 9.9145 | 9.8529 | 9.7613 | 9.6665 | 9.5702 | 9.4564 | 9.3321 | 9.2006 | 8.6061 | 7.9521 | 7.5858 | 7.3509 | 12.4084 | 12.3796 | 12.3442 | 12.2997 | 12.2428 | 12.1832 | 12.1213 | 12.045 | 11.9603 | 11.8781 | 11.4702 | 11.0375 | 10.7834 | 10.5568 | 11.3264 | 11.2862 | 11.2381 | 11.1796 | 11.0943 | 11.0059 | 10.9159 | 10.8085 | 10.6911 | 10.5681 | 10.0009 | 9.3922 | 9.0608 | 8.8506
|  | OAKRIDGE | SP |  |  | 10.0363 | 10.0028 | 9.9686 | 9.9292 | 9.8481 | 9.7698 | 9.6935 | 9.5997 | 9.5044 | 9.366 | 8.8591 | 7.7028 | 7.0746 | 6.6702 | 12.4188 | 12.3922 | 12.3644 | 12.3314 | 12.2839 | 12.2376 | 12.1905 | 12.1308 | 12.0689 | 11.9912 | 11.682 | 10.9456 | 10.6051 | 10.368 | 11.3509 | 11.3189 | 11.2863 | 11.2484 | 11.1737 | 11.1018 | 11.0313 | 10.944 | 10.8551 | 10.728 | 10.2555 | 9.1729 | 8.6068 | 8.2469
COWLEY GSP | HEADINGTON BSP | OLD ROAD | MINIMUM HEADROOM | SP 55274 06426 | NO | 18.943 | 18.5788 | 18.1133 | 17.6094 | 16.8414 | 16.0713 | 15.2474 | 14.4322 | 13.4675 | 12.4372 | 9.4297 | 5.9749 | 3.4694 | 2.1926 | 21.8884 | 21.6659 | 21.371 | 21.0521 | 20.6251 | 20.1865 | 19.7029 | 19.2125 | 18.6035 | 17.9476 | 16.0578 | 13.7931 | 11.9428 | 10.3294 | 19.7633 | 19.4557 | 19.0703 | 18.6533 | 17.9837 | 17.3102 | 16.5956 | 15.8862 | 15.0634 | 14.1737 | 11.3786 | 8.1823 | 5.8944 | 4.6986
|  | OLD ROAD | CT |  |  | 19.048 | 18.7541 | 18.4096 | 17.9468 | 17.3697 | 16.8035 | 16.2182 | 15.6498 | 15.0011 | 13.9815 | 10.9294 | 6.3579 | 3.4694 | 2.1926 | 21.9065 | 21.6981 | 21.4566 | 21.1249 | 20.7588 | 20.3894 | 19.9972 | 19.6011 | 19.1365 | 18.4796 | 16.5021 | 13.7931 | 11.9428 | 10.3294 | 19.8718 | 19.6336 | 19.3537 | 18.9847 | 18.501 | 18.0242 | 17.5347 | 17.0577 | 16.5217 | 15.6144 | 12.7519 | 8.5884 | 5.8944 | 4.6986
|  | OLD ROAD | LW |  |  | 18.943 | 18.5788 | 18.1133 | 17.6094 | 16.8414 | 16.0713 | 15.2474 | 14.4322 | 13.4675 | 12.4372 | 9.4297 | 5.9749 | 4.7276 | 4.2968 | 21.8884 | 21.6659 | 21.371 | 21.0521 | 20.6251 | 20.1865 | 19.7029 | 19.2125 | 18.6035 | 17.9476 | 16.0578 | 14.0919 | 13.5303 | 13.3293 | 19.7633 | 19.4557 | 19.0703 | 18.6533 | 17.9837 | 17.3102 | 16.5956 | 15.8862 | 15.0634 | 14.1737 | 11.3786 | 8.1823 | 7.0774 | 6.7013
|  | OLD ROAD | ST |  |  | 19.3069 | 19.1496 | 18.9671 | 18.7671 | 18.5081 | 18.2646 | 18.0077 | 17.7652 | 17.4863 | 17.185 | 15.9493 | 12.7616 | 11.1163 | 10.0202 | 22.0859 | 21.9661 | 21.8286 | 21.6777 | 21.4849 | 21.2965 | 21.0942 | 20.8914 | 20.6556 | 20.412 | 19.3902 | 16.831 | 15.3296 | 13.7808 | 20.0835 | 19.9617 | 19.8202 | 19.6668 | 19.4704 | 19.2818 | 19.0826 | 18.8909 | 18.6707 | 18.4202 | 17.4173 | 14.3845 | 12.8905 | 11.9273
|  | OLD ROAD | SP |  |  | 19.3339 | 19.166 | 18.9849 | 18.7919 | 18.5845 | 18.391 | 18.1886 | 18.0025 | 17.8 | 17.5627 | 16.6807 | 14.2547 | 12.6426 | 12.1209 | 22.0971 | 21.9637 | 21.819 | 21.6639 | 21.5117 | 21.3612 | 21.2005 | 21.0406 | 20.8636 | 20.6442 | 19.7993 | 17.4068 | 15.0354 | 12.3983 | 20.1073 | 19.9806 | 19.8429 | 19.6981 | 19.5405 | 19.3903 | 19.2329 | 19.0847 | 18.9231 | 18.7272 | 18.0148 | 15.7981 | 14.2508 | 13.7739
COWLEY GSP | OXFORD (OSNEY) BSP | OSNEY | MINIMUM HEADROOM | SP 50148 05901 | YES | 12.3062 | 11.7419 | 11.1491 | 10.4984 | 9.6376 | 8.8424 | 8.1309 | 7.378 | 6.5278 | 5.5557 | 2.8783 | -0.8718 | -4.4617 | -7.0131 | 15.4393 | 15.0505 | 14.6697 | 14.2496 | 13.7654 | 13.2906 | 12.8796 | 12.4446 | 11.9265 | 11.3063 | 9.6491 | 6.7318 | 3.8566 | 0.73138 | 13.9249 | 13.4763 | 13.0629 | 12.6052 | 12.0214 | 11.4464 | 10.9185 | 10.3357 | 9.6501 | 8.7394 | 6.2265 | 2.9489 | 0.0065077 | -2.1228
|  | OSNEY | CT |  |  | 12.4417 | 11.9608 | 11.4652 | 10.8825 | 10.2065 | 9.6046 | 9.1166 | 8.6006 | 8.0147 | 7.0626 | 4.3323 | -0.45455 | -4.4617 | -7.0131 | 15.4393 | 15.0727 | 14.704 | 14.2691 | 13.8206 | 13.384 | 13.0221 | 12.6398 | 12.1928 | 11.5434 | 9.662 | 6.7318 | 3.8566 | 0.73138 | 14.0244 | 13.6336 | 13.2823 | 12.8779 | 12.4234 | 11.9824 | 11.6572 | 11.3241 | 10.9174 | 10.0361 | 7.4815 | 3.3901 | 0.0065077 | -2.1228
|  | OSNEY | LW |  |  | 12.3062 | 11.7419 | 11.1491 | 10.4984 | 9.6376 | 8.8424 | 8.1309 | 7.378 | 6.5278 | 5.5557 | 2.8783 | -0.8718 | -3.2648 | -5.0957 | 15.4398 | 15.0505 | 14.6697 | 14.2496 | 13.7654 | 13.2906 | 12.8796 | 12.4446 | 11.9265 | 11.3063 | 9.6491 | 7.6762 | 6.5639 | 5.6778 | 13.9249 | 13.4763 | 13.0629 | 12.6052 | 12.0214 | 11.4464 | 10.9185 | 10.3357 | 9.6501 | 8.7394 | 6.2265 | 2.9489 | 1.0035 | -0.48318
|  | OSNEY | ST |  |  | 12.588 | 12.235 | 11.9093 | 11.5506 | 11.1655 | 10.8196 | 10.5541 | 10.2789 | 9.9449 | 9.5349 | 8.3287 | 5.0833 | 2.8016 | 1.064 | 15.4723 | 15.1382 | 14.8905 | 14.6157 | 14.3638 | 14.0535 | 13.8062 | 13.5486 | 13.235 | 12.8671 | 11.7925 | 8.9695 | 6.6366 | 3.8773 | 14.1023 | 13.7816 | 13.5256 | 13.2428 | 12.9742 | 12.6933 | 12.5042 | 12.3167 | 12.0805 | 11.7472 | 10.9754 | 8.1001 | 6.1686 | 4.7717
|  | OSNEY | SP |  |  | 12.6066 | 12.2592 | 11.9462 | 11.6111 | 11.248 | 10.907 | 10.6575 | 10.3871 | 10.0828 | 9.6807 | 8.616 | 5.9608 | 3.6628 | 2.2464 | 15.4721 | 15.1356 | 14.8864 | 14.6114 | 14.3761 | 14.0689 | 13.828 | 13.5675 | 13.261 | 12.8673 | 11.7632 | 8.9364 | 5.4708 | 0.81158 | 14.1143 | 13.8012 | 13.5553 | 13.2875 | 13.0199 | 12.7307 | 12.5407 | 12.3473 | 12.1199 | 11.7949 | 11.103 | 8.9906 | 6.9448 | 5.7928
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON | MINIMUM HEADROOM | SU 52061 50913 | YES | 9.9508 | 9.8242 | 9.6761 | 9.5012 | 9.2354 | 8.8052 | 8.0046 | 7.1178 | 6.1062 | 5.2105 | 2.5044 | -1.0035 | -2.9618 | -4.5285 | 17.063 | 16.9284 | 16.7701 | 16.5872 | 16.2826 | 15.9043 | 15.5022 | 15.0523 | 14.5049 | 13.9926 | 12.023 | 8.058 | 2.6382 | -7.9196 | 11.2101 | 11.09 | 10.9492 | 10.7826 | 10.5362 | 10.2008 | 9.7324 | 8.9467 | 8.0409 | 7.2251 | 4.731 | 1.2963 | -0.14247 | -1.5043
|  | OVERTON | CT |  |  | 9.9508 | 9.8242 | 9.6761 | 9.5012 | 9.2394 | 8.9006 | 8.5372 | 8.1339 | 7.4307 | 6.6204 | 4.218 | -0.1394 | -2.9618 | -4.5285 | 17.0682 | 16.9285 | 16.7701 | 16.5872 | 16.2826 | 15.9043 | 15.5022 | 15.0523 | 14.5353 | 14.0005 | 12.023 | 8.058 | 3.9877 | -1.5472 | 11.2101 | 11.09 | 10.9492 | 10.7826 | 10.5403 | 10.2305 | 9.8967 | 9.5266 | 9.0753 | 8.4872 | 6.2874 | 2.3392 | -0.14247 | -1.5043
|  | OVERTON | LW |  |  | 9.975 | 9.8383 | 9.6895 | 9.5106 | 9.2354 | 8.8052 | 8.0046 | 7.1178 | 6.1062 | 5.2105 | 2.5044 | -1.0035 | -2.4636 | -3.4384 | 17.063 | 16.9284 | 16.7836 | 16.618 | 16.3132 | 15.9319 | 15.5175 | 15.0564 | 14.5049 | 13.9926 | 12.0944 | 9.2502 | 8.71 | 8.3402 | 11.2332 | 11.1034 | 10.9618 | 10.7913 | 10.5362 | 10.2008 | 9.7324 | 8.9467 | 8.0409 | 7.2251 | 4.731 | 1.2963 | 0.26258 | -0.57468
|  | OVERTON | ST |  |  | 10.065 | 10.0057 | 9.9398 | 9.8629 | 9.6935 | 9.4493 | 9.1851 | 8.8838 | 8.5064 | 8.1511 | 6.8428 | 1.4209 | -1.3652 | -2.0731 | 17.1743 | 17.0926 | 17.0031 | 16.9008 | 16.7239 | 16.4941 | 16.2399 | 15.9508 | 15.5982 | 15.2584 | 13.9286 | 9.9661 | 5.8092 | 0.37304 | 11.3202 | 11.2646 | 11.2029 | 11.1305 | 10.9768 | 10.7578 | 10.5192 | 10.247 | 9.9017 | 9.5704 | 8.3343 | 3.6703 | 1.008 | 0.34967
|  | OVERTON | SP |  |  | 10.0748 | 10.0246 | 9.9673 | 9.9029 | 9.7632 | 9.5591 | 9.3411 | 9.0941 | 8.8084 | 8.5748 | 7.8408 | 4.9121 | 1.2719 | 0.15126 | 17.1794 | 17.0995 | 17.0063 | 16.9022 | 16.7213 | 16.4892 | 16.231 | 15.94 | 15.6044 | 15.2765 | 13.7463 | 9.4444 | 2.6382 | -7.9196 | 11.3294 | 11.2824 | 11.2286 | 11.1682 | 11.0431 | 10.8629 | 10.6688 | 10.4484 | 10.1908 | 9.9751 | 9.2855 | 7.0432 | 3.5574 | 2.5017
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH | MINIMUM HEADROOM | SU 62243 66052 | YES | 14.7414 | 14.5053 | 14.2605 | 14.0038 | 13.6036 | 13.1878 | 12.7533 | 12.2832 | 11.7424 | 11.1944 | 9.8392 | 8.1793 | 7.6309 | 7.0024 | 20.5559 | 20.5241 | 20.487 | 20.4473 | 20.4056 | 20.3595 | 20.2971 | 20.2252 | 20.1317 | 20.0287 | 19.7793 | 19.5113 | 19.4703 | 19.4197 | 15.5073 | 15.3129 | 15.107 | 14.8875 | 14.5657 | 14.2278 | 13.8659 | 13.4637 | 12.9727 | 12.4868 | 11.4253 | 10.0724 | 9.6539 | 9.1922
|  | PADWORTH | CT |  |  | 14.9464 | 14.8209 | 14.6783 | 14.5264 | 14.2894 | 14.043 | 13.7887 | 13.5037 | 13.1883 | 12.6816 | 11.4261 | 9.2041 | 7.6309 | 7.0024 | 20.5559 | 20.5241 | 20.487 | 20.4473 | 20.4056 | 20.3602 | 20.31 | 20.2522 | 20.1872 | 20.0964 | 19.8834 | 19.5965 | 19.4976 | 19.4197 | 15.6376 | 15.519 | 15.3801 | 15.2293 | 15.0231 | 14.8074 | 14.5801 | 14.317 | 14.015 | 13.5517 | 12.5186 | 10.9185 | 9.6827 | 9.1922
|  | PADWORTH | LW |  |  | 14.7414 | 14.5053 | 14.2605 | 14.0038 | 13.6036 | 13.1878 | 12.7533 | 12.2832 | 11.7424 | 11.1944 | 9.8392 | 8.1793 | 7.6595 | 7.4164 | 20.5619 | 20.529 | 20.496 | 20.4572 | 20.4119 | 20.3595 | 20.2971 | 20.2252 | 20.1317 | 20.0287 | 19.7793 | 19.5113 | 19.4703 | 19.4483 | 15.5073 | 15.3129 | 15.107 | 14.8875 | 14.5657 | 14.2278 | 13.8659 | 13.4637 | 12.9727 | 12.4868 | 11.4253 | 10.0724 | 9.6539 | 9.4627
|  | PADWORTH | ST |  |  | 15.036 | 14.9679 | 14.891 | 14.8068 | 14.6883 | 14.5622 | 14.4303 | 14.2867 | 14.1296 | 13.9468 | 13.2045 | 11.8619 | 11.0724 | 10.5194 | 20.5833 | 20.5687 | 20.552 | 20.5338 | 20.5114 | 20.4874 | 20.4589 | 20.4258 | 20.3872 | 20.3394 | 20.1362 | 19.7144 | 19.537 | 19.4539 | 15.7325 | 15.6734 | 15.6035 | 15.5241 | 15.419 | 15.305 | 15.1836 | 15.0493 | 14.8994 | 14.7362 | 14.0101 | 12.8305 | 12.2763 | 11.9186
|  | PADWORTH | SP |  |  | 15.0613 | 15.0048 | 14.9474 | 14.8892 | 14.7321 | 14.573 | 14.4138 | 14.2369 | 14.0589 | 13.8331 | 13.0659 | 11.3098 | 10.3075 | 9.7522 | 20.5839 | 20.5689 | 20.5541 | 20.5395 | 20.5213 | 20.5027 | 20.4831 | 20.4574 | 20.4304 | 20.3968 | 20.27 | 19.8783 | 19.5959 | 19.4778 | 15.7508 | 15.6977 | 15.6435 | 15.5879 | 15.463 | 15.3363 | 15.2101 | 15.0621 | 14.9107 | 14.7243 | 14.0572 | 12.4502 | 11.6459 | 11.2468
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE | MINIMUM HEADROOM | SU 62960 76144 | YES | 3.9317 | 3.8332 | 3.7313 | 3.6257 | 3.4786 | 3.327 | 3.1701 | 2.9966 | 2.8089 | 2.6243 | 2.169 | 1.657 | 1.5561 | 1.5122 | 5.3453 | 5.2993 | 5.2503 | 5.198 | 5.1286 | 5.0563 | 4.9782 | 4.8864 | 4.7788 | 4.675 | 4.4581 | 4.2146 | 4.1699 | 4.1423 | 4.5198 | 4.44 | 4.3562 | 4.2684 | 4.1485 | 4.0245 | 3.8939 | 3.7451 | 3.5776 | 3.4126 | 2.9935 | 2.5235 | 2.433 | 2.3945
|  | PANGBOURNE | CT |  |  | 4.0299 | 3.9824 | 3.929 | 3.8727 | 3.7872 | 3.6989 | 3.609 | 3.5072 | 3.3987 | 3.2368 | 2.8647 | 2.241 | 1.9545 | 1.8833 | 5.3743 | 5.3441 | 5.3085 | 5.2699 | 5.2217 | 5.1714 | 5.1173 | 5.0532 | 4.9824 | 4.8806 | 4.6838 | 4.3847 | 4.2341 | 4.1423 | 4.5885 | 4.5456 | 4.4961 | 4.4431 | 4.3695 | 4.2931 | 4.2135 | 4.1209 | 4.0203 | 3.8706 | 3.5612 | 3.0589 | 2.8007 | 2.7369
|  | PANGBOURNE | LW |  |  | 3.9317 | 3.8332 | 3.7313 | 3.6257 | 3.4786 | 3.327 | 3.1701 | 2.9966 | 2.8089 | 2.6243 | 2.169 | 1.657 | 1.5561 | 1.5122 | 5.3453 | 5.2993 | 5.2503 | 5.198 | 5.1286 | 5.0563 | 4.9782 | 4.8864 | 4.7788 | 4.675 | 4.4581 | 4.2146 | 4.1699 | 4.1503 | 4.5198 | 4.44 | 4.3562 | 4.2684 | 4.1485 | 4.0245 | 3.8939 | 3.7451 | 3.5776 | 3.4126 | 2.9935 | 2.5235 | 2.433 | 2.3945
|  | PANGBOURNE | ST |  |  | 4.0629 | 4.0361 | 4.0061 | 3.9752 | 3.9254 | 3.874 | 3.8203 | 3.7629 | 3.7014 | 3.6341 | 3.3591 | 2.9176 | 2.6688 | 2.511 | 5.398 | 5.3822 | 5.363 | 5.3427 | 5.3141 | 5.284 | 5.2511 | 5.2149 | 5.1738 | 5.1332 | 4.9453 | 4.6555 | 4.5043 | 4.3828 | 4.6214 | 4.5988 | 4.5723 | 4.5446 | 4.5019 | 4.4576 | 4.4104 | 4.3592 | 4.3029 | 4.2437 | 3.9835 | 3.5904 | 3.3947 | 3.2774
|  | PANGBOURNE | SP |  |  | 4.0751 | 4.0546 | 4.035 | 4.012 | 3.951 | 3.8895 | 3.8288 | 3.7612 | 3.6932 | 3.6043 | 3.3071 | 2.6347 | 2.2258 | 1.9799 | 5.4021 | 5.3876 | 5.3733 | 5.3557 | 5.3259 | 5.2955 | 5.2643 | 5.2277 | 5.1902 | 5.1448 | 4.9805 | 4.5702 | 4.3482 | 4.2153 | 4.6305 | 4.6119 | 4.5944 | 4.573 | 4.524 | 4.4748 | 4.4255 | 4.3693 | 4.3126 | 4.2395 | 3.9861 | 3.3898 | 3.0425 | 2.8287
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE | MINIMUM HEADROOM | SU 51369 08259 | NO | 18.0549 | 17.7106 | 17.3413 | 16.944 | 16.3725 | 15.778 | 15.1385 | 14.4368 | 13.6167 | 12.8808 | 11.1007 | 8.8636 | 8.1616 | 7.8271 | 23.7969 | 23.6071 | 23.4083 | 23.196 | 22.9091 | 22.6057 | 22.2635 | 21.8753 | 21.3898 | 20.9764 | 20.097 | 19.0617 | 18.4743 | 17.8461 | 19.4559 | 19.1183 | 18.7689 | 18.4032 | 17.882 | 17.3385 | 16.7496 | 16.0999 | 15.3319 | 14.6491 | 13.0321 | 11.0818 | 10.5073 | 10.236
|  | PARK GATE | CT |  |  | 18.3064 | 18.1023 | 17.8676 | 17.6299 | 17.3022 | 16.9555 | 16.5753 | 16.136 | 15.6588 | 14.9615 | 13.3798 | 10.6076 | 8.6791 | 7.9552 | 23.8776 | 23.7349 | 23.5676 | 23.3962 | 23.1913 | 22.9715 | 22.7213 | 22.4381 | 22.1217 | 21.6931 | 20.822 | 19.4333 | 18.4743 | 17.8461 | 19.705 | 19.5059 | 19.2772 | 19.0454 | 18.7244 | 18.3849 | 18.0131 | 17.5999 | 17.1492 | 16.4955 | 15.047 | 12.5657 | 10.9566 | 10.3792
|  | PARK GATE | LW |  |  | 18.0549 | 17.7106 | 17.3413 | 16.944 | 16.3725 | 15.778 | 15.1385 | 14.4368 | 13.6167 | 12.8808 | 11.1007 | 8.8636 | 8.1616 | 7.8271 | 23.7969 | 23.6071 | 23.4083 | 23.196 | 22.9091 | 22.6057 | 22.2635 | 21.8753 | 21.3898 | 20.9764 | 20.097 | 19.0617 | 18.7686 | 18.6268 | 19.4559 | 19.1183 | 18.7689 | 18.4032 | 17.882 | 17.3385 | 16.7496 | 16.0999 | 15.3319 | 14.6491 | 13.0321 | 11.0818 | 10.5073 | 10.236
|  | PARK GATE | ST |  |  | 18.4701 | 18.3719 | 18.2497 | 18.1143 | 17.9343 | 17.7395 | 17.5357 | 17.3098 | 17.0539 | 16.7808 | 15.5376 | 13.674 | 12.621 | 11.9015 | 23.9953 | 23.9278 | 23.8405 | 23.7415 | 23.6224 | 23.4912 | 23.3498 | 23.19 | 23.0053 | 22.823 | 21.9597 | 20.7006 | 19.9825 | 19.3276 | 19.8644 | 19.7683 | 19.6491 | 19.5172 | 19.3411 | 19.1508 | 18.9515 | 18.7308 | 18.4809 | 18.2142 | 17.0298 | 15.2896 | 14.3438 | 13.7093
|  | PARK GATE | SP |  |  | 18.5023 | 18.4191 | 18.3338 | 18.2367 | 18.0126 | 17.7903 | 17.5612 | 17.2997 | 17.0159 | 16.6647 | 15.4344 | 12.6569 | 11.136 | 10.2386 | 24.0063 | 23.9421 | 23.874 | 23.7945 | 23.6659 | 23.5361 | 23.4005 | 23.24 | 23.0717 | 22.8768 | 22.144 | 20.3567 | 19.3942 | 18.7045 | 19.8961 | 19.8149 | 19.7318 | 19.6373 | 19.4174 | 19.1992 | 18.9743 | 18.7229 | 18.4626 | 18.1413 | 17.0038 | 14.4114 | 13.0265 | 12.2284
MELKSHAM GSP | AMESBURY | PARK HOUSE | MINIMUM HEADROOM | SU 23138 43780 | YES | 14.8086 | 14.4284 | 14.0088 | 13.5396 | 12.7576 | 11.9292 | 10.9541 | 9.8586 | 8.4898 | 7.1544 | 4.2698 | 0.82423 | -1.6305 | -3.2406 | 19.0151 | 18.7823 | 18.5258 | 18.2137 | 17.7665 | 17.286 | 16.7064 | 16.0437 | 15.1435 | 14.2797 | 12.6353 | 10.4451 | 8.4893 | 6.7022 | 16.6786 | 16.3254 | 15.9434 | 15.525 | 14.8137 | 14.0613 | 13.1578 | 12.1408 | 10.8477 | 9.5906 | 6.9608 | 3.8577 | 1.7742 | 0.41032
|  | PARK HOUSE | CT |  |  | 14.9487 | 14.6586 | 14.3278 | 13.9261 | 13.3991 | 12.8352 | 12.1817 | 11.4149 | 10.513 | 9.1015 | 5.9406 | 1.4605 | -1.6305 | -3.2406 | 19.0323 | 18.8254 | 18.5788 | 18.2605 | 17.9031 | 17.5172 | 17.066 | 16.5324 | 15.8906 | 14.9466 | 13.001 | 10.4451 | 8.4893 | 6.7022 | 16.7965 | 16.5383 | 16.2473 | 15.8919 | 15.394 | 14.8608 | 14.2491 | 13.5307 | 12.6796 | 11.3514 | 8.4613 | 4.4679 | 1.7742 | 0.41032
|  | PARK HOUSE | LW |  |  | 14.8086 | 14.4284 | 14.0088 | 13.5396 | 12.7576 | 11.9292 | 10.9541 | 9.8586 | 8.4898 | 7.1544 | 4.2698 | 0.82423 | -0.66456 | -1.4208 | 19.0151 | 18.7823 | 18.5258 | 18.2137 | 17.7665 | 17.286 | 16.7064 | 16.0437 | 15.1435 | 14.2797 | 12.6353 | 10.8109 | 10.1425 | 9.7828 | 16.6786 | 16.3254 | 15.9434 | 15.525 | 14.8137 | 14.0613 | 13.1578 | 12.1408 | 10.8477 | 9.5906 | 6.9608 | 3.8577 | 2.5758 | 1.9437
|  | PARK HOUSE | ST |  |  | 15.2225 | 15.1101 | 14.9792 | 14.8089 | 14.5913 | 14.3466 | 14.0272 | 13.6546 | 13.2286 | 12.7867 | 10.6553 | 7.2645 | 5.5399 | 4.2883 | 19.2222 | 19.1259 | 19.0105 | 18.8694 | 18.7065 | 18.5128 | 18.2599 | 17.966 | 17.625 | 17.2872 | 15.6171 | 12.9528 | 11.4181 | 9.7532 | 17.0495 | 16.9568 | 16.8324 | 16.6786 | 16.4882 | 16.2745 | 16.002 | 15.6592 | 15.2595 | 14.8494 | 12.8327 | 9.6554 | 8.1378 | 7.0724
|  | PARK HOUSE | SP |  |  | 15.2522 | 15.1459 | 15.0399 | 14.9162 | 14.7371 | 14.5533 | 14.321 | 14.0231 | 13.6872 | 13.3088 | 11.8116 | 8.1004 | 6.4695 | 5.6975 | 19.2308 | 19.1319 | 19.0262 | 18.9095 | 18.7763 | 18.635 | 18.4532 | 18.2139 | 17.9425 | 17.6241 | 16.339 | 12.9597 | 10.5438 | 7.5721 | 17.0765 | 16.9887 | 16.887 | 16.7763 | 16.6188 | 16.458 | 16.2618 | 16.0108 | 15.7083 | 15.3589 | 13.965 | 10.4074 | 8.9012 | 8.2351
MINETY GSP | STRATTON (2 X 90) | PARK NORTH | MINIMUM HEADROOM | SU 18052 84542 | YES | 0.45908 | 0.36367 | 0.2606 | 0.15237 | 0.0082932 | -0.14012 | -0.29275 | -0.45493 | -0.67673 | -0.86759 | -1.2421 | -1.6316 | -1.7095 | -1.7463 | 2.6432 | 2.5961 | 2.5438 | 2.4878 | 2.4151 | 2.3394 | 2.2591 | 2.1728 | 2.0471 | 1.9349 | 1.7418 | 1.5401 | 1.504 | 1.4848 | 2.1752 | 2.0873 | 1.9932 | 1.8938 | 1.7609 | 1.6242 | 1.4842 | 1.3355 | 1.1309 | 0.95071 | 0.60822 | 0.25235 | 0.18187 | 0.14951
|  | PARK NORTH | CT |  |  | 0.54231 | 0.49377 | 0.43807 | 0.36959 | 0.27983 | 0.18506 | 0.086177 | -0.025828 | -0.16441 | -0.33195 | -0.65744 | -1.0836 | -1.3056 | -1.3972 | 2.6732 | 2.644 | 2.6097 | 2.5661 | 2.5149 | 2.4602 | 2.4026 | 2.336 | 2.2494 | 2.1371 | 1.9434 | 1.7118 | 1.5825 | 1.4848 | 2.253 | 2.2075 | 2.1548 | 2.0895 | 2.0057 | 1.9171 | 1.8245 | 1.719 | 1.5871 | 1.4271 | 1.1246 | 0.73943 | 0.5439 | 0.46466
|  | PARK NORTH | LW |  |  | 0.45908 | 0.36367 | 0.2606 | 0.15237 | 0.0082932 | -0.14012 | -0.29275 | -0.45493 | -0.67673 | -0.86759 | -1.2421 | -1.6316 | -1.7095 | -1.7463 | 2.6432 | 2.5961 | 2.5438 | 2.4878 | 2.4151 | 2.3394 | 2.2591 | 2.1728 | 2.0471 | 1.9349 | 1.7418 | 1.5401 | 1.504 | 1.4871 | 2.1752 | 2.0873 | 1.9932 | 1.8938 | 1.7609 | 1.6242 | 1.4842 | 1.3355 | 1.1309 | 0.95071 | 0.60822 | 0.25235 | 0.18187 | 0.14951
|  | PARK NORTH | ST |  |  | 0.58895 | 0.56961 | 0.54497 | 0.51434 | 0.46746 | 0.4181 | 0.36466 | 0.30708 | 0.24098 | 0.1683 | -0.14883 | -0.5668 | -0.74529 | -0.83886 | 2.6998 | 2.6874 | 2.6712 | 2.6505 | 2.6227 | 2.5931 | 2.5601 | 2.524 | 2.4823 | 2.4389 | 2.2343 | 1.9434 | 1.8192 | 1.7211 | 2.2969 | 2.279 | 2.2557 | 2.2265 | 2.1827 | 2.1365 | 2.0862 | 2.0318 | 1.9693 | 1.9011 | 1.5983 | 1.2035 | 1.0434 | 0.96247
|  | PARK NORTH | SP |  |  | 0.60562 | 0.59 | 0.57189 | 0.55183 | 0.518 | 0.48008 | 0.4451 | 0.40276 | 0.35617 | 0.28449 | 0.028168 | -0.63734 | -1 | -1.2033 | 2.7073 | 2.6956 | 2.6817 | 2.6662 | 2.6457 | 2.6222 | 2.6004 | 2.5732 | 2.5424 | 2.5015 | 2.3475 | 1.9095 | 1.6828 | 1.5197 | 2.312 | 2.2971 | 2.2796 | 2.2603 | 2.2287 | 2.1932 | 2.1605 | 2.1206 | 2.0764 | 2.01 | 1.77 | 1.1416 | 0.81233 | 0.63253
WILLESDEN GSP | ACTON LANE | PARK ROYAL | MINIMUM HEADROOM | TQ 20137 82215 | YES | 11.9052 | 11.4943 | 11.0495 | 10.5582 | 9.6975 | 8.7591 | 7.7651 | 6.7035 | 5.3704 | 3.9457 | -0.19288 | -5.6651 | -10.744 | -13.4978 | 16.2899 | 16.0376 | 15.7294 | 15.3823 | 14.8835 | 14.3296 | 13.7179 | 13.0521 | 12.1867 | 11.2356 | 8.627 | 4.8538 | 1.5815 | -1.5948 | 12.6292 | 12.2648 | 11.8492 | 11.3883 | 10.6009 | 9.7429 | 8.8258 | 7.8427 | 6.5993 | 5.2668 | 1.3156 | -3.602 | -7.7867 | -10.1099
|  | PARK ROYAL | CT |  |  | 11.9853 | 11.6748 | 11.4012 | 10.9734 | 10.3759 | 9.718 | 9.0094 | 8.2424 | 7.3655 | 5.9315 | 1.6687 | -5.6159 | -10.744 | -13.4978 | 16.2899 | 16.0597 | 15.8408 | 15.4773 | 15.0547 | 14.5889 | 14.0818 | 13.5228 | 12.8636 | 11.8681 | 9.0367 | 4.8538 | 1.5815 | -1.5948 | 12.6969 | 12.4219 | 12.1666 | 11.7586 | 11.2042 | 10.5961 | 9.9371 | 9.221 | 8.3961 | 7.0633 | 2.9512 | -3.3668 | -7.7867 | -10.1099
|  | PARK ROYAL | LW |  |  | 11.9052 | 11.4943 | 11.0495 | 10.5582 | 9.6975 | 8.7591 | 7.7651 | 6.7035 | 5.3704 | 3.9457 | -0.19288 | -5.6651 | -8.2455 | -9.6772 | 16.2908 | 16.0376 | 15.7294 | 15.3823 | 14.8835 | 14.3296 | 13.7179 | 13.0521 | 12.1867 | 11.2356 | 8.627 | 5.6582 | 4.5252 | 3.8268 | 12.6292 | 12.2648 | 11.8492 | 11.3883 | 10.6009 | 9.7429 | 8.8258 | 7.8427 | 6.5993 | 5.2668 | 1.3156 | -3.602 | -5.7154 | -6.8993
|  | PARK ROYAL | ST |  |  | 12.3553 | 12.21 | 12.0984 | 11.9669 | 11.7358 | 11.4661 | 11.1727 | 10.8506 | 10.4486 | 9.9936 | 8.032 | 2.765 | -0.64263 | -2.7419 | 16.5401 | 16.4215 | 16.3163 | 16.1905 | 15.982 | 15.7424 | 15.4748 | 15.1783 | 14.811 | 14.4164 | 12.6676 | 8.1919 | 5.2085 | 2.2762 | 13.0456 | 12.9266 | 12.825 | 12.7037 | 12.4879 | 12.2385 | 11.9626 | 11.6581 | 11.2748 | 10.8452 | 8.9799 | 3.6626 | 0.65054 | -1.0142
|  | PARK ROYAL | SP |  |  | 12.5003 | 12.3461 | 12.2302 | 12.1015 | 11.9388 | 11.7453 | 11.5517 | 11.3268 | 11.0629 | 10.7496 | 9.5093 | 5.8257 | 2.9007 | 1.6285 | 16.5892 | 16.4516 | 16.3289 | 16.1919 | 16.0355 | 15.8555 | 15.663 | 15.4389 | 15.1746 | 14.8292 | 13.4433 | 9.3027 | 4.7366 | -1.0079 | 13.1732 | 13.0437 | 12.9363 | 12.8164 | 12.6674 | 12.4929 | 12.3143 | 12.1049 | 11.8565 | 11.5619 | 10.3918 | 6.5777 | 3.7429 | 2.6626
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH | MINIMUM HEADROOM | SZ 03222 92233 | YES | 6.478 | 6.4525 | 6.4229 | 6.388 | 6.3461 | 6.2971 | 6.2389 | 6.1724 | 6.0959 | 5.9994 | 5.6592 | 5.1412 | 4.6732 | 4.1754 | 5.5533 | 5.534 | 5.5129 | 5.4887 | 5.4564 | 5.4198 | 5.3783 | 5.3318 | 5.278 | 5.2134 | 4.9888 | 4.6404 | 4.3862 | 4.1158 | 5.4534 | 5.4334 | 5.4102 | 5.3827 | 5.3499 | 5.3115 | 5.2661 | 5.2142 | 5.1544 | 5.0338 | 4.5952 | 3.9774 | 3.6611 | 3.2311
|  | PARKSTONE NORTH | CT |  |  | 6.478 | 6.453 | 6.425 | 6.3927 | 6.3563 | 6.3144 | 6.2677 | 6.2154 | 6.1595 | 6.0853 | 5.8191 | 5.2543 | 4.6732 | 4.1754 | 5.5563 | 5.54 | 5.5218 | 5.5006 | 5.4745 | 5.445 | 5.4126 | 5.3766 | 5.3381 | 5.2855 | 5.1007 | 4.6997 | 4.3862 | 4.1158 | 5.4534 | 5.4334 | 5.4111 | 5.3853 | 5.3565 | 5.3234 | 5.2866 | 5.2452 | 5.2008 | 5.1426 | 4.8214 | 4.151 | 3.6611 | 3.2311
|  | PARKSTONE NORTH | LW |  |  | 6.4798 | 6.4525 | 6.4229 | 6.388 | 6.3461 | 6.2971 | 6.2389 | 6.1724 | 6.0959 | 5.9994 | 5.6592 | 5.1412 | 4.7809 | 4.4092 | 5.5533 | 5.534 | 5.5129 | 5.4887 | 5.4564 | 5.4198 | 5.3783 | 5.3318 | 5.278 | 5.2134 | 4.9888 | 4.6404 | 4.4342 | 4.2519 | 5.4551 | 5.4336 | 5.4102 | 5.3827 | 5.3499 | 5.3115 | 5.2661 | 5.2142 | 5.1544 | 5.0338 | 4.5952 | 3.9774 | 3.6646 | 3.4359
|  | PARKSTONE NORTH | ST |  |  | 6.4953 | 6.4815 | 6.4672 | 6.451 | 6.4306 | 6.4068 | 6.3795 | 6.3478 | 6.3097 | 6.2602 | 6.0611 | 5.4786 | 5.0461 | 4.7571 | 5.5679 | 5.5592 | 5.5501 | 5.5398 | 5.5265 | 5.5111 | 5.4937 | 5.4737 | 5.4496 | 5.4188 | 5.297 | 4.9219 | 4.6438 | 4.4583 | 5.4668 | 5.4555 | 5.4438 | 5.4306 | 5.414 | 5.3947 | 5.3727 | 5.3473 | 5.317 | 5.2781 | 5.1208 | 4.4208 | 3.9407 | 3.6542
|  | PARKSTONE NORTH | SP |  |  | 6.4966 | 6.4844 | 6.472 | 6.4588 | 6.4432 | 6.4257 | 6.4068 | 6.3859 | 6.3634 | 6.3341 | 6.2282 | 5.8309 | 5.3705 | 5.1052 | 5.5692 | 5.5615 | 5.5536 | 5.5452 | 5.534 | 5.5219 | 5.5091 | 5.4946 | 5.4794 | 5.4595 | 5.3884 | 5.1404 | 4.8614 | 4.6906 | 5.468 | 5.4579 | 5.4476 | 5.4368 | 5.4241 | 5.4099 | 5.3946 | 5.3778 | 5.3596 | 5.3365 | 5.2517 | 4.8695 | 4.3313 | 4.062
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH | MINIMUM HEADROOM | SZ 04762 89848 | YES | 4.2285 | 3.4424 | 2.5062 | 1.7283 | -0.00079303 | -1.827 | -3.7666 | -5.8536 | -8.315 | -11.0604 | -18.182 | -26.4544 | -33.1436 | -37.2345 | 13.2684 | 12.7939 | 12.2047 | 11.6839 | 10.7353 | 9.7211 | 8.5607 | 7.3002 | 5.7689 | 4.0195 | -0.33489 | -7.0483 | -12.9931 | -21.7837 | 7.481 | 6.7581 | 5.8769 | 5.1063 | 3.5338 | 1.8663 | 0.070291 | -1.8617 | -4.1104 | -6.6308 | -13.1313 | -20.641 | -26.3246 | -29.8187
|  | PARKSTONE SOUTH | CT |  |  | 4.5481 | 3.9668 | 3.3004 | 2.678 | 1.4362 | 0.11136 | -1.3124 | -2.8826 | -4.6505 | -7.3743 | -14.7791 | -25.4174 | -33.1436 | -37.2345 | 13.3046 | 12.8501 | 12.3372 | 11.7757 | 10.9297 | 9.9992 | 8.9791 | 7.8662 | 6.588 | 4.8122 | -0.13574 | -7.0483 | -12.9931 | -19.6036 | 7.7365 | 7.1887 | 6.5608 | 5.9076 | 4.7513 | 3.515 | 2.2045 | 0.78284 | -0.82176 | -3.2533 | -10.0187 | -19.6115 | -26.3246 | -29.8187
|  | PARKSTONE SOUTH | LW |  |  | 4.2285 | 3.4424 | 2.5062 | 1.7283 | -0.00079303 | -1.827 | -3.7666 | -5.8536 | -8.315 | -11.0604 | -18.182 | -26.4544 | -30.2251 | -32.5699 | 13.2684 | 12.7939 | 12.2047 | 11.6839 | 10.7353 | 9.7211 | 8.5607 | 7.3002 | 5.7689 | 4.0195 | -0.33489 | -4.9273 | -6.6017 | -7.6756 | 7.481 | 6.7581 | 5.8769 | 5.1063 | 3.5338 | 1.8663 | 0.070291 | -1.8617 | -4.1104 | -6.6308 | -13.1313 | -20.641 | -23.8651 | -25.8273
|  | PARKSTONE SOUTH | ST |  |  | 4.8928 | 4.5744 | 4.2225 | 3.9838 | 3.4026 | 2.7723 | 2.0972 | 1.3545 | 0.48519 | -0.51235 | -4.0853 | -12.2895 | -16.7881 | -19.6802 | 13.5541 | 13.277 | 12.9714 | 12.7177 | 12.2262 | 11.6914 | 11.1043 | 10.4537 | 9.6945 | 8.8762 | 5.8256 | -1.3274 | -6.5834 | -12.6951 | 8.0886 | 7.8038 | 7.4873 | 7.2458 | 6.7046 | 6.1156 | 5.4766 | 4.7706 | 3.9538 | 3.0637 | -0.11463 | -7.8087 | -11.7883 | -14.2339
|  | PARKSTONE SOUTH | SP |  |  | 4.9581 | 4.6493 | 4.3168 | 4.1049 | 3.5733 | 3.014 | 2.4224 | 1.7666 | 1.059 | 0.24336 | -2.4118 | -9.26 | -14.1147 | -16.2433 | 13.5775 | 13.2827 | 12.9596 | 12.6938 | 12.2437 | 11.7573 | 11.2137 | 10.6037 | 9.9203 | 9.1188 | 6.3328 | -1.2094 | -9.9911 | -21.7837 | 8.1497 | 7.8647 | 7.5595 | 7.3385 | 6.8654 | 6.3669 | 5.8261 | 5.2213 | 4.5617 | 3.8067 | 1.4027 | -4.9184 | -9.4005 | -11.2295
BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM | MINIMUM HEADROOM | SU 84770 68709 | YES | 19.7879 | 19.319 | 18.813 | 18.2694 | 17.2691 | 16.2277 | 15.1011 | 13.9019 | 12.4821 | 10.9804 | 7.2948 | 2.5241 | 0.29425 | -1.5952 | 21.8696 | 21.5965 | 21.2961 | 20.964 | 20.4282 | 19.8592 | 19.2179 | 18.527 | 17.6283 | 16.6789 | 14.4742 | 11.7538 | 10.2334 | 8.8698 | 21.1192 | 20.7001 | 20.2442 | 19.7492 | 18.8836 | 17.9752 | 16.9775 | 15.9108 | 14.6027 | 13.2181 | 9.8971 | 5.6676 | 3.8603 | 2.2367
|  | PEACOCK FARM | CT |  |  | 20.0198 | 19.7032 | 19.3328 | 18.918 | 18.2348 | 17.5226 | 16.8062 | 16.0251 | 15.0788 | 13.6394 | 10.0177 | 4.1598 | 0.29425 | -1.5952 | 21.9165 | 21.6853 | 21.4089 | 21.0927 | 20.6799 | 20.2319 | 19.7562 | 19.2328 | 18.577 | 17.6629 | 15.4508 | 12.2196 | 10.2334 | 8.8698 | 21.2876 | 20.9887 | 20.6355 | 20.2366 | 19.6278 | 18.9886 | 18.3327 | 17.615 | 16.7314 | 15.4145 | 12.1685 | 7.1824 | 3.8603 | 2.2367
|  | PEACOCK FARM | LW |  |  | 19.7879 | 19.319 | 18.813 | 18.2694 | 17.2691 | 16.2277 | 15.1011 | 13.9019 | 12.4821 | 10.9804 | 7.2948 | 2.5241 | 0.77419 | -0.26691 | 21.8696 | 21.5965 | 21.2961 | 20.964 | 20.4282 | 19.8592 | 19.2179 | 18.527 | 17.6283 | 16.6789 | 14.4742 | 11.7538 | 10.9554 | 10.4881 | 21.1192 | 20.7001 | 20.2442 | 19.7492 | 18.8836 | 17.9752 | 16.9775 | 15.9108 | 14.6027 | 13.2181 | 9.8971 | 5.6676 | 4.1916 | 3.3117
|  | PEACOCK FARM | ST |  |  | 20.3091 | 20.169 | 19.9974 | 19.7973 | 19.4861 | 19.157 | 18.8 | 18.4052 | 17.9355 | 17.4179 | 15.3055 | 10.917 | 8.5195 | 7.083 | 22.1208 | 22.0134 | 21.8794 | 21.7205 | 21.5012 | 21.2655 | 21.0037 | 20.7108 | 20.3527 | 19.9858 | 18.3857 | 15.2016 | 13.559 | 12.3678 | 21.5658 | 21.4363 | 21.2747 | 21.0839 | 20.8013 | 20.4995 | 20.1674 | 19.7981 | 19.351 | 18.8697 | 16.8246 | 12.7009 | 10.6286 | 9.4589
|  | PEACOCK FARM | SP |  |  | 20.3684 | 20.2376 | 20.0963 | 19.9356 | 19.6244 | 19.2994 | 18.9714 | 18.5836 | 18.1602 | 17.6628 | 15.9627 | 11.4484 | 8.5833 | 7.2997 | 22.1498 | 22.0401 | 21.9175 | 21.7749 | 21.577 | 21.3632 | 21.1397 | 20.8726 | 20.5684 | 20.2302 | 19.0151 | 15.5881 | 13.228 | 11.7001 | 21.6183 | 21.4932 | 21.3566 | 21.1991 | 20.9308 | 20.6441 | 20.351 | 20.0014 | 19.6141 | 19.1643 | 17.5903 | 13.3036 | 10.6594 | 9.558
BRAMLEY (FLEE) | FERNHURST | PETERSFIELD | MINIMUM HEADROOM | SU 74173 23420 | YES | 10.2859 | 9.2743 | 8.289 | 6.3669 | 6.1887 | 6.0135 | 5.826 | 5.6498 | 5.462 | 5.2566 | 4.8045 | 4.1671 | 3.7621 | 3.4169 | 11.0396 | 9.8574 | 8.7006 | 6.3591 | 6.248 | 6.1415 | 6.0271 | 5.9164 | 5.7888 | 5.6484 | 5.3666 | 5.0054 | 4.7028 | 4.4327 | 10.6422 | 9.4323 | 8.2528 | 5.8899 | 5.7624 | 5.6276 | 5.4568 | 5.2935 | 5.1164 | 4.9207 | 4.4065 | 3.7483 | 3.5951 | 3.3083
|  | PETERSFIELD | CT |  |  | 10.3048 | 9.3069 | 8.338 | 6.424 | 6.2828 | 6.1449 | 6.0144 | 5.8966 | 5.7639 | 5.565 | 5.102 | 4.3337 | 3.7621 | 3.4169 | 11.0423 | 9.863 | 8.711 | 6.3674 | 6.2694 | 6.1758 | 6.0848 | 5.9978 | 5.8981 | 5.7615 | 5.4643 | 5.0246 | 4.7028 | 4.4327 | 10.6466 | 9.4458 | 8.2747 | 5.9207 | 5.8124 | 5.7095 | 5.6072 | 5.5069 | 5.3866 | 5.1888 | 4.7483 | 4.0795 | 3.5964 | 3.3083
|  | PETERSFIELD | LW |  |  | 10.2859 | 9.2743 | 8.289 | 6.3669 | 6.1887 | 6.0135 | 5.826 | 5.6498 | 5.462 | 5.2566 | 4.8045 | 4.1671 | 3.8263 | 3.5985 | 11.0396 | 9.8574 | 8.7006 | 6.3591 | 6.248 | 6.1415 | 6.0271 | 5.9164 | 5.7888 | 5.6484 | 5.3666 | 5.0054 | 4.8433 | 4.7297 | 10.6422 | 9.4323 | 8.2528 | 5.8899 | 5.7624 | 5.6276 | 5.4568 | 5.2935 | 5.1164 | 4.9207 | 4.4065 | 3.7483 | 3.5951 | 3.4558
|  | PETERSFIELD | ST |  |  | 10.3431 | 9.3701 | 8.4292 | 6.5524 | 6.4701 | 6.3957 | 6.3182 | 6.2504 | 6.175 | 6.1063 | 5.8431 | 5.2198 | 4.8521 | 4.6005 | 11.0675 | 9.9046 | 8.7713 | 6.4534 | 6.3859 | 6.3259 | 6.2643 | 6.207 | 6.1425 | 6.0876 | 5.8782 | 5.4088 | 5.1377 | 4.9044 | 10.6813 | 9.4955 | 8.346 | 6.0225 | 5.955 | 5.896 | 5.8364 | 5.7777 | 5.7076 | 5.6295 | 5.3626 | 4.6678 | 4.3163 | 4.2107
|  | PETERSFIELD | SP |  |  | 10.3476 | 9.375 | 8.4345 | 6.5611 | 6.4895 | 6.425 | 6.3614 | 6.3042 | 6.2432 | 6.187 | 6.0055 | 5.4462 | 5.0527 | 4.8537 | 11.0694 | 9.9058 | 8.7713 | 6.4546 | 6.3947 | 6.3416 | 6.2891 | 6.2392 | 6.1852 | 6.1374 | 5.9825 | 5.5124 | 5.1468 | 4.8549 | 10.6813 | 9.4957 | 8.346 | 6.0234 | 5.9599 | 5.9059 | 5.8534 | 5.8037 | 5.7525 | 5.7004 | 5.5419 | 5.023 | 4.5439 | 4.4178
IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE | MINIMUM HEADROOM | SU 98108 80286 | YES | 8.4482 | 7.6982 | 6.8856 | 6.0175 | 4.7011 | 3.3267 | 1.8623 | 0.24324 | -1.6997 | -3.6459 | -8.4285 | -13.9968 | -15.6267 | -17.5914 | 9.435 | 9.0312 | 8.5798 | 8.0833 | 7.3921 | 6.6583 | 5.8464 | 4.9197 | 3.7353 | 2.5527 | -0.11618 | -3.0466 | -6.1973 | -9.7349 | 3.8842 | 3.1911 | 2.4431 | 1.6455 | 0.42723 | -0.84386 | -2.1943 | -3.682 | -5.4549 | -7.2364 | -11.6859 | -16.8243 | -18.2688 | -19.9322
|  | PETERSFIELD AVENUE | CT |  |  | 8.9222 | 8.4894 | 7.9944 | 7.4131 | 6.5943 | 5.7234 | 4.796 | 3.7499 | 2.5718 | 0.76111 | -3.74 | -10.7321 | -15.4984 | -17.5914 | 9.5611 | 9.2371 | 8.8622 | 8.4144 | 7.8814 | 7.3108 | 6.6845 | 5.9628 | 5.1264 | 3.9389 | 1.0985 | -3.0466 | -6.1973 | -9.2201 | 4.3781 | 3.9737 | 3.5146 | 2.9817 | 2.2243 | 1.4266 | 0.55511 | -0.43351 | -1.553 | -3.2604 | -7.447 | -13.8178 | -18.0924 | -19.9322
|  | PETERSFIELD AVENUE | LW |  |  | 8.4482 | 7.6982 | 6.8856 | 6.0175 | 4.7011 | 3.3267 | 1.8623 | 0.24324 | -1.6997 | -3.6459 | -8.4285 | -13.9968 | -15.6267 | -16.6193 | 9.435 | 9.0312 | 8.5798 | 8.0833 | 7.3921 | 6.6583 | 5.8464 | 4.9197 | 3.7353 | 2.5527 | -0.11618 | -2.9987 | -3.6496 | -4.0182 | 3.8842 | 3.1911 | 2.4431 | 1.6455 | 0.42723 | -0.84386 | -2.1943 | -3.682 | -5.4549 | -7.2364 | -11.6859 | -16.8243 | -18.2688 | -19.1414
|  | PETERSFIELD AVENUE | ST |  |  | 9.3156 | 9.1192 | 8.8822 | 8.6105 | 8.2193 | 7.7917 | 7.324 | 6.7988 | 6.1852 | 5.5186 | 2.6046 | -2.8368 | -5.5671 | -7.1284 | 9.8368 | 9.6783 | 9.4851 | 9.26 | 8.9642 | 8.6424 | 8.2864 | 7.8789 | 7.3928 | 6.902 | 4.654 | 0.32992 | -2.3979 | -5.2777 | 4.7378 | 4.5498 | 4.3276 | 4.0753 | 3.7041 | 3.3071 | 2.8814 | 2.4046 | 1.848 | 1.2338 | -1.5611 | -6.7257 | -9.2115 | -10.5866
|  | PETERSFIELD AVENUE | SP |  |  | 9.3896 | 9.2157 | 9.0326 | 8.8335 | 8.4299 | 8.0177 | 7.5647 | 7.0607 | 6.5149 | 5.8091 | 3.2966 | -3.0212 | -6.7512 | -8.5136 | 9.864 | 9.7051 | 9.5309 | 9.3376 | 9.0481 | 8.748 | 8.4232 | 8.0466 | 7.6227 | 7.1125 | 5.1712 | -0.093028 | -4.5756 | -9.7349 | 4.8148 | 4.6543 | 4.4856 | 4.3033 | 3.9073 | 3.5097 | 3.0918 | 2.6294 | 2.1293 | 1.4783 | -0.8206 | -6.7825 | -10.2548 | -11.8402
MANNINGTON GSP | SALISBURY | PETERSFINGER | MINIMUM HEADROOM | SU 15608 29334 | YES | 27.623 | 26.8435 | 25.579 | 24.1789 | 22.3088 | 20.3841 | 18.3158 | 16.0718 | 13.6554 | 11.5389 | 6.4059 | 0.16313 | -3.543 | -6.4743 | 34.8845 | 34.6572 | 34.2689 | 33.8259 | 33.2572 | 32.6651 | 32.0182 | 31.0093 | 29.7523 | 28.5431 | 25.4712 | 20.3194 | 15.6777 | 8.1791 | 30.8593 | 30.5622 | 30.0912 | 29.5692 | 28.9946 | 27.4679 | 25.7397 | 23.8533 | 21.7746 | 19.9061 | 15.2442 | 9.6344 | 6.7387 | 4.3424
|  | PETERSFINGER | CT |  |  | 27.8803 | 27.2503 | 26.1785 | 24.8918 | 23.2961 | 21.6542 | 19.9365 | 18.0562 | 16.0779 | 14.03 | 9.0416 | 1.5192 | -3.543 | -6.4743 | 34.8845 | 34.6572 | 34.3033 | 33.8507 | 33.3113 | 32.753 | 32.1618 | 31.3732 | 30.2354 | 28.9773 | 25.5999 | 20.3194 | 15.6777 | 10.3195 | 30.8593 | 30.5622 | 30.0912 | 29.5692 | 28.9946 | 28.4063 | 26.9578 | 25.3629 | 23.6623 | 21.8702 | 17.4402 | 10.9343 | 6.7387 | 4.3424
|  | PETERSFINGER | LW |  |  | 27.623 | 26.8435 | 25.579 | 24.1789 | 22.3088 | 20.3841 | 18.3158 | 16.0718 | 13.6554 | 11.5389 | 6.4059 | 0.16313 | -2.8563 | -4.7334 | 34.9235 | 34.671 | 34.2689 | 33.8259 | 33.2572 | 32.6651 | 32.0182 | 31.0093 | 29.7523 | 28.5431 | 25.4712 | 21.8007 | 20.3106 | 19.3446 | 30.8906 | 30.5912 | 30.1174 | 29.6115 | 29.0206 | 27.4679 | 25.7397 | 23.8533 | 21.7746 | 19.9061 | 15.2442 | 9.6344 | 7.1279 | 5.5907
|  | PETERSFINGER | ST |  |  | 28.2029 | 27.8543 | 27.2432 | 26.5789 | 25.6777 | 24.7643 | 23.783 | 22.7009 | 21.5562 | 20.5659 | 17.7903 | 12.0836 | 8.6335 | 6.3947 | 34.9934 | 34.8389 | 34.5872 | 34.3183 | 33.9785 | 33.6314 | 33.2553 | 32.796 | 32.259 | 31.7205 | 29.8957 | 24.8301 | 20.5689 | 15.4809 | 30.9936 | 30.7861 | 30.4285 | 30.0509 | 29.5849 | 29.1155 | 28.6134 | 28.037 | 27.4041 | 26.8086 | 24.8507 | 19.5364 | 16.6493 | 14.8713
|  | PETERSFINGER | SP |  |  | 28.255 | 27.9234 | 27.3625 | 26.7632 | 26.0499 | 25.3339 | 24.5226 | 23.6305 | 22.723 | 21.9059 | 19.79 | 15.0753 | 11.3997 | 9.5064 | 34.995 | 34.8439 | 34.5973 | 34.3356 | 34.0262 | 33.7084 | 33.357 | 32.9324 | 32.472 | 32.0133 | 30.3597 | 24.9796 | 17.9805 | 8.1791 | 30.9997 | 30.7995 | 30.454 | 30.0921 | 29.6735 | 29.2539 | 28.7985 | 28.2738 | 27.7225 | 27.2289 | 25.8947 | 22.189 | 18.8561 | 17.2808
MELKSHAM GSP | AMESBURY | PEWSEY | MINIMUM HEADROOM | SU 14710 59252 | YES | 10.1236 | 9.6963 | 9.2144 | 8.7096 | 7.9458 | 7.144 | 6.2945 | 5.3145 | 4.1446 | 3.0451 | 0.46992 | -2.3387 | -3.186 | -3.9147 | 15.7833 | 15.5605 | 15.2886 | 14.994 | 14.5953 | 14.1662 | 13.69 | 13.1265 | 12.4055 | 11.7193 | 10.308 | 8.5804 | 6.6652 | 3.2082 | 11.8531 | 11.4628 | 11.0183 | 10.5507 | 9.8529 | 9.118 | 8.335 | 7.4358 | 6.3548 | 5.3315 | 2.9679 | 0.42242 | -0.3247 | -0.93098
|  | PEWSEY | CT |  |  | 10.4789 | 10.2515 | 9.988 | 9.6578 | 9.1941 | 8.7031 | 8.1775 | 7.5313 | 6.7896 | 5.7265 | 3.26 | -0.46361 | -2.8962 | -3.9147 | 15.8629 | 15.6879 | 15.4785 | 15.2036 | 14.888 | 14.5469 | 14.1705 | 13.7105 | 13.1707 | 12.4334 | 10.822 | 8.5804 | 6.6652 | 4.5553 | 12.1604 | 11.9462 | 11.6964 | 11.38 | 10.9484 | 10.4902 | 9.998 | 9.3997 | 8.7126 | 7.7195 | 5.4443 | 2.1035 | -0.038497 | -0.93098
|  | PEWSEY | LW |  |  | 10.1236 | 9.6963 | 9.2144 | 8.7096 | 7.9458 | 7.144 | 6.2945 | 5.3145 | 4.1446 | 3.0451 | 0.46992 | -2.3387 | -3.186 | -3.511 | 15.7833 | 15.5605 | 15.2886 | 14.994 | 14.5953 | 14.1662 | 13.69 | 13.1265 | 12.4055 | 11.7193 | 10.308 | 8.9375 | 8.6124 | 8.4914 | 11.8531 | 11.4628 | 11.0183 | 10.5507 | 9.8529 | 9.118 | 8.335 | 7.4358 | 6.3548 | 5.3315 | 2.9679 | 0.42242 | -0.3247 | -0.60872
|  | PEWSEY | ST |  |  | 10.6842 | 10.5743 | 10.4465 | 10.3064 | 10.0754 | 9.8253 | 9.5607 | 9.2307 | 8.848 | 8.4673 | 6.9347 | 4.1663 | 2.7635 | 1.8742 | 16.014 | 15.9235 | 15.8141 | 15.6884 | 15.5072 | 15.3065 | 15.0859 | 14.8164 | 14.4988 | 14.2003 | 12.8945 | 10.4545 | 8.7837 | 6.7225 | 12.3571 | 12.2552 | 12.1353 | 12.003 | 11.7868 | 11.5518 | 11.3022 | 10.998 | 10.6461 | 10.2934 | 8.8344 | 6.2222 | 4.9589 | 4.1793
|  | PEWSEY | SP |  |  | 10.7399 | 10.6446 | 10.5407 | 10.4328 | 10.1971 | 9.9542 | 9.7128 | 9.4042 | 9.059 | 8.6544 | 7.296 | 4.0175 | 2.1834 | 1.2922 | 16.0286 | 15.9327 | 15.8237 | 15.7058 | 15.5321 | 15.3464 | 15.1513 | 14.8992 | 14.6075 | 14.2887 | 13.101 | 9.9277 | 7.053 | 3.2082 | 12.406 | 12.3155 | 12.2165 | 12.1134 | 11.8969 | 11.6736 | 11.4512 | 11.1716 | 10.8601 | 10.4913 | 9.2275 | 6.1308 | 4.4368 | 3.6419
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE | MINIMUM HEADROOM | SY 70169 99809 | YES | 7.1625 | 6.5781 | 5.961 | 5.3296 | 4.4881 | 3.6229 | 2.7103 | 1.7428 | 0.63146 | -0.44532 | -3.1336 | -4.6162 | -4.7472 | -5.8902 | 12.0971 | 11.8332 | 11.5497 | 11.2567 | 10.8711 | 10.4712 | 10.0546 | 9.6117 | 9.067 | 8.5447 | 7.3624 | 6.6659 | 6.4606 | 5.4591 | 8.5504 | 8.4883 | 8.0036 | 7.515 | 6.8384 | 6.0576 | 5.2521 | 4.4008 | 3.3753 | 2.3936 | 0.11882 | -1.1996 | -1.3191 | -2.253
|  | PIDDLETRENTHIDE | CT |  |  | 7.215 | 7.1879 | 7.1545 | 6.9463 | 6.4627 | 5.9619 | 5.435 | 4.8645 | 4.2295 | 3.3236 | 1.2484 | 0.0033491 | -0.35647 | -0.51482 | 12.3545 | 12.2219 | 12.076 | 11.901 | 11.6608 | 11.4099 | 11.1437 | 10.8511 | 10.4825 | 9.9623 | 8.8914 | 8.1617 | 7.8379 | 7.5124 | 8.5504 | 8.5234 | 8.4902 | 8.4424 | 8.3973 | 8.111 | 7.6275 | 7.1019 | 6.5121 | 5.67 | 3.7784 | 2.6449 | 2.3213 | 2.1804
|  | PIDDLETRENTHIDE | LW |  |  | 7.1625 | 6.5781 | 5.961 | 5.3296 | 4.4881 | 3.6229 | 2.7103 | 1.7428 | 0.63146 | -0.44532 | -3.1336 | -4.6162 | -4.7472 | -4.7908 | 12.0971 | 11.8332 | 11.5497 | 11.2567 | 10.8711 | 10.4712 | 10.0546 | 9.6117 | 9.067 | 8.5447 | 7.3624 | 6.6659 | 6.5943 | 6.5677 | 8.5579 | 8.4883 | 8.0036 | 7.515 | 6.8384 | 6.0576 | 5.2521 | 4.4008 | 3.3753 | 2.3936 | 0.11882 | -1.1996 | -1.3191 | -1.3583
|  | PIDDLETRENTHIDE | ST |  |  | 7.2443 | 7.2343 | 7.2199 | 7.2015 | 7.0924 | 6.7676 | 6.4379 | 6.0899 | 5.7171 | 5.3113 | 3.7496 | 1.2824 | -0.019886 | -0.87349 | 12.4319 | 12.349 | 12.2568 | 12.1561 | 12.002 | 11.8393 | 11.6711 | 11.4911 | 11.294 | 11.0859 | 10.2185 | 8.7569 | 8.0444 | 7.4618 | 8.5795 | 8.5696 | 8.5552 | 8.5369 | 8.5119 | 8.4839 | 8.4524 | 8.2509 | 7.907 | 7.5355 | 6.0803 | 3.7995 | 2.6396 | 1.8889
|  | PIDDLETRENTHIDE | SP |  |  | 7.2438 | 7.231 | 7.2172 | 7.2013 | 7.1844 | 6.7594 | 6.3226 | 5.8602 | 5.3883 | 4.7961 | 2.8317 | -1.4608 | -4.1293 | -5.8902 | 12.4634 | 12.3934 | 12.3201 | 12.2416 | 12.0443 | 11.8421 | 11.6366 | 11.4159 | 11.1871 | 10.9069 | 9.9492 | 7.7823 | 6.4606 | 5.4591 | 8.5789 | 8.5662 | 8.5525 | 8.5367 | 8.52 | 8.5012 | 8.3723 | 7.9975 | 7.6218 | 7.1095 | 5.3325 | 1.4661 | -0.76596 | -2.253
BRAMLEY (FLEE) | FERNHURST | PLAISTOW | MINIMUM HEADROOM | TQ 02071 29626 | YES | 2.768 | 2.6025 | 2.4283 | 2.2506 | 2.012 | 1.7663 | 1.5297 | 1.2925 | 1.0083 | 0.74143 | 0.066262 | -0.63279 | -0.71093 | -0.77716 | 3.6698 | 3.5997 | 3.5235 | 3.4447 | 3.3416 | 3.2335 | 3.1263 | 3.0163 | 2.8739 | 2.7432 | 2.4578 | 2.1632 | 2.127 | 2.0185 | 2.371 | 2.2397 | 2.096 | 1.9477 | 1.7539 | 1.5509 | 1.3497 | 1.1426 | 0.87004 | 0.62407 | 0.11433 | -0.40671 | -0.46817 | -0.51721
|  | PLAISTOW | CT |  |  | 2.9596 | 2.8918 | 2.8171 | 2.7367 | 2.6068 | 2.4726 | 2.3331 | 2.1854 | 2.0257 | 1.787 | 1.2732 | 0.47376 | 0.2831 | 0.22712 | 3.7259 | 3.7016 | 3.661 | 3.6154 | 3.552 | 3.4855 | 3.4154 | 3.3373 | 3.2522 | 3.1353 | 2.8989 | 2.5373 | 2.4224 | 2.3432 | 2.4985 | 2.4351 | 2.3614 | 2.2785 | 2.1625 | 2.0409 | 1.9132 | 1.7692 | 1.6115 | 1.3904 | 0.97234 | 0.37044 | 0.2259 | 0.18285
|  | PLAISTOW | LW |  |  | 2.768 | 2.6025 | 2.4283 | 2.2506 | 2.012 | 1.7663 | 1.5297 | 1.2925 | 1.0083 | 0.74143 | 0.066262 | -0.63279 | -0.71093 | -0.77716 | 3.6698 | 3.5997 | 3.5235 | 3.4447 | 3.3416 | 3.2335 | 3.1263 | 3.0163 | 2.8739 | 2.7432 | 2.4578 | 2.1632 | 2.127 | 2.0982 | 2.371 | 2.2397 | 2.096 | 1.9477 | 1.7539 | 1.5509 | 1.3497 | 1.1426 | 0.87004 | 0.62407 | 0.11433 | -0.40671 | -0.46817 | -0.51721
|  | PLAISTOW | ST |  |  | 2.9946 | 2.9498 | 2.9024 | 2.8522 | 2.7666 | 2.6793 | 2.5908 | 2.4972 | 2.3979 | 2.2855 | 1.8623 | 1.2137 | 0.86249 | 0.6356 | 3.7292 | 3.7275 | 3.712 | 3.6856 | 3.6441 | 3.6016 | 3.5573 | 3.5094 | 3.4569 | 3.4014 | 3.1713 | 2.8393 | 2.6542 | 2.5086 | 2.5384 | 2.5005 | 2.4586 | 2.4124 | 2.3375 | 2.2611 | 2.1819 | 2.0964 | 2.0027 | 1.9035 | 1.481 | 0.92589 | 0.66089 | 0.49479
|  | PLAISTOW | SP |  |  | 3.0202 | 2.9897 | 2.9573 | 2.9237 | 2.8123 | 2.6963 | 2.5833 | 2.4619 | 2.3408 | 2.1729 | 1.6348 | 0.4728 | -0.26511 | -0.74488 | 3.7295 | 3.7276 | 3.7257 | 3.7121 | 3.6642 | 3.6133 | 3.5634 | 3.5079 | 3.4518 | 3.3783 | 3.1298 | 2.5607 | 2.2332 | 2.0185 | 2.5574 | 2.5281 | 2.4975 | 2.4652 | 2.3789 | 2.2873 | 2.1983 | 2.0993 | 1.9995 | 1.8659 | 1.4115 | 0.38066 | -0.16915 | -0.50937
MINETY GSP | STRATTON (2 X 90) | PLESSEY Swindon | MINIMUM HEADROOM | SU 16381 86720 | YES | 7.5161 | 8.7621 | 8.4623 | 8.1503 | 7.7379 | 7.3147 | 6.85 | 6.3268 | 5.7984 | 5.4212 | 4.4884 | 3.4799 | 3.2594 | 3.1338 | 6.0996 | 9.753 | 9.6115 | 9.4572 | 9.2645 | 9.0645 | 8.8224 | 8.5297 | 8.2195 | 8.0362 | 7.6514 | 7.2113 | 7.1196 | 7.0692 | 5.2913 | 8.8173 | 8.5488 | 8.2657 | 7.8973 | 7.5182 | 7.0903 | 6.5983 | 6.0941 | 5.7547 | 4.9527 | 4.0758 | 3.8891 | 3.7853
|  | PLESSEY Swindon | CT |  |  | 7.7844 | 9.1778 | 9.001 | 8.8267 | 8.5945 | 8.3522 | 8.0651 | 7.7593 | 7.4486 | 7.0702 | 6.4057 | 5.3019 | 4.6097 | 4.3118 | 6.1633 | 9.8609 | 9.7415 | 9.6233 | 9.4912 | 9.3515 | 9.1714 | 8.9774 | 8.7783 | 8.5481 | 8.2255 | 7.6886 | 7.3448 | 7.0757 | 5.5097 | 9.1617 | 8.9936 | 8.8281 | 8.6129 | 8.3879 | 8.1178 | 7.8296 | 7.5366 | 7.1813 | 6.5801 | 5.5929 | 5.0196 | 4.7749
|  | PLESSEY Swindon | LW |  |  | 7.5161 | 8.7621 | 8.4623 | 8.1503 | 7.7379 | 7.3147 | 6.85 | 6.3268 | 5.7984 | 5.4212 | 4.4884 | 3.4799 | 3.2594 | 3.1338 | 6.0996 | 9.753 | 9.6115 | 9.4572 | 9.2645 | 9.0645 | 8.8224 | 8.5297 | 8.2195 | 8.0362 | 7.6514 | 7.2113 | 7.1196 | 7.0692 | 5.2913 | 8.8173 | 8.5488 | 8.2657 | 7.8973 | 7.5182 | 7.0903 | 6.5983 | 6.0941 | 5.7547 | 4.9527 | 4.0758 | 3.8891 | 3.7853
|  | PLESSEY Swindon | ST |  |  | 7.9291 | 9.4045 | 9.3135 | 9.2089 | 9.0659 | 8.9209 | 8.765 | 8.591 | 8.4158 | 8.2356 | 7.3603 | 6.497 | 5.9847 | 5.7066 | 6.2615 | 10.0143 | 9.953 | 9.8795 | 9.7979 | 9.7138 | 9.6187 | 9.5086 | 9.3918 | 9.2828 | 8.6784 | 8.143 | 7.8197 | 7.5506 | 5.6485 | 9.3792 | 9.2935 | 9.1942 | 9.0622 | 8.9282 | 8.783 | 8.62 | 8.4548 | 8.2866 | 7.4501 | 6.6528 | 6.1945 | 5.9511
|  | PLESSEY Swindon | SP |  |  | 7.9779 | 9.4782 | 9.4255 | 9.3634 | 9.2325 | 9.1101 | 8.9813 | 8.8308 | 8.6775 | 8.4547 | 7.647 | 5.9768 | 5.0662 | 4.4605 | 6.2779 | 10.0405 | 9.9997 | 9.9495 | 9.8787 | 9.8129 | 9.7406 | 9.6509 | 9.5564 | 9.4357 | 8.9556 | 7.9341 | 7.4661 | 7.1449 | 5.6916 | 9.4447 | 9.3948 | 9.3354 | 9.2156 | 9.1039 | 8.9859 | 8.8465 | 8.7041 | 8.4993 | 7.7466 | 6.1896 | 5.37 | 4.8549
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSY TITCHFIELD | MINIMUM HEADROOM | SU 53390 06922 | YES | 8.443 | 8.346 | 8.2301 | 8.0988 | 7.8167 | 7.3477 | 6.8424 | 6.2977 | 5.6478 | 4.9104 | 2.7292 | -0.53007 | -3.9297 | -6.0998 | 6.837 | 6.7358 | 6.596 | 6.4408 | 6.2135 | 5.9668 | 5.6941 | 5.3977 | 5.0424 | 4.6322 | 3.4154 | 1.1901 | -1.1066 | -3.302 | 4.3612 | 4.1974 | 3.9913 | 3.7662 | 3.3853 | 2.9797 | 2.5462 | 2.0823 | 1.5282 | 0.9037 | -1.0004 | -3.8642 | -6.8214 | -8.6371
|  | PLESSY TITCHFIELD | CT |  |  | 8.4663 | 8.3891 | 8.3029 | 8.1853 | 8.0397 | 7.8796 | 7.5546 | 7.149 | 6.7066 | 5.9884 | 3.7473 | -0.43424 | -3.9297 | -6.0998 | 6.8693 | 6.7872 | 6.6941 | 6.5431 | 6.3591 | 6.16 | 5.9385 | 5.6933 | 5.4224 | 5.0032 | 3.6695 | 1.1901 | -1.1066 | -3.302 | 4.4633 | 4.3597 | 4.2427 | 4.0642 | 3.8095 | 3.5367 | 3.2316 | 2.899 | 2.5392 | 1.929 | 0.00053346 | -3.7738 | -6.8214 | -8.6371
|  | PLESSY TITCHFIELD | LW |  |  | 8.443 | 8.346 | 8.2301 | 8.0988 | 7.8167 | 7.3477 | 6.8424 | 6.2977 | 5.6478 | 4.9104 | 2.7292 | -0.53007 | -2.5949 | -3.9853 | 6.837 | 6.7358 | 6.596 | 6.4408 | 6.2135 | 5.9668 | 5.6941 | 5.3977 | 5.0424 | 4.6322 | 3.4154 | 1.6758 | 0.63881 | -0.086088 | 4.3612 | 4.1974 | 3.9913 | 3.7662 | 3.3853 | 2.9797 | 2.5462 | 2.0823 | 1.5282 | 0.9037 | -1.0004 | -3.8642 | -5.5929 | -6.7012
|  | PLESSY TITCHFIELD | ST |  |  | 8.5197 | 8.4776 | 8.4325 | 8.3818 | 8.3102 | 8.2281 | 8.1354 | 8.0307 | 7.9052 | 7.7517 | 6.8589 | 4.0139 | 1.8553 | 0.23717 | 6.9236 | 6.8774 | 6.8255 | 6.7667 | 6.6737 | 6.569 | 6.4513 | 6.3209 | 6.1708 | 5.9965 | 5.2696 | 3.2053 | 1.3313 | -0.67403 | 4.539 | 4.4871 | 4.4295 | 4.3655 | 4.2598 | 4.1416 | 4.0111 | 3.8673 | 3.7032 | 3.5079 | 2.7127 | 0.37893 | -1.4734 | -2.8682
|  | PLESSY TITCHFIELD | SP |  |  | 8.5275 | 8.4876 | 8.4467 | 8.4021 | 8.3432 | 8.2781 | 8.2097 | 8.1309 | 8.0461 | 7.9426 | 7.3203 | 5.1553 | 3.2832 | 2.0964 | 6.9305 | 6.8795 | 6.8229 | 6.7625 | 6.6822 | 6.5942 | 6.5001 | 6.3908 | 6.2733 | 6.0979 | 5.4229 | 3.4362 | 0.75354 | -2.9293 | 4.5556 | 4.5052 | 4.4507 | 4.3933 | 4.2956 | 4.1907 | 4.0826 | 3.9557 | 3.8289 | 3.6676 | 3.081 | 1.421 | -0.04546 | -1.0185
LOVEDEAN GSP | WYMERING BSP | PORTCHESTER | MINIMUM HEADROOM | SU 62043 05575 | NO | 16.4203 | 15.974 | 15.5448 | 15.0763 | 14.4305 | 13.7558 | 13.0226 | 12.2238 | 11.2113 | 10.2262 | 7.9787 | 4.6299 | 2.1067 | 0.20813 | 16.756 | 16.6007 | 16.4368 | 16.2219 | 15.8961 | 15.5512 | 15.1676 | 14.7453 | 14.0269 | 13.3273 | 11.9315 | 10.0274 | 8.3265 | 6.9204 | 16.9829 | 16.7142 | 16.315 | 15.8747 | 15.2793 | 14.6461 | 13.948 | 13.1807 | 12.1571 | 11.1735 | 9.077 | 6.0851 | 4.0881 | 2.537
|  | PORTCHESTER | CT |  |  | 16.5015 | 16.1296 | 15.7524 | 15.3384 | 14.8868 | 14.4123 | 13.935 | 13.384 | 12.7331 | 11.7248 | 9.4021 | 5.2343 | 2.1067 | 0.20813 | 16.756 | 16.6284 | 16.4789 | 16.2713 | 16.0165 | 15.7457 | 15.4644 | 15.1288 | 14.6207 | 13.8916 | 12.3878 | 10.0334 | 8.3265 | 6.9204 | 16.9829 | 16.7667 | 16.4513 | 16.0454 | 15.6214 | 15.1711 | 14.7073 | 14.1612 | 13.4984 | 12.4891 | 10.3058 | 6.6763 | 4.0881 | 2.537
|  | PORTCHESTER | LW |  |  | 16.4203 | 15.974 | 15.5448 | 15.0763 | 14.4305 | 13.7558 | 13.0226 | 12.2238 | 11.2113 | 10.2262 | 7.9787 | 4.6299 | 2.7985 | 1.5302 | 16.7704 | 16.6007 | 16.4368 | 16.2219 | 15.8961 | 15.5512 | 15.1676 | 14.7453 | 14.0269 | 13.3273 | 11.9315 | 10.0274 | 9.1424 | 8.5043 | 16.9923 | 16.7142 | 16.315 | 15.8747 | 15.2793 | 14.6461 | 13.948 | 13.1807 | 12.1571 | 11.1735 | 9.077 | 6.0851 | 4.57 | 3.533
|  | PORTCHESTER | ST |  |  | 16.6846 | 16.5617 | 16.3879 | 16.1766 | 15.9784 | 15.7704 | 15.5384 | 15.2778 | 14.968 | 14.63 | 13.002 | 9.6675 | 7.5704 | 6.1618 | 16.8389 | 16.7631 | 16.6913 | 16.6122 | 16.5344 | 16.4466 | 16.3171 | 16.1435 | 15.9338 | 15.709 | 14.4638 | 11.8832 | 10.3636 | 9.1318 | 17.1384 | 17.0211 | 16.9094 | 16.7852 | 16.6519 | 16.4799 | 16.2423 | 15.9744 | 15.6532 | 15.3152 | 13.614 | 10.4336 | 8.6355 | 7.4878
|  | PORTCHESTER | SP |  |  | 16.6899 | 16.573 | 16.4623 | 16.3028 | 16.1434 | 15.9867 | 15.8198 | 15.6146 | 15.3813 | 15.1174 | 14.0734 | 10.8917 | 8.8333 | 7.716 | 16.8424 | 16.7714 | 16.7069 | 16.6392 | 16.5787 | 16.5153 | 16.4417 | 16.3297 | 16.17 | 15.9887 | 15.2727 | 12.4653 | 10.5332 | 8.9081 | 17.1442 | 17.0377 | 16.9385 | 16.8317 | 16.7283 | 16.6178 | 16.4957 | 16.3302 | 16.0904 | 15.8234 | 14.7432 | 11.4581 | 9.6001 | 8.6669
CHICKERELL GSP | CHICKERELL BSP | PORTLAND | MINIMUM HEADROOM | SY 68307 73941 | YES | 3.716 | 3.101 | 2.5678 | 2.0579 | 1.1609 | 0.19336 | -0.83667 | -1.9214 | -3.1848 | -4.6355 | -8.2341 | -13.218 | -17.9139 | -21.1034 | 3.7245 | 3.3739 | 3.0537 | 2.7391 | 2.2631 | 1.6964 | 1.0427 | 0.33895 | -0.55141 | -1.5531 | -3.7553 | -6.8701 | -9.9356 | -12.8418 | 0.90143 | 0.35239 | -0.16378 | -0.67204 | -1.5156 | -2.4278 | -3.4145 | -4.4616 | -5.7146 | -7.1179 | -10.5283 | -14.9201 | -18.782 | -21.4581
|  | PORTLAND | CT |  |  | 3.9147 | 3.4234 | 3.0712 | 2.6498 | 2.0635 | 1.4163 | 0.72463 | -0.0089406 | -0.84593 | -2.2976 | -6.3024 | -12.6777 | -17.9139 | -21.1034 | 3.7721 | 3.4536 | 3.2092 | 2.8936 | 2.5144 | 2.0367 | 1.5149 | 0.95037 | 0.28913 | -0.71943 | -3.3051 | -6.8701 | -9.9356 | -12.8418 | 1.0603 | 0.61697 | 0.27435 | -0.17007 | -0.74545 | -1.3794 | -2.0625 | -2.7926 | -3.632 | -5.0628 | -8.8015 | -14.3467 | -18.782 | -21.4581
|  | PORTLAND | LW |  |  | 3.716 | 3.101 | 2.5678 | 2.0579 | 1.1609 | 0.19336 | -0.83667 | -1.9214 | -3.1848 | -4.6355 | -8.2341 | -13.218 | -16.2176 | -18.3444 | 3.7245 | 3.3739 | 3.0537 | 2.7391 | 2.2631 | 1.6964 | 1.0427 | 0.33895 | -0.55141 | -1.5531 | -3.7553 | -6.378 | -7.7516 | -8.7766 | 0.90143 | 0.35239 | -0.16378 | -0.67204 | -1.5156 | -2.4278 | -3.4145 | -4.4616 | -5.7146 | -7.1179 | -10.5283 | -14.9201 | -17.3679 | -19.0929
|  | PORTLAND | ST |  |  | 4.2347 | 3.9596 | 3.791 | 3.6373 | 3.4004 | 3.1223 | 2.824 | 2.5004 | 2.1395 | 1.7412 | -0.069812 | -5.0582 | -8.0175 | -10.2286 | 3.981 | 3.7915 | 3.6613 | 3.5329 | 3.3493 | 3.135 | 2.9006 | 2.6424 | 2.3049 | 1.9428 | 0.2736 | -3.5768 | -6.0258 | -8.594 | 1.3936 | 1.1664 | 1.0095 | 0.85368 | 0.61196 | 0.32983 | 0.023666 | -0.31282 | -0.69268 | -1.0965 | -2.988 | -7.6179 | -10.1452 | -11.9647
|  | PORTLAND | SP |  |  | 4.2752 | 4.0054 | 3.8438 | 3.7102 | 3.5262 | 3.3277 | 3.1124 | 2.8739 | 2.615 | 2.2876 | 1.0442 | -3.3405 | -6.3573 | -8.028 | 3.9968 | 3.8001 | 3.663 | 3.5379 | 3.3928 | 3.233 | 3.0562 | 2.8562 | 2.6345 | 2.3199 | 0.95154 | -3.1838 | -7.1031 | -11.7962 | 1.4307 | 1.2024 | 1.0476 | 0.90943 | 0.72664 | 0.53166 | 0.31653 | 0.073106 | -0.19454 | -0.52663 | -1.8097 | -6.02 | -8.7058 | -10.0771
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH | MINIMUM HEADROOM | SZ 63405 99685 | YES | 12.6418 | 12.2098 | 11.7712 | 11.4082 | 10.8363 | 10.2134 | 9.5354 | 8.8154 | 7.9789 | 7.0425 | 4.2426 | 0.92135 | -1.9158 | -3.5275 | 15.931 | 15.7816 | 15.6457 | 15.5192 | 15.3774 | 15.2108 | 15.0122 | 14.7907 | 14.5154 | 14.0723 | 12.3442 | 10.3403 | 8.5971 | 7.1696 | 13.9384 | 13.5706 | 13.1785 | 12.8397 | 12.3123 | 11.7378 | 11.1092 | 10.4394 | 9.6557 | 8.774 | 6.1448 | 3.1065 | 0.7309 | -0.67075
|  | PORTSMOUTH | CT |  |  | 12.7619 | 12.407 | 12.1093 | 11.7932 | 11.4038 | 10.9674 | 10.4911 | 9.9759 | 9.4139 | 8.5031 | 5.6322 | 1.206 | -1.9158 | -3.5275 | 15.931 | 15.7882 | 15.6653 | 15.5435 | 15.419 | 15.2766 | 15.1145 | 14.9384 | 14.7327 | 14.4678 | 12.8253 | 10.3403 | 8.5971 | 7.1696 | 14.0426 | 13.7435 | 13.4837 | 13.1833 | 12.8176 | 12.4087 | 11.9625 | 11.478 | 10.9458 | 10.0943 | 7.4085 | 3.4065 | 0.7309 | -0.67075
|  | PORTSMOUTH | LW |  |  | 12.6418 | 12.2098 | 11.7712 | 11.4082 | 10.8363 | 10.2134 | 9.5354 | 8.8154 | 7.9789 | 7.0425 | 4.2426 | 0.92135 | -0.48595 | -1.2543 | 15.9339 | 15.7816 | 15.6457 | 15.5192 | 15.3774 | 15.2108 | 15.0122 | 14.7907 | 14.5154 | 14.0723 | 12.3442 | 10.507 | 9.8519 | 9.4839 | 13.9384 | 13.5706 | 13.1785 | 12.8397 | 12.3123 | 11.7378 | 11.1092 | 10.4394 | 9.6557 | 8.774 | 6.1448 | 3.1065 | 1.8757 | 1.2159
|  | PORTSMOUTH | ST |  |  | 12.9284 | 12.7109 | 12.5509 | 12.4435 | 12.29 | 12.11 | 11.9028 | 11.6803 | 11.4187 | 11.137 | 10.0073 | 6.8199 | 5.0139 | 3.796 | 15.9954 | 15.8942 | 15.8235 | 15.769 | 15.7069 | 15.6308 | 15.541 | 15.4389 | 15.3075 | 15.1487 | 14.5121 | 12.8177 | 11.4923 | 10.1751 | 14.2015 | 14.0316 | 13.9016 | 13.8044 | 13.6589 | 13.4896 | 13.2942 | 13.0832 | 12.8323 | 12.5649 | 11.4826 | 8.4632 | 6.8392 | 5.7805
|  | PORTSMOUTH | SP |  |  | 12.9529 | 12.732 | 12.5703 | 12.4602 | 12.3282 | 12.1805 | 12.031 | 11.853 | 11.6667 | 11.4384 | 10.5952 | 8.2511 | 6.5167 | 5.7922 | 15.9997 | 15.901 | 15.8323 | 15.7827 | 15.7365 | 15.6809 | 15.6202 | 15.5499 | 15.4683 | 15.369 | 15.0095 | 13.5762 | 11.3757 | 8.991 | 14.2237 | 14.0488 | 13.9157 | 13.8146 | 13.6921 | 13.556 | 13.4188 | 13.2531 | 13.078 | 12.8636 | 12.0645 | 9.8346 | 8.2094 | 7.5709
BRAMLEY (ANDO-THAT) | ANDOVER BSP | PORTWAY | MINIMUM HEADROOM | SU 34402 46001 | YES | 27.6095 | 26.821 | 26.1874 | 25.3766 | 24.0581 | 22.6394 | 21.5017 | 20.2881 | 18.6224 | 16.9106 | 11.1857 | 3.3541 | 0.84513 | -1.1129 | 32.0835 | 31.7273 | 31.3916 | 30.9341 | 30.2448 | 29.5017 | 28.9076 | 28.2652 | 27.3843 | 26.406 | 23.0639 | 17.233 | 13.0513 | 4.072 | 28.0796 | 27.4416 | 26.9132 | 26.239 | 25.1419 | 23.9583 | 22.9924 | 21.9594 | 20.5491 | 19.0985 | 14.255 | 7.6858 | 5.648 | 4.0137
|  | PORTWAY | CT |  |  | 27.8062 | 27.1258 | 26.6161 | 25.9055 | 24.7462 | 23.493 | 22.5696 | 21.5769 | 20.1508 | 18.4949 | 12.9343 | 4.2779 | 0.84513 | -1.1129 | 32.0835 | 31.7321 | 31.3916 | 30.9341 | 30.2448 | 29.5017 | 28.9076 | 28.2652 | 27.3843 | 26.406 | 23.0639 | 17.233 | 13.0513 | 7.651 | 28.2511 | 27.7083 | 27.2908 | 26.7036 | 25.7469 | 24.7097 | 23.9342 | 23.0979 | 21.9037 | 20.5074 | 15.8289 | 8.5527 | 5.648 | 4.0137
|  | PORTWAY | LW |  |  | 27.6095 | 26.821 | 26.1874 | 25.3766 | 24.0581 | 22.6394 | 21.5017 | 20.2881 | 18.6224 | 16.9106 | 11.1857 | 3.3541 | 1.1124 | -0.31289 | 32.1059 | 31.7273 | 31.3954 | 30.9725 | 30.3093 | 29.5967 | 29.0231 | 28.4116 | 27.5582 | 26.6702 | 23.6768 | 19.5783 | 18.4811 | 17.7697 | 28.0796 | 27.4416 | 26.9132 | 26.239 | 25.1419 | 23.9583 | 22.9924 | 21.9594 | 20.5491 | 19.0985 | 14.255 | 7.6858 | 5.8307 | 4.663
|  | PORTWAY | ST |  |  | 27.9838 | 27.5684 | 27.2881 | 26.9162 | 26.2513 | 25.5338 | 25.0161 | 24.4579 | 23.6201 | 22.7047 | 19.4247 | 13.6734 | 11.3482 | 9.9786 | 32.1323 | 31.9467 | 31.7395 | 31.4533 | 30.9714 | 30.4523 | 30.0367 | 29.5833 | 28.9525 | 28.29 | 25.8996 | 21.0214 | 17.0824 | 11.9115 | 28.4136 | 28.1142 | 27.9056 | 27.6275 | 27.1105 | 26.5385 | 26.1145 | 25.6546 | 24.9682 | 24.2201 | 21.5459 | 16.7659 | 14.7894 | 13.6696
|  | PORTWAY | SP |  |  | 28.0127 | 27.6254 | 27.3745 | 27.0434 | 26.5235 | 25.9653 | 25.5414 | 25.0973 | 24.4364 | 23.6706 | 20.9986 | 16.2372 | 13.8692 | 12.5398 | 32.1301 | 31.9476 | 31.7452 | 31.461 | 31.0226 | 30.5399 | 30.1021 | 29.6285 | 28.9894 | 28.3049 | 25.8356 | 20.4673 | 14.1159 | 4.072 | 28.4395 | 28.1654 | 27.9837 | 27.7428 | 27.3619 | 26.9352 | 26.5805 | 26.2084 | 25.6577 | 25.0356 | 22.8767 | 18.8986 | 16.9351 | 15.8734
IVER 132KV | LONGFORD | POYLE | MINIMUM HEADROOM | TQ 03425 75555 | YES | 15.1718 | 15.0203 | 14.7251 | 14.3588 | 13.9354 | 13.4434 | 12.8819 | 12.1881 | 11.2825 | 10.2365 | 6.495 | 2.7106 | 2.1389 | 1.8706 | 19.4893 | 19.3815 | 19.1195 | 18.7988 | 18.4288 | 17.9929 | 17.5023 | 16.8604 | 16.0226 | 15.0473 | 11.816 | 9.0653 | 8.7849 | 8.6322 | 17.1697 | 16.9505 | 16.5912 | 16.1744 | 15.5968 | 14.9626 | 14.2752 | 13.5347 | 12.5785 | 11.5108 | 7.7898 | 4.1836 | 3.6629 | 3.4168
|  | POYLE | CT |  |  | 15.1718 | 15.0203 | 14.7276 | 14.3719 | 13.9689 | 13.5101 | 13.0087 | 12.4485 | 11.7062 | 10.8263 | 7.9233 | 4.2681 | 2.7693 | 2.1519 | 19.4893 | 19.3815 | 19.1195 | 18.7988 | 18.4338 | 18.0162 | 17.5614 | 17.0686 | 16.4791 | 15.6907 | 12.9913 | 10.0839 | 9.4073 | 9.1263 | 17.2794 | 17.1316 | 16.8411 | 16.4909 | 16.0363 | 15.5326 | 14.9999 | 14.4251 | 13.7648 | 12.8924 | 9.6984 | 5.6554 | 4.2947 | 3.7428
|  | POYLE | LW |  |  | 15.1907 | 15.0245 | 14.7251 | 14.3588 | 13.9354 | 13.4434 | 12.8819 | 12.1881 | 11.2825 | 10.2365 | 6.495 | 2.7106 | 2.1389 | 1.8706 | 19.5059 | 19.3913 | 19.1273 | 18.8036 | 18.4288 | 17.9929 | 17.5023 | 16.8604 | 16.0226 | 15.0473 | 11.816 | 9.0653 | 8.7849 | 8.6322 | 17.1697 | 16.9505 | 16.5912 | 16.1744 | 15.5968 | 14.9626 | 14.2752 | 13.5347 | 12.5785 | 11.5108 | 7.7898 | 4.1836 | 3.6629 | 3.4168
|  | POYLE | ST |  |  | 15.2871 | 15.2119 | 15.0082 | 14.7613 | 14.462 | 14.1111 | 13.7221 | 13.2934 | 12.768 | 12.1451 | 9.5629 | 5.2361 | 3.4354 | 3.1376 | 19.5671 | 19.511 | 19.309 | 19.0627 | 18.7671 | 18.4216 | 18.0424 | 17.6288 | 17.142 | 16.5707 | 14.3653 | 10.6499 | 9.0951 | 8.8351 | 17.3871 | 17.3115 | 17.1018 | 16.8504 | 16.535 | 16.1717 | 15.7766 | 15.3476 | 14.8481 | 14.2503 | 11.8018 | 7.1676 | 5.2186 | 4.8963
|  | POYLE | SP |  |  | 15.2966 | 15.2283 | 15.033 | 14.7985 | 14.5269 | 14.2123 | 13.8701 | 13.4955 | 13.0646 | 12.5627 | 10.8223 | 7.7846 | 5.2848 | 4.6721 | 19.5728 | 19.5206 | 19.3235 | 19.0848 | 18.8088 | 18.4884 | 18.1415 | 17.7645 | 17.3416 | 16.8497 | 15.1874 | 12.8159 | 10.6314 | 10.0869 | 17.4088 | 17.345 | 17.1497 | 16.9158 | 16.6088 | 16.2587 | 15.8862 | 15.4839 | 15.0357 | 14.5018 | 12.7147 | 9.8543 | 7.1206 | 6.4446
MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON SE | MINIMUM HEADROOM | SU 16963 86368 | YES | 12.219 | 12.0174 | 11.7743 | 11.4812 | 11.1308 | 10.5051 | 9.7383 | 8.8761 | 7.8187 | 6.5488 | 2.1616 | -3.3127 | -4.6331 | -5.3662 | 16.211 | 16.0926 | 15.9539 | 15.7828 | 15.5706 | 15.1948 | 14.7399 | 14.2197 | 13.4692 | 12.5412 | 9.2463 | 5.2801 | 4.4146 | 3.9087 | 13.1589 | 12.8955 | 12.5851 | 12.153 | 11.5534 | 10.8727 | 10.0822 | 9.2003 | 8.1365 | 6.8613 | 2.4871 | -2.7271 | -3.9586 | -4.6432
|  | PRESSED STEEL SWINDON SE | CT |  |  | 12.219 | 12.0222 | 11.7933 | 11.5178 | 11.2071 | 10.8544 | 10.3655 | 9.7326 | 9.0131 | 8.0461 | 4.7083 | -1.1138 | -3.5879 | -4.89 | 16.211 | 16.0926 | 15.9561 | 15.7886 | 15.603 | 15.3215 | 14.9617 | 14.5578 | 14.0846 | 13.4369 | 11.03 | 6.845 | 5.3832 | 4.5329 | 13.2267 | 13.0375 | 12.7786 | 12.4055 | 11.9391 | 11.4197 | 10.8492 | 10.2196 | 9.5151 | 8.5409 | 5.2036 | -0.62645 | -2.9215 | -4.1286
|  | PRESSED STEEL SWINDON SE | LW |  |  | 12.2385 | 12.0174 | 11.7743 | 11.4812 | 11.1308 | 10.5051 | 9.7383 | 8.8761 | 7.8187 | 6.5488 | 2.1616 | -3.3127 | -4.6331 | -5.3662 | 16.2254 | 16.0969 | 15.9539 | 15.7828 | 15.5706 | 15.1948 | 14.7399 | 14.2197 | 13.4692 | 12.5412 | 9.2463 | 5.2801 | 4.4146 | 3.9087 | 13.1589 | 12.8955 | 12.5851 | 12.153 | 11.5534 | 10.8727 | 10.0822 | 9.2003 | 8.1365 | 6.8613 | 2.4871 | -2.7271 | -3.9586 | -4.6432
|  | PRESSED STEEL SWINDON SE | ST |  |  | 12.3854 | 12.2963 | 12.1991 | 12.0856 | 11.9291 | 11.7453 | 11.5251 | 11.2639 | 10.917 | 10.47 | 8.0588 | 1.4479 | -2.0146 | -3.2462 | 16.3068 | 16.2503 | 16.1889 | 16.118 | 16.0218 | 15.9103 | 15.777 | 15.6201 | 15.3951 | 14.9868 | 13.304 | 8.1742 | 5.5134 | 4.5751 | 13.4206 | 13.3399 | 13.2439 | 13.1324 | 12.966 | 12.7824 | 12.5181 | 12.1779 | 11.7384 | 11.1397 | 8.7665 | 2.3697 | -0.99007 | -2.1687
|  | PRESSED STEEL SWINDON SE | SP |  |  | 12.3995 | 12.324 | 12.2427 | 12.1497 | 12.0384 | 11.9095 | 11.7647 | 11.5979 | 11.3913 | 11.1339 | 10.1421 | 5.6329 | 1.1126 | -0.35016 | 16.3148 | 16.2641 | 16.2107 | 16.15 | 16.0803 | 16.0003 | 15.9108 | 15.8071 | 15.6795 | 15.5217 | 14.7386 | 11.4152 | 7.9279 | 6.7659 | 13.5216 | 13.4445 | 13.365 | 13.2727 | 13.1536 | 13.0193 | 12.8548 | 12.6298 | 12.3607 | 11.995 | 10.7468 | 6.3533 | 1.992 | 0.61332
BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER | MINIMUM HEADROOM | SU 60879 41131 | YES | 4.4463 | 4.2162 | 3.8358 | 3.5031 | 3.0339 | 2.5359 | 1.9883 | 1.4312 | 0.75854 | 0.11001 | -2.7045 | -5.6657 | -8.4829 | -10.2328 | 4.1026 | 3.8847 | 3.5324 | 3.2269 | 2.7282 | 2.1771 | 1.597 | 1.0258 | 0.37058 | -0.27001 | -2.3683 | -4.2159 | -5.6844 | -6.948 | 2.067 | 1.78 | 1.3296 | 0.91701 | 0.22163 | -0.53139 | -1.3279 | -2.1149 | -3.026 | -3.9621 | -6.7773 | -9.4582 | -11.9156 | -13.3989
|  | PRESTON CANDOVER | CT |  |  | 4.4463 | 4.2162 | 3.8454 | 3.5069 | 3.044 | 2.5565 | 2.0273 | 1.5375 | 0.95349 | 0.38214 | -2.0078 | -5.6657 | -8.4829 | -10.2328 | 4.1215 | 3.9171 | 3.5977 | 3.2926 | 2.8415 | 2.342 | 1.8212 | 1.3105 | 0.73339 | 0.084161 | -2.156 | -4.2159 | -5.6844 | -6.948 | 2.1271 | 1.8827 | 1.5128 | 1.121 | 0.54826 | -0.074626 | -0.72661 | -1.3658 | -2.0974 | -3.0444 | -6.0937 | -9.4582 | -11.9156 | -13.3989
|  | PRESTON CANDOVER | LW |  |  | 4.4519 | 4.2195 | 3.8358 | 3.5031 | 3.0339 | 2.5359 | 1.9883 | 1.4312 | 0.75854 | 0.11001 | -2.7045 | -5.5971 | -7.3184 | -8.454 | 4.1026 | 3.8847 | 3.5324 | 3.2269 | 2.7282 | 2.1771 | 1.597 | 1.0258 | 0.37058 | -0.27001 | -2.3683 | -3.9771 | -4.7535 | -5.3331 | 2.067 | 1.78 | 1.3296 | 0.91701 | 0.22163 | -0.53139 | -1.3279 | -2.1149 | -3.026 | -3.9621 | -6.7773 | -9.3912 | -10.8389 | -11.7545
|  | PRESTON CANDOVER | ST |  |  | 4.478 | 4.2678 | 3.9208 | 3.6296 | 3.2011 | 2.7497 | 2.2597 | 1.8117 | 1.2716 | 0.79216 | -1.135 | -2.8378 | -3.6442 | -4.9054 | 4.1686 | 3.9939 | 3.71 | 3.4781 | 3.105 | 2.686 | 2.2431 | 1.8057 | 1.3059 | 0.87293 | -0.90662 | -2.6874 | -3.7157 | -4.8302 | 2.2151 | 2.0266 | 1.7229 | 1.4673 | 1.0541 | 0.59566 | 0.11395 | -0.34427 | -0.88131 | -1.3676 | -3.3762 | -5.9726 | -7.3274 | -8.424
|  | PRESTON CANDOVER | SP |  |  | 4.4796 | 4.2672 | 3.9194 | 3.63 | 3.2145 | 2.779 | 2.3091 | 1.8814 | 1.369 | 0.91659 | -0.86871 | -2.3824 | -3.2363 | -3.7716 | 4.1722 | 3.9928 | 3.7054 | 3.4731 | 3.1175 | 2.7174 | 2.2814 | 1.8598 | 1.3817 | 0.96615 | -0.7174 | -2.2573 | -3.7128 | -5.3022 | 2.2247 | 2.0286 | 1.7213 | 1.4681 | 1.0865 | 0.6619 | 0.22621 | -0.1932 | -0.67742 | -1.1183 | -2.8734 | -4.9871 | -6.1654 | -6.821
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN | MINIMUM HEADROOM | SY 74226 95039 | YES | 9.1193 | 8.6264 | 7.9959 | 7.307 | 6.4749 | 5.6599 | 4.9743 | 4.2096 | 3.3413 | 2.5165 | 0.34477 | -1.2916 | -1.5546 | -1.6405 | 11.7105 | 11.5584 | 11.2766 | 10.9529 | 10.5707 | 10.0765 | 9.6339 | 9.1313 | 8.5471 | 7.9841 | 6.4933 | 5.514 | 5.3914 | 5.3293 | 9.4248 | 8.996 | 8.4438 | 7.8383 | 7.1061 | 6.3817 | 5.7553 | 5.0534 | 4.2519 | 3.4939 | 1.5034 | -0.03817 | -0.27994 | -0.35892
|  | PUDDLETOWN | CT |  |  | 9.3728 | 9.017 | 8.5069 | 7.951 | 7.282 | 6.6306 | 6.1106 | 5.5303 | 4.9 | 4.1095 | 2.1655 | 0.30914 | -0.45859 | -0.6337 | 11.7436 | 11.6152 | 11.3517 | 11.0483 | 10.7006 | 10.3317 | 9.9834 | 9.5863 | 9.1222 | 8.5469 | 7.1495 | 6.054 | 5.5957 | 5.3293 | 9.6444 | 9.3358 | 8.8873 | 8.3978 | 7.8106 | 7.2318 | 6.7531 | 6.2176 | 5.6363 | 4.9031 | 3.131 | 1.4663 | 0.75629 | 0.5926
|  | PUDDLETOWN | LW |  |  | 9.1193 | 8.6264 | 7.9959 | 7.307 | 6.4749 | 5.6599 | 4.9743 | 4.2096 | 3.3413 | 2.5165 | 0.34477 | -1.2916 | -1.5546 | -1.6405 | 11.7105 | 11.5584 | 11.2766 | 10.9529 | 10.5707 | 10.0765 | 9.6339 | 9.1313 | 8.5471 | 7.9841 | 6.4933 | 5.514 | 5.3914 | 5.3463 | 9.4248 | 8.996 | 8.4438 | 7.8383 | 7.1061 | 6.3817 | 5.7553 | 5.0534 | 4.2519 | 3.4939 | 1.5034 | -0.03817 | -0.27994 | -0.35892
|  | PUDDLETOWN | ST |  |  | 9.5525 | 9.3332 | 8.9781 | 8.5744 | 8.0793 | 7.5881 | 7.1828 | 6.743 | 6.258 | 5.7215 | 3.7975 | 2.3316 | 1.7583 | 1.4217 | 11.7905 | 11.6947 | 11.4687 | 11.2066 | 10.9032 | 10.5758 | 10.265 | 9.9294 | 9.5648 | 9.1349 | 7.7008 | 6.6644 | 6.3504 | 6.2145 | 9.8158 | 9.6359 | 9.3324 | 8.9831 | 8.5529 | 8.1192 | 7.7472 | 7.3433 | 6.8979 | 6.406 | 4.6194 | 3.2673 | 2.7535 | 2.4563
|  | PUDDLETOWN | SP |  |  | 9.5891 | 9.3966 | 9.0832 | 8.7308 | 8.2572 | 7.788 | 7.3845 | 6.9459 | 6.4758 | 5.9017 | 4.0182 | 1.776 | 0.73418 | 0.11052 | 11.7958 | 11.7047 | 11.485 | 11.2322 | 10.9333 | 10.6155 | 10.3104 | 9.9823 | 9.6329 | 9.2156 | 7.8687 | 6.7391 | 6.1754 | 5.799 | 9.8476 | 9.6918 | 9.4272 | 9.1261 | 8.7187 | 8.3079 | 7.9403 | 7.5394 | 7.1108 | 6.5874 | 4.859 | 2.7858 | 1.8483 | 1.2946
AXMINSTER | YEOVIL BSP | PULHAM | MINIMUM HEADROOM | ST 71579 09451 | YES | 3.3343 | 3.167 | 2.9921 | 2.8116 | 2.5567 | 2.304 | 2.0431 | 1.7696 | 1.4428 | 1.1252 | 0.3716 | -0.43255 | -0.59841 | -0.71186 | 4.0585 | 3.9824 | 3.9011 | 3.8155 | 3.6986 | 3.5812 | 3.456 | 3.3225 | 3.1462 | 2.9791 | 2.639 | 2.2833 | 2.2135 | 2.091 | 3.3266 | 3.1745 | 3.016 | 2.8524 | 2.6209 | 2.3915 | 2.1551 | 1.9076 | 1.6149 | 1.3289 | 0.63806 | -0.10022 | -0.25153 | -0.35505
|  | PULHAM | CT |  |  | 3.5101 | 3.4336 | 3.3486 | 3.2559 | 3.1149 | 2.9711 | 2.82 | 2.6553 | 2.4696 | 2.1949 | 1.5624 | 0.52644 | 0.050188 | -0.014558 | 4.1193 | 4.0753 | 4.0246 | 3.9675 | 3.8946 | 3.8179 | 3.7351 | 3.6428 | 3.5329 | 3.3766 | 3.0617 | 2.5964 | 2.3639 | 2.2628 | 3.4886 | 3.42 | 3.3441 | 3.2617 | 3.1344 | 3.0049 | 2.8689 | 2.7213 | 2.5559 | 2.3107 | 1.7357 | 0.78309 | 0.34604 | 0.28716
|  | PULHAM | LW |  |  | 3.3343 | 3.167 | 2.9921 | 2.8116 | 2.5567 | 2.304 | 2.0431 | 1.7696 | 1.4428 | 1.1252 | 0.3716 | -0.43255 | -0.59841 | -0.71186 | 4.0585 | 3.9824 | 3.9011 | 3.8155 | 3.6986 | 3.5812 | 3.456 | 3.3225 | 3.1462 | 2.9791 | 2.639 | 2.2833 | 2.2135 | 2.168 | 3.3266 | 3.1745 | 3.016 | 2.8524 | 2.6209 | 2.3915 | 2.1551 | 1.9076 | 1.6149 | 1.3289 | 0.63806 | -0.10022 | -0.25153 | -0.35505
|  | PULHAM | ST |  |  | 3.5531 | 3.5037 | 3.4492 | 3.3916 | 3.3024 | 3.2115 | 3.1165 | 3.016 | 2.9078 | 2.7903 | 2.3167 | 1.5746 | 1.144 | 0.85742 | 4.1484 | 4.1225 | 4.0923 | 4.0593 | 4.013 | 3.9654 | 3.9138 | 3.8581 | 3.7952 | 3.7323 | 3.4467 | 3.0137 | 2.7842 | 2.601 | 3.5264 | 3.4817 | 3.4327 | 3.3811 | 3.3006 | 3.2186 | 3.1331 | 3.0427 | 2.9458 | 2.8394 | 2.417 | 1.7452 | 1.3494 | 1.0865
|  | PULHAM | SP |  |  | 3.5774 | 3.5405 | 3.5017 | 3.4631 | 3.3415 | 3.2183 | 3.0902 | 2.957 | 2.8218 | 2.6481 | 2.0747 | 0.81462 | 0.077944 | -0.38026 | 4.158 | 4.1361 | 4.1123 | 4.0883 | 4.0341 | 3.9782 | 3.9182 | 3.8541 | 3.7874 | 3.7062 | 3.4196 | 2.736 | 2.3572 | 2.091 | 3.5486 | 3.5155 | 3.4808 | 3.4462 | 3.3353 | 3.2231 | 3.1065 | 2.9857 | 2.8632 | 2.705 | 2.1864 | 1.0517 | 0.37677 | -0.043218
LOVEDEAN GSP | FORT WIDLEY | PURBROOK | MINIMUM HEADROOM | SU 67047 07819 | NO | 2.2373 | 1.9626 | 1.7218 | 1.4944 | 1.1897 | 0.88632 | 0.53397 | 0.10103 | -0.44481 | -0.90677 | -1.8529 | -2.9166 | -3.1513 | -3.3436 | 1.5768 | 1.389 | 1.2242 | 1.0727 | 0.88404 | 0.69435 | 0.49762 | 0.27765 | -0.0065308 | -0.24206 | -0.68844 | -1.1983 | -1.3153 | -1.4035 | 0.5806 | 0.28335 | 0.00099302 | -0.26898 | -0.61987 | -0.97707 | -1.3409 | -1.74 | -2.2387 | -2.6636 | -3.5614 | -4.5694 | -4.7841 | -4.9547
|  | PURBROOK | CT |  |  | 2.5188 | 2.3895 | 2.287 | 2.1963 | 2.0404 | 1.882 | 1.6337 | 1.3468 | 1.0066 | 0.59002 | -0.16164 | -1.4451 | -2.1742 | -2.4343 | 1.677 | 1.5458 | 1.4402 | 1.334 | 1.2083 | 1.081 | 0.94608 | 0.78846 | 0.59855 | 0.37483 | -0.0032029 | -0.64371 | -1.0301 | -1.2417 | 0.81979 | 0.65418 | 0.50624 | 0.34966 | 0.14133 | -0.07382 | -0.30209 | -0.56433 | -0.87273 | -1.2508 | -1.9566 | -3.1739 | -3.8635 | -4.1087
|  | PURBROOK | LW |  |  | 2.2373 | 1.9626 | 1.7218 | 1.4944 | 1.1897 | 0.88632 | 0.53397 | 0.10103 | -0.44481 | -0.90677 | -1.8529 | -2.9166 | -3.1513 | -3.3436 | 1.5768 | 1.389 | 1.2242 | 1.0727 | 0.88404 | 0.69435 | 0.49762 | 0.27765 | -0.0065308 | -0.24206 | -0.68844 | -1.1983 | -1.3153 | -1.4035 | 0.5806 | 0.28335 | 0.00099302 | -0.26898 | -0.61987 | -0.97707 | -1.3409 | -1.74 | -2.2387 | -2.6636 | -3.5614 | -4.5694 | -4.7841 | -4.9547
|  | PURBROOK | ST |  |  | 2.5597 | 2.4532 | 2.372 | 2.3015 | 2.1836 | 2.0695 | 1.9565 | 1.8444 | 1.7355 | 1.5789 | 0.7909 | -0.16454 | -0.70648 | -1.0602 | 1.72 | 1.6149 | 1.5383 | 1.4733 | 1.3821 | 1.2969 | 1.2071 | 1.1127 | 1.0088 | 0.91034 | 0.47514 | -0.069676 | -0.38981 | -0.64294 | 0.89204 | 0.76964 | 0.66803 | 0.57492 | 0.42587 | 0.28112 | 0.13177 | -0.022982 | -0.18877 | -0.35911 | -1.0745 | -1.9649 | -2.4791 | -2.8133
|  | PURBROOK | SP |  |  | 2.6161 | 2.5307 | 2.4717 | 2.424 | 2.2774 | 2.1352 | 1.9964 | 1.8503 | 1.7076 | 1.499 | 0.75765 | -1.0852 | -2.0448 | -2.695 | 1.7412 | 1.6414 | 1.5749 | 1.5217 | 1.4291 | 1.3413 | 1.2574 | 1.1603 | 1.0637 | 0.94412 | 0.52633 | -0.43468 | -0.91838 | -1.2555 | 0.94149 | 0.83382 | 0.75489 | 0.68723 | 0.52597 | 0.36765 | 0.21741 | 0.046716 | -0.12114 | -0.3511 | -1.1262 | -2.8207 | -3.7303 | -4.3448
MINETY GSP | TOOTHILL BSP | QUARRY ROAD | MINIMUM HEADROOM | SU 15334 83380 | YES | 12.6137 | 12.3656 | 11.9923 | 11.589 | 10.999 | 10.2897 | 9.5436 | 8.7327 | 7.8192 | 6.852 | 4.5952 | 1.5838 | -1.3112 | -3.328 | 5.3979 | 5.2676 | 5.068 | 4.8523 | 4.5535 | 4.1916 | 3.8073 | 3.3814 | 2.8587 | 2.2995 | 1.0939 | -0.77951 | -2.6496 | -4.3931 | 1.775 | 1.6793 | 1.5475 | 1.4042 | 1.1151 | 0.70994 | 0.2916 | -0.15941 | -0.63354 | -1.358 | -3.3764 | -6.0018 | -8.3917 | -10.0216
|  | QUARRY ROAD | CT |  |  | 12.7077 | 12.5239 | 12.2534 | 11.8862 | 11.4436 | 10.8927 | 10.3136 | 9.6774 | 9.0133 | 8.0309 | 5.5613 | 1.7911 | -1.3112 | -3.328 | 5.4268 | 5.3161 | 5.1575 | 4.9425 | 4.6969 | 4.3939 | 4.0733 | 3.7112 | 3.3044 | 2.718 | 1.2918 | -0.77951 | -2.6496 | -4.3931 | 1.8051 | 1.7323 | 1.6269 | 1.5014 | 1.3428 | 1.1421 | 0.83722 | 0.50279 | 0.17337 | -0.33385 | -2.512 | -5.7918 | -8.3917 | -10.0216
|  | QUARRY ROAD | LW |  |  | 12.6137 | 12.3656 | 11.9923 | 11.589 | 10.999 | 10.2897 | 9.5436 | 8.7327 | 7.8192 | 6.852 | 4.5952 | 1.5838 | -0.26992 | -1.6725 | 5.3979 | 5.2676 | 5.068 | 4.8523 | 4.5535 | 4.1916 | 3.8073 | 3.3814 | 2.8587 | 2.2995 | 1.0939 | -0.4419 | -1.3294 | -2.0289 | 1.775 | 1.6793 | 1.5475 | 1.4042 | 1.1151 | 0.70994 | 0.2916 | -0.15941 | -0.63354 | -1.358 | -3.3764 | -6.0018 | -7.5503 | -8.704
|  | QUARRY ROAD | ST |  |  | 12.8273 | 12.733 | 12.5843 | 12.4176 | 12.1955 | 11.8998 | 11.5929 | 11.2539 | 10.9184 | 10.5865 | 9.1473 | 6.4645 | 4.7718 | 3.3994 | 5.4939 | 5.4324 | 5.339 | 5.234 | 5.0978 | 4.9193 | 4.7325 | 4.5259 | 4.3179 | 4.1094 | 3.1421 | 1.2382 | -0.097164 | -1.5896 | 1.8534 | 1.8141 | 1.7547 | 1.6901 | 1.6119 | 1.5021 | 1.3898 | 1.2647 | 1.1413 | 1.0034 | 0.37795 | -1.7552 | -3.1336 | -4.2274
|  | QUARRY ROAD | SP |  |  | 12.8412 | 12.7411 | 12.602 | 12.4509 | 12.2573 | 12.019 | 11.7545 | 11.4615 | 11.1875 | 10.8867 | 9.7603 | 7.0353 | 5.4343 | 4.3654 | 5.4983 | 5.4311 | 5.3392 | 5.2387 | 5.1212 | 4.9758 | 4.8132 | 4.6319 | 4.4584 | 4.2495 | 3.4378 | 1.2236 | -0.75813 | -3.2992 | 1.8569 | 1.8188 | 1.7638 | 1.7053 | 1.6307 | 1.5355 | 1.4356 | 1.3259 | 1.2262 | 1.1098 | 0.64569 | -1.2563 | -2.6464 | -3.5117
BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD | MINIMUM HEADROOM | SU 87062 55683 | YES | 11.5361 | 11.014 | 10.4095 | 9.7176 | 8.7136 | 7.6636 | 6.535 | 5.3046 | 3.9171 | 2.5469 | -1.3638 | -6.3446 | -9.6901 | -12.2095 | 10.7862 | 10.4558 | 10.074 | 9.6282 | 9.0523 | 8.443 | 7.773 | 7.0486 | 6.2202 | 5.3867 | 2.9587 | -1.1016 | -4.652 | -8.7989 | 6.6137 | 6.1311 | 5.568 | 4.9379 | 4.0136 | 3.0528 | 2.0069 | 0.87588 | -0.41257 | -1.6995 | -5.3667 | -9.8777 | -12.6604 | -14.7814
|  | QUEENSMEAD | CT |  |  | 11.6587 | 11.2242 | 10.7171 | 10.0903 | 9.308 | 8.4915 | 7.6489 | 6.7271 | 5.7061 | 4.4102 | 0.53947 | -5.4956 | -9.6901 | -12.2095 | 10.7936 | 10.4627 | 10.0803 | 9.6282 | 9.0818 | 8.5215 | 7.9231 | 7.2755 | 6.5581 | 5.6914 | 3.0396 | -1.1016 | -4.652 | -8.5624 | 6.7165 | 6.3108 | 5.8347 | 5.2592 | 4.532 | 3.7798 | 2.9918 | 2.1409 | 1.1926 | -0.016486 | -3.6323 | -9.05 | -12.6604 | -14.7814
|  | QUEENSMEAD | LW |  |  | 11.5361 | 11.014 | 10.4095 | 9.7176 | 8.7136 | 7.6636 | 6.535 | 5.3046 | 3.9171 | 2.5469 | -1.3638 | -6.3446 | -8.8588 | -10.5088 | 10.7862 | 10.4558 | 10.074 | 9.6452 | 9.0523 | 8.443 | 7.773 | 7.0486 | 6.2202 | 5.3867 | 2.9587 | 0.12571 | -1.1169 | -1.9638 | 6.6137 | 6.1311 | 5.568 | 4.9379 | 4.0136 | 3.0528 | 2.0069 | 0.87588 | -0.41257 | -1.6995 | -5.3667 | -9.8777 | -12.0009 | -13.3591
|  | QUEENSMEAD | ST |  |  | 11.952 | 11.7125 | 11.4348 | 11.0936 | 10.6711 | 10.2377 | 9.7622 | 9.2272 | 8.6389 | 8.0882 | 6.0012 | 1.1046 | -1.8164 | -3.7221 | 10.964 | 10.7443 | 10.4923 | 10.2024 | 9.8392 | 9.4739 | 9.0646 | 8.6148 | 8.1204 | 7.6667 | 5.9612 | 1.8537 | -1.3822 | -5.036 | 6.9922 | 6.7704 | 6.5093 | 6.2042 | 5.808 | 5.4091 | 4.9611 | 4.4704 | 3.9284 | 3.4171 | 1.4323 | -3.1339 | -5.6863 | -7.2666
|  | QUEENSMEAD | SP |  |  | 11.9829 | 11.7478 | 11.4838 | 11.1687 | 10.8215 | 10.4746 | 10.0917 | 9.6507 | 9.1931 | 8.7596 | 7.2812 | 3.3866 | 0.26706 | -1.2839 | 10.9715 | 10.7487 | 10.4934 | 10.206 | 9.8754 | 9.5448 | 9.1718 | 8.7568 | 8.3161 | 7.8864 | 6.3676 | 2.2775 | -2.5639 | -8.7989 | 7.0191 | 6.7982 | 6.5473 | 6.2647 | 5.9396 | 5.6219 | 5.2601 | 4.8559 | 4.4348 | 4.0344 | 2.6472 | -0.9932 | -3.8164 | -5.1183
MELKSHAM GSP | WEST GRAFTON | RAMSBURY | MINIMUM HEADROOM | SU 27380 72108 | YES | 5.5207 | 5.2045 | 4.5886 | 4.2537 | 3.7516 | 2.7727 | 1.7162 | 0.6712 | -0.48049 | -1.5364 | -3.8328 | -6.7745 | -8.3306 | -9.843 | 7.7021 | 7.5063 | 7.1273 | 6.9097 | 6.6258 | 6.0987 | 5.5086 | 4.9116 | 4.1959 | 3.52 | 2.0782 | 0.28389 | -1.2738 | -2.7844 | 5.9868 | 5.7098 | 5.1603 | 4.8466 | 4.3811 | 3.5275 | 2.6031 | 1.6782 | 0.6213 | -0.36414 | -2.4934 | -5.1335 | -6.3465 | -7.5523
|  | RAMSBURY | CT |  |  | 5.6317 | 5.3874 | 4.8548 | 4.5777 | 4.2191 | 3.3929 | 2.5336 | 1.6919 | 0.78334 | -0.25134 | -2.4914 | -5.9288 | -8.3306 | -9.843 | 7.7094 | 7.5223 | 7.1627 | 6.9377 | 6.6897 | 6.2042 | 5.693 | 5.1734 | 4.5809 | 3.9127 | 2.437 | 0.28389 | -1.2738 | -2.7844 | 6.0578 | 5.8322 | 5.3493 | 5.072 | 4.739 | 4.0349 | 3.2821 | 2.5346 | 1.7101 | 0.7622 | -1.3021 | -4.3498 | -6.3276 | -7.5523
|  | RAMSBURY | LW |  |  | 5.5207 | 5.2045 | 4.5886 | 4.2537 | 3.7516 | 2.7727 | 1.7162 | 0.6712 | -0.48049 | -1.5364 | -3.8328 | -6.7745 | -8.2556 | -9.364 | 7.7021 | 7.5063 | 7.1273 | 6.9097 | 6.6258 | 6.0987 | 5.5086 | 4.9116 | 4.1959 | 3.52 | 2.0782 | 0.353 | -0.36202 | -0.91312 | 5.9868 | 5.7098 | 5.1603 | 4.8466 | 4.3811 | 3.5275 | 2.6031 | 1.6782 | 0.6213 | -0.36414 | -2.4934 | -5.1335 | -6.3465 | -7.2452
|  | RAMSBURY | ST |  |  | 5.8065 | 5.6845 | 5.3721 | 5.2599 | 5.0933 | 4.6222 | 4.1107 | 3.6186 | 3.0913 | 2.5949 | 1.0897 | -2.0838 | -3.9485 | -4.9991 | 7.8257 | 7.72 | 7.4891 | 7.3838 | 7.2408 | 6.9177 | 6.567 | 6.223 | 5.8473 | 5.504 | 4.3558 | 1.8756 | 0.27661 | -1.0699 | 6.2231 | 6.1136 | 5.8292 | 5.7153 | 5.5497 | 5.1359 | 4.6875 | 4.2518 | 3.7827 | 3.3472 | 1.9534 | -0.95334 | -2.585 | -3.4424
|  | RAMSBURY | SP |  |  | 5.8281 | 5.7118 | 5.4279 | 5.3328 | 5.2175 | 4.8566 | 4.4528 | 4.0659 | 3.6618 | 3.2758 | 2.2734 | -0.49437 | -2.613 | -3.6712 | 7.8318 | 7.7225 | 7.5032 | 7.4025 | 7.2883 | 7.0315 | 6.7353 | 6.4403 | 6.1278 | 5.8367 | 4.9875 | 2.5775 | 0.36016 | -1.7294 | 6.24 | 6.1315 | 5.8719 | 5.7723 | 5.6544 | 5.3454 | 4.9901 | 4.6344 | 4.2659 | 3.9252 | 3.0057 | 0.4514 | -1.4016 | -2.2751
BRAMLEY (FLEE) | READING BSP | READING | MINIMUM HEADROOM | SU 74591 73788 | YES | 3.1194 | 2.9583 | 2.7833 | 2.5988 | 2.3292 | 2.0523 | 1.7558 | 1.4334 | 1.0212 | 0.60997 | -0.26737 | -1.285 | -1.6567 | -2.0216 | 1.8917 | 1.8086 | 1.716 | 1.6164 | 1.4786 | 1.3358 | 1.1781 | 1.0035 | 0.7688 | 0.53734 | 0.095973 | -0.38532 | -0.77078 | -1.0817 | 0.99043 | 0.84221 | 0.68012 | 0.50859 | 0.26082 | 0.0059798 | -0.26878 | -0.56876 | -0.95694 | -1.3428 | -2.1427 | -3.0582 | -3.3781 | -3.6979
|  | READING | CT |  |  | 3.2359 | 3.1437 | 3.0375 | 2.9133 | 2.7444 | 2.5704 | 2.3803 | 2.1671 | 1.911 | 1.5181 | 0.66069 | -0.70939 | -1.6567 | -2.0216 | 1.9287 | 1.8689 | 1.7987 | 1.7152 | 1.6154 | 1.5117 | 1.3966 | 1.2652 | 1.1027 | 0.87165 | 0.40195 | -0.28165 | -0.77078 | -1.0817 | 1.0907 | 1.0033 | 0.90197 | 0.78264 | 0.62461 | 0.46169 | 0.2831 | 0.081771 | -0.16217 | -0.53278 | -1.3224 | -2.5444 | -3.3781 | -3.6979
|  | READING | LW |  |  | 3.1194 | 2.9583 | 2.7833 | 2.5988 | 2.3292 | 2.0523 | 1.7558 | 1.4334 | 1.0212 | 0.60997 | -0.26737 | -1.285 | -1.5977 | -1.748 | 1.8917 | 1.8086 | 1.716 | 1.6164 | 1.4786 | 1.3358 | 1.1781 | 1.0035 | 0.7688 | 0.53734 | 0.095973 | -0.38532 | -0.51707 | -0.57952 | 0.99043 | 0.84221 | 0.68012 | 0.50859 | 0.26082 | 0.0059798 | -0.26878 | -0.56876 | -0.95694 | -1.3428 | -2.1427 | -3.0582 | -3.3338 | -3.4655
|  | READING | ST |  |  | 3.301 | 3.2531 | 3.1935 | 3.127 | 3.0353 | 2.938 | 2.8341 | 2.7234 | 2.5923 | 2.4559 | 1.8536 | 0.88709 | 0.40255 | 0.06574 | 1.9716 | 1.9408 | 1.9013 | 1.8561 | 1.7989 | 1.7374 | 1.6697 | 1.5967 | 1.5084 | 1.4237 | 1.0288 | 0.39458 | 0.069088 | -0.23073 | 1.1542 | 1.1099 | 1.0539 | 0.991 | 0.90511 | 0.81367 | 0.71548 | 0.6108 | 0.48587 | 0.35748 | -0.2199 | -1.1302 | -1.5637 | -1.859
|  | READING | SP |  |  | 3.3199 | 3.2783 | 3.2316 | 3.183 | 3.0684 | 2.9482 | 2.8299 | 2.6969 | 2.5596 | 2.3953 | 1.8093 | 0.41542 | -0.22611 | -0.56872 | 1.9781 | 1.9481 | 1.9136 | 1.8766 | 1.8151 | 1.7493 | 1.6834 | 1.6064 | 1.5246 | 1.4337 | 1.0912 | 0.21658 | -0.19576 | -0.47564 | 1.1708 | 1.1315 | 1.0874 | 1.0413 | 0.93707 | 0.82745 | 0.71956 | 0.59711 | 0.47032 | 0.3194 | -0.22545 | -1.539 | -2.1261 | -2.4306
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN | MINIMUM HEADROOM | SU 71540 74122 | YES | 13.4896 | 13.2209 | 12.8722 | 12.5033 | 11.8796 | 11.1736 | 10.4214 | 9.6134 | 8.7134 | 7.7904 | 5.6491 | 3.3799 | 1.9411 | 0.99316 | 2.6285 | 2.4939 | 2.3052 | 2.1019 | 1.7876 | 1.4262 | 1.0324 | 0.60499 | 0.03711 | -0.57056 | -1.7985 | -2.9285 | -4.0379 | -4.8817 | 0.12535 | -0.11696 | -0.42702 | -0.75467 | -1.3084 | -1.9294 | -2.5902 | -3.2994 | -4.0929 | -4.9332 | -6.9089 | -8.9592 | -10.2262 | -11.0945
|  | READING TOWN | CT |  |  | 13.6937 | 13.543 | 13.3667 | 13.0845 | 12.6559 | 12.1542 | 11.6236 | 11.0465 | 10.4622 | 9.5416 | 7.2526 | 4.1325 | 1.9411 | 0.99316 | 2.6942 | 2.5978 | 2.4829 | 2.2942 | 2.0479 | 1.7596 | 1.4509 | 1.0991 | 0.67749 | 0.059428 | -1.3546 | -2.9285 | -4.0379 | -4.8817 | 0.31351 | 0.17903 | 0.022565 | -0.22351 | -0.59854 | -1.0327 | -1.4919 | -1.9909 | -2.5005 | -3.3539 | -5.4411 | -8.2798 | -10.2262 | -11.0945
|  | READING TOWN | LW |  |  | 13.4896 | 13.2209 | 12.8722 | 12.5033 | 11.8796 | 11.1736 | 10.4214 | 9.6134 | 8.7134 | 7.7904 | 5.6491 | 3.3799 | 2.5558 | 2.2553 | 2.6285 | 2.4939 | 2.3052 | 2.1019 | 1.7876 | 1.4262 | 1.0324 | 0.60499 | 0.03711 | -0.57056 | -1.7985 | -2.8854 | -3.2086 | -3.3281 | 0.12535 | -0.11696 | -0.42702 | -0.75467 | -1.3084 | -1.9294 | -2.5902 | -3.2994 | -4.0929 | -4.9332 | -6.9089 | -8.9592 | -9.6857 | -9.949
|  | READING TOWN | ST |  |  | 13.834 | 13.7659 | 13.6853 | 13.5929 | 13.3981 | 13.1528 | 12.8937 | 12.6101 | 12.3296 | 12.0472 | 10.8309 | 8.3034 | 7.1952 | 6.4332 | 2.7749 | 2.7256 | 2.667 | 2.5987 | 2.4722 | 2.3137 | 2.1439 | 1.9566 | 1.7655 | 1.5818 | 0.66022 | -1.2247 | -2.0536 | -2.8538 | 0.43869 | 0.37816 | 0.30699 | 0.22573 | 0.060538 | -0.14321 | -0.35894 | -0.59525 | -0.83576 | -1.0845 | -2.1655 | -4.4568 | -5.5016 | -6.2214
|  | READING TOWN | SP |  |  | 13.8633 | 13.7929 | 13.7177 | 13.6333 | 13.4622 | 13.257 | 13.0413 | 12.7969 | 12.573 | 12.3104 | 11.3532 | 8.753 | 7.4207 | 6.8757 | 2.7851 | 2.7286 | 2.6669 | 2.5968 | 2.492 | 2.3652 | 2.2265 | 2.0693 | 1.919 | 1.7483 | 1.0931 | -1.0082 | -2.334 | -3.5371 | 0.46547 | 0.40417 | 0.33879 | 0.26547 | 0.11941 | -0.051033 | -0.22978 | -0.43289 | -0.62467 | -0.85626 | -1.6983 | -4.0371 | -5.2625 | -5.7713
MANNINGTON GSP | REDHILL BSP | REDHILL | MINIMUM HEADROOM | SZ 08512 96149 | YES | 26.1175 | 25.4562 | 24.6955 | 23.8536 | 22.4848 | 21.0181 | 19.4173 | 17.6431 | 15.4091 | 13.1854 | 8.117 | 1.1637 | -4.5597 | -8.3655 | 20.8948 | 20.4596 | 19.9502 | 19.3358 | 18.626 | 17.8533 | 17.009 | 16.0092 | 14.636 | 13.2313 | 9.2536 | 2.3586 | -5.2869 | -21.8105 | 14.854 | 14.2314 | 13.5115 | 12.7117 | 11.4416 | 10.076 | 8.5757 | 6.9053 | 4.774 | 2.6569 | -2.0708 | -8.3658 | -13.2129 | -16.3727
|  | REDHILL | CT |  |  | 26.2897 | 25.7777 | 25.1688 | 24.4282 | 23.4816 | 22.4617 | 21.3836 | 20.1756 | 18.746 | 16.431 | 10.9965 | 2.0707 | -4.5597 | -8.3655 | 20.8948 | 20.4596 | 19.9502 | 19.3358 | 18.626 | 17.8533 | 17.009 | 16.0545 | 14.9187 | 13.3022 | 9.2536 | 2.3586 | -5.0469 | -14.2829 | 14.9853 | 14.4922 | 13.9005 | 13.1725 | 12.3118 | 11.3495 | 10.3253 | 9.1737 | 7.8017 | 5.6029 | 0.53845 | -7.4583 | -13.2129 | -16.3727
|  | REDHILL | LW |  |  | 26.1175 | 25.4562 | 24.6955 | 23.8536 | 22.4848 | 21.0181 | 19.4173 | 17.6431 | 15.4091 | 13.1854 | 8.117 | 1.1637 | -2.4386 | -4.5738 | 20.9402 | 20.5404 | 20.0758 | 19.5526 | 18.7949 | 17.9722 | 17.0486 | 16.0092 | 14.636 | 13.2313 | 10.1692 | 6.3339 | 4.6181 | 3.5434 | 14.854 | 14.2314 | 13.5115 | 12.7117 | 11.4416 | 10.076 | 8.5757 | 6.9053 | 4.774 | 2.6569 | -2.0708 | -8.3658 | -11.4467 | -13.2239
|  | REDHILL | ST |  |  | 26.7985 | 26.5896 | 26.3267 | 26.013 | 25.6104 | 25.1667 | 24.664 | 24.099 | 23.4386 | 22.7437 | 19.3103 | 12.4396 | 8.3834 | 5.4844 | 21.2216 | 20.9874 | 20.7031 | 20.3699 | 19.9603 | 19.5089 | 18.9934 | 18.412 | 17.7362 | 17.0516 | 13.9145 | 6.8999 | 0.43911 | -8.4545 | 15.4812 | 15.2812 | 15.0246 | 14.7154 | 14.323 | 13.8903 | 13.3975 | 12.8423 | 12.1908 | 11.5198 | 8.1437 | 1.6986 | -1.7352 | -4.1838
|  | REDHILL | SP |  |  | 26.8378 | 26.6285 | 26.4029 | 26.1509 | 25.8386 | 25.4966 | 25.1362 | 24.698 | 24.2085 | 23.6306 | 21.3282 | 14.4917 | 10.5934 | 8.593 | 21.2254 | 20.9687 | 20.6784 | 20.3526 | 19.9602 | 19.5175 | 19.0298 | 18.455 | 17.7945 | 17.0362 | 14.0331 | 5.2828 | -5.2869 | -21.8105 | 15.5136 | 15.3072 | 15.0859 | 14.8384 | 14.5407 | 14.2126 | 13.868 | 13.4433 | 12.9636 | 12.4105 | 10.1649 | 3.4927 | -0.05798 | -1.7323
CHICKERELL GSP | CHICKERELL BSP | REDLANDS | MINIMUM HEADROOM | SY 67131 82321 | YES | 62.3893 | 61.4556 | 60.3105 | 58.612 | 56.4451 | 54.2544 | 52.1234 | 49.9182 | 47.6369 | 45.3679 | 38.2422 | 31.3366 | 28.5432 | 25.9515 | 65.5654 | 64.5225 | 63.296 | 62.0368 | 60.8156 | 59.5959 | 58.3333 | 56.988 | 55.7221 | 54.2296 | 49.2895 | 42.5109 | 34.8179 | 17.351 | 62.139 | 61.142 | 59.955 | 58.7614 | 57.1482 | 55.3517 | 53.5436 | 51.6 | 49.5531 | 47.5019 | 41.0718 | 34.8922 | 32.642 | 30.4621
|  | REDLANDS | CT |  |  | 62.3893 | 61.4556 | 60.3198 | 59.1959 | 57.5058 | 55.6245 | 53.8959 | 52.1113 | 50.288 | 48.1424 | 41.4041 | 33.2689 | 28.5432 | 25.9515 | 65.5911 | 64.5536 | 63.3099 | 62.0368 | 60.8156 | 59.6032 | 58.3785 | 57.0646 | 55.7394 | 54.2296 | 49.2895 | 42.5109 | 35.8218 | 26.7407 | 62.1844 | 61.2351 | 60.0877 | 58.9352 | 57.8621 | 56.6266 | 55.1804 | 53.5454 | 51.9133 | 49.9839 | 43.9378 | 36.7063 | 32.642 | 30.4621
|  | REDLANDS | LW |  |  | 62.419 | 61.4733 | 60.3105 | 58.612 | 56.4451 | 54.2544 | 52.1234 | 49.9182 | 47.6369 | 45.3679 | 38.2422 | 31.3366 | 28.7427 | 27.1629 | 65.5654 | 64.5225 | 63.296 | 62.0508 | 60.8169 | 59.5959 | 58.3333 | 56.988 | 55.7221 | 54.4163 | 50.19 | 46.4504 | 45.2774 | 44.5342 | 62.139 | 61.142 | 59.955 | 58.7614 | 57.1482 | 55.3517 | 53.5436 | 51.6 | 49.5531 | 47.5019 | 41.0718 | 34.8922 | 32.7129 | 31.4188
|  | REDLANDS | ST |  |  | 62.5695 | 61.7452 | 60.7443 | 59.7702 | 58.8813 | 58.0229 | 57.1697 | 56.2699 | 55.4379 | 54.4476 | 50.3351 | 44.3739 | 40.8988 | 38.9517 | 65.77 | 64.8967 | 63.893 | 62.8885 | 61.9716 | 61.0774 | 60.133 | 59.1045 | 58.182 | 57.1825 | 53.3584 | 47.0266 | 40.471 | 31.6468 | 62.3994 | 61.594 | 60.6428 | 59.7101 | 58.8789 | 58.0699 | 57.2452 | 56.361 | 55.5608 | 54.6968 | 51.6097 | 46.4241 | 43.4733 | 41.9174
|  | REDLANDS | SP |  |  | 62.5777 | 61.7599 | 60.7733 | 59.8143 | 58.9719 | 58.1638 | 57.3545 | 56.511 | 55.7707 | 55.0116 | 52.293 | 47.5754 | 43.7928 | 42.007 | 65.7703 | 64.8974 | 63.906 | 62.9059 | 62.0125 | 61.1305 | 60.1716 | 59.1318 | 58.1869 | 57.0534 | 53.021 | 45.6766 | 34.8179 | 17.351 | 62.4156 | 61.6219 | 60.6932 | 59.7848 | 59.0108 | 58.2654 | 57.4958 | 56.6813 | 55.9882 | 55.2553 | 52.7809 | 49.5677 | 45.6252 | 44.4815
MANNINGTON GSP | SALISBURY | REDLYNCH | MINIMUM HEADROOM | SU 19073 20576 | YES | 21.532 | 20.9756 | 20.2508 | 19.4016 | 18.1069 | 16.7005 | 15.404 | 14.0902 | 12.5403 | 10.8192 | 6.6439 | 1.3003 | -4.495 | -7.7791 | 28.7138 | 28.3765 | 27.838 | 27.2154 | 26.4169 | 25.5557 | 24.7065 | 23.8503 | 22.7946 | 21.6018 | 18.9882 | 15.294 | 11.8479 | 8.6154 | 23.2291 | 22.7329 | 22.0764 | 21.3131 | 20.1569 | 18.9272 | 17.7719 | 16.5569 | 15.1017 | 13.4793 | 9.6097 | 4.897 | -0.11232 | -2.9057
|  | REDLYNCH | CT |  |  | 21.7084 | 21.269 | 20.7363 | 19.9603 | 18.9718 | 17.9036 | 16.9625 | 16.0119 | 14.9504 | 13.2124 | 8.4955 | 1.3003 | -4.495 | -7.7791 | 28.758 | 28.4267 | 27.9942 | 27.3428 | 26.642 | 25.8906 | 25.1764 | 24.4561 | 23.6327 | 22.4198 | 19.2517 | 15.294 | 11.8479 | 8.6154 | 23.3815 | 22.9893 | 22.5118 | 21.8085 | 20.9459 | 20.0246 | 19.1735 | 18.2785 | 17.2745 | 15.646 | 11.2695 | 4.897 | -0.11232 | -2.9057
|  | REDLYNCH | LW |  |  | 21.532 | 20.9756 | 20.2508 | 19.4016 | 18.1069 | 16.7005 | 15.404 | 14.0902 | 12.5403 | 10.8192 | 6.6439 | 1.3591 | -1.725 | -3.6909 | 28.7138 | 28.3765 | 27.838 | 27.2154 | 26.4169 | 25.5557 | 24.7065 | 23.8503 | 22.7946 | 21.6018 | 18.9882 | 16.2469 | 14.8494 | 13.9118 | 23.2291 | 22.7329 | 22.0764 | 21.3131 | 20.1569 | 18.9272 | 17.7719 | 16.5569 | 15.1017 | 13.4793 | 9.6097 | 4.9 | 2.2772 | 0.64128
|  | REDLYNCH | ST |  |  | 21.9411 | 21.6636 | 21.3279 | 20.928 | 20.4204 | 19.8671 | 19.4111 | 18.9424 | 18.4318 | 17.9036 | 15.6831 | 10.3617 | 7.3294 | 4.9721 | 28.8669 | 28.667 | 28.4158 | 28.1101 | 27.6724 | 27.193 | 26.7561 | 26.3298 | 25.8622 | 25.4052 | 23.4212 | 19.1092 | 16.4709 | 13.5469 | 23.6035 | 23.3645 | 23.0726 | 22.7291 | 22.2818 | 21.792 | 21.3635 | 20.9568 | 20.5152 | 20.0419 | 17.9216 | 13.0295 | 10.4088 | 8.3856
|  | REDLYNCH | SP |  |  | 21.9744 | 21.6897 | 21.3603 | 20.9846 | 20.5454 | 20.0787 | 19.7013 | 19.3446 | 18.9477 | 18.5103 | 16.8789 | 12.3372 | 9.3678 | 7.8905 | 28.8694 | 28.6704 | 28.4158 | 28.0902 | 27.7235 | 27.3254 | 26.9704 | 26.6189 | 26.2401 | 25.8102 | 24.1483 | 19.5847 | 15.3729 | 10.2824 | 23.6339 | 23.3858 | 23.0981 | 22.7763 | 22.3972 | 21.9926 | 21.6431 | 21.3116 | 20.9628 | 20.5829 | 19.0914 | 14.878 | 12.1852 | 10.9517
NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK | MINIMUM HEADROOM | SU 39267 13050 | YES | 9.2006 | 9.1224 | 8.6477 | 11.6972 | 10.7501 | 9.6847 | 8.5801 | 7.3739 | 5.9644 | 4.5695 | 1.6017 | -1.4174 | -4.2196 | -5.8036 | 8.291 | 8.1204 | 7.8301 | 14.4491 | 13.9219 | 13.297 | 12.6451 | 11.9527 | 11.099 | 10.2018 | 8.388 | 6.5274 | 4.8743 | 3.4897 | 5.0413 | 4.7641 | 4.3111 | 10.736 | 9.8917 | 8.9355 | 7.937 | 6.8528 | 5.5667 | 4.2685 | 1.5267 | -1.1858 | -3.6187 | -4.9823
|  | REGENTS PARK | CT |  |  | 9.2006 | 9.1245 | 8.9982 | 12.1124 | 11.3775 | 10.5351 | 9.664 | 8.7024 | 7.6257 | 6.2208 | 2.9239 | -1.221 | -4.2196 | -5.8036 | 8.3266 | 8.182 | 7.9654 | 14.5806 | 14.1322 | 13.5921 | 13.0341 | 12.441 | 11.7422 | 10.8344 | 8.7264 | 6.5274 | 4.8743 | 3.4897 | 5.1507 | 4.9495 | 4.6429 | 11.1051 | 10.4499 | 9.6932 | 8.9062 | 8.0443 | 7.0668 | 5.7635 | 2.7081 | -0.984 | -3.6187 | -4.9823
|  | REGENTS PARK | LW |  |  | 9.2041 | 9.1224 | 8.6477 | 11.6972 | 10.7501 | 9.6847 | 8.5801 | 7.3739 | 5.9644 | 4.5695 | 1.6017 | -1.4174 | -2.7772 | -3.5258 | 8.291 | 8.1204 | 7.8301 | 14.4491 | 13.9219 | 13.297 | 12.6451 | 11.9527 | 11.099 | 10.2018 | 8.388 | 6.8322 | 6.2441 | 5.91 | 5.0413 | 4.7641 | 4.3111 | 10.736 | 9.8917 | 8.9355 | 7.937 | 6.8528 | 5.5667 | 4.2685 | 1.5267 | -1.1858 | -2.3567 | -2.9894
|  | REGENTS PARK | ST |  |  | 9.2412 | 9.1907 | 9.0969 | 12.6215 | 12.3947 | 11.952 | 11.4498 | 10.8872 | 10.2529 | 9.7149 | 8.026 | 4.8052 | 3.2867 | 2.1531 | 8.4297 | 8.3531 | 8.2299 | 15.0435 | 14.7608 | 14.3911 | 14.0258 | 13.6351 | 13.1704 | 12.7682 | 11.5158 | 9.1121 | 7.9646 | 6.7754 | 5.3099 | 5.2152 | 5.0572 | 11.8312 | 11.4699 | 11.0199 | 10.5737 | 10.0758 | 9.5097 | 9.0248 | 7.4266 | 4.3854 | 3.067 | 2.0978
|  | REGENTS PARK | SP |  |  | 9.2424 | 9.1875 | 9.0914 | 12.6158 | 12.4067 | 12.1201 | 11.6893 | 11.2165 | 10.6721 | 10.1843 | 8.8238 | 5.885 | 4.3801 | 3.7577 | 8.4379 | 8.347 | 8.2184 | 15.0315 | 14.7939 | 14.4827 | 14.1624 | 13.8283 | 13.4204 | 13.0341 | 11.9449 | 9.4993 | 7.6517 | 5.6759 | 5.3288 | 5.2174 | 5.0588 | 11.8408 | 11.5444 | 11.1831 | 10.8047 | 10.3946 | 9.917 | 9.4819 | 8.2149 | 5.4011 | 4.0204 | 3.4887
COWLEY GSP | WITNEY BSP | RISSINGTON | MINIMUM HEADROOM | SP 19225 19563 | NO | 7.0876 | 6.7812 | 6.4461 | 6.0971 | 5.5507 | 4.9898 | 4.3939 | 3.7206 | 2.9094 | 2.1356 | 0.49714 | -1.5446 | -2.5734 | -3.5267 | 9.989 | 9.8266 | 9.6376 | 9.4356 | 9.1497 | 8.8529 | 8.5135 | 8.1118 | 7.5871 | 7.111 | 6.3425 | 5.4577 | 4.7017 | 4.0742 | 8.2809 | 8.0014 | 7.6935 | 7.3717 | 6.874 | 6.3624 | 5.8171 | 5.2014 | 4.4396 | 3.7179 | 2.2383 | 0.41121 | -0.46818 | -1.3052
|  | RISSINGTON | CT |  |  | 7.3552 | 7.1875 | 7.0022 | 6.7765 | 6.4401 | 6.0899 | 5.7098 | 5.2779 | 4.7513 | 3.9545 | 2.3666 | -0.42292 | -2.5734 | -3.5267 | 10.0627 | 9.9395 | 9.7997 | 9.6265 | 9.4194 | 9.1899 | 8.9337 | 8.6327 | 8.2688 | 7.7624 | 6.8952 | 5.6439 | 4.7017 | 4.0742 | 8.513 | 8.355 | 8.1797 | 7.9709 | 7.6717 | 7.3454 | 6.9888 | 6.5825 | 6.1106 | 5.3794 | 3.9201 | 1.4095 | -0.46818 | -1.3052
|  | RISSINGTON | LW |  |  | 7.0876 | 6.7812 | 6.4461 | 6.0971 | 5.5507 | 4.9898 | 4.3939 | 3.7206 | 2.9094 | 2.1356 | 0.49714 | -1.5446 | -2.2803 | -2.6545 | 9.989 | 9.8266 | 9.6376 | 9.4356 | 9.1497 | 8.8529 | 8.5135 | 8.1118 | 7.5871 | 7.111 | 6.3425 | 5.4577 | 5.175 | 5.0349 | 8.2809 | 8.0014 | 7.6935 | 7.3717 | 6.874 | 6.3624 | 5.8171 | 5.2014 | 4.4396 | 3.7179 | 2.2383 | 0.41121 | -0.22633 | -0.54994
|  | RISSINGTON | ST |  |  | 7.4766 | 7.3853 | 7.2818 | 7.1638 | 6.9919 | 6.8137 | 6.6283 | 6.417 | 6.1728 | 5.9184 | 4.7089 | 2.9435 | 1.993 | 1.2519 | 10.1632 | 10.1016 | 10.0277 | 9.9385 | 9.8213 | 9.6977 | 9.5646 | 9.4105 | 9.2317 | 9.0568 | 8.1588 | 6.9684 | 6.3724 | 5.8082 | 8.631 | 8.547 | 8.4509 | 8.3403 | 8.1804 | 8.0144 | 7.8409 | 7.646 | 7.4299 | 7.191 | 6.0758 | 4.4272 | 3.5601 | 2.8918
|  | RISSINGTON | SP |  |  | 7.5087 | 7.432 | 7.3527 | 7.2701 | 7.056 | 6.8322 | 6.612 | 6.3698 | 6.1223 | 5.8148 | 4.7214 | 2.1554 | 1.0355 | 0.35821 | 10.1726 | 10.1118 | 10.0466 | 9.9764 | 9.8587 | 9.7355 | 9.6104 | 9.4647 | 9.3111 | 9.1339 | 8.4418 | 6.6486 | 5.9305 | 5.4181 | 8.6592 | 8.5873 | 8.513 | 8.4354 | 8.2413 | 8.0386 | 7.8386 | 7.6172 | 7.3904 | 7.1095 | 6.1113 | 3.7309 | 2.6858 | 2.0814
BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE | MINIMUM HEADROOM | SU 47846 67187 | YES | 16.6267 | 16.4553 | 16.2581 | 16.037 | 15.6569 | 15.2483 | 14.8061 | 14.3333 | 13.6909 | 12.9574 | 10.5806 | 7.174 | 5.377 | 3.9731 | 12.3729 | 12.2917 | 12.1989 | 12.0784 | 11.9455 | 11.7957 | 11.6221 | 11.4123 | 11.0765 | 10.6227 | 8.3853 | 5.9315 | 3.6447 | -2.4649 | 10.6813 | 10.524 | 10.3414 | 10.1358 | 9.789 | 9.4148 | 9.0076 | 8.5711 | 7.9742 | 7.2891 | 5.0718 | 1.8387 | 0.41719 | -0.80595
|  | RIVERSIDE | CT |  |  | 16.7071 | 16.5911 | 16.4596 | 16.2857 | 16.0289 | 15.7512 | 15.4416 | 15.1092 | 14.6749 | 13.9989 | 11.747 | 7.9104 | 5.377 | 3.9731 | 12.3729 | 12.2917 | 12.1989 | 12.0784 | 11.9455 | 11.7957 | 11.6274 | 11.4414 | 11.1534 | 10.7956 | 9.2203 | 6.2809 | 3.6447 | 0.43128 | 10.7508 | 10.6428 | 10.52 | 10.3556 | 10.118 | 9.8605 | 9.5728 | 9.2636 | 8.8559 | 8.2291 | 6.1428 | 2.6542 | 0.41719 | -0.80595
|  | RIVERSIDE | LW |  |  | 16.6267 | 16.4553 | 16.2581 | 16.037 | 15.6569 | 15.2483 | 14.8061 | 14.3333 | 13.6909 | 12.9574 | 10.5806 | 7.174 | 6.1633 | 5.4135 | 12.3893 | 12.307 | 12.2117 | 12.0968 | 11.9638 | 11.8088 | 11.6221 | 11.4123 | 11.0765 | 10.6227 | 8.3853 | 5.9315 | 5.3984 | 5.0467 | 10.6813 | 10.524 | 10.3414 | 10.1358 | 9.789 | 9.4148 | 9.0076 | 8.5711 | 7.9742 | 7.2891 | 5.0718 | 1.8387 | 0.92054 | 0.38793
|  | RIVERSIDE | ST |  |  | 16.8116 | 16.7613 | 16.7086 | 16.6458 | 16.5498 | 16.4391 | 16.3153 | 16.1757 | 15.9396 | 15.6305 | 14.4204 | 10.6215 | 8.4453 | 7.6702 | 12.4349 | 12.3917 | 12.3469 | 12.2931 | 12.2191 | 12.1317 | 12.0298 | 11.9127 | 11.6989 | 11.4297 | 10.3609 | 7.4158 | 5.4287 | 2.2963 | 10.849 | 10.8028 | 10.7541 | 10.6957 | 10.6058 | 10.5018 | 10.3849 | 10.2527 | 10.0278 | 9.7352 | 8.1488 | 4.507 | 2.5724 | 1.9171
|  | RIVERSIDE | SP |  |  | 16.8288 | 16.7857 | 16.7377 | 16.6861 | 16.6162 | 16.5358 | 16.4481 | 16.3504 | 16.1826 | 15.9533 | 15.1251 | 13.2201 | 10.5409 | 9.6452 | 12.4386 | 12.3984 | 12.3535 | 12.303 | 12.2421 | 12.172 | 12.0938 | 12.0025 | 11.8358 | 11.6168 | 10.8068 | 8.0434 | 3.8085 | -2.4649 | 10.8646 | 10.8245 | 10.7799 | 10.7316 | 10.6668 | 10.5922 | 10.5105 | 10.4187 | 10.2597 | 10.0434 | 9.2505 | 6.8253 | 4.4889 | 3.7084
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE | MINIMUM HEADROOM | SU 11617 17810 | YES | 17.1261 | 16.7476 | 16.3319 | 15.904 | 15.2937 | 14.6684 | 14.031 | 13.3639 | 12.5928 | 11.7759 | 9.7104 | 7.7296 | 7.2521 | 7.0658 | 19.6919 | 19.5265 | 19.333 | 19.1301 | 18.8529 | 18.5635 | 18.2606 | 17.9386 | 17.5371 | 17.1166 | 16.1523 | 15.2628 | 15.066 | 14.5692 | 17.9267 | 17.6013 | 17.2345 | 16.8545 | 16.3214 | 15.7664 | 15.1895 | 14.5843 | 13.8768 | 13.1286 | 11.2647 | 9.4885 | 9.0666 | 8.9034
|  | ROCKBOURNE | CT |  |  | 17.5364 | 17.37 | 17.186 | 16.9527 | 16.604 | 16.2432 | 15.8685 | 15.4725 | 15.0026 | 14.3138 | 12.5567 | 10.0648 | 9.1018 | 8.9476 | 19.8345 | 19.7441 | 19.6414 | 19.5036 | 19.3219 | 19.1317 | 18.9301 | 18.7156 | 18.4447 | 18.0579 | 17.134 | 16.0346 | 15.5524 | 15.3207 | 18.2574 | 18.1041 | 17.9335 | 17.7137 | 17.3936 | 17.0616 | 16.7155 | 16.3493 | 15.9093 | 15.2711 | 13.6676 | 11.5493 | 10.699 | 10.5632
|  | ROCKBOURNE | LW |  |  | 17.1261 | 16.7476 | 16.3319 | 15.904 | 15.2937 | 14.6684 | 14.031 | 13.3639 | 12.5928 | 11.7759 | 9.7104 | 7.7296 | 7.2521 | 7.0658 | 19.6919 | 19.5265 | 19.333 | 19.1301 | 18.8529 | 18.5635 | 18.2606 | 17.9386 | 17.5371 | 17.1166 | 16.1523 | 15.2628 | 15.066 | 14.9897 | 17.9267 | 17.6013 | 17.2345 | 16.8545 | 16.3214 | 15.7664 | 15.1895 | 14.5843 | 13.8768 | 13.1286 | 11.2647 | 9.4885 | 9.0666 | 8.9034
|  | ROCKBOURNE | ST |  |  | 17.61 | 17.4864 | 17.3557 | 17.2167 | 17.0027 | 16.774 | 16.5429 | 16.2935 | 16.032 | 15.7413 | 14.6535 | 12.6304 | 11.4597 | 10.6587 | 19.8868 | 19.8267 | 19.7606 | 19.6872 | 19.5798 | 19.461 | 19.3385 | 19.2022 | 19.0551 | 18.9011 | 18.265 | 17.0616 | 16.4914 | 16.0365 | 18.3337 | 18.2261 | 18.1103 | 17.9851 | 17.794 | 17.5868 | 17.3763 | 17.1462 | 16.9024 | 16.6379 | 15.6017 | 13.72 | 12.7358 | 12.0835
|  | ROCKBOURNE | SP |  |  | 17.654 | 17.5522 | 17.4527 | 17.3446 | 16.9942 | 16.6353 | 16.2742 | 15.9017 | 15.5204 | 15.0557 | 13.5571 | 10.3669 | 8.4773 | 7.3034 | 19.9032 | 19.8469 | 19.7915 | 19.7285 | 19.5774 | 19.4213 | 19.2623 | 19.0927 | 18.9155 | 18.704 | 17.9822 | 16.307 | 15.3006 | 14.5692 | 18.3701 | 18.2772 | 18.1869 | 18.0869 | 17.7899 | 17.4852 | 17.1776 | 16.8566 | 16.5259 | 16.1211 | 14.7704 | 11.8641 | 10.1661 | 9.1303
NURSLING GSP | ROWNHAMS | ROMSEY | MINIMUM HEADROOM | SU 36092 21110 | YES | 8.8073 | 8.4096 | 7.8807 | 7.4812 | 7.003 | 6.3357 | 5.6533 | 4.9224 | 4.2085 | 3.4658 | 0.89518 | -2.4995 | -3.4884 | -4.1015 | 6.6652 | 6.3853 | 6.1544 | 5.9732 | 5.7603 | 5.4662 | 5.1587 | 4.8164 | 4.4711 | 4.0999 | 2.8269 | 1.186 | 0.41823 | -0.73533 | 6.46 | 5.9371 | 5.4954 | 5.1473 | 4.7193 | 4.1392 | 3.5406 | 2.8917 | 2.2518 | 1.5805 | -0.6982 | -3.6643 | -4.509 | -5.017
|  | ROMSEY | CT |  |  | 8.8073 | 8.5244 | 8.3033 | 8.0105 | 7.6974 | 7.2013 | 6.7531 | 6.2679 | 5.7536 | 5.079 | 2.7143 | -1.1397 | -2.9473 | -3.9573 | 6.7302 | 6.487 | 6.2871 | 6.1373 | 5.9802 | 5.7455 | 5.5235 | 5.2712 | 5.0064 | 4.6666 | 3.4852 | 1.5037 | 0.41823 | -0.73533 | 6.6362 | 6.2141 | 5.8639 | 5.609 | 5.3268 | 4.8984 | 4.5081 | 4.0785 | 3.622 | 3.0152 | 0.93295 | -2.4298 | -4.0025 | -4.8622
|  | ROMSEY | LW |  |  | 8.8152 | 8.4096 | 7.8807 | 7.4812 | 7.003 | 6.3357 | 5.6533 | 4.9224 | 4.2085 | 3.4658 | 0.89518 | -2.4995 | -3.4884 | -4.1015 | 6.6652 | 6.3853 | 6.1544 | 5.9732 | 5.7603 | 5.4662 | 5.1587 | 4.8164 | 4.4711 | 4.0999 | 2.8269 | 1.186 | 0.73427 | 0.45353 | 6.46 | 5.9371 | 5.4954 | 5.1473 | 4.7193 | 4.1392 | 3.5406 | 2.8917 | 2.2518 | 1.5805 | -0.6982 | -3.6643 | -4.509 | -5.017
|  | ROMSEY | ST |  |  | 8.9066 | 8.6763 | 8.5193 | 8.4281 | 8.3578 | 8.2137 | 8.0657 | 7.8939 | 7.6875 | 7.3678 | 5.9711 | 3.0964 | 1.7113 | 0.89804 | 6.8849 | 6.7325 | 6.6182 | 6.539 | 6.4623 | 6.334 | 6.2005 | 6.0421 | 5.8759 | 5.6893 | 4.8973 | 3.0358 | 1.8139 | 1.1714 | 6.8621 | 6.665 | 6.5289 | 6.432 | 6.3106 | 6.1029 | 5.89 | 5.6493 | 5.3967 | 5.1164 | 3.9012 | 1.3523 | 0.11972 | -0.56858
|  | ROMSEY | SP |  |  | 8.913 | 8.6885 | 8.5397 | 8.4573 | 8.4009 | 8.2774 | 8.1535 | 8.0098 | 7.8633 | 7.7031 | 6.7876 | 4.3771 | 2.7317 | 1.892 | 6.9019 | 6.7603 | 6.6578 | 6.5898 | 6.5295 | 6.4276 | 6.3214 | 6.1931 | 6.0641 | 5.9074 | 5.2918 | 3.7702 | 2.2673 | 0.50245 | 6.8684 | 6.6768 | 6.5485 | 6.4753 | 6.4235 | 6.3116 | 6.1519 | 5.9688 | 5.7813 | 5.5546 | 4.6638 | 2.5471 | 1.045 | 0.31868
LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN | MINIMUM HEADROOM | SZ 89974 99335 | NO | -0.16506 | -0.25015 | -0.34309 | -0.43839 | -0.56414 | -0.68897 | -0.82077 | -0.96811 | -1.1568 | -1.3164 | -1.6761 | -2.0643 | -2.1533 | -2.2057 | 0.89202 | 0.85381 | 0.80835 | 0.76066 | 0.70026 | 0.63873 | 0.56993 | 0.48779 | 0.3787 | 0.29283 | 0.15692 | 0.014221 | -0.0185 | -0.069998 | 0.3598 | 0.28291 | 0.19826 | 0.11126 | -0.003096 | -0.11691 | -0.23779 | -0.37389 | -0.54889 | -0.69577 | -1.0165 | -1.3617 | -1.4404 | -1.4864
|  | ROSE GREEN | CT |  |  | -0.084313 | -0.12498 | -0.16708 | -0.22348 | -0.2978 | -0.373 | -0.46285 | -0.56947 | -0.68374 | -0.83388 | -1.1058 | -1.5815 | -1.8949 | -2.0178 | 0.91109 | 0.88576 | 0.85914 | 0.81866 | 0.77545 | 0.73057 | 0.67731 | 0.6092 | 0.53662 | 0.44361 | 0.31783 | 0.13432 | 0.0087323 | -0.069998 | 0.42978 | 0.39195 | 0.35274 | 0.29927 | 0.23056 | 0.16082 | 0.07757 | -0.022134 | -0.12624 | -0.2623 | -0.51467 | -0.93638 | -1.2122 | -1.3203
|  | ROSE GREEN | LW |  |  | -0.16506 | -0.25015 | -0.34309 | -0.43839 | -0.56414 | -0.68897 | -0.82077 | -0.96811 | -1.1568 | -1.3164 | -1.6761 | -2.0643 | -2.1533 | -2.2057 | 0.89202 | 0.85381 | 0.80835 | 0.76066 | 0.70026 | 0.63873 | 0.56993 | 0.48779 | 0.3787 | 0.29283 | 0.15692 | 0.014221 | -0.0185 | -0.037486 | 0.3598 | 0.28291 | 0.19826 | 0.11126 | -0.003096 | -0.11691 | -0.23779 | -0.37389 | -0.54889 | -0.69577 | -1.0165 | -1.3617 | -1.4404 | -1.4864
|  | ROSE GREEN | ST |  |  | -0.051239 | -0.07209 | -0.096347 | -0.1255 | -0.17039 | -0.21845 | -0.2661 | -0.32024 | -0.38234 | -0.44807 | -0.72105 | -1.0438 | -1.2239 | -1.343 | 0.93458 | 0.9231 | 0.9084 | 0.88869 | 0.86311 | 0.83456 | 0.80586 | 0.77118 | 0.73107 | 0.69364 | 0.5101 | 0.31824 | 0.22824 | 0.15029 | 0.46128 | 0.44229 | 0.41992 | 0.39267 | 0.35136 | 0.30695 | 0.26287 | 0.2124 | 0.15444 | 0.093812 | -0.16094 | -0.46076 | -0.62101 | -0.7259
|  | ROSE GREEN | SP |  |  | -0.037083 | -0.054307 | -0.072888 | -0.091656 | -0.14064 | -0.19136 | -0.23884 | -0.29557 | -0.34812 | -0.42691 | -0.70034 | -1.3149 | -1.6477 | -1.8622 | 0.93816 | 0.92588 | 0.91239 | 0.89817 | 0.87371 | 0.84854 | 0.82519 | 0.79461 | 0.76591 | 0.72831 | 0.58081 | 0.2226 | 0.083934 | -0.00755 | 0.4736 | 0.45747 | 0.44006 | 0.42241 | 0.37795 | 0.33197 | 0.28902 | 0.23719 | 0.18921 | 0.11786 | -0.1327 | -0.70014 | -0.99645 | -1.1854
COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL | MINIMUM HEADROOM | SP 53637 03027 | NO | 3.9915 | 3.3974 | 2.6271 | 1.7731 | 0.37314 | -1.0865 | -2.6138 | -4.2937 | -6.2606 | -8.2259 | -13.3517 | -18.3044 | -20.2575 | -22.0471 | 11.3832 | 11.2194 | 10.8216 | 10.2929 | 9.5268 | 8.7221 | 7.86 | 6.8944 | 5.7113 | 4.548 | 1.6764 | -1.2181 | -3.9808 | -6.6147 | 6.8219 | 6.2712 | 5.5563 | 4.7814 | 3.5235 | 2.2114 | 0.83917 | -0.66675 | -2.4237 | -4.1843 | -8.8113 | -13.3931 | -15.1838 | -16.7553
|  | ROSE HILL | CT |  |  | 4.357 | 3.9771 | 3.4472 | 2.7748 | 1.7513 | 0.67921 | -0.41753 | -1.6312 | -3.0094 | -4.9425 | -9.9137 | -16.2511 | -20.2575 | -22.0471 | 11.3832 | 11.2194 | 10.8912 | 10.5271 | 9.8796 | 9.1975 | 8.4865 | 7.6926 | 6.7761 | 5.5628 | 2.5494 | -1.2181 | -3.9808 | -6.6147 | 7.1715 | 6.8235 | 6.3333 | 5.7329 | 4.8292 | 3.8815 | 2.912 | 1.8406 | 0.62524 | -1.0985 | -5.5632 | -11.4713 | -15.1838 | -16.7553
|  | ROSE HILL | LW |  |  | 3.9915 | 3.3974 | 2.6271 | 1.7731 | 0.37314 | -1.0865 | -2.6138 | -4.2937 | -6.2606 | -8.2259 | -13.3517 | -18.3044 | -19.7645 | -20.3769 | 11.4096 | 11.2497 | 10.8216 | 10.2929 | 9.5268 | 8.7221 | 7.86 | 6.8944 | 5.7113 | 4.548 | 1.6764 | -0.96625 | -1.5975 | -1.8557 | 6.8219 | 6.2712 | 5.5563 | 4.7814 | 3.5235 | 2.2114 | 0.83917 | -0.66675 | -2.4237 | -4.1843 | -8.8113 | -13.3931 | -14.7565 | -15.3285
|  | ROSE HILL | ST |  |  | 4.6463 | 4.4405 | 4.1135 | 3.7505 | 3.1726 | 2.5737 | 1.9609 | 1.2964 | 0.53368 | -0.28023 | -3.4029 | -8.0552 | -10.4147 | -11.8162 | 11.4708 | 11.3584 | 11.0934 | 10.8979 | 10.6746 | 10.3871 | 9.9447 | 9.4623 | 8.9007 | 8.3283 | 6.0236 | 2.3158 | -0.064004 | -2.5991 | 7.4315 | 7.2404 | 6.933 | 6.6099 | 6.1177 | 5.6065 | 5.0824 | 4.5144 | 3.861 | 3.1572 | 0.44308 | -3.8089 | -6.0286 | -7.3517
|  | ROSE HILL | SP |  |  | 4.7014 | 4.5067 | 4.2052 | 3.8906 | 3.3212 | 2.7408 | 2.1601 | 1.5391 | 0.84254 | 0.053422 | -2.6002 | -7.6496 | -10.4748 | -11.7139 | 11.4727 | 11.3593 | 11.0952 | 10.9046 | 10.7007 | 10.4741 | 10.0664 | 9.6207 | 9.1125 | 8.5446 | 6.5265 | 2.1387 | -1.6889 | -6.2669 | 7.4834 | 7.3046 | 7.0218 | 6.7437 | 6.2535 | 5.754 | 5.2543 | 4.7221 | 4.1248 | 3.4427 | 1.1429 | -3.418 | -6.0388 | -7.1964
MELKSHAM GSP | CHIPPENHAM | ROWDEN | MINIMUM HEADROOM | ST 90805 72608 | YES | 12.5643 | 12.2155 | 11.7475 | 11.2372 | 10.5546 | 9.8786 | 9.2131 | 8.5374 | 7.6968 | 6.658 | 4.1644 | 1.4326 | -1.4747 | -2.9217 | 11.4898 | 11.2339 | 10.8407 | 10.4126 | 9.9407 | 9.4575 | 8.9475 | 8.4149 | 7.7538 | 7.0464 | 5.5022 | 3.9258 | 2.5253 | 1.456 | 7.7701 | 7.5802 | 7.3388 | 7.0701 | 6.6564 | 6.2501 | 5.7517 | 4.9402 | 3.9652 | 2.9321 | 0.54697 | -1.7886 | -4.1626 | -5.3367
|  | ROWDEN | CT |  |  | 12.6415 | 12.4226 | 12.0771 | 11.6293 | 11.1545 | 10.6936 | 10.2213 | 9.744 | 9.2299 | 8.1779 | 5.2983 | 1.4326 | -1.4747 | -2.9217 | 11.5147 | 11.2826 | 11.0005 | 10.5636 | 10.1604 | 9.7578 | 9.3379 | 8.8998 | 8.3887 | 7.6745 | 5.7974 | 3.9258 | 2.5253 | 1.456 | 7.8805 | 7.7517 | 7.5778 | 7.3688 | 7.1107 | 6.8614 | 6.6037 | 6.0222 | 5.3224 | 4.2801 | 1.495 | -1.7886 | -4.1626 | -5.3367
|  | ROWDEN | LW |  |  | 12.5643 | 12.2155 | 11.7475 | 11.2372 | 10.5546 | 9.8786 | 9.2131 | 8.5374 | 7.6968 | 6.658 | 4.1644 | 1.5135 | 0.19332 | -0.48636 | 11.4898 | 11.2339 | 10.8407 | 10.4126 | 9.9407 | 9.4575 | 8.9475 | 8.4149 | 7.7538 | 7.0464 | 5.5022 | 4.2389 | 3.702 | 3.4073 | 7.7701 | 7.5802 | 7.3388 | 7.0701 | 6.6564 | 6.2501 | 5.7517 | 4.9402 | 3.9652 | 2.9321 | 0.54697 | -1.7471 | -2.8259 | -3.3777
|  | ROWDEN | ST |  |  | 12.6995 | 12.558 | 12.3905 | 12.2208 | 12.0641 | 11.8534 | 11.6536 | 11.4517 | 11.2175 | 10.9832 | 10.0994 | 6.9981 | 5.5758 | 4.4764 | 11.6627 | 11.5243 | 11.3538 | 11.1668 | 10.932 | 10.6944 | 10.4576 | 10.2082 | 9.9147 | 9.6658 | 8.5651 | 6.179 | 5.1933 | 4.2406 | 7.9488 | 7.8888 | 7.8159 | 7.7382 | 7.655 | 7.5742 | 7.4991 | 7.4246 | 7.3413 | 7.2489 | 6.0323 | 2.9779 | 1.7312 | 0.82633
|  | ROWDEN | SP |  |  | 12.702 | 12.5556 | 12.3857 | 12.2157 | 12.0814 | 11.9602 | 11.8546 | 11.7273 | 11.5542 | 11.3789 | 10.7654 | 8.4579 | 7.0255 | 6.5226 | 11.6729 | 11.5157 | 11.3368 | 11.1495 | 10.9796 | 10.8138 | 10.6508 | 10.4654 | 10.2513 | 10.0378 | 9.1953 | 6.854 | 5.1834 | 3.5699 | 7.9629 | 7.9129 | 7.8532 | 7.7924 | 7.731 | 7.6733 | 7.6219 | 7.5688 | 7.5094 | 7.4344 | 6.9902 | 4.3448 | 3.0105 | 2.5826
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK | MINIMUM HEADROOM | SU 58018 00782 | YES | 11.2575 | 10.5721 | 10.0787 | 9.5926 | 8.6598 | 7.5149 | 6.1183 | 4.7427 | 2.987 | 1.223 | -4.8374 | -10.8516 | -14.6851 | -17.2054 | 7.9783 | 7.5564 | 7.238 | 6.8972 | 6.3567 | 5.7234 | 4.9413 | 4.1395 | 3.1278 | 2.1223 | -1.3167 | -5.5519 | -8.519 | -11.7451 | 5.9039 | 5.3283 | 4.8898 | 4.4425 | 3.617 | 2.621 | 1.4099 | 0.20044 | -1.3363 | -2.8832 | -8.1663 | -13.3667 | -16.5107 | -18.6141
|  | ROWNER PARK | CT |  |  | 11.3537 | 10.7347 | 10.3431 | 9.9072 | 9.1601 | 8.2108 | 7.0395 | 5.8942 | 4.4339 | 2.6513 | -3.4632 | -10.6492 | -14.6851 | -17.2054 | 7.9818 | 7.5597 | 7.2664 | 6.906 | 6.4047 | 5.8145 | 5.0919 | 4.347 | 3.4343 | 2.3766 | -1.2449 | -5.5519 | -8.519 | -11.7451 | 5.9858 | 5.469 | 5.1244 | 4.7196 | 4.059 | 3.2377 | 2.2301 | 1.229 | -0.035556 | -1.594 | -6.9053 | -13.1207 | -16.5107 | -18.6141
|  | ROWNER PARK | LW |  |  | 11.2575 | 10.5721 | 10.0787 | 9.5926 | 8.6598 | 7.5149 | 6.1183 | 4.7427 | 2.987 | 1.223 | -4.8374 | -10.8516 | -13.2011 | -14.8399 | 7.9783 | 7.5564 | 7.238 | 6.8972 | 6.3567 | 5.7234 | 4.9413 | 4.1395 | 3.1278 | 2.1223 | -1.3167 | -4.527 | -5.634 | -6.4402 | 5.9039 | 5.3283 | 4.8898 | 4.4425 | 3.617 | 2.621 | 1.4099 | 0.20044 | -1.3363 | -2.8832 | -8.1663 | -13.3667 | -15.3376 | -16.6861
|  | ROWNER PARK | ST |  |  | 11.6191 | 11.1928 | 10.9499 | 10.7068 | 10.2795 | 9.7371 | 9.0326 | 8.3267 | 7.4308 | 6.5516 | 3.1732 | -1.9406 | -4.4275 | -6.1652 | 8.156 | 7.8507 | 7.6499 | 7.4236 | 7.0828 | 6.6882 | 6.185 | 5.6493 | 5.0026 | 4.3891 | 2.0278 | -1.9463 | -4.5505 | -7.5035 | 6.2391 | 5.9036 | 5.6995 | 5.4807 | 5.112 | 4.6596 | 4.0741 | 3.4709 | 2.7168 | 1.9806 | -0.86319 | -5.3778 | -7.5217 | -8.9515
|  | ROWNER PARK | SP |  |  | 11.6415 | 11.2149 | 10.9694 | 10.7291 | 10.3709 | 9.9334 | 9.3308 | 8.7326 | 7.9819 | 7.2395 | 4.4889 | 0.5944 | -1.7659 | -3.033 | 8.1619 | 7.8477 | 7.6327 | 7.3959 | 7.0964 | 6.7607 | 6.3044 | 5.8182 | 5.2321 | 4.6407 | 2.4301 | -1.3783 | -5.2951 | -10.4743 | 6.2595 | 5.9224 | 5.7144 | 5.4973 | 5.1956 | 4.8437 | 4.3537 | 3.8516 | 3.2319 | 2.6203 | 0.35513 | -3.0391 | -5.1441 | -6.1831
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE | MINIMUM HEADROOM | SZ 59554 91973 | NO | 10.5517 | 9.6396 | 8.6922 | 7.5917 | 6.3977 | 5.2787 | 4.0634 | 2.7774 | 1.218 | -0.44907 | -4.4791 | -9.0478 | -12.0835 | -13.9403 | 11.6988 | 11.1271 | 10.5457 | 9.8378 | 9.1284 | 8.4849 | 7.7731 | 7.0206 | 6.078 | 5.0705 | 2.7361 | -0.066352 | -2.6577 | -4.9009 | 7.9536 | 7.1557 | 6.3246 | 5.3453 | 4.2479 | 3.2175 | 2.1033 | 0.92749 | -0.48822 | -2.0453 | -5.7986 | -9.9831 | -12.6471 | -14.2732
|  | RYDE | CT |  |  | 10.8022 | 10.0515 | 9.2916 | 8.3139 | 7.4398 | 6.6455 | 5.8101 | 4.9135 | 3.8824 | 2.2749 | -1.8595 | -7.9172 | -12.0835 | -13.9403 | 11.766 | 11.2405 | 10.7205 | 10.0267 | 9.4285 | 8.8966 | 8.3316 | 7.7275 | 7.0256 | 6.0209 | 3.4366 | -0.066352 | -2.6577 | -4.9009 | 8.1934 | 7.5476 | 6.8908 | 6.0303 | 5.2336 | 4.5088 | 3.7489 | 2.9054 | 1.9274 | 0.41267 | -3.4452 | -8.9192 | -12.6471 | -14.2732
|  | RYDE | LW |  |  | 10.5517 | 9.6396 | 8.6922 | 7.5917 | 6.3977 | 5.2787 | 4.0634 | 2.7774 | 1.218 | -0.44907 | -4.4791 | -9.0478 | -10.6067 | -11.2957 | 11.6988 | 11.1271 | 10.5457 | 9.8378 | 9.1284 | 8.4849 | 7.7731 | 7.0206 | 6.078 | 5.0705 | 2.7361 | 0.29935 | -0.37684 | -0.6718 | 7.9536 | 7.1557 | 6.3246 | 5.3453 | 4.2479 | 3.2175 | 2.1033 | 0.92749 | -0.48822 | -2.0453 | -5.7986 | -9.9831 | -11.4042 | -12.0042
|  | RYDE | ST |  |  | 11.1539 | 10.6524 | 10.178 | 9.5832 | 9.0865 | 8.6696 | 8.2177 | 7.7432 | 7.2069 | 6.6592 | 4.3419 | -0.37657 | -2.683 | -4.1121 | 11.9947 | 11.6209 | 11.2734 | 10.8148 | 10.4231 | 10.1015 | 9.7515 | 9.3863 | 8.9736 | 8.5674 | 6.8421 | 3.2804 | 1.208 | -0.91506 | 8.5078 | 8.0873 | 7.6893 | 7.174 | 6.7245 | 6.3461 | 5.938 | 5.5118 | 5.0304 | 4.5314 | 2.326 | -2.1616 | -4.2541 | -5.5067
|  | RYDE | SP |  |  | 11.1971 | 10.7091 | 10.2703 | 9.7274 | 9.2259 | 8.8064 | 8.3769 | 7.9146 | 7.4232 | 6.8892 | 5.0035 | 0.32615 | -2.2304 | -3.2316 | 12.0111 | 11.6361 | 11.2995 | 10.8613 | 10.4865 | 10.181 | 9.8656 | 9.5244 | 9.1594 | 8.7577 | 7.2942 | 3.4979 | 0.29139 | -3.2975 | 8.5479 | 8.1416 | 7.7766 | 7.3088 | 6.8497 | 6.4643 | 6.0704 | 5.651 | 5.2052 | 4.7179 | 3.0076 | -1.4285 | -3.8374 | -4.7397
MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL | MINIMUM HEADROOM | SU 14215 30481 | YES | 20.9167 | 20.7102 | 20.4141 | 20.1183 | 19.6291 | 19.1098 | 18.5581 | 17.9712 | 17.2507 | 16.496 | 14.2029 | 11.1693 | 8.8189 | 7.1579 | 7.8488 | 7.7532 | 7.6119 | 7.4844 | 7.2899 | 7.0802 | 6.8557 | 6.6018 | 6.2696 | 5.9072 | 4.7058 | 3.2529 | 1.9669 | 0.31916 | 7.9181 | 7.7732 | 7.5855 | 7.4076 | 7.0716 | 6.7194 | 6.3556 | 5.9715 | 5.5155 | 5.0409 | 3.2887 | 0.56102 | -1.4004 | -2.7963
|  | SALISBURY CENTRAL | CT |  |  | 21.024 | 20.8844 | 20.6913 | 20.4435 | 20.0992 | 19.7317 | 19.3492 | 18.9349 | 18.4528 | 17.7246 | 15.4735 | 11.626 | 8.8189 | 7.1579 | 7.8771 | 7.8077 | 7.6905 | 7.569 | 7.4147 | 7.2478 | 7.0743 | 6.8861 | 6.6536 | 6.352 | 5.3659 | 3.6688 | 1.9669 | 0.31916 | 8.0118 | 7.9256 | 7.7957 | 7.6741 | 7.4604 | 7.235 | 7.0051 | 6.7597 | 6.4836 | 6.0323 | 4.4194 | 1.0097 | -1.4004 | -2.7963
|  | SALISBURY CENTRAL | LW |  |  | 20.9167 | 20.7102 | 20.4141 | 20.1183 | 19.6291 | 19.1098 | 18.5581 | 17.9712 | 17.2507 | 16.496 | 14.2029 | 11.1693 | 9.6091 | 8.5253 | 7.8488 | 7.7532 | 7.6119 | 7.4844 | 7.2899 | 7.0802 | 6.8557 | 6.6018 | 6.2696 | 5.9072 | 4.7058 | 3.2529 | 2.8271 | 2.5101 | 7.9181 | 7.7732 | 7.5855 | 7.4076 | 7.0716 | 6.7194 | 6.3556 | 5.9715 | 5.5155 | 5.0409 | 3.2887 | 0.56102 | -0.74907 | -1.6399
|  | SALISBURY CENTRAL | ST |  |  | 21.1597 | 21.1014 | 21.0055 | 20.9208 | 20.785 | 20.6375 | 20.4786 | 20.3021 | 20.0856 | 19.8395 | 18.8157 | 15.9911 | 14.1514 | 12.957 | 7.9426 | 7.9133 | 7.8454 | 7.7999 | 7.7354 | 7.6551 | 7.5649 | 7.462 | 7.3159 | 7.1377 | 6.4245 | 4.4879 | 3.43 | 2.5407 | 8.1004 | 8.0698 | 8.0052 | 7.9599 | 7.8886 | 7.8095 | 7.7271 | 7.6351 | 7.5112 | 7.3458 | 6.7192 | 4.806 | 3.2351 | 2.2789
|  | SALISBURY CENTRAL | SP |  |  | 21.1794 | 21.1219 | 21.0227 | 20.9444 | 20.85 | 20.7496 | 20.6469 | 20.5278 | 20.3858 | 20.2076 | 19.516 | 17.3935 | 15.577 | 14.6432 | 7.9488 | 7.9252 | 7.8609 | 7.822 | 7.7712 | 7.7125 | 7.6473 | 7.5731 | 7.4755 | 7.3593 | 6.9392 | 5.5581 | 3.6599 | 0.9075 | 8.1145 | 8.0931 | 8.0362 | 8.0013 | 7.9502 | 7.8958 | 7.8419 | 7.7808 | 7.7039 | 7.5913 | 7.2025 | 6.0096 | 4.4484 | 3.6806
BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST | MINIMUM HEADROOM | SU 83597 60930 | YES | 10.1063 | 9.5483 | 8.7031 | 7.8139 | 6.5645 | 5.2453 | 3.8288 | 2.4472 | 0.86696 | -0.82824 | -5.6963 | -10.8928 | -15.2905 | -17.6363 | 17.9158 | 17.6078 | 17.1044 | 16.5684 | 15.8892 | 15.1649 | 14.3612 | 13.56 | 12.6183 | 11.5825 | 8.6616 | 4.9373 | 1.5838 | -1.7377 | 11.8391 | 11.3492 | 10.5962 | 9.7965 | 8.6682 | 7.4753 | 6.1848 | 4.9092 | 3.4371 | 1.8471 | -2.7064 | -7.4475 | -11.1511 | -13.0631
|  | SANDHURST | CT |  |  | 10.3524 | 9.9456 | 9.3805 | 8.5905 | 7.6954 | 6.74 | 5.6938 | 4.7 | 3.645 | 1.9759 | -3.1115 | -10.3441 | -15.2905 | -17.6363 | 17.9724 | 17.6976 | 17.3277 | 16.7758 | 16.2018 | 15.5859 | 14.9064 | 14.2361 | 13.4977 | 12.4426 | 9.1707 | 4.9373 | 1.5838 | -1.7377 | 12.052 | 11.696 | 11.2053 | 10.4871 | 9.6732 | 8.8039 | 7.8478 | 6.9239 | 5.9313 | 4.3751 | -0.37434 | -6.8912 | -11.1511 | -13.0631
|  | SANDHURST | LW |  |  | 10.1063 | 9.5483 | 8.7031 | 7.8139 | 6.5645 | 5.2453 | 3.8288 | 2.4472 | 0.86696 | -0.82824 | -5.6963 | -10.8928 | -12.8232 | -13.6663 | 17.9158 | 17.6078 | 17.1044 | 16.5684 | 15.8892 | 15.1649 | 14.3612 | 13.56 | 12.6183 | 11.5825 | 8.6616 | 5.9435 | 5.1454 | 4.7957 | 11.8391 | 11.3492 | 10.5962 | 9.7965 | 8.6682 | 7.4753 | 6.1848 | 4.9092 | 3.4371 | 1.8471 | -2.7064 | -7.4475 | -9.1427 | -9.8764
|  | SANDHURST | ST |  |  | 10.6473 | 10.4371 | 10.1399 | 9.834 | 9.4167 | 8.9594 | 8.4664 | 8.0093 | 7.5267 | 7.0283 | 4.9877 | -0.40696 | -3.1866 | -4.9386 | 18.1595 | 18.008 | 17.8017 | 17.5794 | 17.265 | 16.9192 | 16.5391 | 16.1653 | 15.7575 | 15.3533 | 13.6495 | 9.2117 | 6.3556 | 3.1978 | 12.3325 | 12.1618 | 11.9225 | 11.6696 | 11.2969 | 10.8874 | 10.4419 | 10.0149 | 9.5564 | 9.0861 | 7.1286 | 1.9859 | -0.53284 | -2.0658
|  | SANDHURST | SP |  |  | 10.6904 | 10.4644 | 10.1621 | 9.8626 | 9.5537 | 9.2144 | 8.8501 | 8.511 | 8.1812 | 7.7751 | 6.2846 | 2.2562 | -0.41328 | -1.2911 | 18.1742 | 17.9994 | 17.7678 | 17.5299 | 17.2865 | 17.0165 | 16.7156 | 16.4149 | 16.102 | 15.7071 | 14.1877 | 9.9323 | 5.2768 | -0.64415 | 12.3714 | 12.1824 | 11.9349 | 11.6851 | 11.4183 | 11.1243 | 10.8043 | 10.4933 | 10.1848 | 9.8041 | 8.3858 | 4.5148 | 1.9812 | 1.1937
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN | MINIMUM HEADROOM | SZ 59877 85052 | NO | 26.3884 | 25.8722 | 25.2076 | 24.5714 | 23.4088 | 22.1205 | 20.7991 | 19.3463 | 17.6534 | 15.9357 | 11.1225 | 5.4661 | 1.5241 | -0.74957 | 22.227 | 22.0443 | 21.703 | 21.4616 | 20.8994 | 20.0896 | 19.3133 | 18.4295 | 17.3605 | 16.2985 | 13.3261 | 9.1361 | 5.4997 | 1.6826 | 16.7781 | 16.4667 | 15.8355 | 15.2209 | 14.1167 | 12.8494 | 11.6014 | 10.2273 | 8.6176 | 6.9939 | 2.3923 | -2.8204 | -6.0911 | -8.0792
|  | SANDOWN | CT |  |  | 26.6927 | 26.3598 | 25.9125 | 25.4306 | 24.6682 | 23.8013 | 22.9415 | 21.9701 | 20.8687 | 19.1932 | 14.3683 | 6.6216 | 1.5241 | -0.74957 | 22.227 | 22.0443 | 21.703 | 21.4616 | 21.1394 | 20.4442 | 19.8043 | 19.0616 | 18.2035 | 17.1121 | 13.8193 | 9.1361 | 5.4997 | 1.6826 | 16.9035 | 16.6773 | 16.3113 | 15.9717 | 15.2217 | 14.3291 | 13.495 | 12.5539 | 11.4838 | 9.8743 | 5.2381 | -1.6771 | -6.0911 | -8.0792
|  | SANDOWN | LW |  |  | 26.3884 | 25.8722 | 25.2076 | 24.5714 | 23.4088 | 22.1205 | 20.7991 | 19.3463 | 17.6534 | 15.9357 | 11.1225 | 5.4661 | 3.3945 | 2.6609 | 22.2659 | 22.0932 | 21.7617 | 21.5454 | 20.8994 | 20.0896 | 19.3133 | 18.4295 | 17.3605 | 16.2985 | 13.3261 | 10.2028 | 9.3724 | 9.0607 | 16.7781 | 16.4667 | 15.8355 | 15.2209 | 14.1167 | 12.8494 | 11.6014 | 10.2273 | 8.6176 | 6.9939 | 2.3923 | -2.8204 | -4.5936 | -5.2156
|  | SANDOWN | ST |  |  | 27.0437 | 26.9083 | 26.6813 | 26.5035 | 26.1923 | 25.7952 | 25.4053 | 24.9236 | 24.3842 | 23.8168 | 21.5287 | 16.2473 | 13.0983 | 11.1352 | 22.3434 | 22.2285 | 21.9677 | 21.8335 | 21.6088 | 21.2467 | 20.9719 | 20.6079 | 20.1942 | 19.7275 | 17.714 | 13.0511 | 9.7543 | 6.1074 | 17.0856 | 16.9836 | 16.7493 | 16.6168 | 16.3799 | 16.0228 | 15.7298 | 15.3021 | 14.7557 | 14.2001 | 11.9637 | 6.6449 | 3.8987 | 2.2394
|  | SANDOWN | SP |  |  | 27.0996 | 26.9725 | 26.7645 | 26.6121 | 26.3616 | 26.032 | 25.7403 | 25.3519 | 24.9458 | 24.4821 | 22.8222 | 18.6239 | 15.7115 | 14.58 | 22.3436 | 22.2286 | 21.9695 | 21.8368 | 21.6306 | 21.2917 | 21.0468 | 20.717 | 20.3611 | 19.9711 | 18.2033 | 13.5664 | 8.4806 | 2.0501 | 17.0897 | 16.9912 | 16.7734 | 16.6611 | 16.4817 | 16.1622 | 15.9221 | 15.6037 | 15.27 | 14.8356 | 13.2124 | 8.9872 | 5.6355 | 4.6288
LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY | MINIMUM HEADROOM | SZ 85667 94289 | NO | 7.6809 | 7.0038 | 6.2159 | 5.3532 | 3.9194 | 2.3802 | 0.68058 | -1.2535 | -3.7409 | -6.0396 | -10.9048 | -17.6171 | -22.0149 | -25.1116 | 12.3537 | 11.9337 | 11.4323 | 10.8525 | 9.9974 | 9.0742 | 8.0257 | 6.797 | 5.1067 | 3.5901 | 0.71303 | -3.1736 | -6.6369 | -9.4822 | 8.4838 | 7.8129 | 7.0238 | 6.1522 | 4.7905 | 3.341 | 1.7408 | -0.090577 | -2.4767 | -4.6685 | -9.2031 | -15.3612 | -19.0813 | -21.6145
|  | SELSEY | CT |  |  | 7.9587 | 7.4768 | 6.8941 | 6.1325 | 5.1294 | 4.0538 | 2.9064 | 1.5485 | -0.068448 | -2.5221 | -7.5413 | -16.0952 | -22.0149 | -25.1116 | 12.3943 | 12.0256 | 11.5753 | 10.964 | 10.2747 | 9.5258 | 8.7055 | 7.7167 | 6.5138 | 4.8433 | 1.7168 | -3.1736 | -6.6369 | -9.4822 | 8.6815 | 8.1799 | 7.5657 | 6.7951 | 5.843 | 4.8187 | 3.7211 | 2.4159 | 0.85347 | -1.4871 | -6.1589 | -13.892 | -19.0813 | -21.6145
|  | SELSEY | LW |  |  | 7.6809 | 7.0038 | 6.2159 | 5.3532 | 3.9194 | 2.3802 | 0.68058 | -1.2535 | -3.7409 | -6.0396 | -10.9048 | -17.6171 | -20.2979 | -21.8546 | 12.3537 | 11.9337 | 11.4323 | 10.8525 | 9.9974 | 9.0742 | 8.0257 | 6.797 | 5.1067 | 3.5901 | 0.71303 | -3.0459 | -4.2669 | -4.981 | 8.4838 | 7.8129 | 7.0238 | 6.1522 | 4.7905 | 3.341 | 1.7408 | -0.090577 | -2.4767 | -4.6685 | -9.2031 | -15.3612 | -17.6885 | -19.0099
|  | SELSEY | ST |  |  | 8.3864 | 8.1894 | 7.9316 | 7.6123 | 7.2044 | 6.7498 | 6.2236 | 5.611 | 4.8734 | 4.0979 | 0.24789 | -6.1797 | -9.7113 | -11.951 | 12.7176 | 12.5393 | 12.3197 | 12.0506 | 11.7288 | 11.3659 | 10.9309 | 10.4299 | 9.8204 | 9.2159 | 6.1488 | 1.2135 | -1.6393 | -4.2222 | 9.1603 | 8.9418 | 8.6683 | 8.3307 | 7.906 | 7.4298 | 6.8988 | 6.3045 | 5.586 | 4.8385 | 1.0879 | -5.0021 | -8.1655 | -10.0873
|  | SELSEY | SP |  |  | 8.4409 | 8.2604 | 8.0414 | 7.7962 | 7.4131 | 7.0108 | 6.603 | 6.108 | 5.5136 | 4.8244 | 2.1445 | -5.2417 | -8.8685 | -10.5453 | 12.7399 | 12.5577 | 12.352 | 12.1218 | 11.8457 | 11.5451 | 11.2314 | 10.8349 | 10.3583 | 9.8113 | 7.6156 | 1.3906 | -2.5989 | -6.4995 | 9.2108 | 8.9989 | 8.7644 | 8.5032 | 8.1248 | 7.7233 | 7.3139 | 6.8094 | 6.2385 | 5.58 | 3.0018 | -4.1196 | -7.4982 | -8.9795
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY | MINIMUM HEADROOM | ST 85605 23325 | YES | 1.3504 | 0.95575 | 0.50338 | -0.034508 | -0.85624 | -1.7137 | -2.6312 | -3.605 | -4.7655 | -5.9937 | -9.5474 | -13.5461 | -16.5271 | -18.2377 | 5.1886 | 4.9597 | 4.6627 | 4.3034 | 3.8696 | 3.407 | 2.8778 | 2.3057 | 1.5909 | 0.80703 | -1.3011 | -3.3006 | -5.2052 | -6.7343 | 2.9104 | 2.5271 | 2.0799 | 1.5522 | 0.79091 | -0.0070725 | -0.87412 | -1.7979 | -2.9105 | -4.1021 | -7.4843 | -11.0872 | -13.5285 | -14.9628
|  | SHAFTESBURY | CT |  |  | 1.5999 | 1.3498 | 1.1062 | 0.69222 | 0.14912 | -0.41911 | -1.0395 | -1.7077 | -2.4793 | -3.6456 | -7.1587 | -12.7351 | -16.5271 | -18.2377 | 5.2345 | 5.04 | 4.8528 | 4.5008 | 4.1383 | 3.7551 | 3.3322 | 2.8705 | 2.3155 | 1.5682 | -0.64319 | -3.3006 | -5.2052 | -6.7343 | 3.1149 | 2.8543 | 2.606 | 2.1764 | 1.6517 | 1.1013 | 0.49821 | -0.15321 | -0.91332 | -2.0587 | -5.4915 | -10.3252 | -13.5285 | -14.9628
|  | SHAFTESBURY | LW |  |  | 1.3504 | 0.95575 | 0.50338 | -0.034508 | -0.85624 | -1.7137 | -2.6312 | -3.605 | -4.7655 | -5.9937 | -9.5474 | -13.5461 | -14.9363 | -15.6882 | 5.1886 | 4.9597 | 4.6627 | 4.3034 | 3.8696 | 3.407 | 2.8778 | 2.3057 | 1.5909 | 0.80703 | -1.3011 | -3.2494 | -3.7703 | -4.0512 | 2.9104 | 2.5271 | 2.0799 | 1.5522 | 0.79091 | -0.0070725 | -0.87412 | -1.7979 | -2.9105 | -4.1021 | -7.4843 | -11.0872 | -12.2641 | -12.8957
|  | SHAFTESBURY | ST |  |  | 1.7421 | 1.5794 | 1.4402 | 1.2603 | 1.0052 | 0.72998 | 0.43229 | 0.10064 | -0.28923 | -0.69939 | -2.3054 | -6.4054 | -8.6518 | -9.9744 | 5.3423 | 5.2123 | 5.1038 | 4.9658 | 4.7713 | 4.5574 | 4.3187 | 4.0478 | 3.7284 | 3.42 | 2.1083 | -1.1036 | -2.6369 | -3.9588 | 3.2589 | 3.086 | 2.9432 | 2.7653 | 2.5148 | 2.2429 | 1.9456 | 1.6128 | 1.2214 | 0.81762 | -0.82449 | -5.0568 | -7.0046 | -8.0421
|  | SHAFTESBURY | SP |  |  | 1.7789 | 1.6174 | 1.4821 | 1.3122 | 1.0408 | 0.76123 | 0.47044 | 0.15373 | -0.19589 | -0.58867 | -1.9314 | -5.3189 | -7.673 | -8.594 | 5.3547 | 5.2067 | 5.0818 | 4.9301 | 4.7674 | 4.5937 | 4.41 | 4.194 | 3.948 | 3.6687 | 2.6206 | -0.29936 | -2.8411 | -5.4287 | 3.2911 | 3.1127 | 2.9675 | 2.7928 | 2.5423 | 2.2827 | 2.0116 | 1.7108 | 1.377 | 1.0031 | -0.30122 | -3.7523 | -6.0678 | -6.8487
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET | MINIMUM HEADROOM | SZ 40828 88643 | NO | 1.8241 | 1.4864 | 1.1064 | 0.76725 | 0.19364 | -0.42925 | -1.105 | -1.8158 | -2.6373 | -3.5528 | -5.756 | -7.8825 | -9.8907 | -11.0636 | 4.2668 | 4.0698 | 3.8362 | 3.6184 | 3.3035 | 2.9594 | 2.5716 | 2.1614 | 1.675 | 1.121 | -0.14597 | -1.2893 | -2.4716 | -3.3824 | 1.6159 | 1.3177 | 0.98112 | 0.67383 | 0.15571 | -0.404 | -1.0101 | -1.6474 | -2.3832 | -3.2026 | -5.2016 | -7.1741 | -9.022 | -10.0427
|  | SHALFLEET | CT |  |  | 1.9768 | 1.7263 | 1.5108 | 1.2285 | 0.83059 | 0.3882 | -0.10445 | -0.62611 | -1.1929 | -2.1134 | -4.4964 | -7.5719 | -9.8907 | -11.0636 | 4.314 | 4.1462 | 4.003 | 3.7881 | 3.5378 | 3.2615 | 2.9521 | 2.6237 | 2.2603 | 1.6926 | 0.24095 | -1.2893 | -2.4716 | -3.3824 | 1.761 | 1.5451 | 1.3573 | 1.1059 | 0.75328 | 0.36341 | -0.072102 | -0.53351 | -1.0341 | -1.8575 | -4.0371 | -6.8795 | -9.022 | -10.0427
|  | SHALFLEET | LW |  |  | 1.8241 | 1.4864 | 1.1064 | 0.76725 | 0.19364 | -0.42925 | -1.105 | -1.8158 | -2.6373 | -3.5528 | -5.756 | -7.8825 | -8.8125 | -9.3364 | 4.2668 | 4.0698 | 3.8362 | 3.6184 | 3.3035 | 2.9594 | 2.5716 | 2.1614 | 1.675 | 1.121 | -0.14597 | -1.1506 | -1.5444 | -1.7705 | 1.6159 | 1.3177 | 0.98112 | 0.67383 | 0.15571 | -0.404 | -1.0101 | -1.6474 | -2.3832 | -3.2026 | -5.2016 | -7.1741 | -8.0315 | -8.5075
|  | SHALFLEET | ST |  |  | 2.0949 | 1.9303 | 1.8 | 1.7009 | 1.4983 | 1.2596 | 1.0052 | 0.72627 | 0.43445 | 0.1242 | -0.95641 | -3.419 | -4.5503 | -5.4027 | 4.3947 | 4.2816 | 4.1925 | 4.1172 | 3.9796 | 3.8179 | 3.6422 | 3.4479 | 3.2416 | 3.0299 | 2.2384 | 0.4494 | -0.35139 | -1.171 | 1.8672 | 1.7288 | 1.6184 | 1.5279 | 1.3535 | 1.15 | 0.93235 | 0.69347 | 0.44334 | 0.17385 | -0.77786 | -3.079 | -4.0804 | -4.8209
|  | SHALFLEET | SP |  |  | 2.1214 | 1.9486 | 1.813 | 1.7124 | 1.5272 | 1.3223 | 1.1024 | 0.86693 | 0.61354 | 0.31867 | -0.60988 | -2.8506 | -4.1226 | -4.6544 | 4.4062 | 4.2802 | 4.1795 | 4.0958 | 3.9828 | 3.8558 | 3.7187 | 3.5639 | 3.3963 | 3.1929 | 2.5054 | 0.71821 | -0.73403 | -2.2785 | 1.8918 | 1.7476 | 1.6339 | 1.5432 | 1.382 | 1.2064 | 1.0168 | 0.81492 | 0.59702 | 0.3404 | -0.48093 | -2.5128 | -3.695 | -4.1588
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN | MINIMUM HEADROOM | SZ 57809 81912 | NO | 11.4202 | 10.7088 | 10.0216 | 9.1617 | 8.1902 | 7.1746 | 6.1196 | 5.027 | 3.7856 | 2.4404 | -0.78264 | -4.4794 | -5.6561 | -6.6958 | 16.176 | 15.8137 | 15.4527 | 14.9441 | 14.4602 | 13.945 | 13.3893 | 12.8055 | 12.0857 | 11.3 | 9.679 | 8.0048 | 6.9096 | 5.7594 | 13.1226 | 12.547 | 11.9688 | 11.2369 | 10.4171 | 9.5119 | 8.5601 | 7.5656 | 6.4019 | 5.138 | 2.2677 | -1.0181 | -2.0693 | -3.0152
|  | SHANKLIN | CT |  |  | 11.9622 | 11.5252 | 11.1493 | 10.5437 | 9.9515 | 9.3205 | 8.6611 | 7.9778 | 7.2036 | 5.9847 | 2.9923 | -1.914 | -5.3903 | -6.6958 | 16.3423 | 16.0659 | 15.824 | 15.3806 | 15.0265 | 14.6436 | 14.2359 | 13.8095 | 13.3011 | 12.5601 | 10.8527 | 8.5804 | 6.9096 | 5.7594 | 13.5051 | 13.1282 | 12.7928 | 12.236 | 11.715 | 11.1561 | 10.567 | 9.9489 | 9.2308 | 8.1305 | 5.3746 | 1.2176 | -1.8254 | -3.0152
|  | SHANKLIN | LW |  |  | 11.4202 | 10.7088 | 10.0216 | 9.1617 | 8.1902 | 7.1746 | 6.1196 | 5.027 | 3.7856 | 2.4404 | -0.78264 | -4.4794 | -5.6561 | -6.2659 | 16.176 | 15.8137 | 15.4527 | 14.9441 | 14.4602 | 13.945 | 13.3893 | 12.8055 | 12.0857 | 11.3 | 9.679 | 8.0048 | 7.5348 | 7.2936 | 13.1226 | 12.547 | 11.9688 | 11.2369 | 10.4171 | 9.5119 | 8.5601 | 7.5656 | 6.4019 | 5.138 | 2.2677 | -1.0181 | -2.0693 | -2.6181
|  | SHANKLIN | ST |  |  | 12.1217 | 11.8118 | 11.5584 | 11.1514 | 10.7975 | 10.4252 | 10.0367 | 9.6414 | 9.22 | 8.7594 | 7.0104 | 3.692 | 1.8868 | 0.60824 | 16.4703 | 16.2838 | 16.1303 | 15.8417 | 15.6217 | 15.3878 | 15.1351 | 14.8756 | 14.5887 | 14.2958 | 13.0745 | 10.859 | 9.6653 | 8.524 | 13.6755 | 13.4254 | 13.2131 | 12.866 | 12.5564 | 12.2295 | 11.8825 | 11.5238 | 11.1341 | 10.7234 | 9.0647 | 5.9953 | 4.4239 | 3.3785
|  | SHANKLIN | SP |  |  | 12.1961 | 11.9152 | 11.6983 | 11.3364 | 10.8393 | 10.3331 | 9.82 | 9.2949 | 8.7644 | 8.1369 | 6.0813 | 1.6493 | -0.89856 | -2.3671 | 16.4973 | 16.3126 | 16.1662 | 15.8932 | 15.6437 | 15.3845 | 15.1213 | 14.8436 | 14.5548 | 14.2139 | 13.0105 | 10.1059 | 8.1302 | 6.2189 | 13.732 | 13.4972 | 13.309 | 12.9969 | 12.5994 | 12.1927 | 11.7819 | 11.351 | 10.9112 | 10.382 | 8.5247 | 4.3777 | 2.1144 | 0.88809
AXMINSTER | YEOVIL BSP | SHERBORNE | MINIMUM HEADROOM | ST 63978 18163 | YES | 7.4454 | 7.1236 | 6.7328 | 6.3108 | 5.7518 | 5.1668 | 4.5579 | 3.939 | 3.2168 | 2.5359 | 0.94412 | -0.62658 | -0.99303 | -1.2783 | 10.3699 | 10.2379 | 10.0549 | 9.8542 | 9.602 | 9.3333 | 9.047 | 8.7447 | 8.3386 | 7.9547 | 7.2368 | 6.6078 | 6.448 | 6.3316 | 8.6698 | 8.3693 | 8.0109 | 7.6268 | 7.1146 | 6.5819 | 6.0333 | 5.4704 | 4.8057 | 4.1785 | 2.7483 | 1.3534 | 1.0266 | 0.77357
|  | SHERBORNE | CT |  |  | 7.7848 | 7.6419 | 7.461 | 7.1969 | 6.857 | 6.4946 | 6.1002 | 5.7009 | 5.2645 | 4.6475 | 3.3079 | 1.4491 | 0.33316 | -0.11463 | 10.4601 | 10.38 | 10.2754 | 10.1077 | 9.9269 | 9.7292 | 9.5156 | 9.2911 | 9.0306 | 8.658 | 7.9855 | 7.2132 | 6.7184 | 6.4273 | 8.9909 | 8.8583 | 8.6923 | 8.4481 | 8.1398 | 7.8097 | 7.4498 | 7.0808 | 6.6728 | 6.093 | 4.8636 | 3.1742 | 2.1878 | 1.7902
|  | SHERBORNE | LW |  |  | 7.4454 | 7.1236 | 6.7328 | 6.3108 | 5.7518 | 5.1668 | 4.5579 | 3.939 | 3.2168 | 2.5359 | 0.94412 | -0.62658 | -0.99303 | -1.2783 | 10.3699 | 10.2379 | 10.0549 | 9.8542 | 9.602 | 9.3333 | 9.047 | 8.7447 | 8.3386 | 7.9547 | 7.2368 | 6.6078 | 6.448 | 6.3316 | 8.6698 | 8.3693 | 8.0109 | 7.6268 | 7.1146 | 6.5819 | 6.0333 | 5.4704 | 4.8057 | 4.1785 | 2.7483 | 1.3534 | 1.0266 | 0.77357
|  | SHERBORNE | ST |  |  | 7.8775 | 7.7968 | 7.6907 | 7.5588 | 7.332 | 7.0914 | 6.8487 | 6.6115 | 6.3687 | 6.1146 | 5.0729 | 3.5014 | 2.729 | 2.2085 | 10.5211 | 10.4818 | 10.4251 | 10.3508 | 10.2306 | 10.1001 | 9.9663 | 9.8328 | 9.6874 | 9.5505 | 8.9051 | 7.9868 | 7.6282 | 7.2966 | 9.076 | 9.001 | 8.9062 | 8.7911 | 8.5892 | 8.3745 | 8.1553 | 7.9374 | 7.7116 | 7.4773 | 6.4965 | 5.0316 | 4.343 | 3.8684
|  | SHERBORNE | SP |  |  | 7.9215 | 7.8574 | 7.7733 | 7.6764 | 7.464 | 7.242 | 7.0189 | 6.7915 | 6.5697 | 6.2624 | 5.2095 | 2.7618 | 1.3779 | 0.44431 | 10.5324 | 10.492 | 10.4375 | 10.3761 | 10.2773 | 10.1733 | 10.0644 | 9.9495 | 9.8363 | 9.697 | 9.1665 | 7.8155 | 7.1471 | 6.7304 | 9.1178 | 9.0578 | 8.9815 | 8.8963 | 8.7092 | 8.5134 | 8.3133 | 8.1062 | 7.9028 | 7.6182 | 6.6484 | 4.3957 | 3.1156 | 2.2918
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE | MINIMUM HEADROOM | SP 03884 19102 | YES | 17.0733 | 16.6673 | 16.1557 | 15.6172 | 14.8075 | 13.9687 | 13.0744 | 12.1261 | 10.9956 | 9.791 | 6.4849 | 2.7066 | -0.22234 | -1.9572 | 21.2272 | 21.0292 | 20.7623 | 20.4769 | 20.0843 | 19.6731 | 19.2212 | 18.7361 | 18.1431 | 17.5161 | 15.8149 | 13.5817 | 11.1188 | 8.9203 | 18.3197 | 17.9584 | 17.4931 | 17 | 16.2608 | 15.4937 | 14.6713 | 13.7972 | 12.7558 | 11.6562 | 8.6148 | 5.1679 | 2.625 | 1.1025
|  | SHIPTON OLIFFE | CT |  |  | 17.3801 | 17.1397 | 16.8666 | 16.4442 | 15.9374 | 15.4062 | 14.8115 | 14.1753 | 13.4385 | 12.2824 | 8.9157 | 3.7019 | -0.22234 | -1.9572 | 21.3291 | 21.182 | 21.0149 | 20.7569 | 20.4671 | 20.1604 | 19.8153 | 19.4429 | 19.0051 | 18.3674 | 16.4832 | 13.5817 | 11.1188 | 8.9203 | 18.5923 | 18.3815 | 18.1414 | 17.7708 | 17.3099 | 16.8272 | 16.2877 | 15.7111 | 15.0469 | 13.992 | 10.9086 | 6.0783 | 2.625 | 1.1025
|  | SHIPTON OLIFFE | LW |  |  | 17.0733 | 16.6673 | 16.1557 | 15.6172 | 14.8075 | 13.9687 | 13.0744 | 12.1261 | 10.9956 | 9.791 | 6.4849 | 2.7066 | 1.2697 | 0.48034 | 21.2272 | 21.0292 | 20.7623 | 20.4769 | 20.0843 | 19.6731 | 19.2212 | 18.7361 | 18.1431 | 17.5161 | 15.8149 | 14.0055 | 13.3976 | 13.0645 | 18.3197 | 17.9584 | 17.4931 | 17 | 16.2608 | 15.4937 | 14.6713 | 13.7972 | 12.7558 | 11.6562 | 8.6148 | 5.1679 | 3.9019 | 3.2106
|  | SHIPTON OLIFFE | ST |  |  | 17.5174 | 17.3795 | 17.23 | 17.0631 | 16.8274 | 16.5732 | 16.2913 | 15.9832 | 15.6363 | 15.2654 | 13.7342 | 10.123 | 8.1731 | 6.8624 | 21.4086 | 21.3183 | 21.2194 | 21.1084 | 20.9574 | 20.7926 | 20.6068 | 20.4013 | 20.1661 | 19.9191 | 18.8916 | 16.3828 | 14.5653 | 12.4946 | 18.7179 | 18.5992 | 18.4702 | 18.3259 | 18.1128 | 17.8834 | 17.6302 | 17.3539 | 17.0432 | 16.7055 | 15.3254 | 12.0376 | 10.2208 | 8.9845
|  | SHIPTON OLIFFE | SP |  |  | 17.5569 | 17.4159 | 17.2675 | 17.1123 | 16.8588 | 16.5875 | 16.3094 | 16.0145 | 15.6836 | 15.2908 | 13.8938 | 10.4622 | 8.3868 | 7.4602 | 21.422 | 21.3246 | 21.2185 | 21.1052 | 20.9481 | 20.7768 | 20.5953 | 20.3965 | 20.1689 | 19.8917 | 18.8601 | 16.1466 | 13.2974 | 9.5449 | 18.7533 | 18.6347 | 18.5096 | 18.3776 | 18.1442 | 17.8945 | 17.6395 | 17.3704 | 17.0689 | 16.7084 | 15.4359 | 12.3306 | 10.4273 | 9.5638
NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY | MINIMUM HEADROOM | SU 39988 13808 | YES | 4.3194 | 4.0149 | 3.6642 | 3.2997 | 2.7109 | 2.0624 | 1.3964 | 0.69786 | -0.17711 | -1.1412 | -4.0573 | -7.7512 | -9.6364 | -11.0059 | 4.4904 | 4.3553 | 4.1786 | 3.9894 | 3.7146 | 3.4019 | 3.0684 | 2.7133 | 2.2509 | 1.738 | 0.25808 | -1.5153 | -3.1675 | -4.5497 | 2.0213 | 1.7491 | 1.4313 | 1.0998 | 0.57042 | -0.0090291 | -0.60723 | -1.2431 | -2.0418 | -2.9232 | -5.5323 | -8.734 | -10.3029 | -11.4991
|  | SHIRLEY | CT |  |  | 4.6379 | 4.4986 | 4.3442 | 4.1355 | 3.7914 | 3.3927 | 2.9764 | 2.532 | 1.9386 | 1.0395 | -1.7718 | -6.5691 | -9.6364 | -11.0059 | 4.5854 | 4.4976 | 4.396 | 4.2416 | 4.0406 | 3.8061 | 3.5566 | 3.2867 | 2.9311 | 2.4347 | 0.88967 | -1.5153 | -3.1675 | -4.5497 | 2.2941 | 2.1639 | 2.015 | 1.7934 | 1.4699 | 1.098 | 0.70635 | 0.28607 | -0.26043 | -1.0721 | -3.5778 | -7.6948 | -10.3029 | -11.4991
|  | SHIRLEY | LW |  |  | 4.3194 | 4.0149 | 3.6642 | 3.2997 | 2.7109 | 2.0624 | 1.3964 | 0.69786 | -0.17711 | -1.1412 | -4.0573 | -7.7512 | -8.8131 | -9.5314 | 4.4904 | 4.3553 | 4.1786 | 3.9894 | 3.7146 | 3.4019 | 3.0684 | 2.7133 | 2.2509 | 1.738 | 0.25808 | -1.4643 | -1.886 | -2.1639 | 2.0213 | 1.7491 | 1.4313 | 1.0998 | 0.57042 | -0.0090291 | -0.60723 | -1.2431 | -2.0418 | -2.9232 | -5.5323 | -8.734 | -9.6319 | -10.2343
|  | SHIRLEY | ST |  |  | 4.7073 | 4.6101 | 4.5086 | 4.4009 | 4.2209 | 4.0021 | 3.7755 | 3.5363 | 3.2205 | 2.8607 | 1.4889 | -1.4023 | -2.8688 | -3.8796 | 4.6406 | 4.5839 | 4.5223 | 4.4536 | 4.3413 | 4.2014 | 4.0509 | 3.8888 | 3.6738 | 3.4437 | 2.5327 | 0.55971 | -0.63017 | -1.9002 | 2.3662 | 2.2792 | 2.188 | 2.0907 | 1.9253 | 1.7237 | 1.5123 | 1.2854 | 0.98613 | 0.6584 | -0.60916 | -3.2609 | -4.5158 | -5.3418
|  | SHIRLEY | SP |  |  | 4.7413 | 4.6574 | 4.5715 | 4.4791 | 4.1883 | 3.8773 | 3.5577 | 3.233 | 2.8438 | 2.3837 | 0.83629 | -2.317 | -4.0688 | -5.0465 | 4.6518 | 4.5925 | 4.5275 | 4.4549 | 4.312 | 4.1509 | 3.9797 | 3.7979 | 3.5702 | 3.2996 | 2.3184 | 0.09091 | -1.8064 | -4.1097 | 2.3963 | 2.3194 | 2.238 | 2.1487 | 1.8954 | 1.6249 | 1.3438 | 1.0574 | 0.71912 | 0.31787 | -1.0497 | -3.901 | -5.4909 | -6.3355
MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM | MINIMUM HEADROOM | SU 23782 87902 | NO | 0.067378 | -0.094018 | -0.2589 | -0.42617 | -0.65419 | -0.88801 | -1.1229 | -1.4059 | -1.7405 | -2.0451 | -2.7859 | -3.3781 | -3.8993 | -4.4548 | 0.67152 | 0.60618 | 0.53909 | 0.47028 | 0.3774 | 0.2806 | 0.18159 | 0.078384 | -0.029311 | -0.14143 | -0.46624 | -0.76248 | -0.88148 | -1.1158 | -0.081572 | -0.24789 | -0.42231 | -0.60208 | -0.84092 | -1.0871 | -1.3432 | -1.619 | -1.9364 | -2.2178 | -2.8616 | -3.39 | -3.8227 | -4.2952
|  | SHRIVENHAM | CT |  |  | 0.12841 | 0.11738 | 0.10231 | 0.085773 | 0.0010265 | -0.12267 | -0.24859 | -0.39764 | -0.59691 | -0.86936 | -1.3983 | -1.9716 | -2.093 | -2.1531 | 0.75934 | 0.72984 | 0.69752 | 0.66311 | 0.61204 | 0.55694 | 0.49959 | 0.43635 | 0.37588 | 0.26109 | 0.016089 | -0.26339 | -0.36112 | -0.4499 | 0.12936 | 0.051497 | -0.040711 | -0.13774 | -0.27581 | -0.41986 | -0.57541 | -0.7558 | -0.94277 | -1.1983 | -1.6755 | -2.1865 | -2.2973 | -2.3517
|  | SHRIVENHAM | LW |  |  | 0.067378 | -0.094018 | -0.2589 | -0.42617 | -0.65419 | -0.88801 | -1.1229 | -1.4059 | -1.7405 | -2.0451 | -2.7859 | -3.3781 | -3.4358 | -3.5024 | 0.67152 | 0.60618 | 0.53909 | 0.47028 | 0.3774 | 0.2806 | 0.18159 | 0.078384 | -0.029311 | -0.14143 | -0.46624 | -0.76248 | -0.79601 | -0.8264 | -0.081572 | -0.24789 | -0.42231 | -0.60208 | -0.84092 | -1.0871 | -1.3432 | -1.619 | -1.9364 | -2.2178 | -2.8616 | -3.39 | -3.4437 | -3.5012
|  | SHRIVENHAM | ST |  |  | 0.14062 | 0.1363 | 0.12977 | 0.12215 | 0.055566 | -0.023267 | -0.10303 | -0.18666 | -0.27428 | -0.38201 | -0.82783 | -1.5545 | -1.9766 | -2.2381 | 0.76918 | 0.74186 | 0.71415 | 0.69222 | 0.66013 | 0.62692 | 0.59266 | 0.55603 | 0.51663 | 0.46739 | 0.28299 | -0.088553 | -0.29681 | -0.43718 | 0.16108 | 0.092147 | 0.016777 | -0.045696 | -0.13341 | -0.22394 | -0.31824 | -0.41942 | -0.53071 | -0.65157 | -1.1499 | -1.8111 | -2.188 | -2.4181
|  | SHRIVENHAM | SP |  |  | 0.14077 | 0.13586 | 0.13067 | 0.1253 | 0.0072493 | -0.19651 | -0.40111 | -0.60631 | -0.81213 | -1.0765 | -1.7397 | -3.0684 | -3.8993 | -4.4548 | 0.78049 | 0.76141 | 0.74163 | 0.72124 | 0.64406 | 0.56599 | 0.48684 | 0.40759 | 0.32727 | 0.22386 | -0.026424 | -0.53841 | -0.88148 | -1.1158 | 0.19088 | 0.138 | 0.083909 | 0.029981 | -0.16332 | -0.35906 | -0.55414 | -0.75616 | -0.95989 | -1.2166 | -1.873 | -3.1019 | -3.8227 | -4.2952
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON | MINIMUM HEADROOM | ST 85356 13659 | YES | 14.6327 | 14.2196 | 13.7122 | 13.1588 | 12.242 | 11.2651 | 10.2127 | 9.0843 | 7.7396 | 6.2729 | 1.8825 | -3.7598 | -8.1851 | -11.335 | 20.3263 | 20.2079 | 20.0322 | 19.6114 | 19.1123 | 18.5669 | 17.9743 | 17.3102 | 16.5561 | 15.5078 | 12.1465 | 6.4554 | -0.68748 | -15.8888 | 16.4978 | 16.1189 | 15.647 | 15.1303 | 14.2897 | 13.3911 | 12.4161 | 11.364 | 10.1043 | 8.7226 | 4.6124 | -0.47487 | -4.11 | -6.6553
|  | SHROTON | CT |  |  | 14.8175 | 14.5278 | 14.1905 | 13.7226 | 13.087 | 12.4021 | 11.682 | 10.8928 | 10.0121 | 8.5952 | 4.1817 | -2.9283 | -8.1851 | -11.335 | 20.3263 | 20.2079 | 20.0322 | 19.6114 | 19.1123 | 18.5669 | 17.9743 | 17.3102 | 16.5561 | 15.5078 | 12.1465 | 6.4554 | 0.39636 | -7.6931 | 16.6559 | 16.3864 | 16.0707 | 15.6256 | 15.035 | 14.3967 | 13.7226 | 12.978 | 12.1456 | 10.8188 | 6.7007 | 0.34739 | -4.11 | -6.6553
|  | SHROTON | LW |  |  | 14.6327 | 14.2196 | 13.7122 | 13.1588 | 12.242 | 11.2651 | 10.2127 | 9.0843 | 7.7396 | 6.2729 | 1.8825 | -3.7598 | -6.6917 | -8.5618 | 20.3445 | 20.2434 | 20.0624 | 19.7134 | 19.2106 | 18.6654 | 18.0553 | 17.3881 | 16.5656 | 15.6466 | 12.9493 | 9.8462 | 8.476 | 7.5475 | 16.4978 | 16.1189 | 15.647 | 15.1303 | 14.2897 | 13.3911 | 12.4161 | 11.364 | 10.1043 | 8.7226 | 4.6124 | -0.47487 | -2.9464 | -4.4815
|  | SHROTON | ST |  |  | 15.1059 | 14.9909 | 14.8514 | 14.6905 | 14.4402 | 14.1592 | 13.8516 | 13.5024 | 13.0886 | 12.6354 | 10.7013 | 5.2619 | 1.9182 | -0.35953 | 20.4024 | 20.3304 | 20.2492 | 20.1567 | 19.9727 | 19.6515 | 19.2904 | 18.8756 | 18.3945 | 17.8947 | 15.817 | 10.0366 | 4.4126 | -3.1819 | 16.9296 | 16.825 | 16.695 | 16.5431 | 16.306 | 16.0384 | 15.7429 | 15.403 | 15.0027 | 14.5781 | 12.7279 | 7.646 | 4.7717 | 2.8858
|  | SHROTON | SP |  |  | 15.1395 | 15.0176 | 14.8794 | 14.7273 | 14.547 | 14.3479 | 14.1343 | 13.8734 | 13.5846 | 13.2315 | 11.8415 | 7.6468 | 4.2075 | 2.469 | 20.4021 | 20.3245 | 20.2347 | 20.134 | 19.9119 | 19.5967 | 19.2445 | 18.8235 | 18.3448 | 17.7671 | 15.4853 | 8.867 | -0.68748 | -15.8888 | 16.9564 | 16.8394 | 16.7064 | 16.5593 | 16.3888 | 16.2007 | 15.9989 | 15.7447 | 15.4645 | 15.1357 | 13.8164 | 9.8339 | 6.7141 | 5.2799
LALEHAM | STAINES | SIDNEY ROAD | MINIMUM HEADROOM | TQ 04100 71760 | NO | 7.7946 | 7.508 | 7.2153 | 6.901 | 6.6125 | 6.2915 | 5.9499 | 5.5804 | 5.109 | 4.666 | 3.7856 | 2.7831 | 2.4756 | 2.2041 | 10.4574 | 10.3938 | 10.3299 | 10.2604 | 10.2174 | 10.0667 | 9.8725 | 9.6588 | 9.3634 | 9.0861 | 8.6207 | 8.1243 | 7.7311 | 7.3716 | 8.1088 | 7.8613 | 7.6048 | 7.3281 | 7.0629 | 6.7685 | 6.4532 | 6.1112 | 5.6676 | 5.2503 | 4.4462 | 3.5421 | 3.2709 | 3.0413
|  | SIDNEY ROAD | CT |  |  | 7.8978 | 7.6732 | 7.4405 | 7.1815 | 6.9911 | 6.7793 | 6.5544 | 6.3026 | 6.0138 | 5.5747 | 4.6939 | 3.3994 | 2.5637 | 2.2041 | 10.4574 | 10.3938 | 10.3299 | 10.2604 | 10.2174 | 10.1685 | 10.0601 | 9.8925 | 9.693 | 9.4026 | 8.8805 | 8.1979 | 7.7311 | 7.3716 | 8.1922 | 7.9998 | 7.7974 | 7.5709 | 7.3931 | 7.1969 | 6.9874 | 6.752 | 6.4792 | 6.0633 | 5.2506 | 4.0934 | 3.3569 | 3.0413
|  | SIDNEY ROAD | LW |  |  | 7.7946 | 7.508 | 7.2153 | 6.901 | 6.6125 | 6.2915 | 5.9499 | 5.5804 | 5.109 | 4.666 | 3.7856 | 2.7831 | 2.4756 | 2.347 | 10.4667 | 10.4046 | 10.3448 | 10.2796 | 10.2354 | 10.0667 | 9.8725 | 9.6588 | 9.3634 | 9.0861 | 8.6207 | 8.1243 | 7.9926 | 7.9369 | 8.1088 | 7.8613 | 7.6048 | 7.3281 | 7.0629 | 6.7685 | 6.4532 | 6.1112 | 5.6676 | 5.2503 | 4.4462 | 3.5421 | 3.2709 | 3.1584
|  | SIDNEY ROAD | ST |  |  | 8.0625 | 7.9379 | 7.8126 | 7.6739 | 7.5796 | 7.4689 | 7.3524 | 7.2198 | 7.0757 | 6.9266 | 6.242 | 5.2053 | 4.7241 | 4.4089 | 10.494 | 10.4498 | 10.4082 | 10.3625 | 10.3386 | 10.3086 | 10.2753 | 10.2366 | 10.1931 | 10.1445 | 9.73 | 8.9678 | 8.6033 | 8.2598 | 8.349 | 8.2493 | 8.1456 | 8.0285 | 7.9417 | 7.8407 | 7.7336 | 7.6108 | 7.4761 | 7.3392 | 6.6821 | 5.704 | 5.2714 | 4.9946
|  | SIDNEY ROAD | SP |  |  | 8.077 | 7.9628 | 7.8559 | 7.7439 | 7.6657 | 7.5769 | 7.4853 | 7.3764 | 7.2657 | 7.1226 | 6.5984 | 5.2345 | 4.6175 | 4.3051 | 10.4927 | 10.4493 | 10.4088 | 10.3662 | 10.3476 | 10.3244 | 10.2997 | 10.2693 | 10.2377 | 10.2021 | 10.0019 | 8.9828 | 8.509 | 8.1548 | 8.3597 | 8.2682 | 8.1807 | 8.0877 | 8.0184 | 7.9398 | 7.858 | 7.7593 | 7.6577 | 7.5293 | 7.0356 | 5.7351 | 5.1661 | 4.8871
NURSLING GSP | ROWNHAMS | SILKSTEAD | MINIMUM HEADROOM | SU 44578 24565 | YES | 11.5086 | 11.0608 | 10.5422 | 9.9703 | 9.1611 | 8.329 | 7.4568 | 6.5206 | 5.4093 | 4.3135 | 1.7945 | -1.068 | -1.957 | -2.8663 | 15.2822 | 15.0862 | 14.8499 | 14.5848 | 14.2215 | 13.8105 | 13.3594 | 12.8643 | 12.2463 | 11.607 | 10.4202 | 9.1885 | 8.4665 | 7.6807 | 9.0169 | 8.6105 | 8.1439 | 7.6303 | 6.8995 | 6.1458 | 5.3511 | 4.4951 | 3.4692 | 2.4553 | 0.18154 | -2.3746 | -3.1647 | -3.9984
|  | SILKSTEAD | CT |  |  | 11.9476 | 11.7309 | 11.4881 | 11.1077 | 10.6045 | 10.078 | 9.5081 | 8.8725 | 8.1568 | 7.1216 | 4.8386 | 1.0647 | -1.733 | -2.8663 | 15.4425 | 15.3304 | 15.2041 | 15.008 | 14.7437 | 14.4444 | 14.1189 | 13.7434 | 13.2863 | 12.6516 | 11.4094 | 9.7376 | 8.4665 | 7.6807 | 9.4147 | 9.2166 | 8.9955 | 8.6581 | 8.2027 | 7.7264 | 7.2106 | 6.6368 | 5.9935 | 5.0549 | 2.9443 | -0.48929 | -2.956 | -3.9984
|  | SILKSTEAD | LW |  |  | 11.5086 | 11.0608 | 10.5422 | 9.9703 | 9.1611 | 8.329 | 7.4568 | 6.5206 | 5.4093 | 4.3135 | 1.7945 | -1.068 | -1.957 | -2.5321 | 15.2822 | 15.0862 | 14.8499 | 14.5848 | 14.2215 | 13.8105 | 13.3594 | 12.8643 | 12.2463 | 11.607 | 10.4202 | 9.1885 | 8.8224 | 8.5921 | 9.0169 | 8.6105 | 8.1439 | 7.6303 | 6.8995 | 6.1458 | 5.3511 | 4.4951 | 3.4692 | 2.4553 | 0.18154 | -2.3746 | -3.1647 | -3.6928
|  | SILKSTEAD | ST |  |  | 12.0847 | 11.9531 | 11.8117 | 11.6292 | 11.3352 | 11.0232 | 10.6966 | 10.3437 | 9.9641 | 9.5805 | 7.9801 | 5.4645 | 4.1412 | 3.182 | 15.5152 | 15.4474 | 15.3738 | 15.2762 | 15.1275 | 14.969 | 14.802 | 14.6071 | 14.3733 | 14.1493 | 13.1099 | 11.4886 | 10.7047 | 10.0014 | 9.5422 | 9.4225 | 9.2929 | 9.1288 | 8.862 | 8.5801 | 8.2871 | 7.9709 | 7.6307 | 7.2804 | 5.8353 | 3.5207 | 2.2666 | 1.3834
|  | SILKSTEAD | SP |  |  | 12.1556 | 12.0412 | 11.9203 | 11.7757 | 11.4219 | 11.0599 | 10.6941 | 10.3 | 9.902 | 9.4067 | 7.7432 | 4.0186 | 2.0469 | 0.85013 | 15.5416 | 15.4783 | 15.4103 | 15.328 | 15.1597 | 14.9891 | 14.815 | 14.6241 | 14.4276 | 14.1775 | 13.2574 | 10.9564 | 9.7774 | 8.83 | 9.6048 | 9.5007 | 9.3912 | 9.2648 | 8.9411 | 8.6173 | 8.2904 | 7.9365 | 7.5775 | 7.1301 | 5.6089 | 2.165 | 0.38191 | -0.67635
BRAMLEY (FLEE) | READING BSP | SILVER STREET | MINIMUM HEADROOM | SU 71957 72821 | YES | 16.1831 | 15.3675 | 14.9081 | 14.358 | 13.5167 | 12.5876 | 11.7095 | 10.8369 | 9.5851 | 8.1207 | 3.3348 | -0.82566 | -3.2744 | -4.9407 | 20.2172 | 19.7693 | 19.5129 | 19.2044 | 18.7689 | 18.2841 | 17.8125 | 17.2837 | 16.4774 | 15.4779 | 12.5782 | 9.8178 | 7.6943 | 5.6393 | 17.7781 | 17.475 | 17.337 | 16.8742 | 16.1173 | 15.2816 | 14.4665 | 13.6434 | 12.4484 | 11.0139 | 6.6323 | 2.8335 | 0.94621 | -0.40694
|  | SILVER STREET | CT |  |  | 16.3427 | 15.6316 | 15.2934 | 14.8218 | 14.1968 | 13.4916 | 12.878 | 12.2762 | 11.3697 | 9.9482 | 5.1044 | -0.048975 | -3.2744 | -4.9407 | 20.2532 | 19.8289 | 19.6051 | 19.2979 | 18.927 | 18.5093 | 18.0972 | 17.6564 | 17.0066 | 16.0144 | 12.9478 | 9.8178 | 7.6943 | 5.6393 | 17.7781 | 17.475 | 17.337 | 17.1556 | 16.6742 | 16.0278 | 15.4438 | 14.8576 | 13.9853 | 12.6015 | 8.1641 | 3.6104 | 0.94621 | -0.40694
|  | SILVER STREET | LW |  |  | 16.1831 | 15.3675 | 14.9081 | 14.358 | 13.5167 | 12.5876 | 11.7095 | 10.8369 | 9.5851 | 8.1207 | 3.3348 | -0.82566 | -2.4281 | -3.3022 | 20.2172 | 19.7693 | 19.5129 | 19.2044 | 18.7689 | 18.2841 | 17.8125 | 17.2837 | 16.4774 | 15.4779 | 12.5782 | 10.1737 | 9.4546 | 9.04 | 17.7919 | 17.4827 | 17.3386 | 16.8742 | 16.1173 | 15.2816 | 14.4665 | 13.6434 | 12.4484 | 11.0139 | 6.6323 | 2.8335 | 1.5072 | 0.7965
|  | SILVER STREET | ST |  |  | 16.6935 | 16.2554 | 16.087 | 15.8733 | 15.5748 | 15.2307 | 14.9366 | 14.6511 | 14.171 | 13.5577 | 10.7068 | 6.6913 | 4.7248 | 3.479 | 20.4504 | 20.1876 | 20.0632 | 19.9088 | 19.702 | 19.4656 | 19.2503 | 19.0324 | 18.6724 | 18.1772 | 15.9978 | 12.7463 | 10.8689 | 8.9473 | 17.8817 | 17.6428 | 17.5641 | 17.4635 | 17.3338 | 17.1803 | 17.0501 | 16.9221 | 16.6731 | 16.0634 | 13.3337 | 9.5334 | 7.7906 | 6.7373
|  | SILVER STREET | SP |  |  | 16.7294 | 16.3091 | 16.1561 | 15.9617 | 15.7106 | 15.4139 | 15.1613 | 14.9221 | 14.5318 | 13.9902 | 11.7004 | 8.0565 | 5.8598 | 4.8842 | 20.4629 | 20.2044 | 20.0813 | 19.9289 | 19.753 | 19.5454 | 19.356 | 19.167 | 18.8559 | 18.3814 | 16.5339 | 13.1211 | 10.1932 | 6.9033 | 17.8863 | 17.6493 | 17.5741 | 17.4779 | 17.3685 | 17.2385 | 17.1342 | 17.0378 | 16.8345 | 16.4964 | 14.3468 | 10.8146 | 8.783 | 7.9392
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD | MINIMUM HEADROOM | SZ 18262 93590 | YES | 4.3285 | 3.9687 | 3.5964 | 3.1904 | 2.591 | 1.9505 | 1.2493 | 0.48588 | -0.51301 | -1.5098 | -4.1155 | -7.2541 | -7.9616 | -8.8152 | 3.7029 | 3.4883 | 3.2644 | 3.0135 | 2.6762 | 2.3087 | 1.8903 | 1.4255 | 0.7628 | 0.11571 | -1.4964 | -3.3458 | -3.9744 | -4.6588 | 2.749 | 2.4158 | 2.0712 | 1.6955 | 1.138 | 0.54275 | -0.10772 | -0.81465 | -1.7331 | -2.6553 | -5.1127 | -8.0637 | -8.6844 | -9.3916
|  | SOMERFORD | CT |  |  | 4.5013 | 4.251 | 3.9595 | 3.6613 | 3.2561 | 2.8207 | 2.3672 | 1.8598 | 1.2102 | 0.29014 | -2.0177 | -5.835 | -7.9616 | -8.8152 | 3.7375 | 3.5536 | 3.3363 | 3.1126 | 2.8477 | 2.5595 | 2.2472 | 1.8922 | 1.4229 | 0.80938 | -0.66014 | -2.8945 | -3.9744 | -4.6588 | 2.9151 | 2.6862 | 2.4204 | 2.1474 | 1.7724 | 1.3699 | 0.9515 | 0.48477 | -0.11183 | -0.95711 | -3.1185 | -6.729 | -8.6428 | -9.3916
|  | SOMERFORD | LW |  |  | 4.3285 | 3.9687 | 3.5964 | 3.1904 | 2.591 | 1.9505 | 1.2493 | 0.48588 | -0.51301 | -1.5098 | -4.1155 | -7.2541 | -7.9568 | -8.3099 | 3.7029 | 3.4883 | 3.2644 | 3.0135 | 2.6762 | 2.3087 | 1.8903 | 1.4255 | 0.7628 | 0.11571 | -1.4964 | -3.3458 | -3.6274 | -3.7634 | 2.749 | 2.4158 | 2.0712 | 1.6955 | 1.138 | 0.54275 | -0.10772 | -0.81465 | -1.7331 | -2.6553 | -5.1127 | -8.0637 | -8.6844 | -8.9935
|  | SOMERFORD | ST |  |  | 4.7149 | 4.5912 | 4.4406 | 4.277 | 4.0693 | 3.839 | 3.5867 | 3.3051 | 2.9415 | 2.5396 | 0.73426 | -2.8749 | -4.6699 | -5.3073 | 3.9015 | 3.8137 | 3.7034 | 3.5813 | 3.4365 | 3.2736 | 3.0903 | 2.8826 | 2.6077 | 2.3187 | 0.96902 | -1.6948 | -2.9951 | -3.6332 | 3.1078 | 2.9936 | 2.8561 | 2.7066 | 2.5152 | 2.3034 | 2.071 | 1.8117 | 1.4755 | 1.1009 | -0.56429 | -3.955 | -5.7747 | -6.2625
|  | SOMERFORD | SP |  |  | 4.7456 | 4.6438 | 4.5341 | 4.4123 | 4.1569 | 3.8901 | 3.6208 | 3.3119 | 2.961 | 2.5682 | 1.1484 | -2.5141 | -4.8193 | -5.6655 | 3.9147 | 3.8365 | 3.75 | 3.6517 | 3.5042 | 3.3466 | 3.1833 | 2.9889 | 2.7574 | 2.5068 | 1.554 | -1.0862 | -2.8485 | -3.7223 | 3.1367 | 3.0434 | 2.9428 | 2.8313 | 2.5935 | 2.3454 | 2.0944 | 1.8079 | 1.4819 | 1.1164 | -0.19738 | -3.5802 | -5.7583 | -6.5534
LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTEAD | MINIMUM HEADROOM | SU 94025 00705 | YES | 17.7371 | 17.3145 | 16.8467 | 16.3334 | 15.4915 | 14.5944 | 13.644 | 12.6254 | 11.4912 | 10.2891 | 6.2798 | 0.42045 | -2.7135 | -5.6552 | 15.7344 | 15.539 | 15.3267 | 15.0905 | 14.711 | 14.3049 | 13.8697 | 13.4025 | 12.8348 | 12.0206 | 9.2654 | 3.7049 | -2.5224 | -15.6661 | 11.6573 | 11.5412 | 11.4029 | 11.2382 | 11.0436 | 10.2752 | 9.4062 | 8.4789 | 7.4644 | 6.3904 | 2.8285 | -2.4973 | -5.0947 | -7.5799
|  | SOUTH BERSTEAD | CT |  |  | 17.9733 | 17.6929 | 17.3712 | 16.9867 | 16.3974 | 15.7665 | 15.1696 | 14.5228 | 13.7856 | 12.68 | 9.0684 | 2.1838 | -2.7135 | -5.6552 | 15.7847 | 15.5985 | 15.3876 | 15.1435 | 14.7962 | 14.4218 | 14.0243 | 13.4749 | 12.8348 | 12.0206 | 9.2654 | 3.7049 | -1.8984 | -9.23 | 11.6573 | 11.5412 | 11.4029 | 11.2392 | 11.0614 | 10.8629 | 10.6463 | 10.3482 | 9.7064 | 8.715 | 5.3716 | -0.82261 | -5.0947 | -7.5799
|  | SOUTH BERSTEAD | LW |  |  | 17.7371 | 17.3145 | 16.8467 | 16.3334 | 15.4915 | 14.5944 | 13.644 | 12.6254 | 11.4912 | 10.2891 | 6.2798 | 0.42045 | -2.3485 | -4.2131 | 15.7344 | 15.539 | 15.3267 | 15.0905 | 14.711 | 14.3049 | 13.8697 | 13.4025 | 12.8689 | 12.143 | 9.6907 | 6.2819 | 4.9394 | 3.9983 | 11.6763 | 11.5493 | 11.4072 | 11.2382 | 11.0436 | 10.2752 | 9.4062 | 8.4789 | 7.4644 | 6.3904 | 2.8285 | -2.4973 | -4.8347 | -6.3693
|  | SOUTH BERSTEAD | ST |  |  | 18.2607 | 18.1473 | 18.0197 | 17.8708 | 17.6575 | 17.4251 | 17.1679 | 16.881 | 16.5222 | 16.1046 | 14.4184 | 9.5628 | 6.0983 | 3.9742 | 15.9173 | 15.8092 | 15.6903 | 15.5551 | 15.377 | 15.1807 | 14.959 | 14.7102 | 14.3755 | 13.926 | 12.1302 | 6.9808 | 1.6001 | -5.3391 | 11.7566 | 11.6986 | 11.6338 | 11.5594 | 11.4637 | 11.3534 | 11.2263 | 11.0818 | 10.8857 | 10.6516 | 9.4225 | 5.2489 | 2.7448 | 0.9862
|  | SOUTH BERSTEAD | SP |  |  | 18.3088 | 18.1999 | 18.0771 | 17.9439 | 17.764 | 17.5724 | 17.3589 | 17.1328 | 16.8627 | 16.5215 | 15.2888 | 11.542 | 7.9349 | 5.9979 | 15.9267 | 15.8156 | 15.6861 | 15.5418 | 15.3519 | 15.1395 | 14.8985 | 14.6324 | 14.2399 | 13.7279 | 11.78 | 6.0643 | -2.5224 | -15.6661 | 11.765 | 11.7093 | 11.6472 | 11.5778 | 11.5014 | 11.4166 | 11.3221 | 11.2178 | 11.0847 | 10.9335 | 10.3655 | 7.5851 | 4.4281 | 2.7915
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE | MINIMUM HEADROOM | SZ 13563 92074 | YES | 10.5457 | 9.999 | 9.1429 | 8.1678 | 6.6898 | 5.2173 | 3.6385 | 1.9279 | 0.13817 | -1.7756 | -6.6647 | -12.357 | -17.8719 | -20.8124 | 6.9057 | 6.5816 | 6.0339 | 5.4091 | 4.5849 | 3.7485 | 2.8157 | 1.7941 | 0.63627 | -0.63046 | -3.6101 | -6.9001 | -9.8487 | -12.1158 | 2.0502 | 1.5622 | 0.79748 | -0.074422 | -1.3928 | -2.7179 | -4.1491 | -5.7012 | -7.367 | -9.1808 | -13.8017 | -18.8963 | -23.5758 | -26.1154
|  | SOUTHBOURNE | CT |  |  | 10.7777 | 10.3848 | 9.7915 | 8.9275 | 7.8561 | 6.7954 | 5.6454 | 4.3888 | 3.198 | 1.2478 | -4.1595 | -11.9867 | -17.8719 | -20.8124 | 6.9499 | 6.6677 | 6.261 | 5.6333 | 4.9487 | 4.2532 | 3.4946 | 2.6651 | 1.8076 | 0.55268 | -2.8162 | -6.9001 | -9.8487 | -12.1158 | 2.2494 | 1.8975 | 1.3775 | 0.59888 | -0.35859 | -1.3181 | -2.3623 | -3.5028 | -4.6406 | -6.4966 | -11.5452 | -18.4496 | -23.5758 | -26.1154
|  | SOUTHBOURNE | LW |  |  | 10.5457 | 9.999 | 9.1429 | 8.1678 | 6.6898 | 5.2173 | 3.6385 | 1.9279 | 0.13817 | -1.7756 | -6.6647 | -12.357 | -15.0383 | -16.4849 | 6.9057 | 6.5816 | 6.0339 | 5.4091 | 4.5849 | 3.7485 | 2.8157 | 1.7941 | 0.63627 | -0.63046 | -3.6101 | -6.5683 | -7.7098 | -8.3514 | 2.0502 | 1.5622 | 0.79748 | -0.074422 | -1.3928 | -2.7179 | -4.1491 | -5.7012 | -7.367 | -9.1808 | -13.8017 | -18.8963 | -21.142 | -22.3696
|  | SOUTHBOURNE | ST |  |  | 11.0383 | 10.8437 | 10.5295 | 10.1602 | 9.638 | 9.1308 | 8.5779 | 7.9663 | 7.4224 | 6.8547 | 4.4525 | -1.4939 | -4.5464 | -6.704 | 7.1403 | 6.9971 | 6.7747 | 6.5103 | 6.1265 | 5.7431 | 5.3168 | 4.8453 | 4.3882 | 3.9469 | 2.0199 | -2.375 | -4.5714 | -6.6076 | 2.4987 | 2.3353 | 2.0782 | 1.7732 | 1.3204 | 0.87149 | 0.37694 | -0.16978 | -0.68034 | -1.2101 | -3.5463 | -9.1732 | -11.8766 | -13.7321
|  | SOUTHBOURNE | SP |  |  | 11.0945 | 10.8816 | 10.5743 | 10.2306 | 9.8092 | 9.4093 | 8.984 | 8.4835 | 8.083 | 7.6172 | 5.933 | 0.93703 | -2.0638 | -3.2853 | 7.1645 | 6.9896 | 6.7526 | 6.4882 | 6.1954 | 5.9077 | 5.5895 | 5.212 | 4.8792 | 4.4934 | 3.0034 | -1.273 | -4.6548 | -7.942 | 2.5496 | 2.3655 | 2.112 | 1.8288 | 1.4759 | 1.1334 | 0.76435 | 0.32685 | -0.041759 | -0.47252 | -2.0629 | -6.8815 | -9.6736 | -10.7314
BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE | MINIMUM HEADROOM | SU 68199 71325 | YES | 7.2566 | 6.3555 | 5.597 | 4.8432 | 3.8406 | 2.8167 | 1.7069 | 0.53191 | -0.89746 | -2.4166 | -6.2859 | -10.7952 | -14.9351 | -17.2199 | 7.0692 | 6.3017 | 5.8336 | 5.3669 | 4.7734 | 4.1698 | 3.4944 | 2.7728 | 1.8661 | 0.89539 | -1.4041 | -4.3983 | -7.1454 | -9.6436 | 1.9761 | 1.1282 | 0.43522 | -0.24798 | -1.1522 | -2.0728 | -3.0682 | -4.121 | -5.3978 | -6.7509 | -10.2173 | -14.2962 | -18.0166 | -20.0356
|  | SOUTHCOTE | CT |  |  | 7.4379 | 6.6616 | 6.1217 | 5.4461 | 4.75 | 4.047 | 3.26 | 2.4169 | 1.4624 | -0.085886 | -4.3321 | -10.4582 | -14.9351 | -17.2199 | 7.0692 | 6.3104 | 5.8696 | 5.4456 | 5.0485 | 4.554 | 4.001 | 3.4041 | 2.7146 | 1.7216 | -0.89686 | -4.3983 | -7.1454 | -9.6436 | 2.1437 | 1.4097 | 0.9095 | 0.30102 | -0.32279 | -0.95007 | -1.6518 | -2.4027 | -3.2512 | -4.6107 | -8.321 | -13.9869 | -18.0166 | -20.0356
|  | SOUTHCOTE | LW |  |  | 7.2566 | 6.3555 | 5.597 | 4.8432 | 3.8406 | 2.8167 | 1.7069 | 0.53191 | -0.89746 | -2.4166 | -6.2859 | -10.7952 | -12.8704 | -14.0086 | 7.0695 | 6.3017 | 5.8336 | 5.3669 | 4.7734 | 4.1698 | 3.4944 | 2.7728 | 1.8661 | 0.89539 | -1.4041 | -3.774 | -4.6848 | -5.2117 | 1.9761 | 1.1282 | 0.43522 | -0.24798 | -1.1522 | -2.0728 | -3.0682 | -4.121 | -5.3978 | -6.7509 | -10.2173 | -14.2962 | -16.1137 | -17.0763
|  | SOUTHCOTE | ST |  |  | 7.6591 | 7.0216 | 6.6371 | 6.2875 | 5.9485 | 5.6113 | 5.2411 | 4.8344 | 4.3687 | 3.9047 | 1.9827 | -2.9634 | -5.5143 | -7.195 | 7.147 | 6.4366 | 6.0528 | 5.7295 | 5.5196 | 5.3325 | 5.1286 | 4.8961 | 4.4973 | 4.1221 | 2.5786 | -1.1131 | -3.3772 | -5.681 | 2.3413 | 1.7315 | 1.3702 | 1.0454 | 0.74137 | 0.44183 | 0.11311 | -0.24745 | -0.66128 | -1.0775 | -2.7509 | -6.9338 | -9.2698 | -10.8154
|  | SOUTHCOTE | SP |  |  | 7.6986 | 7.0461 | 6.6554 | 6.3079 | 6.0572 | 5.8318 | 5.5828 | 5.2951 | 4.9874 | 4.6337 | 3.3894 | -0.55395 | -3.0609 | -4.0359 | 7.1527 | 6.4393 | 6.0528 | 5.7295 | 5.5422 | 5.3833 | 5.2152 | 5.0301 | 4.8265 | 4.5098 | 3.2973 | -0.28277 | -3.7737 | -7.8893 | 2.3771 | 1.7563 | 1.3914 | 1.0701 | 0.84366 | 0.64197 | 0.41977 | 0.16396 | -0.11049 | -0.42531 | -1.5112 | -4.7152 | -6.822 | -7.6413
AXMINSTER | YEOVIL BSP | SPARKFORD | MINIMUM HEADROOM | ST 60767 25496 | YES | 6.6917 | 6.2501 | 5.7104 | 5.1158 | 4.1051 | 3.0326 | 1.8822 | 0.65933 | -0.72395 | -2.2678 | -6.7804 | -13.207 | -18.3334 | -22.2144 | 6.9582 | 6.7036 | 6.3754 | 6.0063 | 5.4613 | 4.8721 | 4.2157 | 3.5074 | 2.6541 | 1.6761 | -1.1082 | -5.2379 | -9.1951 | -13.0434 | 3.94 | 3.5378 | 3.0396 | 2.488 | 1.5655 | 0.58339 | -0.4782 | -1.6101 | -2.906 | -4.3617 | -8.5815 | -14.3519 | -18.6059 | -21.8512
|  | SPARKFORD | CT |  |  | 6.8921 | 6.58 | 6.2128 | 5.7114 | 5.0179 | 4.2792 | 3.5185 | 2.6968 | 1.773 | 0.28467 | -4.3035 | -12.1776 | -18.3334 | -22.2144 | 6.9957 | 6.7654 | 6.4929 | 6.1108 | 5.6586 | 5.17 | 4.6455 | 4.0718 | 3.4104 | 2.4427 | -0.54764 | -5.2379 | -9.1951 | -13.0434 | 4.1121 | 3.8244 | 3.4835 | 3.0099 | 2.3684 | 1.6836 | 0.97269 | 0.20272 | -0.6687 | -2.0617 | -6.3341 | -13.3416 | -18.6059 | -21.8512
|  | SPARKFORD | LW |  |  | 6.6917 | 6.2501 | 5.7104 | 5.1158 | 4.1051 | 3.0326 | 1.8822 | 0.65933 | -0.72395 | -2.2678 | -6.7804 | -13.207 | -16.9872 | -19.7471 | 6.9582 | 6.7036 | 6.3754 | 6.0063 | 5.4613 | 4.8721 | 4.2157 | 3.5074 | 2.6541 | 1.6761 | -1.1082 | -4.6896 | -6.5112 | -7.8792 | 3.94 | 3.5378 | 3.0396 | 2.488 | 1.5655 | 0.58339 | -0.4782 | -1.6101 | -2.906 | -4.3617 | -8.5815 | -14.3519 | -17.5214 | -19.7871
|  | SPARKFORD | ST |  |  | 7.1758 | 7.0398 | 6.8757 | 6.6881 | 6.415 | 6.1124 | 5.7817 | 5.418 | 4.9923 | 4.528 | 2.5561 | -3.1777 | -6.917 | -9.6905 | 7.1823 | 7.0659 | 6.9256 | 6.7631 | 6.5415 | 6.2943 | 6.0175 | 5.7091 | 5.3403 | 4.9612 | 3.3287 | -1.1791 | -4.3761 | -7.7864 | 4.383 | 4.2629 | 4.1157 | 3.9451 | 3.693 | 3.4124 | 3.103 | 2.7612 | 2.3569 | 1.9195 | 0.0513 | -5.2428 | -8.4308 | -10.6989
|  | SPARKFORD | SP |  |  | 7.234 | 7.0888 | 6.9275 | 6.752 | 6.5404 | 6.3216 | 6.0812 | 5.8074 | 5.4953 | 5.1198 | 3.6722 | -0.98604 | -4.9439 | -7.187 | 7.2097 | 7.0757 | 6.9222 | 6.753 | 6.5682 | 6.3713 | 6.1491 | 5.8933 | 5.5959 | 5.2362 | 3.8208 | -0.60214 | -5.443 | -10.9454 | 4.4371 | 4.3061 | 4.1596 | 3.9992 | 3.8062 | 3.6064 | 3.3842 | 3.1291 | 2.836 | 2.4838 | 1.1262 | -3.1901 | -6.7163 | -8.5619
MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST | MINIMUM HEADROOM | ST 84368 68717 | NO | 10.677 | 10.3877 | 10.0201 | 9.6144 | 8.995 | 8.3247 | 7.6119 | 6.8416 | 5.8826 | 4.8759 | 2.1682 | -2.4851 | -7.2406 | -10.842 | 14.1126 | 13.9546 | 13.7521 | 13.5181 | 13.165 | 12.7756 | 12.3499 | 11.8831 | 11.2698 | 10.624 | 8.9973 | 6.0316 | 3.0526 | 0.1854 | 12.2798 | 12.0408 | 11.7422 | 11.412 | 10.8759 | 10.299 | 9.6888 | 9.0126 | 8.1559 | 7.2197 | 4.7283 | 0.66097 | -3.3833 | -6.4226
|  | SPRING QUARRY WEST | CT |  |  | 10.7592 | 10.5313 | 10.261 | 9.8882 | 9.4277 | 8.9291 | 8.4071 | 7.8391 | 7.1688 | 6.1494 | 3.3313 | -2.2455 | -7.2406 | -10.842 | 14.1295 | 13.9842 | 13.8131 | 13.5616 | 13.2559 | 12.9219 | 12.5648 | 12.1719 | 11.6953 | 11.0214 | 9.2292 | 6.0316 | 3.0526 | 0.1854 | 12.3656 | 12.1861 | 11.9723 | 11.6804 | 11.2977 | 10.8843 | 10.4477 | 9.946 | 9.3305 | 8.3766 | 5.7882 | 0.92675 | -3.3833 | -6.4226
|  | SPRING QUARRY WEST | LW |  |  | 10.677 | 10.3877 | 10.0201 | 9.6144 | 8.995 | 8.3247 | 7.6119 | 6.8416 | 5.8826 | 4.8759 | 2.1682 | -2.4851 | -6.0182 | -8.869 | 14.1126 | 13.9546 | 13.7521 | 13.5181 | 13.165 | 12.7756 | 12.3499 | 11.8831 | 11.2698 | 10.624 | 8.9973 | 6.4784 | 4.7364 | 3.2802 | 12.2798 | 12.0408 | 11.7422 | 11.412 | 10.8759 | 10.299 | 9.6888 | 9.0126 | 8.1559 | 7.2197 | 4.7283 | 0.66097 | -2.2515 | -4.5702
|  | SPRING QUARRY WEST | ST |  |  | 10.9239 | 10.8115 | 10.6733 | 10.5202 | 10.3055 | 10.0713 | 9.8202 | 9.5402 | 9.2118 | 8.8756 | 7.3322 | 3.1523 | -0.062274 | -2.5468 | 14.2251 | 14.1454 | 14.049 | 13.9417 | 13.7974 | 13.6397 | 13.4536 | 13.229 | 12.9626 | 12.6975 | 11.4761 | 8.3718 | 5.9173 | 3.4939 | 12.501 | 12.4177 | 12.3152 | 12.201 | 12.0378 | 11.8591 | 11.6663 | 11.4507 | 11.195 | 10.915 | 9.5029 | 5.7543 | 3.0832 | 1.0974
|  | SPRING QUARRY WEST | SP |  |  | 10.9446 | 10.8249 | 10.6949 | 10.5499 | 10.3689 | 10.1746 | 9.9749 | 9.7424 | 9.4859 | 9.2065 | 8.0824 | 4.4208 | 1.3266 | -0.82032 | 14.2327 | 14.1455 | 14.0486 | 13.9401 | 13.8161 | 13.6798 | 13.5355 | 13.3594 | 13.1446 | 12.8971 | 11.8923 | 8.7141 | 5.3833 | 1.5445 | 12.5196 | 12.4333 | 12.3394 | 12.234 | 12.0923 | 11.9411 | 11.7855 | 11.6047 | 11.4039 | 11.1807 | 10.2432 | 6.9455 | 4.3175 | 2.607
NORTH HYDE GSP | NORTH HYDE (D) | SPRINGFIELD ROAD | MINIMUM HEADROOM | TQ 11409 80620 | YES | 2.2319 | 1.856 | 1.4804 | 1.1107 | 0.64271 | 0.18593 | -0.15325 | -0.3377 | -0.52618 | -0.7097 | -1.4713 | -4.4412 | -6.2387 | -6.5122 | 2.3928 | 2.1997 | 2.0173 | 1.842 | 1.6258 | 1.4193 | 1.2588 | 1.1542 | 1.0231 | 0.90178 | 0.7169 | -0.58454 | -1.3257 | -1.4787 | 0.98984 | 0.63384 | 0.2809 | -0.065863 | -0.50528 | -0.92285 | -1.2299 | -1.4027 | -1.585 | -1.7498 | -2.3444 | -4.9732 | -6.561 | -6.804
|  | SPRINGFIELD ROAD | CT |  |  | 2.6195 | 2.4333 | 2.2678 | 2.0857 | 1.8168 | 1.5597 | 1.3307 | 1.1871 | 1.0394 | 0.86413 | 0.61268 | 0.33669 | 0.17968 | 0.090929 | 2.5491 | 2.4346 | 2.3392 | 2.2339 | 2.0985 | 1.968 | 1.8448 | 1.7473 | 1.6308 | 1.495 | 1.3082 | 1.1159 | 0.99307 | 0.88126 | 1.3573 | 1.1813 | 1.0259 | 0.85745 | 0.60626 | 0.3669 | 0.15464 | 0.02402 | -0.10729 | -0.26269 | -0.49244 | -0.75491 | -0.90279 | -0.98612
|  | SPRINGFIELD ROAD | LW |  |  | 2.2319 | 1.856 | 1.4804 | 1.1107 | 0.64271 | 0.18593 | -0.15325 | -0.3377 | -0.52618 | -0.7097 | -0.96018 | -1.2292 | -1.2974 | -1.3799 | 2.3928 | 2.1997 | 2.0173 | 1.842 | 1.6258 | 1.4193 | 1.2588 | 1.1542 | 1.0231 | 0.90178 | 0.74693 | 0.58324 | 0.53993 | 0.49814 | 0.98984 | 0.63384 | 0.2809 | -0.065863 | -0.50528 | -0.92285 | -1.2299 | -1.4027 | -1.585 | -1.7498 | -1.9854 | -2.2402 | -2.3037 | -2.3809
|  | SPRINGFIELD ROAD | ST |  |  | 2.6356 | 2.4672 | 2.3219 | 2.183 | 1.978 | 1.7694 | 1.5617 | 1.344 | 1.1152 | 0.87114 | 0.0070607 | -0.89698 | -1.045 | -1.1262 | 2.5646 | 2.4603 | 2.3792 | 2.3054 | 2.2039 | 2.1021 | 1.9998 | 1.8916 | 1.7761 | 1.6575 | 1.2076 | 0.69931 | 0.56652 | 0.45265 | 1.3709 | 1.2105 | 1.0731 | 0.94234 | 0.75008 | 0.55515 | 0.36099 | 0.15771 | -0.055271 | -0.28364 | -1.0832 | -1.9266 | -2.0674 | -2.1436
|  | SPRINGFIELD ROAD | SP |  |  | 2.6802 | 2.5376 | 2.4184 | 2.3103 | 1.9535 | 1.5922 | 1.2368 | 0.87501 | 0.49872 | 0.026472 | -1.4713 | -4.4412 | -6.2387 | -6.5122 | 2.5829 | 2.4886 | 2.4175 | 2.3562 | 2.1938 | 2.0308 | 1.8702 | 1.7055 | 1.5354 | 1.3404 | 0.7169 | -0.58454 | -1.3257 | -1.4787 | 1.4132 | 1.2775 | 1.1651 | 1.0635 | 0.72657 | 0.38612 | 0.050884 | -0.2901 | -0.63844 | -1.0508 | -2.3444 | -4.9732 | -6.561 | -6.804
NURSLING GSP | WINCHESTER | ST CROSS | MINIMUM HEADROOM | SU 47287 28156 | YES | 15.8323 | 11.5617 | 7.2607 | 2.9491 | -5.5684 | -5.947 | -6.3469 | -6.7696 | -7.3153 | -7.8555 | -9.0033 | -10.325 | -10.8399 | -11.3529 | 18.9331 | 13.725 | 8.4896 | 3.2445 | -7.1527 | -7.3663 | -7.6007 | -7.8526 | -8.2178 | -8.5775 | -9.2017 | -9.9472 | -10.7103 | -11.4388 | 15.7524 | 10.4755 | 5.1635 | -0.16018 | -10.6907 | -11.0435 | -11.4209 | -11.822 | -12.3636 | -12.8971 | -13.9437 | -15.1054 | -15.5049 | -15.9518
|  | ST CROSS | CT |  |  | 15.9638 | 11.7713 | 7.5592 | 3.3141 | -5.0716 | -5.3083 | -5.5579 | -5.8317 | -6.1597 | -6.6829 | -7.8694 | -9.6426 | -10.8399 | -11.3529 | 18.9603 | 13.7698 | 8.5609 | 3.3201 | -7.0387 | -7.2067 | -7.3883 | -7.5917 | -7.848 | -8.2189 | -8.9755 | -9.9472 | -10.7103 | -11.4388 | 15.8549 | 10.6413 | 5.4057 | 0.13255 | -10.2873 | -10.5188 | -10.7646 | -11.0363 | -11.3705 | -11.8917 | -13.0065 | -14.5213 | -15.5049 | -15.9518
|  | ST CROSS | LW |  |  | 15.8323 | 11.5617 | 7.2607 | 2.9491 | -5.5684 | -5.947 | -6.3469 | -6.7696 | -7.3153 | -7.8555 | -9.0033 | -10.325 | -10.7643 | -10.9311 | 18.9331 | 13.725 | 8.4896 | 3.2445 | -7.1527 | -7.3663 | -7.6007 | -7.8526 | -8.2178 | -8.5775 | -9.2017 | -9.8455 | -10.0145 | -10.0778 | 15.7524 | 10.4755 | 5.1635 | -0.16018 | -10.6907 | -11.0435 | -11.4209 | -11.822 | -12.3636 | -12.8971 | -13.9437 | -15.1054 | -15.4689 | -15.6047
|  | ST CROSS | ST |  |  | 16.0749 | 11.9465 | 7.8048 | 3.6569 | -4.6111 | -4.7224 | -4.8435 | -4.9739 | -5.1231 | -5.2838 | -6.0301 | -7.3252 | -7.9741 | -8.415 | 19.0402 | 13.896 | 8.7384 | 3.5737 | -6.7163 | -6.809 | -6.9133 | -7.0274 | -7.1625 | -7.2914 | -7.9309 | -9.019 | -9.6354 | -10.3375 | 15.9679 | 10.8195 | 5.6559 | 0.48511 | -9.824 | -9.9361 | -10.0595 | -10.1928 | -10.3481 | -10.5081 | -11.287 | -12.5675 | -13.1216 | -13.4791
|  | ST CROSS | SP |  |  | 16.1062 | 11.9845 | 7.8551 | 3.7238 | -4.5246 | -4.6084 | -4.7002 | -4.8067 | -4.921 | -5.0721 | -5.6406 | -7.1718 | -7.9193 | -8.2734 | 19.0509 | 13.9051 | 8.7501 | 3.5916 | -6.6834 | -6.7575 | -6.8396 | -6.9386 | -7.049 | -7.1722 | -7.6706 | -9.0919 | -10.035 | -11.1149 | 15.9945 | 10.8501 | 5.6971 | 0.5421 | -9.7448 | -9.8272 | -9.9174 | -10.0246 | -10.1408 | -10.2876 | -10.8593 | -12.4337 | -13.1312 | -13.4357
COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES | MINIMUM HEADROOM | SP 51259 05741 | YES | 12.514 | 4.132 | -4.3079 | -12.7695 | -21.4813 | -22.0614 | -22.6782 | -23.3319 | -24.1436 | -25.0585 | -27.9343 | -33.0273 | -38.4147 | -42.1178 | 12.8309 | 2.5252 | -7.7787 | -18.1115 | -28.5265 | -28.8743 | -29.3215 | -29.814 | -30.3675 | -31.0851 | -33.4778 | -38.211 | -45.3762 | -59.5235 | 9.4063 | -1.0075 | -11.5162 | -22.0545 | -32.7673 | -33.3056 | -33.8964 | -34.5289 | -35.3139 | -36.1837 | -38.8916 | -43.1982 | -47.5863 | -50.5785
|  | ST EBBES | CT |  |  | 12.6016 | 4.273 | -4.0678 | -12.4958 | -21.0427 | -21.4615 | -21.9355 | -22.4448 | -23.001 | -23.9376 | -26.9787 | -33.0273 | -38.4147 | -42.1178 | 12.8309 | 2.5252 | -7.7787 | -18.1115 | -28.5265 | -28.8743 | -29.3215 | -29.814 | -30.3675 | -31.0851 | -33.4778 | -38.211 | -44.1462 | -51.9507 | 9.4641 | -0.90905 | -11.299 | -21.8297 | -32.4257 | -32.8439 | -33.3134 | -33.8231 | -34.3862 | -35.2434 | -38.0166 | -43.1982 | -47.5863 | -50.5785
|  | ST EBBES | LW |  |  | 12.514 | 4.132 | -4.3079 | -12.7695 | -21.4813 | -22.0614 | -22.6782 | -23.3319 | -24.1436 | -25.0585 | -27.9343 | -32.7557 | -36.3827 | -39.0941 | 12.8514 | 2.5688 | -7.7237 | -18.0197 | -28.4193 | -28.6657 | -29.0168 | -29.4362 | -29.9549 | -30.5378 | -32.298 | -34.8239 | -36.4973 | -37.8748 | 9.4063 | -1.0075 | -11.5162 | -22.0545 | -32.7673 | -33.3056 | -33.8964 | -34.5289 | -35.3139 | -36.1837 | -38.8916 | -43.1276 | -46.0793 | -48.274
|  | ST EBBES | ST |  |  | 12.7127 | 4.4606 | -3.7911 | -12.0463 | -20.3501 | -20.5017 | -20.6641 | -20.8603 | -21.0853 | -21.3273 | -22.3799 | -26.1309 | -29.3217 | -31.9138 | 12.8649 | 2.5812 | -7.6974 | -17.9779 | -28.2852 | -28.3957 | -28.5496 | -28.8032 | -29.1604 | -29.5099 | -30.9424 | -35.292 | -40.3978 | -47.7546 | 9.5918 | -0.69868 | -10.9937 | -21.2963 | -31.6695 | -31.8536 | -32.0563 | -32.2787 | -32.533 | -32.7882 | -33.8963 | -37.4443 | -40.1021 | -42.16
|  | ST EBBES | SP |  |  | 12.7296 | 4.4699 | -3.7851 | -12.0418 | -20.3163 | -20.4294 | -20.5503 | -20.6877 | -20.8449 | -21.0304 | -21.7726 | -24.4644 | -27.1341 | -29.042 | 12.8623 | 2.5709 | -7.7184 | -18.0102 | -28.3301 | -28.463 | -28.7024 | -29.0201 | -29.3881 | -29.8285 | -31.597 | -36.8439 | -45.3762 | -59.5235 | 9.6079 | -0.70273 | -11.012 | -21.327 | -31.6577 | -31.7853 | -31.9275 | -32.0879 | -32.2612 | -32.4583 | -33.2689 | -35.8995 | -38.3204 | -39.9019
BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS | MINIMUM HEADROOM | SU 47113 66363 | YES | 9.1851 | 8.7918 | 8.288 | 7.582 | 6.5034 | 5.3775 | 4.1849 | 3.0097 | 1.6164 | 0.099754 | -4.0533 | -8.4993 | -10.908 | -12.3477 | 9.4824 | 9.2498 | 8.9229 | 8.4086 | 7.7543 | 7.0542 | 6.295 | 5.5623 | 4.6447 | 3.6445 | 1.0107 | -2.141 | -4.6278 | -7.0533 | 4.6225 | 4.2529 | 3.7771 | 3.1119 | 2.1134 | 1.0688 | -0.044463 | -1.145 | -2.4655 | -3.9052 | -7.8197 | -11.9413 | -13.984 | -15.2324
|  | ST JOHNS | CT |  |  | 9.3297 | 9.041 | 8.6495 | 8.0298 | 7.2139 | 6.369 | 5.5214 | 4.7062 | 3.8081 | 2.329 | -1.8107 | -7.5301 | -10.908 | -12.3477 | 9.4824 | 9.2498 | 8.9287 | 8.4086 | 7.8075 | 7.1826 | 6.534 | 5.916 | 5.2254 | 4.2143 | 1.4191 | -2.141 | -4.6278 | -7.0533 | 4.7429 | 4.4652 | 4.0891 | 3.4976 | 2.7336 | 1.9414 | 1.1415 | 0.36881 | -0.4876 | -1.8866 | -5.779 | -10.9995 | -13.984 | -15.2324
|  | ST JOHNS | LW |  |  | 9.1851 | 8.7918 | 8.288 | 7.582 | 6.5034 | 5.3775 | 4.1849 | 3.0097 | 1.6164 | 0.099754 | -4.0533 | -8.4993 | -9.8134 | -10.2874 | 9.4888 | 9.2519 | 8.9229 | 8.4204 | 7.7543 | 7.0542 | 6.295 | 5.5623 | 4.6447 | 3.6445 | 1.0107 | -1.5199 | -2.0758 | -2.275 | 4.6225 | 4.2529 | 3.7771 | 3.1119 | 2.1134 | 1.0688 | -0.044463 | -1.145 | -2.4655 | -3.9052 | -7.8197 | -11.9413 | -13.1007 | -13.5115
|  | ST JOHNS | ST |  |  | 9.6669 | 9.553 | 9.362 | 8.9912 | 8.5198 | 8.0358 | 7.5305 | 7.0755 | 6.5673 | 6.0246 | 3.7639 | -1.1195 | -3.4075 | -4.6 | 9.7216 | 9.6129 | 9.4356 | 9.0992 | 8.6876 | 8.2629 | 7.8136 | 7.4061 | 6.9515 | 6.498 | 4.588 | 0.53297 | -1.7688 | -4.0723 | 5.0689 | 4.9601 | 4.7781 | 4.4289 | 3.9849 | 3.5284 | 3.0491 | 2.6139 | 2.1249 | 1.6062 | -0.57515 | -5.2636 | -7.3665 | -8.4085
|  | ST JOHNS | SP |  |  | 9.6973 | 9.5833 | 9.4089 | 9.0574 | 8.6034 | 8.1464 | 7.6811 | 7.2759 | 6.8424 | 6.3664 | 4.6535 | 0.50616 | -2.155 | -2.9784 | 9.7307 | 9.6108 | 9.4329 | 9.0956 | 8.7107 | 8.3153 | 7.9072 | 7.5416 | 7.147 | 6.7241 | 5.1482 | 1.1701 | -2.4759 | -6.4366 | 5.0967 | 4.9862 | 4.8194 | 4.4878 | 4.0654 | 3.6394 | 3.2044 | 2.8217 | 2.4103 | 1.9594 | 0.32521 | -3.6837 | -6.2361 | -6.9934
COWLEY GSP | WITNEY BSP | STANDLAKE | MINIMUM HEADROOM | SP 38923 02349 | YES | 11.1564 | 10.8684 | 10.566 | 10.1683 | 9.788 | 9.245 | 8.6206 | 7.9338 | 7.3022 | 6.6934 | 4.6867 | 1.6961 | -0.012321 | -1.6012 | 17.2272 | 16.9945 | 16.7583 | 16.4125 | 16.1298 | 15.7534 | 15.4059 | 14.9996 | 14.6491 | 14.3092 | 13.2559 | 11.5977 | 9.4861 | 7.205 | 11.4862 | 11.2177 | 10.9364 | 10.5522 | 10.1999 | 9.7991 | 9.3782 | 8.7404 | 8.1596 | 7.5989 | 5.8409 | 3.2315 | 1.835 | 0.69061
|  | STANDLAKE | CT |  |  | 11.2817 | 11.0593 | 10.8218 | 10.4885 | 10.2059 | 9.8821 | 9.6119 | 9.2902 | 9.0137 | 8.5124 | 6.7414 | 3.1304 | 0.24501 | -1.6012 | 17.2669 | 17.0734 | 16.8583 | 16.5315 | 16.2931 | 15.9942 | 15.7428 | 15.4078 | 15.1259 | 14.7887 | 13.7445 | 11.5977 | 9.4861 | 7.205 | 11.5951 | 11.384 | 11.1594 | 10.8311 | 10.565 | 10.2517 | 9.9917 | 9.6795 | 9.4169 | 9.0811 | 7.5667 | 4.487 | 2.1712 | 0.69061
|  | STANDLAKE | LW |  |  | 11.1564 | 10.8684 | 10.566 | 10.1683 | 9.788 | 9.245 | 8.6206 | 7.9338 | 7.3022 | 6.6934 | 4.6867 | 1.6961 | -0.012321 | -1.358 | 17.2272 | 16.9945 | 16.7583 | 16.4125 | 16.1298 | 15.7534 | 15.4059 | 14.9996 | 14.6491 | 14.3092 | 13.2559 | 11.8878 | 11.0614 | 10.3923 | 11.4862 | 11.2177 | 10.9364 | 10.5522 | 10.1999 | 9.7991 | 9.3782 | 8.7404 | 8.1596 | 7.5989 | 5.8409 | 3.2315 | 1.835 | 0.7373
|  | STANDLAKE | ST |  |  | 11.386 | 11.2339 | 11.0783 | 10.8404 | 10.6896 | 10.4964 | 10.3313 | 10.1184 | 9.9414 | 9.7473 | 9.1144 | 7.5512 | 5.7396 | 4.4444 | 17.3104 | 17.1512 | 16.9955 | 16.7371 | 16.5905 | 16.3753 | 16.1906 | 15.9481 | 15.7589 | 15.5677 | 14.9547 | 13.3972 | 11.5846 | 9.5176 | 11.6904 | 11.5434 | 11.3933 | 11.152 | 11.0039 | 10.8077 | 10.6427 | 10.4287 | 10.2557 | 10.0685 | 9.4647 | 8.1165 | 6.5419 | 5.4982
|  | STANDLAKE | SP |  |  | 11.3997 | 11.2549 | 11.1101 | 10.8829 | 10.7489 | 10.5723 | 10.4269 | 10.2352 | 10.093 | 9.9231 | 9.408 | 8.2147 | 6.3644 | 5.0559 | 17.3115 | 17.1527 | 16.9976 | 16.739 | 16.5977 | 16.3946 | 16.2275 | 15.9943 | 15.8215 | 15.632 | 15.0378 | 13.3619 | 10.8649 | 7.5494 | 11.7025 | 11.5619 | 11.4215 | 11.1897 | 11.057 | 10.8762 | 10.7292 | 10.535 | 10.3941 | 10.23 | 9.739 | 8.6682 | 7.0939 | 5.9936
MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN | MINIMUM HEADROOM | SU 17585 90987 | NO | 7.4597 | 7.3937 | 7.3372 | 7.2816 | 7.2174 | 6.9447 | 6.631 | 6.2848 | 5.8887 | 5.4893 | 4.0655 | 2.9007 | 2.4044 | 1.9389 | 12.2645 | 12.1955 | 12.1419 | 12.0907 | 12.0421 | 11.8876 | 11.7137 | 11.5223 | 11.3062 | 11.0863 | 10.3074 | 9.5148 | 9.0367 | 8.493 | 6.9919 | 6.9161 | 6.8568 | 6.8013 | 6.7399 | 6.5132 | 6.2521 | 5.9637 | 5.6305 | 5.2953 | 4.1102 | 3.1286 | 2.7427 | 2.3673
|  | STANTON FITZWARREN | CT |  |  | 7.4694 | 7.4098 | 7.3591 | 7.308 | 7.2536 | 6.992 | 6.6942 | 6.3644 | 5.9927 | 5.603 | 4.207 | 2.9798 | 2.4044 | 1.9389 | 12.2645 | 12.1955 | 12.1419 | 12.0907 | 12.0421 | 11.8876 | 11.7137 | 11.5223 | 11.3062 | 11.0863 | 10.3074 | 9.5148 | 9.0367 | 8.493 | 6.9993 | 6.9286 | 6.8739 | 6.8217 | 6.7686 | 6.5513 | 6.3045 | 6.0309 | 5.7211 | 5.3956 | 4.2416 | 3.2123 | 2.7427 | 2.3673
|  | STANTON FITZWARREN | LW |  |  | 7.4597 | 7.3937 | 7.3372 | 7.2816 | 7.2174 | 6.9447 | 6.631 | 6.2848 | 5.8887 | 5.4893 | 4.0655 | 2.9007 | 2.4251 | 2.0044 | 12.27 | 12.2078 | 12.1625 | 12.1215 | 12.079 | 11.9309 | 11.7614 | 11.5758 | 11.3606 | 11.1445 | 10.3793 | 9.7346 | 9.4895 | 9.2708 | 6.9919 | 6.9161 | 6.8568 | 6.8013 | 6.7399 | 6.5132 | 6.2521 | 5.9637 | 5.6305 | 5.2953 | 4.1102 | 3.1286 | 2.7432 | 2.4029
|  | STANTON FITZWARREN | ST |  |  | 7.4883 | 7.443 | 7.4103 | 7.3805 | 7.3489 | 7.181 | 6.9899 | 6.7799 | 6.5441 | 6.3012 | 5.3752 | 4.3795 | 3.8988 | 3.597 | 12.2773 | 12.2178 | 12.176 | 12.1387 | 12.1032 | 11.9891 | 11.8602 | 11.7192 | 11.5607 | 11.4048 | 10.8122 | 10.0523 | 9.5675 | 9.0885 | 7.0176 | 6.9608 | 6.9235 | 6.892 | 6.8598 | 6.7217 | 6.5646 | 6.3918 | 6.1966 | 5.9968 | 5.2325 | 4.3685 | 3.9599 | 3.7202
|  | STANTON FITZWARREN | SP |  |  | 7.4923 | 7.449 | 7.4183 | 7.3905 | 7.3642 | 7.2263 | 7.0582 | 6.8785 | 6.6825 | 6.4826 | 5.7494 | 4.9464 | 4.4155 | 4.0772 | 12.2781 | 12.2184 | 12.1752 | 12.1358 | 12.1049 | 12.0096 | 11.8911 | 11.764 | 11.6235 | 11.487 | 10.9851 | 10.322 | 9.8007 | 9.3045 | 7.0215 | 6.9664 | 6.9309 | 6.901 | 6.8744 | 6.7662 | 6.6288 | 6.4819 | 6.3209 | 6.1582 | 5.5633 | 4.8711 | 4.4057 | 4.1287
LALEHAM | STAINES | STANWELL | MINIMUM HEADROOM | TQ 06003 72766 | NO | 0.029611 | -0.24343 | 7.9669 | 7.67 | 7.2651 | 6.8569 | 6.4489 | 5.9972 | 5.4958 | 5.0159 | 3.9698 | 2.8829 | 2.7577 | 2.2918 | -0.57935 | -0.643 | 8.0933 | 8.0233 | 7.9308 | 7.8333 | 7.7275 | 7.6071 | 7.4736 | 7.3209 | 6.8348 | 6.3215 | 6.2221 | 5.9339 | -3.1323 | -3.3837 | 5.1625 | 4.9037 | 4.5453 | 4.1857 | 3.8336 | 3.4585 | 3.071 | 2.6814 | 1.6722 | 0.67861 | 0.56295 | 0.21146
|  | STANWELL | CT |  |  | 0.26291 | 0.15173 | 8.5103 | 8.363 | 8.1499 | 7.9253 | 7.6924 | 7.4212 | 7.1251 | 6.7038 | 5.8414 | 4.7794 | 4.5475 | 4.4211 | -0.54083 | -0.57975 | 8.1782 | 8.1304 | 8.0693 | 8.003 | 7.9335 | 7.8544 | 7.7699 | 7.6523 | 7.3256 | 6.8048 | 6.6337 | 6.5307 | -2.8554 | -2.9448 | 5.7452 | 5.6317 | 5.4413 | 5.2466 | 5.0584 | 4.8509 | 4.6348 | 4.3213 | 3.5406 | 2.502 | 2.2803 | 2.1589
|  | STANWELL | LW |  |  | 0.029611 | -0.24343 | 7.9669 | 7.67 | 7.2651 | 6.8569 | 6.4489 | 5.9972 | 5.4958 | 5.0159 | 3.9698 | 2.8829 | 2.7577 | 2.6256 | -0.57935 | -0.643 | 8.0933 | 8.0233 | 7.9308 | 7.8333 | 7.7275 | 7.6071 | 7.4736 | 7.3209 | 6.8348 | 6.3215 | 6.2221 | 6.1505 | -3.1323 | -3.3837 | 5.1625 | 4.9037 | 4.5453 | 4.1857 | 3.8336 | 3.4585 | 3.071 | 2.6814 | 1.6722 | 0.67861 | 0.56295 | 0.44381
|  | STANWELL | ST |  |  | 0.30424 | 0.24832 | 8.6857 | 8.586 | 8.4459 | 8.3012 | 8.1482 | 7.9782 | 7.7964 | 7.6016 | 6.8002 | 5.6795 | 5.0327 | 4.603 | -0.51395 | -0.53483 | 8.2438 | 8.218 | 8.1827 | 8.1445 | 8.102 | 8.0548 | 8.0005 | 7.9326 | 7.6618 | 7.0816 | 6.762 | 6.6047 | -2.8199 | -2.8773 | 5.8519 | 5.769 | 5.6402 | 5.5086 | 5.3761 | 5.2368 | 5.0935 | 4.929 | 4.3337 | 3.3605 | 2.7177 | 2.2879
|  | STANWELL | SP |  |  | 0.32952 | 0.28978 | 8.7498 | 8.7062 | 8.5141 | 8.3167 | 8.1006 | 7.8721 | 7.6376 | 7.3412 | 6.3606 | 4.2712 | 3.0928 | 2.2918 | -0.50795 | -0.52426 | 8.2595 | 8.2402 | 8.1997 | 8.1576 | 8.1131 | 8.0652 | 8.0148 | 7.9497 | 7.7293 | 6.9138 | 6.3316 | 5.9339 | -2.7911 | -2.8311 | 5.9286 | 5.8839 | 5.6874 | 5.4887 | 5.2904 | 5.0853 | 4.8777 | 4.6102 | 3.7634 | 2.0293 | 0.91452 | 0.21146
MANNINGTON GSP | SALISBURY | STAPLEFORD | MINIMUM HEADROOM | SU 06871 37078 | YES | 4.5623 | 4.2506 | 3.8196 | 3.3701 | 2.8705 | 2.4565 | 1.7882 | 0.4723 | -1.0913 | -2.642 | -6.2887 | -9.379 | -11.268 | -12.3385 | 0.42232 | 0.030303 | -0.53191 | -1.1319 | -1.8966 | -2.5753 | -3.217 | -3.9047 | -4.7326 | -5.5565 | -7.4641 | -9.1359 | -10.6039 | -11.6597 | -1.3746 | -1.6443 | -2.2972 | -3.0425 | -4.0808 | -5.0154 | -5.8907 | -6.8118 | -7.8567 | -8.9275 | -11.7397 | -14.3965 | -16.1006 | -17.0892
|  | STAPLEFORD | CT |  |  | 4.5623 | 4.2506 | 3.8196 | 3.3701 | 2.8705 | 2.4568 | 2.0928 | 1.7196 | 0.56757 | -0.98687 | -4.7217 | -8.7039 | -11.268 | -12.3385 | 0.47564 | 0.11629 | -0.39951 | -0.98526 | -1.6739 | -2.2761 | -2.83 | -3.4138 | -4.0977 | -4.9368 | -6.9448 | -9.1359 | -10.6039 | -11.6597 | -1.3746 | -1.6443 | -2.0139 | -2.5794 | -3.4352 | -4.1832 | -4.8648 | -5.5781 | -6.3809 | -7.4305 | -10.2048 | -13.7595 | -16.1006 | -17.0892
|  | STAPLEFORD | LW |  |  | 4.5795 | 4.2683 | 3.8357 | 3.396 | 2.8858 | 2.4565 | 1.7882 | 0.4723 | -1.0913 | -2.642 | -6.2887 | -9.379 | -10.4662 | -10.9051 | 0.42232 | 0.030303 | -0.53191 | -1.1319 | -1.8966 | -2.5753 | -3.217 | -3.9047 | -4.7326 | -5.5565 | -7.4641 | -9.0632 | -9.576 | -9.7866 | -1.3575 | -1.6435 | -2.2972 | -3.0425 | -4.0808 | -5.0154 | -5.8907 | -6.8118 | -7.8567 | -8.9275 | -11.7397 | -14.3965 | -15.3857 | -15.7977
|  | STAPLEFORD | ST |  |  | 4.6633 | 4.4083 | 4.0445 | 3.6796 | 3.2374 | 2.8844 | 2.5832 | 2.278 | 1.9386 | 1.5806 | 0.4393 | -1.7729 | -3.1499 | -4.0656 | 0.67238 | 0.44013 | 0.10744 | -0.24055 | -0.70681 | -1.099 | -1.4533 | -1.8213 | -2.2343 | -2.6547 | -4.119 | -6.0244 | -7.1008 | -8.1247 | -1.2767 | -1.4916 | -1.7964 | -2.1035 | -2.4785 | -2.7806 | -3.0412 | -3.3067 | -3.6032 | -4.0213 | -5.4461 | -7.5439 | -8.904 | -9.8902
|  | STAPLEFORD | SP |  |  | 4.6642 | 4.4115 | 4.0557 | 3.7023 | 3.2978 | 2.9773 | 2.7054 | 2.4284 | 2.1302 | 1.8162 | 0.91579 | -0.83751 | -2.2921 | -2.9445 | 0.68223 | 0.45587 | 0.1444 | -0.17466 | -0.56175 | -0.89448 | -1.2032 | -1.5312 | -1.8854 | -2.2728 | -3.4916 | -5.6139 | -7.0616 | -8.5416 | -1.2758 | -1.4884 | -1.7854 | -2.0812 | -2.4196 | -2.6901 | -2.9223 | -3.1603 | -3.417 | -3.6891 | -4.7436 | -6.6283 | -7.7794 | -8.3622
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH | MINIMUM HEADROOM | SU 77124 94355 | YES | 20.5878 | 20.2009 | 19.4668 | 18.5342 | 17.418 | 16.2297 | 14.9796 | 13.6043 | 12.1868 | 10.7794 | 6.3951 | 2.1102 | -0.53127 | -2.5368 | 22.927 | 22.7795 | 22.5389 | 22.2496 | 21.7491 | 21.1321 | 20.4732 | 19.7138 | 18.9124 | 18.1032 | 15.5715 | 13.0905 | 11.3904 | 9.8762 | 20.9319 | 20.5729 | 19.903 | 19.09 | 18.1232 | 17.0917 | 15.9934 | 14.7851 | 13.5209 | 12.2506 | 8.3341 | 4.5206 | 2.4585 | 0.82635
|  | STOKENCHURCH | CT |  |  | 20.6593 | 20.3287 | 19.6698 | 18.7748 | 17.7707 | 16.7011 | 15.6002 | 14.3781 | 13.1594 | 11.8288 | 7.565 | 2.6023 | -0.53127 | -2.5368 | 22.927 | 22.7795 | 22.5389 | 22.2496 | 21.8622 | 21.2894 | 20.6965 | 20.0094 | 19.3135 | 18.5564 | 16.1082 | 13.2065 | 11.3904 | 9.8762 | 20.9831 | 20.6716 | 20.078 | 19.2877 | 18.4124 | 17.4785 | 16.511 | 15.4456 | 14.3739 | 13.188 | 9.3975 | 5.0501 | 2.4585 | 0.82635
|  | STOKENCHURCH | LW |  |  | 20.5878 | 20.2009 | 19.4668 | 18.5342 | 17.418 | 16.2297 | 14.9796 | 13.6043 | 12.1868 | 10.7794 | 6.3951 | 2.1102 | 0.038801 | -1.446 | 22.943 | 22.7867 | 22.5395 | 22.2497 | 21.7491 | 21.1321 | 20.4732 | 19.7138 | 18.9124 | 18.1032 | 15.5715 | 13.0905 | 12.0523 | 11.2844 | 20.9319 | 20.5729 | 19.903 | 19.09 | 18.1232 | 17.0917 | 15.9934 | 14.7851 | 13.5209 | 12.2506 | 8.3341 | 4.5206 | 2.8192 | 1.6098
|  | STOKENCHURCH | ST |  |  | 20.8045 | 20.613 | 20.2379 | 19.7742 | 19.1994 | 18.5907 | 17.9611 | 17.2444 | 16.5299 | 15.8391 | 13.247 | 8.9205 | 6.4415 | 5.0211 | 23.0071 | 22.9107 | 22.7404 | 22.5434 | 22.3132 | 22.069 | 21.813 | 21.426 | 20.9998 | 20.5596 | 18.9173 | 15.8056 | 13.8788 | 12.8439 | 21.1421 | 20.9728 | 20.6457 | 20.2534 | 19.7477 | 19.2112 | 18.6518 | 18.0267 | 17.4056 | 16.8019 | 14.5437 | 10.5873 | 8.4265 | 7.2663
|  | STOKENCHURCH | SP |  |  | 20.8251 | 20.644 | 20.2994 | 19.8771 | 19.4129 | 18.9226 | 18.3944 | 17.8263 | 17.2668 | 16.7314 | 14.8375 | 11.5824 | 8.8616 | 7.5263 | 23.0144 | 22.9223 | 22.7591 | 22.5697 | 22.3721 | 22.1629 | 21.9386 | 21.694 | 21.3858 | 21.0455 | 19.7853 | 17.4057 | 14.9075 | 12.8721 | 21.1633 | 20.9989 | 20.7007 | 20.3452 | 19.9651 | 19.5564 | 19.0912 | 18.5898 | 18.1089 | 17.6474 | 16.0338 | 13.0895 | 10.648 | 9.5387
MINETY GSP | STRATTON (2 X 60) | STRATTON | MINIMUM HEADROOM | SU 16998 88837 | NO | 5.1522 | 4.7362 | 4.2901 | 3.8464 | 3.2411 | 2.6313 | 2.0153 | 1.3753 | 0.5988 | -0.15576 | -1.517 | -2.2618 | -2.9982 | -4.081 | 4.6219 | 4.5009 | 4.3437 | 4.186 | 3.9698 | 3.75 | 3.5277 | 3.2972 | 3.043 | 2.7725 | 2.1131 | 1.5802 | 1.3327 | 0.79933 | 4.3697 | 4.1381 | 3.7987 | 3.4618 | 2.994 | 2.5241 | 1.9909 | 1.4161 | 0.69384 | -0.0029034 | -1.185 | -1.848 | -2.44 | -3.3308
|  | STRATTON | CT |  |  | 5.6238 | 5.4398 | 5.2412 | 5.0092 | 4.6722 | 4.3205 | 3.9547 | 3.5608 | 3.0932 | 2.4489 | 1.3051 | 0.49569 | 0.051115 | -0.1202 | 4.6326 | 4.6203 | 4.6059 | 4.5858 | 4.483 | 4.357 | 4.2237 | 4.0833 | 3.9372 | 3.6702 | 3.0935 | 2.6683 | 2.4626 | 2.2448 | 4.4338 | 4.4115 | 4.3851 | 4.3478 | 4.2437 | 3.9196 | 3.5822 | 3.2172 | 2.7788 | 2.1771 | 1.1231 | 0.40423 | 0.030467 | -0.11274
|  | STRATTON | LW |  |  | 5.1522 | 4.7362 | 4.2901 | 3.8464 | 3.2411 | 2.6313 | 2.0153 | 1.3753 | 0.5988 | -0.15576 | -1.517 | -2.2618 | -2.412 | -2.4622 | 4.6219 | 4.5009 | 4.3437 | 4.186 | 3.9698 | 3.75 | 3.5277 | 3.2972 | 3.043 | 2.7725 | 2.1131 | 1.5802 | 1.5151 | 1.4876 | 4.3697 | 4.1381 | 3.7987 | 3.4618 | 2.994 | 2.5241 | 1.9909 | 1.4161 | 0.69384 | -0.0029034 | -1.185 | -1.848 | -1.9786 | -2.022
|  | STRATTON | ST |  |  | 5.7061 | 5.5813 | 5.4446 | 5.3034 | 5.0745 | 4.8399 | 4.6024 | 4.3496 | 4.0857 | 3.7967 | 2.6712 | 0.97379 | 0.0401 | -0.28058 | 4.6415 | 4.6358 | 4.6288 | 4.6211 | 4.6095 | 4.5577 | 4.4758 | 4.3893 | 4.2992 | 4.1832 | 3.7602 | 2.8937 | 2.4258 | 2.2042 | 4.4544 | 4.4463 | 4.4342 | 4.4202 | 4.3715 | 4.2996 | 4.1303 | 3.9543 | 3.7433 | 3.4814 | 2.4066 | 0.84722 | 0.068575 | -0.19623
|  | STRATTON | SP |  |  | 5.7664 | 5.6693 | 5.5655 | 5.4657 | 5.137 | 4.7993 | 4.4616 | 4.1147 | 3.7497 | 3.3046 | 1.8348 | -1.2674 | -2.9982 | -4.081 | 4.6433 | 4.638 | 4.6312 | 4.6247 | 4.6133 | 4.5359 | 4.4144 | 4.2905 | 4.163 | 3.9999 | 3.4859 | 2.1521 | 1.3327 | 0.79933 | 4.4551 | 4.4454 | 4.433 | 4.4218 | 4.3832 | 4.2358 | 3.9641 | 3.6905 | 3.41 | 3.0528 | 1.8357 | -0.97637 | -2.44 | -3.3308
LALEHAM | STAINES | SUNBURY CROSS | MINIMUM HEADROOM | TQ 10053 69996 | NO | -0.23518 | -0.69039 | -1.134 | 18.6162 | 17.9835 | 17.3357 | 16.653 | 15.898 | 15.0164 | 14.2238 | 12.3011 | 9.973 | 9.2956 | 8.8243 | 1.3157 | 1.0601 | 0.81649 | 20.6695 | 20.3498 | 20.0182 | 19.6444 | 19.2017 | 18.6502 | 18.1842 | 17.2294 | 16.1114 | 15.6745 | 15.0666 | -0.69805 | -1.0824 | -1.4681 | 18.2356 | 17.6989 | 17.1364 | 16.5034 | 15.7899 | 14.9362 | 14.1863 | 12.4715 | 10.4182 | 9.8494 | 9.4545
|  | SUNBURY CROSS | CT |  |  | 0.11218 | -0.16156 | -0.42087 | 19.4958 | 19.1067 | 18.7086 | 18.2683 | 17.784 | 17.2126 | 16.4315 | 14.7739 | 11.8345 | 9.7454 | 8.868 | 1.4274 | 1.2327 | 1.0508 | 20.946 | 20.7032 | 20.4521 | 20.163 | 19.8432 | 19.4573 | 18.9669 | 18.0502 | 16.6301 | 15.6745 | 15.0666 | -0.45714 | -0.70826 | -0.95781 | 18.8601 | 18.5066 | 18.1419 | 17.7293 | 17.2777 | 16.7443 | 16.0288 | 14.5631 | 12.0012 | 10.276 | 9.5161
|  | SUNBURY CROSS | LW |  |  | -0.23518 | -0.69039 | -1.134 | 18.6162 | 17.9835 | 17.3357 | 16.653 | 15.898 | 15.0164 | 14.2238 | 12.3011 | 9.973 | 9.2956 | 8.8243 | 1.3157 | 1.0601 | 0.81649 | 20.6695 | 20.3498 | 20.0182 | 19.6444 | 19.2017 | 18.6502 | 18.1842 | 17.2294 | 16.1114 | 15.8342 | 15.6569 | -0.69805 | -1.0824 | -1.4681 | 18.2356 | 17.6989 | 17.1364 | 16.5034 | 15.7899 | 14.9362 | 14.1863 | 12.4715 | 10.4182 | 9.8494 | 9.4545
|  | SUNBURY CROSS | ST |  |  | 0.26219 | 0.070855 | -0.092027 | 19.9474 | 19.722 | 19.4946 | 19.2572 | 18.9942 | 18.7114 | 18.4052 | 17.0713 | 15.0965 | 14.044 | 13.3468 | 1.5304 | 1.3922 | 1.2783 | 21.2659 | 21.1265 | 20.9846 | 20.8321 | 20.6587 | 20.4565 | 20.2571 | 19.3122 | 17.9994 | 17.3294 | 16.7714 | -0.30086 | -0.46635 | -0.61375 | 19.3367 | 19.1333 | 18.9255 | 18.7046 | 18.4553 | 18.1835 | 17.8997 | 16.611 | 14.8169 | 13.8888 | 13.2925
|  | SUNBURY CROSS | SP |  |  | 0.30987 | 0.14055 | 0.011743 | 20.0869 | 19.8064 | 19.5325 | 19.2505 | 18.9477 | 18.6359 | 18.2375 | 16.8969 | 13.9372 | 12.284 | 11.3253 | 1.5474 | 1.4142 | 1.3142 | 21.3169 | 21.1677 | 21.0224 | 20.8696 | 20.6986 | 20.518 | 20.305 | 19.5175 | 17.5654 | 16.5457 | 15.8222 | -0.26532 | -0.41724 | -0.53626 | 19.4447 | 19.2121 | 18.9847 | 18.7482 | 18.4874 | 18.2158 | 17.8768 | 16.6784 | 13.8324 | 12.3542 | 11.5415
BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL | MINIMUM HEADROOM | SU 93757 67606 | YES | 15.3982 | 14.8488 | 14.204 | 13.4959 | 12.4862 | 11.3997 | 10.2452 | 8.8995 | 7.255 | 5.6382 | 1.7557 | -2.0795 | -5.1718 | -6.9042 | 20.6239 | 20.311 | 19.9366 | 19.5295 | 19.0132 | 18.454 | 17.844 | 17.1372 | 16.2134 | 15.1909 | 12.8991 | 10.3762 | 8.3484 | 6.6441 | 16.4674 | 16.0187 | 15.4914 | 14.9079 | 14.0501 | 13.1265 | 12.1411 | 10.9723 | 9.464 | 7.9512 | 4.4517 | 0.97243 | -1.5471 | -2.9946
|  | SUNNINGHILL | CT |  |  | 15.5005 | 15.0262 | 14.4855 | 13.8207 | 13.0178 | 12.1489 | 11.2547 | 10.1818 | 8.8478 | 7.2179 | 3.0863 | -1.7919 | -5.1718 | -6.9042 | 20.636 | 20.3419 | 20.0118 | 19.594 | 19.1414 | 18.6526 | 18.1369 | 17.5311 | 16.7235 | 15.7366 | 13.2364 | 10.3762 | 8.3484 | 6.6441 | 16.5625 | 16.1826 | 15.7481 | 15.2066 | 14.5381 | 13.8133 | 13.0372 | 12.0693 | 10.8674 | 9.3899 | 5.659 | 1.2933 | -1.5471 | -2.9946
|  | SUNNINGHILL | LW |  |  | 15.3982 | 14.8488 | 14.204 | 13.4959 | 12.4862 | 11.3997 | 10.2452 | 8.8995 | 7.255 | 5.6382 | 1.7557 | -2.0795 | -3.7959 | -4.6497 | 20.6239 | 20.311 | 19.9366 | 19.5295 | 19.0132 | 18.454 | 17.844 | 17.1372 | 16.2134 | 15.1909 | 12.8991 | 10.7201 | 9.8706 | 9.4253 | 16.4674 | 16.0187 | 15.4914 | 14.9079 | 14.0501 | 13.1265 | 12.1411 | 10.9723 | 9.464 | 7.9512 | 4.4517 | 0.97243 | -0.50215 | -1.2225
|  | SUNNINGHILL | ST |  |  | 15.726 | 15.4474 | 15.1423 | 14.8076 | 14.3943 | 13.9403 | 13.466 | 12.8703 | 12.1495 | 11.4855 | 9.1545 | 5.3012 | 3.318 | 1.9094 | 20.7835 | 20.6057 | 20.4076 | 20.1882 | 19.9165 | 19.6179 | 19.3024 | 18.9121 | 18.4432 | 18.0372 | 16.3879 | 13.4571 | 11.8742 | 10.2505 | 16.7622 | 16.5563 | 16.3324 | 16.0838 | 15.768 | 15.4191 | 15.0504 | 14.5889 | 13.9448 | 13.3622 | 11.2553 | 7.6365 | 5.8568 | 4.623
|  | SUNNINGHILL | SP |  |  | 15.7535 | 15.4802 | 15.1989 | 14.9041 | 14.5641 | 14.1994 | 13.8062 | 13.3138 | 12.7379 | 12.2095 | 10.4984 | 7.1239 | 5.1767 | 4.3014 | 20.7957 | 20.6124 | 20.4221 | 20.2209 | 20.0028 | 19.7683 | 19.5079 | 19.1808 | 18.7943 | 18.434 | 17.191 | 14.204 | 11.9327 | 9.4734 | 16.7868 | 16.5867 | 16.3844 | 16.1717 | 15.9192 | 15.648 | 15.3511 | 14.9818 | 14.5389 | 14.0644 | 12.5429 | 9.336 | 7.5124 | 6.7331
MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER | MINIMUM HEADROOM | ST 93394 80051 | YES | 18.549 | 17.5079 | 16.0431 | 14.3891 | 12.0974 | 9.6444 | 7.0028 | 4.1015 | 0.75519 | -2.6458 | -11.743 | -22.8631 | -28.2719 | -32.2639 | 32.8831 | 32.1265 | 31.2169 | 30.2348 | 28.9506 | 27.5431 | 25.9946 | 24.284 | 22.1973 | 20.0419 | 14.1498 | 6.9877 | 1.3928 | -4.0407 | 30.6579 | 29.5996 | 28.259 | 26.7804 | 24.7018 | 22.4912 | 20.1066 | 17.4474 | 14.2908 | 11.0699 | 2.509 | -7.7572 | -12.2543 | -15.7623
|  | SUTTON BENGER | CT |  |  | 18.8548 | 18.0485 | 16.8909 | 15.3885 | 13.5934 | 11.6746 | 9.6691 | 7.437 | 5.059 | 1.8315 | -6.9459 | -20.3686 | -28.2719 | -32.2639 | 32.9509 | 32.257 | 31.4445 | 30.4648 | 29.3135 | 28.0813 | 26.7722 | 25.3137 | 23.6838 | 21.591 | 15.6364 | 6.9877 | 1.3928 | -4.0407 | 30.95 | 30.1131 | 29.0543 | 27.7247 | 26.1115 | 24.351 | 22.5001 | 20.4398 | 18.1906 | 15.146 | 6.9102 | -5.3381 | -12.2543 | -15.7623
|  | SUTTON BENGER | LW |  |  | 18.549 | 17.5079 | 16.0431 | 14.3891 | 12.0974 | 9.6444 | 7.0028 | 4.1015 | 0.75519 | -2.6458 | -11.743 | -22.8631 | -26.7926 | -28.9436 | 32.8831 | 32.1265 | 31.2169 | 30.2348 | 28.9506 | 27.5431 | 25.9946 | 24.284 | 22.1973 | 20.0419 | 14.1498 | 7.4114 | 5.5491 | 4.4821 | 30.6579 | 29.5996 | 28.259 | 26.7804 | 24.7018 | 22.4912 | 20.1066 | 17.4474 | 14.2908 | 11.0699 | 2.509 | -7.7572 | -11.1374 | -12.9363
|  | SUTTON BENGER | ST |  |  | 19.4749 | 19.0429 | 18.4265 | 17.7295 | 16.8214 | 15.8489 | 14.8002 | 13.6163 | 12.3557 | 11.0995 | 5.8477 | -6.3933 | -12.7553 | -15.924 | 33.3259 | 32.8587 | 32.3625 | 31.8506 | 31.2103 | 30.5418 | 29.8127 | 28.9585 | 27.99 | 27.0371 | 23.0139 | 12.2638 | 7.0911 | 2.4433 | 31.5166 | 31.0225 | 30.46 | 29.8614 | 29.0714 | 28.2376 | 27.3313 | 26.2573 | 25.0649 | 23.8788 | 18.8409 | 7.2174 | 1.4047 | -1.2393
|  | SUTTON BENGER | SP |  |  | 19.5703 | 19.1407 | 18.56 | 17.9396 | 17.2039 | 16.4337 | 15.6084 | 14.659 | 13.7278 | 12.7735 | 9.3098 | -0.7793 | -8.0664 | -10.8263 | 33.3678 | 32.8944 | 32.4034 | 31.9181 | 31.3722 | 30.8115 | 30.201 | 29.5009 | 28.7507 | 27.9394 | 24.9 | 15.781 | 6.5971 | -2.8163 | 31.6048 | 31.1168 | 30.5893 | 30.0621 | 29.4255 | 28.7732 | 28.0686 | 27.2408 | 26.3753 | 25.4978 | 22.2102 | 12.5702 | 5.7429 | 3.3122
IVER 132KV | UPTON BSP | SUTTON LANE | MINIMUM HEADROOM | TQ 02185 78595 | YES | 12.5036 | 12.1249 | 11.7988 | 11.4744 | 10.964 | 10.4225 | 9.8284 | 9.1985 | 8.459 | 7.6996 | 5.9373 | 3.7382 | 2.8604 | 2.0095 | 16.9252 | 16.7075 | 16.5193 | 16.3264 | 16.0542 | 15.761 | 15.4238 | 15.0604 | 14.5953 | 14.1209 | 13.1274 | 11.9625 | 10.9794 | 10.1314 | 14.0862 | 13.7562 | 13.467 | 13.1745 | 12.731 | 12.2588 | 11.7096 | 11.1235 | 10.4243 | 9.7073 | 8.0752 | 6.0673 | 5.332 | 4.5937
|  | SUTTON LANE | CT |  |  | 12.6654 | 12.3876 | 12.1392 | 11.9052 | 11.5765 | 11.2226 | 10.8566 | 10.463 | 10.0184 | 9.283 | 7.5431 | 4.7466 | 2.8604 | 2.0095 | 16.958 | 16.766 | 16.5836 | 16.4052 | 16.196 | 15.9688 | 15.7201 | 15.4484 | 15.1323 | 14.6532 | 13.5906 | 12.0523 | 10.9794 | 10.1314 | 14.2033 | 13.9525 | 13.7188 | 13.4948 | 13.1993 | 12.8806 | 12.5444 | 12.1806 | 11.7636 | 11.0856 | 9.5083 | 6.9892 | 5.332 | 4.5937
|  | SUTTON LANE | LW |  |  | 12.5036 | 12.1249 | 11.7988 | 11.4744 | 10.964 | 10.4225 | 9.8284 | 9.1985 | 8.459 | 7.6996 | 5.9373 | 3.7382 | 2.9901 | 2.6215 | 16.9252 | 16.7075 | 16.5193 | 16.3264 | 16.0542 | 15.761 | 15.4238 | 15.0604 | 14.5953 | 14.1209 | 13.1274 | 11.9625 | 11.6357 | 11.4746 | 14.0862 | 13.7562 | 13.467 | 13.1745 | 12.731 | 12.2588 | 11.7096 | 11.1235 | 10.4243 | 9.7073 | 8.0752 | 6.0673 | 5.4132 | 5.0981
|  | SUTTON LANE | ST |  |  | 12.872 | 12.7242 | 12.6043 | 12.484 | 12.3315 | 12.1616 | 11.9774 | 11.7772 | 11.5474 | 11.3008 | 10.179 | 8.1083 | 7.0476 | 6.3625 | 17.1045 | 17 | 16.9071 | 16.8087 | 16.6968 | 16.5711 | 16.4312 | 16.2764 | 16.0936 | 15.9135 | 15.0564 | 13.4948 | 12.6528 | 11.8676 | 14.4032 | 14.2754 | 14.165 | 14.0501 | 13.9091 | 13.7519 | 13.58 | 13.3917 | 13.1723 | 12.942 | 11.8623 | 9.9272 | 9.0193 | 8.4457
|  | SUTTON LANE | SP |  |  | 12.8946 | 12.7618 | 12.6665 | 12.5794 | 12.4171 | 12.244 | 12.0693 | 11.8654 | 11.6522 | 11.3947 | 10.4523 | 8.0404 | 6.6994 | 6.0748 | 17.1116 | 17.0106 | 16.9285 | 16.8475 | 16.7412 | 16.6271 | 16.5086 | 16.3652 | 16.2083 | 16.0313 | 15.3471 | 13.4783 | 12.2649 | 11.2654 | 14.4217 | 14.3055 | 14.2172 | 14.1337 | 13.9897 | 13.8371 | 13.6827 | 13.4986 | 13.3035 | 13.0715 | 12.2039 | 9.9361 | 8.7063 | 8.1495
MANNINGTON GSP | WAREHAM | SWANAGE | MINIMUM HEADROOM | SZ 02010 79296 | YES | 2.9373 | 2.7728 | 2.612 | 2.4471 | 2.2227 | 1.9881 | 1.7431 | 1.4669 | 1.1509 | 0.89017 | 0.33782 | -0.26551 | -0.41109 | -0.49032 | 4.6082 | 4.5241 | 4.4412 | 4.3544 | 4.2419 | 4.1225 | 3.9918 | 3.8347 | 3.6375 | 3.4816 | 3.2381 | 2.9685 | 2.9035 | 2.7156 | 3.4732 | 3.3245 | 3.1779 | 3.0271 | 2.8233 | 2.61 | 2.3858 | 2.1311 | 1.8296 | 1.5819 | 1.0983 | 0.55754 | 0.42857 | 0.35911
|  | SWANAGE | CT |  |  | 3.0647 | 2.9728 | 2.8766 | 2.7785 | 2.6453 | 2.504 | 2.3574 | 2.1764 | 1.9883 | 1.7277 | 1.2975 | 0.61955 | 0.17822 | -0.012618 | 4.6442 | 4.583 | 4.5164 | 4.4475 | 4.3674 | 4.2816 | 4.1892 | 4.0694 | 3.9432 | 3.7699 | 3.534 | 3.1751 | 2.9235 | 2.7156 | 3.5818 | 3.4962 | 3.4047 | 3.3113 | 3.1876 | 3.0565 | 2.9194 | 2.7483 | 2.5702 | 2.3222 | 1.9304 | 1.3243 | 0.94972 | 0.78182
|  | SWANAGE | LW |  |  | 2.9373 | 2.7728 | 2.612 | 2.4471 | 2.2227 | 1.9881 | 1.7431 | 1.4669 | 1.1509 | 0.89017 | 0.33782 | -0.26551 | -0.41109 | -0.49032 | 4.6082 | 4.5241 | 4.4412 | 4.3544 | 4.2419 | 4.1225 | 3.9918 | 3.8347 | 3.6375 | 3.4816 | 3.2381 | 2.9685 | 2.9035 | 2.8681 | 3.4732 | 3.3245 | 3.1779 | 3.0271 | 2.8233 | 2.61 | 2.3858 | 2.1311 | 1.8296 | 1.5819 | 1.0983 | 0.55754 | 0.42857 | 0.35911
|  | SWANAGE | ST |  |  | 3.1611 | 3.1215 | 3.0806 | 3.0315 | 2.9585 | 2.8782 | 2.7975 | 2.7041 | 2.6073 | 2.5063 | 2.0214 | 1.4719 | 1.1945 | 1.0214 | 4.7063 | 4.6785 | 4.648 | 4.6104 | 4.5638 | 4.5114 | 4.4574 | 4.3929 | 4.3239 | 4.2584 | 3.9142 | 3.5253 | 3.3122 | 3.1059 | 3.6736 | 3.6376 | 3.5988 | 3.5519 | 3.484 | 3.4092 | 3.3338 | 3.2458 | 3.154 | 3.0594 | 2.5951 | 2.0807 | 1.8318 | 1.6792
|  | SWANAGE | SP |  |  | 3.1861 | 3.1568 | 3.1316 | 3.1031 | 3.0498 | 2.9944 | 2.94 | 2.8729 | 2.8072 | 2.7022 | 2.3191 | 1.3867 | 0.91865 | 0.62201 | 4.7148 | 4.6908 | 4.6679 | 4.6414 | 4.6062 | 4.5693 | 4.5319 | 4.4835 | 4.4347 | 4.3702 | 4.1179 | 3.4754 | 3.1811 | 2.9419 | 3.6954 | 3.6687 | 3.6445 | 3.6169 | 3.5674 | 3.5162 | 3.4656 | 3.4024 | 3.3403 | 3.243 | 2.8834 | 2.0032 | 1.581 | 1.3183
MINETY GSP | SWINDON BSP | SWINDON | MINIMUM HEADROOM | SU 12449 86967 | NO | 12.8452 | 12.7134 | 12.5726 | 12.4194 | 12.2556 | 12.0517 | 11.8098 | 11.5405 | 10.9468 | 10.2228 | 8.1143 | 5.0578 | 2.7141 | 0.96074 | 15.1353 | 14.9843 | 14.8176 | 14.6242 | 14.3705 | 14.0888 | 13.7584 | 13.3833 | 12.8943 | 12.4206 | 10.9761 | 8.2531 | 5.648 | -0.32496 | 14.6146 | 14.5071 | 14.3929 | 14.2679 | 14.1374 | 13.9782 | 13.7864 | 13.3708 | 12.6709 | 11.9867 | 10.0132 | 7.2576 | 5.314 | 3.8758
|  | SWINDON | CT |  |  | 12.8452 | 12.7134 | 12.5726 | 12.4194 | 12.2556 | 12.0714 | 11.8711 | 11.6531 | 11.3789 | 11.0549 | 9.1032 | 5.4187 | 2.7141 | 0.96074 | 15.1353 | 14.9843 | 14.8176 | 14.6242 | 14.3705 | 14.0888 | 13.7747 | 13.4341 | 13.0293 | 12.4975 | 10.9761 | 8.2531 | 5.648 | 2.4865 | 14.6146 | 14.5071 | 14.3929 | 14.2679 | 14.1374 | 13.9906 | 13.8301 | 13.6556 | 13.437 | 12.85 | 10.9256 | 7.6287 | 5.314 | 3.8758
|  | SWINDON | LW |  |  | 12.8642 | 12.7261 | 12.5834 | 12.4329 | 12.2559 | 12.0517 | 11.8098 | 11.5405 | 10.9468 | 10.2228 | 8.1143 | 5.0578 | 3.3536 | 2.1418 | 15.1413 | 14.9928 | 14.8268 | 14.656 | 14.3976 | 14.1024 | 13.7584 | 13.3833 | 12.8943 | 12.4206 | 11.0792 | 9.3045 | 8.4687 | 7.8499 | 14.6298 | 14.5178 | 14.401 | 14.2801 | 14.1396 | 13.9782 | 13.7864 | 13.3708 | 12.6709 | 11.9867 | 10.0132 | 7.2576 | 5.8291 | 4.836
|  | SWINDON | ST |  |  | 12.9371 | 12.8634 | 12.7921 | 12.7217 | 12.6345 | 12.5325 | 12.4128 | 12.2786 | 12.0905 | 11.8694 | 10.9384 | 8.5036 | 7.1921 | 5.9938 | 15.235 | 15.147 | 15.0522 | 14.9564 | 14.8343 | 14.6961 | 14.5392 | 14.35 | 14.1062 | 13.8486 | 12.7038 | 9.9526 | 7.4994 | 4.5327 | 14.6869 | 14.6245 | 14.5639 | 14.5058 | 14.4348 | 14.3519 | 14.2558 | 14.1485 | 14.0013 | 13.8334 | 13.1117 | 10.9905 | 9.3459 | 8.3148
|  | SWINDON | SP |  |  | 12.9426 | 12.8728 | 12.8084 | 12.7465 | 12.6779 | 12.5992 | 12.5139 | 12.4159 | 12.2915 | 12.1489 | 11.6139 | 9.7972 | 8.0372 | 7.3515 | 15.2405 | 15.1469 | 15.0531 | 14.9558 | 14.8408 | 14.7103 | 14.5671 | 14.4012 | 14.1993 | 13.9316 | 12.8648 | 9.7428 | 5.6494 | -0.32496 | 14.6919 | 14.6311 | 14.5758 | 14.5238 | 14.468 | 14.404 | 14.3353 | 14.256 | 14.1573 | 14.0462 | 13.6203 | 12.1053 | 10.3557 | 9.4792
BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY | MINIMUM HEADROOM | SU 57753 62717 | YES | 2.3544 | 2.039 | 1.6166 | 1.1643 | 0.44412 | -0.31289 | -1.1464 | -2.0363 | -3.105 | -4.2664 | -7.3436 | -10.7568 | -13.0101 | -14.5533 | 3.3775 | 3.2198 | 2.9779 | 2.712 | 2.3352 | 1.9306 | 1.4702 | 0.97043 | 0.35154 | -0.33477 | -2.0452 | -4.007 | -5.9614 | -7.7048 | 0.37593 | 0.084084 | -0.30096 | -0.71506 | -1.3762 | -2.0736 | -2.8422 | -3.6651 | -4.6588 | -5.743 | -8.5811 | -11.6672 | -13.7334 | -15.0873
|  | TADLEY | CT |  |  | 2.6244 | 2.4602 | 2.2613 | 1.9271 | 1.4708 | 0.99209 | 0.42278 | -0.19059 | -0.88019 | -1.9916 | -5.1042 | -9.7714 | -13.0101 | -14.5533 | 3.4557 | 3.3414 | 3.1988 | 2.945 | 2.6506 | 2.3376 | 1.9698 | 1.5686 | 1.1031 | 0.41555 | -1.4749 | -4.007 | -5.9614 | -7.7048 | 0.62349 | 0.46947 | 0.28125 | -0.041869 | -0.46995 | -0.91988 | -1.4509 | -2.024 | -2.6726 | -3.7086 | -6.5873 | -10.767 | -13.7334 | -15.0873
|  | TADLEY | LW |  |  | 2.3544 | 2.039 | 1.6166 | 1.1643 | 0.44412 | -0.31289 | -1.1464 | -2.0363 | -3.105 | -4.2664 | -7.3436 | -10.7568 | -11.9265 | -12.5575 | 3.3775 | 3.2198 | 2.9779 | 2.712 | 2.3352 | 1.9306 | 1.4702 | 0.97043 | 0.35154 | -0.33477 | -2.0452 | -3.7331 | -4.2197 | -4.4743 | 0.37593 | 0.084084 | -0.30096 | -0.71506 | -1.3762 | -2.0736 | -2.8422 | -3.6651 | -4.6588 | -5.743 | -8.5811 | -11.6672 | -12.7269 | -13.3184
|  | TADLEY | ST |  |  | 2.7674 | 2.6848 | 2.5813 | 2.4656 | 2.2527 | 2.0192 | 1.7492 | 1.4507 | 1.1232 | 0.76903 | -0.68537 | -3.8956 | -5.5216 | -6.6565 | 3.5534 | 3.4943 | 3.4174 | 3.3287 | 3.1761 | 3.0053 | 2.8055 | 2.5811 | 2.3302 | 2.0769 | 0.98482 | -1.4528 | -2.9073 | -4.5395 | 0.76095 | 0.68516 | 0.58875 | 0.48027 | 0.2797 | 0.058732 | -0.19425 | -0.47486 | -0.78387 | -1.1136 | -2.4875 | -5.5098 | -6.9707 | -7.9676
|  | TADLEY | SP |  |  | 2.8186 | 2.7298 | 2.6293 | 2.5213 | 2.2899 | 2.0565 | 1.7884 | 1.499 | 1.1952 | 0.81502 | -0.52962 | -3.7428 | -5.6118 | -6.4826 | 3.5738 | 3.4991 | 3.4111 | 3.3139 | 3.1655 | 3.0076 | 2.8253 | 2.6198 | 2.3952 | 2.1248 | 1.0991 | -1.5893 | -4.0227 | -6.9892 | 0.80699 | 0.72268 | 0.62673 | 0.5232 | 0.31118 | 0.096214 | -0.1478 | -0.41306 | -0.6925 | -1.0402 | -2.2829 | -5.3045 | -7.0426 | -7.8192
IVER 132KV | SLOUGH | TAPLOW | MINIMUM HEADROOM | SU 91721 81234 | YES | 29.0651 | 28.3293 | 27.4027 | 26.3451 | 24.5385 | 22.6147 | 20.5045 | 18.2229 | 15.3141 | 12.2344 | 5.1388 | -3.5376 | -10.282 | -14.2561 | 37.6085 | 37.1545 | 36.5504 | 35.8639 | 34.8635 | 33.7837 | 32.5672 | 31.2136 | 29.2671 | 27.2075 | 22.8146 | 16.9709 | 12.0673 | 7.6325 | 31.0386 | 30.3702 | 29.4926 | 28.5127 | 26.8682 | 25.1194 | 23.2071 | 21.143 | 18.5313 | 15.7629 | 9.2884 | 1.3537 | -4.9051 | -8.3899
|  | TAPLOW | CT |  |  | 29.3398 | 28.8062 | 28.1686 | 27.178 | 25.9019 | 24.5307 | 23.1058 | 21.5311 | 19.5956 | 16.4874 | 8.7632 | -2.5627 | -10.282 | -14.2561 | 37.6415 | 37.2273 | 36.7284 | 36.0126 | 35.1946 | 34.3072 | 33.3607 | 32.2731 | 30.8315 | 28.7135 | 23.6453 | 16.9709 | 12.0673 | 7.6325 | 31.2915 | 30.7829 | 30.172 | 29.2986 | 28.1515 | 26.92 | 25.644 | 24.2358 | 22.5102 | 19.7147 | 12.695 | 2.2214 | -4.9051 | -8.3899
|  | TAPLOW | LW |  |  | 29.0651 | 28.3293 | 27.4027 | 26.3451 | 24.5385 | 22.6147 | 20.5045 | 18.2229 | 15.3141 | 12.2344 | 5.1388 | -3.5376 | -7.2115 | -9.0225 | 37.6085 | 37.1545 | 36.5504 | 35.8639 | 34.8635 | 33.7837 | 32.5672 | 31.2136 | 29.2671 | 27.2075 | 22.8146 | 17.9961 | 16.3567 | 15.4976 | 31.0386 | 30.3702 | 29.4926 | 28.5127 | 26.8682 | 25.1194 | 23.2071 | 21.143 | 18.5313 | 15.7629 | 9.2884 | 1.3537 | -1.9473 | -3.5034
|  | TAPLOW | ST |  |  | 29.8713 | 29.6583 | 29.3959 | 29.0763 | 28.6101 | 28.0536 | 27.4056 | 26.6787 | 25.7999 | 24.8793 | 20.5221 | 11.0941 | 6.3065 | 3.2403 | 38.0086 | 37.814 | 37.5761 | 37.2865 | 36.896 | 36.4559 | 35.9536 | 35.3875 | 34.7002 | 33.9981 | 30.5106 | 22.9789 | 18.7441 | 14.6128 | 31.762 | 31.5799 | 31.353 | 31.0469 | 30.5992 | 30.0953 | 29.5251 | 28.8851 | 28.1083 | 27.2827 | 23.4114 | 14.8753 | 10.5959 | 7.8399
|  | TAPLOW | SP |  |  | 29.9271 | 29.6994 | 29.4459 | 29.1702 | 28.8036 | 28.395 | 27.9405 | 27.3932 | 26.7698 | 26.0343 | 23.1042 | 14.4201 | 9.6343 | 7.7558 | 38.027 | 37.8048 | 37.5521 | 37.2733 | 36.9695 | 36.6337 | 36.2714 | 35.833 | 35.3244 | 34.6919 | 32.1565 | 24.0883 | 17.4769 | 10.1359 | 31.8125 | 31.6206 | 31.3924 | 31.1271 | 30.78 | 30.4023 | 30.0001 | 29.5174 | 28.9662 | 28.3109 | 25.7181 | 17.9919 | 13.5127 | 11.879
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON | MINIMUM HEADROOM | ST 94510 07307 | YES | 3.2182 | 2.8955 | 2.5256 | 2.1268 | 1.4986 | 0.83883 | 0.12501 | -0.6402 | -1.5759 | -2.5487 | -4.7327 | -7.4416 | -8.657 | -9.6594 | 6.1324 | 5.944 | 5.7126 | 5.4556 | 5.1061 | 4.7312 | 4.3043 | 3.8362 | 3.2036 | 2.5495 | 1.3019 | -0.1139 | -1.0995 | -1.9439 | 3.9501 | 3.652 | 3.3068 | 2.9331 | 2.3553 | 1.7467 | 1.0839 | 0.37112 | -0.51288 | -1.4314 | -3.4482 | -5.9145 | -6.9476 | -7.8205
|  | TARRANT RUSHTON | CT |  |  | 3.4283 | 3.23 | 2.9993 | 2.7039 | 2.2989 | 1.8704 | 1.4204 | 0.9228 | 0.34418 | -0.61309 | -2.8263 | -6.3928 | -8.657 | -9.6594 | 6.1826 | 6.0311 | 5.8498 | 5.6076 | 5.3352 | 5.0426 | 4.7227 | 4.3614 | 3.9243 | 3.2593 | 1.8926 | 0.058424 | -1.0995 | -1.9439 | 4.1316 | 3.9436 | 3.7233 | 3.4386 | 3.059 | 2.6565 | 2.2314 | 1.7598 | 1.2078 | 0.30302 | -1.7486 | -4.9554 | -6.9476 | -7.8205
|  | TARRANT RUSHTON | LW |  |  | 3.2182 | 2.8955 | 2.5256 | 2.1268 | 1.4986 | 0.83883 | 0.12501 | -0.6402 | -1.5759 | -2.5487 | -4.7327 | -7.4416 | -8.3602 | -8.7512 | 6.1324 | 5.944 | 5.7126 | 5.4556 | 5.1061 | 4.7312 | 4.3043 | 3.8362 | 3.2036 | 2.5495 | 1.3019 | -0.1139 | -0.49883 | -0.66789 | 3.9501 | 3.652 | 3.3068 | 2.9331 | 2.3553 | 1.7467 | 1.0839 | 0.37112 | -0.51288 | -1.4314 | -3.4482 | -5.9145 | -6.7195 | -7.0553
|  | TARRANT RUSHTON | ST |  |  | 3.587 | 3.4904 | 3.3785 | 3.2541 | 3.0713 | 2.8691 | 2.6531 | 2.4115 | 2.1341 | 1.8306 | 0.4681 | -2.1146 | -3.4938 | -4.402 | 6.3015 | 6.2258 | 6.1349 | 6.0312 | 5.892 | 5.7349 | 5.5626 | 5.3665 | 5.1351 | 4.904 | 3.7918 | 1.8208 | 0.86076 | 0.049114 | 4.2841 | 4.1936 | 4.0878 | 3.9694 | 3.7964 | 3.6044 | 3.3983 | 3.1671 | 2.9002 | 2.6117 | 1.2987 | -1.1471 | -2.3819 | -3.1726
|  | TARRANT RUSHTON | SP |  |  | 3.6196 | 3.5304 | 3.4377 | 3.3387 | 3.1467 | 2.9603 | 2.7678 | 2.5411 | 2.2968 | 1.9982 | 0.90908 | -1.9505 | -3.4891 | -4.18 | 6.3145 | 6.2348 | 6.1498 | 6.0569 | 5.9319 | 5.8059 | 5.6732 | 5.5087 | 5.3256 | 5.1119 | 4.278 | 1.9274 | 0.5077 | -0.6775 | 4.3134 | 4.2285 | 4.14 | 4.045 | 3.8673 | 3.6943 | 3.5154 | 3.3027 | 3.0726 | 2.7931 | 1.7638 | -0.96402 | -2.4064 | -3.0243
MANNINGTON GSP | SALISBURY | TEFFONT | MINIMUM HEADROOM | ST 99837 30994 | YES | 15.2698 | 14.8526 | 14.3633 | 13.8212 | 12.9968 | 12.1078 | 11.1316 | 10.0494 | 8.6694 | 7.2749 | 3.5329 | -1.6977 | -4.6972 | -7.15 | 20.0178 | 19.7723 | 19.4783 | 19.1475 | 18.6848 | 18.1562 | 17.5557 | 16.8753 | 15.961 | 15.0378 | 12.6785 | 9.6229 | 7.4271 | 5.4644 | 16.9517 | 16.5642 | 16.1061 | 15.5962 | 14.8331 | 14.0072 | 13.0939 | 12.0769 | 10.7692 | 9.4479 | 5.9542 | 1.2219 | -1.2406 | -3.2969
|  | TEFFONT | CT |  |  | 15.4097 | 15.0969 | 14.728 | 14.2588 | 13.6603 | 13.0143 | 12.3331 | 11.5664 | 10.6349 | 9.2605 | 5.5831 | -0.59617 | -4.6972 | -7.15 | 20.0451 | 19.8282 | 19.5716 | 19.2434 | 18.844 | 18.4038 | 17.9256 | 17.3799 | 16.7104 | 15.7887 | 13.4182 | 9.789 | 7.4271 | 5.4644 | 17.0695 | 16.7746 | 16.4251 | 15.9766 | 15.415 | 14.8073 | 14.1624 | 13.4339 | 12.5485 | 11.2498 | 7.8272 | 2.2868 | -1.2406 | -3.2969
|  | TEFFONT | LW |  |  | 15.2698 | 14.8526 | 14.3633 | 13.8212 | 12.9968 | 12.1078 | 11.1316 | 10.0494 | 8.6694 | 7.2749 | 3.5329 | -1.6977 | -4.1372 | -5.7773 | 20.0178 | 19.7723 | 19.4783 | 19.1475 | 18.6848 | 18.1562 | 17.5557 | 16.8753 | 15.961 | 15.0378 | 12.6785 | 9.6229 | 8.4401 | 7.6125 | 16.9517 | 16.5642 | 16.1061 | 15.5962 | 14.8331 | 14.0072 | 13.0939 | 12.0769 | 10.7692 | 9.4479 | 5.9542 | 1.2219 | -0.83191 | -2.1768
|  | TEFFONT | ST |  |  | 15.6953 | 15.5669 | 15.4092 | 15.2163 | 14.9563 | 14.6706 | 14.3516 | 13.9922 | 13.5249 | 13.0181 | 10.7094 | 5.5361 | 2.6029 | 0.78175 | 20.2273 | 20.1275 | 20.0062 | 19.8578 | 19.6693 | 19.4611 | 19.2253 | 18.9472 | 18.5741 | 18.1886 | 16.4051 | 12.549 | 10.3641 | 8.6496 | 17.3441 | 17.2266 | 17.0804 | 16.8994 | 16.6545 | 16.3848 | 16.0816 | 15.7386 | 15.2936 | 14.8141 | 12.6127 | 7.7988 | 5.2343 | 3.7354
|  | TEFFONT | SP |  |  | 15.7385 | 15.611 | 15.4676 | 15.3041 | 15.1118 | 14.9014 | 14.6776 | 14.4128 | 14.0816 | 13.686 | 12.1439 | 7.4876 | 4.1995 | 2.5763 | 20.2478 | 20.1431 | 20.0237 | 19.8872 | 19.7425 | 19.584 | 19.4104 | 19.2052 | 18.9407 | 18.6227 | 17.3635 | 13.5578 | 10.541 | 8.1466 | 17.3844 | 17.2663 | 17.1328 | 16.9795 | 16.8 | 16.6037 | 16.393 | 16.1419 | 15.8293 | 15.457 | 14.0037 | 9.6311 | 6.6418 | 5.275
BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM | MINIMUM HEADROOM | SU 84178 83872 | YES | 2.7026 | 2.6332 | 2.5564 | 2.4766 | 2.3568 | 2.2321 | 2.0181 | 1.7842 | 1.5112 | 1.2314 | 0.27939 | -1.0068 | -1.216 | -1.4512 | 3.7664 | 3.7321 | 3.6896 | 3.6447 | 3.5826 | 3.5164 | 3.3967 | 3.2634 | 3.1048 | 2.9418 | 2.4335 | 1.7493 | 1.5158 | 1.295 | 3.1552 | 3.11 | 3.0508 | 2.9895 | 2.9051 | 2.8153 | 2.6541 | 2.4739 | 2.2567 | 2.027 | 1.1399 | -0.048532 | -0.22879 | -0.42804
|  | TEMPLE FARM | CT |  |  | 2.7708 | 2.7384 | 2.7023 | 2.6564 | 2.5831 | 2.5057 | 2.3389 | 2.1536 | 1.9509 | 1.696 | 0.80356 | -0.68659 | -1.216 | -1.4512 | 3.7892 | 3.7677 | 3.7422 | 3.7055 | 3.6593 | 3.6091 | 3.508 | 3.394 | 3.2668 | 3.1103 | 2.6051 | 1.8061 | 1.5158 | 1.295 | 3.1901 | 3.1656 | 3.1352 | 3.0877 | 3.0278 | 2.9635 | 2.8314 | 2.6814 | 2.512 | 2.3021 | 1.5546 | 0.22209 | -0.22879 | -0.42804
|  | TEMPLE FARM | LW |  |  | 2.7026 | 2.6332 | 2.5564 | 2.4766 | 2.3568 | 2.2321 | 2.0181 | 1.7842 | 1.5112 | 1.2314 | 0.27939 | -1.0068 | -1.1947 | -1.3229 | 3.7664 | 3.7321 | 3.6896 | 3.6447 | 3.5826 | 3.5164 | 3.3967 | 3.2634 | 3.1048 | 2.9418 | 2.4335 | 1.7493 | 1.6645 | 1.6098 | 3.1552 | 3.11 | 3.0508 | 2.9895 | 2.9051 | 2.8153 | 2.6541 | 2.4739 | 2.2567 | 2.027 | 1.1399 | -0.048532 | -0.21104 | -0.31948
|  | TEMPLE FARM | ST |  |  | 2.7924 | 2.773 | 2.752 | 2.7297 | 2.6928 | 2.6531 | 2.5633 | 2.4647 | 2.3538 | 2.2325 | 1.7138 | 0.8095 | 0.50592 | 0.30554 | 3.8036 | 3.7909 | 3.7759 | 3.7596 | 3.7347 | 3.7071 | 3.643 | 3.5721 | 3.4928 | 3.4103 | 3.0398 | 2.4044 | 2.1866 | 1.9796 | 3.208 | 3.1944 | 3.1769 | 3.1585 | 3.1275 | 3.0936 | 3.012 | 2.9218 | 2.8212 | 2.7191 | 2.2468 | 1.4583 | 1.2163 | 1.063
|  | TEMPLE FARM | SP |  |  | 2.8034 | 2.7874 | 2.7718 | 2.7551 | 2.7066 | 2.6565 | 2.5662 | 2.4691 | 2.3691 | 2.2468 | 1.7822 | 0.85906 | 0.45437 | 0.22079 | 3.8083 | 3.7951 | 3.7817 | 3.767 | 3.7401 | 3.7117 | 3.6514 | 3.5852 | 3.5152 | 3.4342 | 3.1044 | 2.4187 | 2.0902 | 1.7729 | 3.2155 | 3.2006 | 3.1859 | 3.1703 | 3.1368 | 3.1021 | 3.0261 | 2.9427 | 2.8548 | 2.7549 | 2.3428 | 1.4905 | 1.1248 | 0.93131
MELKSHAM GSP | CHIPPENHAM | TETBURY | MINIMUM HEADROOM | ST 89708 93444 | YES | 0.92175 | 0.6538 | 0.3744 | 0.10359 | -0.27309 | -0.66343 | -1.0563 | -1.4702 | -1.9831 | -2.4774 | -3.35 | -3.6055 | -4.7438 | -5.5739 | -0.40347 | -0.50639 | -0.63012 | -0.75225 | -0.90889 | -1.0753 | -1.2493 | -1.4395 | -1.6996 | -1.9367 | -2.2626 | -2.398 | -2.8191 | -3.1088 | 0.36497 | 0.12698 | -0.1242 | -0.36805 | -0.69637 | -1.0338 | -1.3733 | -1.7279 | -2.1463 | -2.5615 | -3.3512 | -3.5855 | -4.5813 | -5.311
|  | TETBURY | CT |  |  | 1.258 | 1.155 | 1.047 | 0.91153 | 0.69588 | 0.4718 | 0.23158 | -0.026392 | -0.32842 | -0.7319 | -1.4051 | -1.599 | -1.6908 | -1.7394 | -0.31462 | -0.37106 | -0.43499 | -0.52103 | -0.62638 | -0.73831 | -0.85855 | -0.99226 | -1.1689 | -1.3864 | -1.7054 | -1.8451 | -1.9327 | -2.025 | 0.65666 | 0.56246 | 0.46292 | 0.35276 | 0.17298 | -0.01288 | -0.21213 | -0.42392 | -0.66031 | -0.99399 | -1.6033 | -1.784 | -1.8676 | -1.9117
|  | TETBURY | LW |  |  | 0.92175 | 0.6538 | 0.3744 | 0.10359 | -0.27309 | -0.66343 | -1.0563 | -1.4702 | -1.9831 | -2.4774 | -3.35 | -3.6055 | -3.6449 | -3.6547 | -0.40347 | -0.50639 | -0.63012 | -0.75225 | -0.90889 | -1.0753 | -1.2493 | -1.4395 | -1.6996 | -1.9367 | -2.2626 | -2.3928 | -2.4177 | -2.4274 | 0.36497 | 0.12698 | -0.1242 | -0.36805 | -0.69637 | -1.0338 | -1.3733 | -1.7279 | -2.1463 | -2.5615 | -3.3512 | -3.5855 | -3.622 | -3.6313
|  | TETBURY | ST |  |  | 1.2769 | 1.1924 | 1.1062 | 1.0186 | 0.87489 | 0.72828 | 0.57842 | 0.41425 | 0.23656 | 0.048074 | -0.66081 | -1.7164 | -2.3579 | -2.5317 | -0.28703 | -0.3228 | -0.36251 | -0.40605 | -0.47917 | -0.55397 | -0.63052 | -0.71217 | -0.80675 | -0.89797 | -1.3016 | -1.8297 | -2.0915 | -2.2227 | 0.6771 | 0.60193 | 0.52455 | 0.44546 | 0.31503 | 0.18194 | 0.050335 | -0.086608 | -0.232 | -0.39137 | -0.95831 | -1.8771 | -2.4578 | -2.6178
|  | TETBURY | SP |  |  | 1.3189 | 1.2569 | 1.192 | 1.1285 | 0.88358 | 0.63432 | 0.38742 | 0.13971 | -0.12221 | -0.43984 | -1.4577 | -3.5503 | -4.7438 | -5.5739 | -0.27544 | -0.30833 | -0.34659 | -0.38296 | -0.47332 | -0.57129 | -0.66237 | -0.7631 | -0.868 | -0.98754 | -1.418 | -2.398 | -2.8191 | -3.1088 | 0.71369 | 0.65739 | 0.59791 | 0.54001 | 0.32355 | 0.10225 | -0.11577 | -0.33615 | -0.56556 | -0.84103 | -1.7208 | -3.5257 | -4.5813 | -5.311
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM | MINIMUM HEADROOM | SU 52758 66466 | YES | 1.2162 | 1.1948 | 1.1743 | 1.147 | 1.0766 | 0.99638 | 0.90814 | 0.80064 | 0.68158 | 0.59162 | 0.37588 | 0.11708 | 0.05352 | 0.018998 | 2.1185 | 2.0894 | 2.0602 | 2.0283 | 1.9879 | 1.9451 | 1.8973 | 1.8377 | 1.7667 | 1.7131 | 1.6001 | 1.4679 | 1.4364 | 1.3764 | 1.2769 | 1.2393 | 1.2024 | 1.1613 | 1.1079 | 1.05 | 0.98728 | 0.91803 | 0.82162 | 0.73646 | 0.52315 | 0.25717 | 0.2141 | 0.19022
|  | THATCHAM | CT |  |  | 1.2201 | 1.2052 | 1.1875 | 1.1665 | 1.1442 | 1.1189 | 1.0914 | 1.0313 | 0.96237 | 0.86689 | 0.7113 | 0.45955 | 0.31675 | 0.24137 | 2.1347 | 2.1149 | 2.0922 | 2.0681 | 2.04 | 2.0098 | 1.9769 | 1.9307 | 1.8855 | 1.8242 | 1.7276 | 1.5646 | 1.4621 | 1.3764 | 1.3038 | 1.2842 | 1.2617 | 1.2359 | 1.2027 | 1.1663 | 1.128 | 1.0845 | 1.0419 | 0.98376 | 0.81546 | 0.53039 | 0.4215 | 0.37245
|  | THATCHAM | LW |  |  | 1.2162 | 1.1948 | 1.1743 | 1.147 | 1.0766 | 0.99638 | 0.90814 | 0.80064 | 0.68158 | 0.59162 | 0.37588 | 0.11708 | 0.05352 | 0.018998 | 2.1185 | 2.0894 | 2.0602 | 2.0283 | 1.9879 | 1.9451 | 1.8973 | 1.8377 | 1.7667 | 1.7131 | 1.6001 | 1.4679 | 1.4364 | 1.4189 | 1.2769 | 1.2393 | 1.2024 | 1.1613 | 1.1079 | 1.05 | 0.98728 | 0.91803 | 0.82162 | 0.73646 | 0.52315 | 0.25717 | 0.2141 | 0.19022
|  | THATCHAM | ST |  |  | 1.2349 | 1.2284 | 1.222 | 1.2138 | 1.2029 | 1.1898 | 1.1753 | 1.1579 | 1.1382 | 1.1111 | 0.96955 | 0.73801 | 0.60563 | 0.56067 | 2.1528 | 2.1434 | 2.1335 | 2.1214 | 2.1051 | 2.0881 | 2.0693 | 2.0475 | 2.0242 | 1.999 | 1.8726 | 1.7111 | 1.6133 | 1.5277 | 1.3236 | 1.3155 | 1.3075 | 1.2979 | 1.2819 | 1.2635 | 1.244 | 1.2216 | 1.1971 | 1.1629 | 1.0343 | 0.7527 | 0.61074 | 0.56074
|  | THATCHAM | SP |  |  | 1.2359 | 1.2307 | 1.2245 | 1.2181 | 1.2098 | 1.2006 | 1.1913 | 1.179 | 1.1673 | 1.1491 | 1.0855 | 0.76302 | 0.57821 | 0.46824 | 2.1553 | 2.147 | 2.1384 | 2.1295 | 2.118 | 2.1065 | 2.0952 | 2.0803 | 2.0641 | 2.0422 | 1.9568 | 1.7208 | 1.5946 | 1.5096 | 1.3276 | 1.3218 | 1.3147 | 1.3075 | 1.2956 | 1.2844 | 1.2732 | 1.2587 | 1.2454 | 1.2198 | 1.1346 | 0.88206 | 0.65391 | 0.56402
NORTH HYDE GSP | NORTH HYDE (D) | THE GREEN | MINIMUM HEADROOM | TQ 12414 79503 | YES | 2.9126 | 2.6689 | 2.3965 | 2.1091 | 1.6605 | 1.1941 | 0.7023 | 0.1705 | -0.45849 | -1.0965 | -2.6902 | -4.5818 | -5.6058 | -6.491 | 3.0729 | 2.9478 | 2.7949 | 2.632 | 2.4038 | 2.1614 | 1.8932 | 1.5926 | 1.2082 | 0.82908 | 0.0061025 | -0.85912 | -1.686 | -2.3637 | 1.3372 | 1.1165 | 0.86051 | 0.592 | 0.18719 | -0.23641 | -0.68987 | -1.1863 | -1.79 | -2.3949 | -3.8303 | -5.4668 | -6.2767 | -6.9741
|  | THE GREEN | CT |  |  | 3.1236 | 2.9843 | 2.8266 | 2.6308 | 2.3559 | 2.0658 | 1.7525 | 1.4113 | 1.0288 | 0.39749 | -1.1275 | -3.6494 | -5.6058 | -6.491 | 3.1302 | 3.0351 | 2.9251 | 2.7833 | 2.6161 | 2.4367 | 2.2379 | 2.0178 | 1.763 | 1.3701 | 0.48899 | -0.74755 | -1.686 | -2.3637 | 1.5051 | 1.3733 | 1.2234 | 1.0355 | 0.77925 | 0.50801 | 0.21392 | -0.10726 | -0.46951 | -1.0628 | -2.4719 | -4.6807 | -6.2767 | -6.9741
|  | THE GREEN | LW |  |  | 2.9126 | 2.6689 | 2.3965 | 2.1091 | 1.6605 | 1.1941 | 0.7023 | 0.1705 | -0.45849 | -1.0965 | -2.6902 | -4.5818 | -5.2578 | -5.6825 | 3.0729 | 2.9478 | 2.7949 | 2.632 | 2.4038 | 2.1614 | 1.8932 | 1.5926 | 1.2082 | 0.82908 | 0.0061025 | -0.85912 | -1.1354 | -1.3002 | 1.3372 | 1.1165 | 0.86051 | 0.592 | 0.18719 | -0.23641 | -0.68987 | -1.1863 | -1.79 | -2.3949 | -3.8303 | -5.4668 | -6.0315 | -6.3756
|  | THE GREEN | ST |  |  | 3.2231 | 3.1476 | 3.0616 | 2.9652 | 2.8191 | 2.6667 | 2.5062 | 2.3261 | 2.1263 | 1.9112 | 0.97597 | -0.72966 | -1.6359 | -2.2811 | 3.2022 | 3.1543 | 3.0959 | 3.0289 | 2.9344 | 2.8333 | 2.724 | 2.5981 | 2.4555 | 2.3124 | 1.6444 | 0.4489 | -0.19059 | -0.81608 | 1.6026 | 1.5335 | 1.4522 | 1.3616 | 1.225 | 1.0819 | 0.93073 | 0.76008 | 0.57016 | 0.36798 | -0.52579 | -2.1318 | -2.9448 | -3.5136
|  | THE GREEN | SP |  |  | 3.2543 | 3.1882 | 3.1166 | 3.0394 | 2.8534 | 2.6607 | 2.461 | 2.2491 | 2.0306 | 1.7535 | 0.82043 | -1.3366 | -2.5061 | -3.1396 | 3.2129 | 3.1644 | 3.1103 | 3.0501 | 2.952 | 2.8481 | 2.741 | 2.619 | 2.4889 | 2.3284 | 1.737 | 0.22335 | -0.76963 | -1.7177 | 1.6293 | 1.5672 | 1.4998 | 1.4268 | 1.2581 | 1.0843 | 0.9071 | 0.71475 | 0.51486 | 0.26412 | -0.60395 | -2.6405 | -3.7152 | -4.2732
BRAMLEY (FLEE) | READING TOWN BSP | THE MALL | MINIMUM HEADROOM | SU 71319 73293 | YES | 5.7773 | 4.7188 | 3.6483 | 2.5363 | 0.86075 | -0.87402 | -2.6649 | -4.6072 | -6.881 | -9.1843 | -14.3468 | -20.4951 | -22.4691 | -24.529 | 12.3208 | 11.6779 | 11.0271 | 10.3433 | 9.4299 | 8.4652 | 7.4379 | 6.2917 | 4.8177 | 3.3531 | 0.37733 | -2.9616 | -5.6028 | -8.1234 | 7.3429 | 6.3602 | 5.3659 | 4.3279 | 2.7885 | 1.1893 | -0.47375 | -2.2872 | -4.4477 | -6.6294 | -11.4312 | -17.0901 | -18.8436 | -20.5624
|  | THE MALL | CT |  |  | 6.3585 | 5.6448 | 4.7957 | 3.9986 | 2.9219 | 1.7912 | 0.70661 | -0.50082 | -1.8463 | -4.1475 | -9.2553 | -17.1507 | -22.3092 | -24.529 | 12.473 | 11.9346 | 11.286 | 10.6769 | 9.9807 | 9.2399 | 8.4946 | 7.6485 | 6.6841 | 5.1507 | 1.9586 | -2.5046 | -5.6028 | -8.1234 | 7.8424 | 7.1637 | 6.3506 | 5.5871 | 4.5809 | 3.5216 | 2.4949 | 1.3464 | 0.059867 | -2.125 | -6.8913 | -14.0478 | -18.6126 | -20.5624
|  | THE MALL | LW |  |  | 5.7773 | 4.7188 | 3.6483 | 2.5363 | 0.86075 | -0.87402 | -2.6649 | -4.6072 | -6.881 | -9.1843 | -14.3468 | -20.4951 | -22.4691 | -23.327 | 12.3208 | 11.6779 | 11.0271 | 10.3433 | 9.4299 | 8.4652 | 7.4379 | 6.2917 | 4.8177 | 3.3531 | 0.37733 | -2.9616 | -3.8433 | -4.2193 | 7.3429 | 6.3602 | 5.3659 | 4.3279 | 2.7885 | 1.1893 | -0.47375 | -2.2872 | -4.4477 | -6.6294 | -11.4312 | -17.0901 | -18.8436 | -19.595
|  | THE MALL | ST |  |  | 6.8487 | 6.4331 | 5.9497 | 5.4442 | 4.8834 | 4.283 | 3.6739 | 3.0074 | 2.2723 | 1.4905 | -2.0702 | -8.4782 | -11.6522 | -13.595 | 12.8305 | 12.5063 | 12.125 | 11.724 | 11.3172 | 10.8763 | 10.4247 | 9.9241 | 9.3519 | 8.7779 | 6.0431 | 1.1954 | -1.4064 | -3.8283 | 8.32 | 7.9309 | 7.4743 | 6.9934 | 6.4661 | 5.8998 | 5.3219 | 4.6871 | 3.981 | 3.237 | -0.20562 | -6.3121 | -9.1992 | -10.9079
|  | THE MALL | SP |  |  | 6.9457 | 6.5867 | 6.2061 | 5.8302 | 5.1861 | 4.5332 | 3.9093 | 3.1895 | 2.41 | 1.5407 | -1.5527 | -9.2776 | -13.3309 | -15.1566 | 12.8707 | 12.5695 | 12.2436 | 11.9182 | 11.5124 | 11.09 | 10.6834 | 10.1982 | 9.6614 | 9.0608 | 6.8128 | 0.77872 | -3.4134 | -7.4974 | 8.4077 | 8.0699 | 7.7104 | 7.3534 | 6.7614 | 6.1597 | 5.5827 | 4.9111 | 4.1809 | 3.3688 | 0.45085 | -6.9305 | -10.7425 | -12.3993
BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE | MINIMUM HEADROOM | SU 64755 71015 | YES | 3.7019 | 3.4228 | 3.1338 | 2.8136 | 2.3566 | 1.8561 | 1.3422 | 0.86382 | 0.38949 | -0.060432 | -1.473 | -3.9725 | -6.6619 | -8.4275 | 6.2841 | 6.1814 | 6.0822 | 5.965 | 5.7556 | 5.5006 | 5.2318 | 4.9776 | 4.7326 | 4.4276 | 3.4483 | 1.3836 | -0.78081 | -3.6523 | 4.5296 | 4.2777 | 4.0036 | 3.7008 | 3.2853 | 2.8303 | 2.3543 | 1.9011 | 1.444 | 1.0084 | -0.37086 | -2.552 | -4.7772 | -6.2445
|  | THEALE | CT |  |  | 3.7567 | 3.51 | 3.269 | 2.9735 | 2.6008 | 2.1867 | 1.7535 | 1.3605 | 1.0215 | 0.55155 | -0.88601 | -3.9725 | -6.6619 | -8.4275 | 6.2841 | 6.1814 | 6.0822 | 5.965 | 5.7556 | 5.5006 | 5.2318 | 4.9776 | 4.7326 | 4.4276 | 3.4483 | 1.3836 | -0.78081 | -3.3168 | 4.5702 | 4.3441 | 4.1224 | 3.8332 | 3.4848 | 3.0984 | 2.6923 | 2.3149 | 1.9765 | 1.5263 | 0.16068 | -2.5268 | -4.7772 | -6.2445
|  | THEALE | LW |  |  | 3.7019 | 3.4228 | 3.1338 | 2.8136 | 2.3566 | 1.8561 | 1.3422 | 0.86382 | 0.38949 | -0.060432 | -1.473 | -3.9062 | -5.6426 | -6.8771 | 6.2851 | 6.1857 | 6.0866 | 5.978 | 5.7683 | 5.5111 | 5.2429 | 4.9905 | 4.7343 | 4.4797 | 3.6411 | 2.3011 | 1.4585 | 0.82445 | 4.5296 | 4.2777 | 4.0036 | 3.7008 | 3.2853 | 2.8303 | 2.3543 | 1.9011 | 1.444 | 1.0084 | -0.37086 | -2.552 | -3.9749 | -4.9808
|  | THEALE | ST |  |  | 3.8884 | 3.7373 | 3.6018 | 3.457 | 3.2696 | 3.061 | 2.8501 | 2.6678 | 2.5149 | 2.3666 | 1.8268 | 0.07612 | -1.5154 | -2.7618 | 6.3281 | 6.254 | 6.186 | 6.1133 | 6.0219 | 5.9207 | 5.7725 | 5.6157 | 5.4699 | 5.3317 | 4.8097 | 3.1776 | 1.3235 | -0.98681 | 4.7249 | 4.5972 | 4.4797 | 4.3504 | 4.1668 | 3.9645 | 3.7571 | 3.5733 | 3.4126 | 3.2645 | 2.6926 | 1.0548 | -0.31377 | -1.3377
|  | THEALE | SP |  |  | 3.9007 | 3.7565 | 3.6292 | 3.4972 | 3.35 | 3.1836 | 3.0087 | 2.8632 | 2.7505 | 2.6358 | 2.2537 | 1.0237 | -0.25034 | -1.1445 | 6.3292 | 6.2557 | 6.1871 | 6.1148 | 6.0296 | 5.9339 | 5.7923 | 5.6346 | 5.4867 | 5.3326 | 4.7684 | 3.0634 | 0.42212 | -3.6523 | 4.7355 | 4.6112 | 4.4981 | 4.3791 | 4.2455 | 4.0947 | 3.9249 | 3.7808 | 3.6657 | 3.5481 | 3.1387 | 1.9697 | 0.85769 | 0.12027
BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON | MINIMUM HEADROOM | SU 29134 45674 | YES | 23.9098 | 23.5196 | 23.0918 | 22.6272 | 21.9269 | 21.169 | 20.3583 | 19.5153 | 18.578 | 17.6125 | 14.4267 | 10.35 | 7.7977 | 5.4959 | 26.6842 | 26.519 | 26.3494 | 26.1625 | 25.9038 | 25.5831 | 25.1675 | 24.7662 | 24.297 | 23.8043 | 22.0763 | 19.5243 | 17.1034 | 14.6702 | 25.1566 | 24.8495 | 24.4869 | 24.081 | 23.47 | 22.7987 | 22.0578 | 21.3057 | 20.4633 | 19.5922 | 16.7314 | 13.1387 | 11.0659 | 9.1651
|  | THRUXTON | CT |  |  | 23.9479 | 23.7888 | 23.494 | 23.1277 | 22.6051 | 22.0326 | 21.4543 | 20.8557 | 20.1859 | 19.2835 | 16.3048 | 11.4092 | 7.7977 | 5.4959 | 26.7196 | 26.5742 | 26.4207 | 26.2468 | 26.0269 | 25.7689 | 25.4473 | 25.1113 | 24.7295 | 24.2288 | 22.5029 | 19.5243 | 17.1034 | 14.6702 | 25.2337 | 25.0586 | 24.8379 | 24.5174 | 24.0631 | 23.556 | 23.0221 | 22.4886 | 21.8885 | 21.0788 | 18.4208 | 14.1226 | 11.0659 | 9.1651
|  | THRUXTON | LW |  |  | 23.9098 | 23.5196 | 23.0918 | 22.6272 | 21.9269 | 21.169 | 20.3583 | 19.5153 | 18.578 | 17.6125 | 14.4267 | 10.35 | 8.1207 | 6.5136 | 26.6842 | 26.519 | 26.3494 | 26.1625 | 25.9038 | 25.5831 | 25.1675 | 24.7662 | 24.297 | 23.8043 | 22.0763 | 19.8093 | 18.7122 | 17.8823 | 25.1566 | 24.8495 | 24.4869 | 24.081 | 23.47 | 22.7987 | 22.0578 | 21.3057 | 20.4633 | 19.5922 | 16.7314 | 13.1387 | 11.3026 | 10.0113
|  | THRUXTON | ST |  |  | 24.0275 | 23.9184 | 23.8111 | 23.6958 | 23.5573 | 23.3653 | 23.0728 | 22.7775 | 22.4201 | 22.0137 | 20.4855 | 17.1489 | 14.6723 | 13.0263 | 26.8061 | 26.7191 | 26.6346 | 26.5421 | 26.4278 | 26.282 | 26.0797 | 25.9069 | 25.6948 | 25.4563 | 24.4259 | 21.8648 | 19.6296 | 17.4412 | 25.3498 | 25.2515 | 25.1553 | 25.0511 | 24.921 | 24.7601 | 24.4982 | 24.2389 | 23.9225 | 23.5619 | 22.1757 | 18.9849 | 16.8195 | 15.4843
|  | THRUXTON | SP |  |  | 24.0314 | 23.9271 | 23.825 | 23.7177 | 23.5973 | 23.45 | 23.261 | 23.0325 | 22.7597 | 22.428 | 21.2686 | 18.663 | 16.0692 | 14.5035 | 26.8124 | 26.7297 | 26.6485 | 26.5616 | 26.4617 | 26.3317 | 26.1472 | 25.9961 | 25.8212 | 25.6181 | 24.733 | 22.388 | 19.3835 | 15.9868 | 25.3568 | 25.2639 | 25.1738 | 25.0787 | 24.9717 | 24.8348 | 24.6501 | 24.4762 | 24.2385 | 23.9486 | 22.9025 | 20.4238 | 18.0706 | 16.7698
MELKSHAM GSP | WEST GRAFTON | TIDWORTH | MINIMUM HEADROOM | SU 24088 49593 | YES | 15.5505 | 15.315 | 15.0692 | 14.7691 | 14.4717 | 14.1663 | 13.87 | 13.5374 | 13.1601 | 12.6943 | 11.242 | 9.4283 | 9.0218 | 8.7885 | 17.1583 | 17.0172 | 16.8814 | 16.7051 | 16.5156 | 16.3338 | 16.1801 | 16.011 | 15.8183 | 15.6017 | 14.7666 | 13.4593 | 13.2274 | 12.9805 | 15.7753 | 15.5926 | 15.4017 | 15.1696 | 14.9482 | 14.7166 | 14.4831 | 14.2178 | 13.91 | 13.5248 | 12.096 | 10.2731 | 9.9015 | 9.6882
|  | TIDWORTH | CT |  |  | 15.5875 | 15.3892 | 15.1763 | 14.9128 | 14.6694 | 14.4311 | 14.2215 | 13.9873 | 13.7423 | 13.3958 | 12.3246 | 10.4436 | 9.5112 | 9.1537 | 17.1763 | 17.0477 | 16.924 | 16.7745 | 16.6486 | 16.5092 | 16.3975 | 16.2725 | 16.1356 | 15.945 | 15.3866 | 14.1833 | 13.5965 | 12.9805 | 15.7808 | 15.6182 | 15.4439 | 15.2311 | 15.04 | 14.8505 | 14.6769 | 14.482 | 14.276 | 13.9942 | 13.1182 | 11.2659 | 10.3861 | 10.059
|  | TIDWORTH | LW |  |  | 15.5505 | 15.315 | 15.0692 | 14.7691 | 14.4717 | 14.1663 | 13.87 | 13.5374 | 13.1601 | 12.6943 | 11.242 | 9.4283 | 9.0218 | 8.7885 | 17.1583 | 17.0172 | 16.8814 | 16.7051 | 16.5156 | 16.3338 | 16.1801 | 16.011 | 15.8183 | 15.6017 | 14.7666 | 13.4593 | 13.2274 | 13.0921 | 15.7753 | 15.5926 | 15.4017 | 15.1696 | 14.9482 | 14.7166 | 14.4831 | 14.2178 | 13.91 | 13.5248 | 12.096 | 10.2731 | 9.9015 | 9.6882
|  | TIDWORTH | ST |  |  | 15.6803 | 15.5401 | 15.4065 | 15.2503 | 15.1096 | 14.9742 | 14.8573 | 14.7202 | 14.5587 | 14.3457 | 13.5638 | 11.5506 | 10.5441 | 10.2144 | 17.2139 | 17.1082 | 17.0171 | 16.9149 | 16.831 | 16.7553 | 16.6966 | 16.6292 | 16.5515 | 16.4627 | 16.109 | 14.9262 | 14.1405 | 13.9066 | 15.863 | 15.75 | 15.6395 | 15.508 | 15.3913 | 15.2785 | 15.1806 | 15.0643 | 14.9255 | 14.7416 | 14.0515 | 12.2731 | 11.4109 | 11.1508
|  | TIDWORTH | SP |  |  | 15.6834 | 15.5518 | 15.4268 | 15.2822 | 15.1417 | 15.0092 | 14.8981 | 14.7756 | 14.6424 | 14.4803 | 13.9564 | 12.3972 | 10.9468 | 10.4987 | 17.2164 | 17.1136 | 17.0264 | 16.9302 | 16.8446 | 16.7672 | 16.7054 | 16.629 | 16.5335 | 16.4286 | 16.0872 | 15.2111 | 14.3181 | 13.0694 | 15.8635 | 15.7563 | 15.6515 | 15.5279 | 15.4229 | 15.3243 | 15.245 | 15.1549 | 15.0545 | 14.9304 | 14.5207 | 13.2145 | 11.8886 | 11.4088
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY | MINIMUM HEADROOM | ST 93438 29127 | YES | 0.8034 | 0.55697 | 0.30704 | 0.050886 | -0.29277 | -0.66368 | -1.0532 | -1.4769 | -2.0035 | -2.4516 | -3.4482 | -4.5968 | -4.8301 | -4.9223 | 0.6455 | 0.50423 | 0.36347 | 0.21788 | 0.036876 | -0.15188 | -0.35711 | -0.58912 | -0.89964 | -1.1534 | -1.5953 | -2.0974 | -2.197 | -2.2514 | -0.50373 | -0.75181 | -1.0014 | -1.2562 | -1.5902 | -1.9347 | -2.2955 | -2.6864 | -3.1683 | -3.5819 | -4.4973 | -5.5439 | -5.7564 | -5.8394
|  | TISBURY | CT |  |  | 1.0053 | 0.86731 | 0.72704 | 0.56845 | 0.36337 | 0.15066 | -0.07846 | -0.34602 | -0.65729 | -1.049 | -1.8093 | -3.1159 | -3.927 | -4.1222 | 0.72106 | 0.62191 | 0.52374 | 0.41082 | 0.28344 | 0.15041 | 0.0059496 | -0.16837 | -0.37843 | -0.63435 | -1.0348 | -1.6648 | -2.0481 | -2.2514 | -0.28555 | -0.41846 | -0.55198 | -0.7006 | -0.90055 | -1.1074 | -1.3299 | -1.5853 | -1.8783 | -2.2483 | -2.9724 | -4.2123 | -4.934 | -5.1061
|  | TISBURY | LW |  |  | 0.8034 | 0.55697 | 0.30704 | 0.050886 | -0.29277 | -0.66368 | -1.0532 | -1.4769 | -2.0035 | -2.4516 | -3.4482 | -4.5968 | -4.8301 | -4.9223 | 0.6455 | 0.50423 | 0.36347 | 0.21788 | 0.036876 | -0.15188 | -0.35711 | -0.58912 | -0.89964 | -1.1534 | -1.5953 | -2.0974 | -2.197 | -2.2383 | -0.50373 | -0.75181 | -1.0014 | -1.2562 | -1.5902 | -1.9347 | -2.2955 | -2.6864 | -3.1683 | -3.5819 | -4.4973 | -5.5439 | -5.7564 | -5.8394
|  | TISBURY | ST |  |  | 1.0935 | 1.0144 | 0.936 | 0.84681 | 0.72443 | 0.59363 | 0.46171 | 0.31642 | 0.15019 | -0.022752 | -0.77991 | -1.782 | -2.318 | -2.6272 | 0.7806 | 0.72132 | 0.66514 | 0.60017 | 0.52331 | 0.43985 | 0.35405 | 0.25763 | 0.14362 | 0.032393 | -0.48696 | -1.142 | -1.5326 | -1.7301 | -0.2033 | -0.28145 | -0.35739 | -0.44209 | -0.56226 | -0.68991 | -0.81849 | -0.95903 | -1.1188 | -1.289 | -2.0046 | -2.9687 | -3.6653 | -3.8754
|  | TISBURY | SP |  |  | 1.1239 | 1.0582 | 0.99813 | 0.9421 | 0.81639 | 0.68957 | 0.56128 | 0.41897 | 0.26805 | 0.070752 | -0.64232 | -2.3789 | -3.3382 | -3.9676 | 0.79265 | 0.73802 | 0.68976 | 0.64409 | 0.57055 | 0.49608 | 0.42005 | 0.33131 | 0.2365 | 0.12307 | -0.30259 | -1.3628 | -1.872 | -2.196 | -0.17097 | -0.23427 | -0.29119 | -0.34446 | -0.4707 | -0.59811 | -0.7273 | -0.8679 | -1.018 | -1.2168 | -1.9067 | -3.5125 | -4.4284 | -4.986
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD | MINIMUM HEADROOM | SU 54104 05695 | YES | 7.5828 | 6.9958 | 6.3677 | 5.7077 | 4.9254 | 4.1479 | 3.3309 | 2.4651 | 1.4865 | 0.46669 | -2.321 | -5.3532 | -6.2203 | -6.8457 | 2.4897 | 2.196 | 1.8694 | 1.5228 | 1.1426 | 0.7571 | 0.33833 | -0.1125 | -0.6535 | -1.2312 | -2.7294 | -4.2142 | -5.3366 | -6.4835 | 0.41517 | -0.089496 | -0.64042 | -1.2224 | -1.9257 | -2.6308 | -3.375 | -4.1653 | -5.068 | -6.0136 | -8.577 | -11.3208 | -12.0835 | -12.5962
|  | TITCHFIELD | CT |  |  | 7.9549 | 7.5678 | 7.1724 | 6.6665 | 6.1435 | 5.634 | 5.1133 | 4.5542 | 3.935 | 3 | 0.38032 | -3.4179 | -5.9355 | -6.8457 | 2.6192 | 2.3961 | 2.1663 | 1.8612 | 1.5666 | 1.2746 | 0.96577 | 0.63117 | 0.2518 | -0.2946 | -1.8159 | -3.8833 | -5.3366 | -6.4835 | 0.74949 | 0.42574 | 0.089463 | -0.3445 | -0.81689 | -1.2802 | -1.7512 | -2.2563 | -2.8136 | -3.6618 | -6.051 | -9.5862 | -11.8011 | -12.5962
|  | TITCHFIELD | LW |  |  | 7.5828 | 6.9958 | 6.3677 | 5.7077 | 4.9254 | 4.1479 | 3.3309 | 2.4651 | 1.4865 | 0.46669 | -2.321 | -5.3532 | -6.2203 | -6.5526 | 2.4897 | 2.196 | 1.8694 | 1.5228 | 1.1426 | 0.7571 | 0.33833 | -0.1125 | -0.6535 | -1.2312 | -2.7294 | -4.2142 | -4.5673 | -4.6981 | 0.41517 | -0.089496 | -0.64042 | -1.2224 | -1.9257 | -2.6308 | -3.375 | -4.1653 | -5.068 | -6.0136 | -8.577 | -11.3208 | -12.0835 | -12.3719
|  | TITCHFIELD | ST |  |  | 8.1724 | 7.9377 | 7.7131 | 7.4689 | 7.2238 | 6.9889 | 6.7324 | 6.4522 | 6.1405 | 5.8023 | 4.483 | 1.6834 | 0.39146 | -0.4428 | 2.7453 | 2.6056 | 2.4693 | 2.3179 | 2.1666 | 2.0185 | 1.8525 | 1.6686 | 1.4614 | 1.245 | 0.36156 | -1.5915 | -2.6808 | -3.8215 | 0.94685 | 0.76255 | 0.58263 | 0.38468 | 0.16844 | -0.042429 | -0.27166 | -0.52157 | -0.79998 | -1.1066 | -2.2942 | -4.8256 | -6.0341 | -6.82
|  | TITCHFIELD | SP |  |  | 8.2228 | 8.0033 | 7.8033 | 7.5901 | 7.3323 | 7.0817 | 6.8288 | 6.5523 | 6.2544 | 5.8786 | 4.6035 | 1.4619 | -0.48561 | -1.3874 | 2.7655 | 2.6272 | 2.497 | 2.3552 | 2.2051 | 2.0567 | 1.9015 | 1.7269 | 1.5341 | 1.2967 | 0.44591 | -1.8113 | -3.7864 | -5.9194 | 0.99388 | 0.82496 | 0.6686 | 0.49983 | 0.26899 | 0.040617 | -0.18883 | -0.43868 | -0.7077 | -1.0513 | -2.2131 | -5.0576 | -6.8452 | -7.6858
BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM | MINIMUM HEADROOM | SU 88310 49487 | YES | 2.9692 | 2.6215 | 2.2259 | 1.7999 | 1.2287 | 0.64053 | 0.042488 | -0.58146 | -1.3 | -2.0437 | -3.3408 | -3.7686 | -5.1393 | -6.3967 | 4.8746 | 4.7262 | 4.5453 | 4.3627 | 4.1256 | 3.8768 | 3.6145 | 3.3382 | 2.9996 | 2.6438 | 2.0885 | 1.8734 | 1.3064 | 0.81316 | 2.8227 | 2.4801 | 2.0981 | 1.7144 | 1.2018 | 0.67298 | 0.133 | -0.42505 | -1.0689 | -1.7376 | -2.8681 | -3.2531 | -4.3771 | -5.4808
|  | TONGHAM | CT |  |  | 3.3723 | 3.2265 | 3.0635 | 2.8608 | 2.5623 | 2.2482 | 1.9188 | 1.5588 | 1.1492 | 0.55461 | -0.50423 | -0.88916 | -1.0708 | -1.1317 | 5.0157 | 4.9395 | 4.8497 | 4.7271 | 4.5734 | 4.4083 | 4.2339 | 4.0456 | 3.8252 | 3.508 | 2.951 | 2.7122 | 2.5808 | 2.4565 | 3.2213 | 3.078 | 2.918 | 2.7199 | 2.4267 | 2.1186 | 1.7953 | 1.4538 | 1.0756 | 0.52625 | -0.44827 | -0.80156 | -0.96212 | -1.0149
|  | TONGHAM | LW |  |  | 2.9692 | 2.6215 | 2.2259 | 1.7999 | 1.2287 | 0.64053 | 0.042488 | -0.58146 | -1.3 | -2.0437 | -3.3408 | -3.7686 | -3.822 | -3.8326 | 4.8746 | 4.7262 | 4.5453 | 4.3627 | 4.1256 | 3.8768 | 3.6145 | 3.3382 | 2.9996 | 2.6438 | 2.0885 | 1.8734 | 1.8509 | 1.846 | 2.8227 | 2.4801 | 2.0981 | 1.7144 | 1.2018 | 0.67298 | 0.133 | -0.42505 | -1.0689 | -1.7376 | -2.8681 | -3.2531 | -3.2987 | -3.3074
|  | TONGHAM | ST |  |  | 3.4305 | 3.322 | 3.2071 | 3.0886 | 2.8866 | 2.6776 | 2.4681 | 2.2477 | 2.0146 | 1.7416 | 0.72758 | -0.9307 | -1.8213 | -2.0476 | 5.0593 | 5.008 | 4.9513 | 4.8909 | 4.7891 | 4.6822 | 4.5724 | 4.4549 | 4.3272 | 4.1955 | 3.649 | 2.77 | 2.3849 | 2.207 | 3.2779 | 3.171 | 3.058 | 2.9415 | 2.7431 | 2.5379 | 2.3322 | 2.1159 | 1.8873 | 1.6376 | 0.70137 | -0.82109 | -1.6082 | -1.8059
|  | TONGHAM | SP |  |  | 3.4757 | 3.3872 | 3.2967 | 3.2035 | 2.9091 | 2.5978 | 2.2904 | 1.95 | 1.5924 | 1.1607 | -0.26116 | -3.2982 | -5.1393 | -6.3967 | 5.0742 | 5.0264 | 4.9762 | 4.9228 | 4.7984 | 4.66 | 4.5251 | 4.3823 | 4.2333 | 4.06 | 3.4472 | 2.0434 | 1.3064 | 0.81316 | 3.3226 | 3.2357 | 3.1469 | 3.0556 | 2.7652 | 2.4586 | 2.1557 | 1.8468 | 1.527 | 1.1422 | -0.12906 | -2.8099 | -4.3771 | -5.4808
MINETY GSP | TOOTHILL BSP | TOOTHILL | MINIMUM HEADROOM | SU 13215 83986 | NO | 4.1622 | 3.4065 | 2.5548 | 1.63 | 0.454 | -0.78355 | -2.0838 | -3.522 | -5.1993 | -6.8883 | -11.4071 | -15.4054 | -17.2321 | -18.4177 | 2.4818 | 2.0558 | 1.575 | 1.0564 | 0.43196 | -0.22612 | -0.93568 | -1.7542 | -2.7733 | -3.7893 | -6.2197 | -8.4947 | -10.0222 | -11.2997 | 0.29993 | -0.34939 | -1.092 | -1.9011 | -2.928 | -4.0108 | -5.1642 | -6.4478 | -7.9884 | -9.5281 | -13.4373 | -16.9202 | -18.3556 | -19.332
|  | TOOTHILL | CT |  |  | 4.3412 | 3.6971 | 2.968 | 2.1304 | 1.1911 | 0.18947 | -0.83256 | -1.9919 | -3.3426 | -5.0889 | -9.7578 | -14.6177 | -17.2321 | -18.4177 | 2.5184 | 2.1175 | 1.6684 | 1.1517 | 0.60707 | 0.025589 | -0.59812 | -1.3111 | -2.1419 | -3.1989 | -5.8263 | -8.4947 | -10.0222 | -11.2997 | 0.435 | -0.1227 | -0.76078 | -1.5059 | -2.3303 | -3.2122 | -4.1205 | -5.1528 | -6.3454 | -7.908 | -11.9665 | -16.1829 | -18.3556 | -19.332
|  | TOOTHILL | LW |  |  | 4.1622 | 3.4065 | 2.5548 | 1.63 | 0.454 | -0.78355 | -2.0838 | -3.522 | -5.1993 | -6.8883 | -11.4071 | -15.4054 | -16.5293 | -17.0686 | 2.4818 | 2.0558 | 1.575 | 1.0564 | 0.43196 | -0.22612 | -0.93568 | -1.7542 | -2.7733 | -3.7893 | -6.2197 | -8.3173 | -8.8144 | -9.0481 | 0.29993 | -0.34939 | -1.092 | -1.9011 | -2.928 | -4.0108 | -5.1642 | -6.4478 | -7.9884 | -9.5281 | -13.4373 | -16.9202 | -17.8653 | -18.3124
|  | TOOTHILL | ST |  |  | 4.6571 | 4.2696 | 3.8455 | 3.3914 | 2.862 | 2.2957 | 1.7101 | 1.0619 | 0.30964 | -0.47531 | -3.614 | -7.2137 | -8.617 | -9.5293 | 2.7321 | 2.486 | 2.2122 | 1.9149 | 1.5672 | 1.1945 | 0.80483 | 0.3739 | -0.1189 | -0.61863 | -2.7318 | -5.3516 | -6.5618 | -7.7677 | 0.7634 | 0.45841 | 0.1141 | -0.26221 | -0.72127 | -1.2154 | -1.7313 | -2.3031 | -2.9584 | -3.625 | -6.3564 | -9.6225 | -10.8834 | -11.6845
|  | TOOTHILL | SP |  |  | 4.6936 | 4.3259 | 3.9487 | 3.5564 | 3.1101 | 2.647 | 2.1411 | 1.5827 | 0.97928 | 0.29948 | -2.195 | -6.0528 | -7.5946 | -8.2742 | 2.7456 | 2.5034 | 2.2507 | 1.9847 | 1.6969 | 1.3947 | 1.0531 | 0.66985 | 0.25117 | -0.19884 | -1.8957 | -4.9578 | -6.658 | -8.3358 | 0.79561 | 0.50572 | 0.20583 | -0.10961 | -0.47725 | -0.86007 | -1.2943 | -1.7787 | -2.3043 | -2.8883 | -5.0015 | -8.5598 | -10 | -10.6134
NURSLING GSP | ROWNHAMS | TOTTON | MINIMUM HEADROOM | SU 35835 13428 | YES | 15.3977 | 14.8004 | 14.0622 | 13.293 | 12.1688 | 10.9942 | 9.7306 | 8.4328 | 6.8031 | 5.1097 | 1.0691 | -4.5957 | -9.2809 | -12.4723 | 20.2276 | 19.8787 | 19.4072 | 18.9189 | 18.2759 | 17.5912 | 16.8305 | 16.033 | 14.9742 | 13.8725 | 11.4365 | 8.1043 | 5.0639 | 2.5974 | 16.0359 | 15.5068 | 14.8312 | 14.1257 | 13.103 | 12.0273 | 10.86 | 9.6502 | 8.1098 | 6.5065 | 2.7485 | -2.3821 | -6.3655 | -8.9882
|  | TOTTON | CT |  |  | 15.5757 | 15.0995 | 14.5512 | 13.8588 | 13.0099 | 12.1286 | 11.198 | 10.2339 | 9.1219 | 7.4445 | 3.2282 | -3.9116 | -9.2809 | -12.4723 | 20.2699 | 19.9501 | 19.5662 | 19.072 | 18.5258 | 17.9499 | 17.3312 | 16.6722 | 15.8859 | 14.782 | 12.1352 | 8.1043 | 5.0639 | 2.5974 | 16.1882 | 15.7666 | 15.2671 | 14.6248 | 13.8473 | 13.0344 | 12.1705 | 11.2644 | 10.2077 | 8.6245 | 4.7033 | -1.7024 | -6.3655 | -8.9882
|  | TOTTON | LW |  |  | 15.3977 | 14.8004 | 14.0622 | 13.293 | 12.1688 | 10.9942 | 9.7306 | 8.4328 | 6.8031 | 5.1097 | 1.0691 | -4.5957 | -7.5153 | -9.4904 | 20.2276 | 19.8787 | 19.4072 | 18.9189 | 18.2759 | 17.5912 | 16.8305 | 16.033 | 14.9742 | 13.8725 | 11.4365 | 8.2632 | 6.8236 | 5.8326 | 16.0359 | 15.5068 | 14.8312 | 14.1257 | 13.103 | 12.0273 | 10.86 | 9.6502 | 8.1098 | 6.5065 | 2.7485 | -2.3821 | -4.8877 | -6.5489
|  | TOTTON | ST |  |  | 15.8883 | 15.6282 | 15.3239 | 15.0236 | 14.6036 | 14.1699 | 13.7097 | 13.2445 | 12.7142 | 12.1597 | 9.6868 | 4.3504 | 1.043 | -1.2856 | 20.475 | 20.304 | 20.0876 | 19.8749 | 19.5729 | 19.2565 | 18.9147 | 18.5588 | 18.1451 | 17.7276 | 15.814 | 11.8596 | 9.4031 | 7.2078 | 16.4904 | 16.2755 | 16.0089 | 15.7458 | 15.3671 | 14.9718 | 14.5478 | 14.1109 | 13.6067 | 13.0817 | 10.7113 | 5.729 | 2.821 | 0.84332
|  | TOTTON | SP |  |  | 15.9287 | 15.6665 | 15.3829 | 15.1085 | 14.7432 | 14.3727 | 13.994 | 13.5999 | 13.1834 | 12.7099 | 10.9192 | 5.8243 | 2.5265 | 0.71975 | 20.4932 | 20.3138 | 20.1017 | 19.8931 | 19.6484 | 19.3937 | 19.1277 | 18.8385 | 18.5253 | 18.1615 | 16.7327 | 12.5666 | 9.2405 | 5.9851 | 16.5277 | 16.3086 | 16.0601 | 15.8204 | 15.4996 | 15.1701 | 14.8301 | 14.4666 | 14.0782 | 13.6354 | 11.9451 | 7.1398 | 4.1505 | 2.6059
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK | MINIMUM HEADROOM | SU 45156 14783 | YES | 45.9664 | 45.5197 | 44.9875 | 44.3933 | 43.557 | 42.6544 | 41.6785 | 40.6226 | 39.3503 | 38.1238 | 34.7051 | 30.4221 | 27.7779 | 25.7631 | 50.0624 | 49.7976 | 49.473 | 49.1075 | 48.6348 | 48.1192 | 47.545 | 46.9203 | 46.1315 | 45.3424 | 43.1472 | 40.603 | 38.7656 | 37.1886 | 46.7044 | 46.3141 | 45.8414 | 45.3098 | 44.5619 | 43.7528 | 42.8702 | 41.914 | 40.7484 | 39.6043 | 36.4067 | 32.5029 | 30.3098 | 28.6626
|  | TOWNHILL PARK | CT |  |  | 46.0698 | 45.7048 | 45.2821 | 44.7365 | 44.0715 | 43.3478 | 42.5994 | 41.7807 | 40.8221 | 39.6538 | 36.3477 | 31.1641 | 27.7779 | 25.7631 | 50.0805 | 49.8419 | 49.5649 | 49.1965 | 48.7827 | 48.3304 | 47.8526 | 47.3291 | 46.7027 | 45.951 | 43.8026 | 40.7138 | 38.7656 | 37.1886 | 46.7924 | 46.4754 | 46.1039 | 45.6127 | 45.0172 | 44.3678 | 43.6919 | 42.9519 | 42.0784 | 40.9944 | 37.9139 | 33.2285 | 30.3098 | 28.6626
|  | TOWNHILL PARK | LW |  |  | 45.9664 | 45.5197 | 44.9875 | 44.3933 | 43.557 | 42.6544 | 41.6785 | 40.6226 | 39.3503 | 38.1238 | 34.7051 | 30.4221 | 28.4972 | 27.2592 | 50.0624 | 49.7976 | 49.473 | 49.1075 | 48.6348 | 48.1192 | 47.545 | 46.9203 | 46.1315 | 45.3424 | 43.1472 | 40.603 | 39.6576 | 39.0224 | 46.7044 | 46.3141 | 45.8414 | 45.3098 | 44.5619 | 43.7528 | 42.8702 | 41.914 | 40.7484 | 39.6043 | 36.4067 | 32.5029 | 30.8671 | 29.8399
|  | TOWNHILL PARK | ST |  |  | 46.3124 | 46.1131 | 45.8914 | 45.6422 | 45.3102 | 44.9417 | 44.548 | 44.1077 | 43.5729 | 43.0944 | 41.2913 | 36.7777 | 34.1809 | 32.6864 | 50.2467 | 50.1144 | 49.9645 | 49.7926 | 49.5634 | 49.308 | 49.0308 | 48.7196 | 48.3359 | 47.9891 | 46.6166 | 43.2396 | 41.2971 | 39.8898 | 47.025 | 46.8649 | 46.6832 | 46.4748 | 46.1872 | 45.8662 | 45.5193 | 45.1299 | 44.6506 | 44.2115 | 42.5073 | 38.2724 | 35.9637 | 34.7104
|  | TOWNHILL PARK | SP |  |  | 46.3481 | 46.1523 | 45.9432 | 45.7203 | 45.4507 | 45.1685 | 44.8561 | 44.5076 | 44.108 | 43.7456 | 42.5361 | 39.0891 | 36.3064 | 35.054 | 50.2657 | 50.1298 | 49.9815 | 49.8207 | 49.6386 | 49.4461 | 49.2281 | 48.979 | 48.6894 | 48.4129 | 47.4362 | 44.5943 | 41.9528 | 39.8453 | 47.0582 | 46.9003 | 46.7295 | 46.5453 | 46.3187 | 46.0819 | 45.8141 | 45.5126 | 45.1635 | 44.8359 | 43.7087 | 40.4714 | 37.9187 | 36.8508
MINETY GSP | SWINDON BSP | TRADING ESTATE | MINIMUM HEADROOM | SU 13490 85868 | NO | 9.5813 | 9.4904 | 9.2569 | 8.9398 | 8.4469 | 7.838 | 7.0741 | 6.2603 | 5.1281 | 3.7542 | -0.43812 | -5.1596 | -8.3803 | -10.1001 | 9.009 | 8.8451 | 8.5571 | 8.2262 | 7.8181 | 7.3576 | 6.8315 | 6.2616 | 5.5528 | 4.6998 | 2.2579 | -0.51908 | -2.4764 | -4.0503 | 5.5648 | 5.3191 | 4.942 | 4.518 | 3.8828 | 3.1788 | 2.3959 | 1.557 | 0.55695 | -0.6304 | -4.4511 | -8.5779 | -11.3556 | -12.8886
|  | TRADING ESTATE | CT |  |  | 9.5813 | 9.4937 | 9.3318 | 9.1122 | 8.9264 | 8.5967 | 8.1865 | 7.5074 | 6.7087 | 5.3484 | 0.95957 | -4.9498 | -8.3803 | -10.1001 | 9.0446 | 8.9074 | 8.6961 | 8.3661 | 8.0359 | 7.6616 | 7.2381 | 6.7786 | 6.25 | 5.396 | 2.7268 | -0.51908 | -2.4764 | -4.0503 | 5.6919 | 5.5281 | 5.2857 | 4.9189 | 4.4869 | 3.9975 | 3.4412 | 2.8411 | 2.1651 | 0.97416 | -3.1596 | -8.3159 | -11.3556 | -12.8886
|  | TRADING ESTATE | LW |  |  | 9.588 | 9.4904 | 9.2569 | 8.9398 | 8.4469 | 7.838 | 7.0741 | 6.2603 | 5.1281 | 3.7542 | -0.43812 | -5.1596 | -6.7926 | -7.5746 | 9.009 | 8.8451 | 8.5571 | 8.2262 | 7.8181 | 7.3576 | 6.8315 | 6.2616 | 5.5528 | 4.6998 | 2.2579 | -0.24724 | -1.0116 | -1.4042 | 5.5648 | 5.3191 | 4.942 | 4.518 | 3.8828 | 3.1788 | 2.3959 | 1.557 | 0.55695 | -0.6304 | -4.4511 | -8.5779 | -9.9493 | -10.6008
|  | TRADING ESTATE | ST |  |  | 9.653 | 9.6125 | 9.5058 | 9.3778 | 9.2679 | 9.1303 | 8.97 | 8.7975 | 8.5932 | 8.3374 | 5.9641 | 1.4377 | -0.41628 | -1.7143 | 9.152 | 9.0877 | 8.9546 | 8.7964 | 8.6242 | 8.4214 | 8.1851 | 7.9273 | 7.6333 | 7.3006 | 5.5814 | 2.4128 | 0.87428 | -0.60056 | 5.8329 | 5.7635 | 5.6234 | 5.4576 | 5.2672 | 5.0423 | 4.7812 | 4.4969 | 4.1747 | 3.7849 | 1.7487 | -2.4754 | -4.2168 | -5.4076
|  | TRADING ESTATE | SP |  |  | 9.6582 | 9.6162 | 9.5105 | 9.386 | 9.2999 | 9.1907 | 9.067 | 8.936 | 8.7894 | 8.596 | 7.062 | 3.1064 | 1.2161 | 0.45043 | 9.1637 | 9.0874 | 8.9478 | 8.7844 | 8.6511 | 8.4912 | 8.3074 | 8.1084 | 7.8848 | 7.5912 | 6.2134 | 3.1523 | 0.91728 | -1.395 | 5.8578 | 5.7832 | 5.6451 | 5.4838 | 5.3322 | 5.1533 | 4.9422 | 4.7264 | 4.4848 | 4.1722 | 2.7258 | -0.86024 | -2.6764 | -3.3877
BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN | MINIMUM HEADROOM | SU 66254 68745 | YES | 9.9706 | 9.2582 | 8.4632 | 7.6114 | 6.4167 | 5.1711 | 3.8222 | 2.3431 | 0.40753 | -1.701 | -7.3126 | -14.1854 | -20.0381 | -23.887 | 15.5248 | 15.0679 | 14.5583 | 14.0124 | 13.3258 | 12.6027 | 11.7992 | 10.927 | 9.8236 | 8.5985 | 5.3695 | 1.3344 | -2.4967 | -6.5522 | 10.2669 | 9.6028 | 8.8508 | 8.0423 | 6.9289 | 5.7626 | 4.4896 | 3.1171 | 1.416 | -0.46282 | -5.2953 | -10.8131 | -14.9841 | -18.1831
|  | TRASH GREEN | CT |  |  | 10.1411 | 9.5551 | 9.0056 | 8.218 | 7.317 | 6.3971 | 5.4132 | 4.3457 | 3.1069 | 1.1849 | -4.6296 | -13.4906 | -20.0381 | -23.887 | 15.5676 | 15.151 | 14.7678 | 14.2129 | 13.6319 | 13.0352 | 12.3895 | 11.6837 | 10.8484 | 9.5607 | 5.9017 | 1.3344 | -2.4967 | -6.5522 | 10.4121 | 9.8609 | 9.3407 | 8.5832 | 7.7311 | 6.8577 | 5.9192 | 4.8989 | 3.708 | 1.8779 | -3.2323 | -10.0754 | -14.9841 | -18.1831
|  | TRASH GREEN | LW |  |  | 9.9706 | 9.2582 | 8.4632 | 7.6114 | 6.4167 | 5.1711 | 3.8222 | 2.3431 | 0.40753 | -1.701 | -7.3126 | -14.1854 | -17.8766 | -20.165 | 15.5248 | 15.0679 | 14.5583 | 14.0124 | 13.3258 | 12.6027 | 11.7992 | 10.927 | 9.8236 | 8.5985 | 5.3695 | 1.9996 | 0.47664 | -0.54404 | 10.2669 | 9.6028 | 8.8508 | 8.0423 | 6.9289 | 5.7626 | 4.4896 | 3.1171 | 1.416 | -0.46282 | -5.2953 | -10.8131 | -13.6004 | -15.3534
|  | TRASH GREEN | ST |  |  | 10.5101 | 10.1819 | 9.8948 | 9.5839 | 9.1696 | 8.7356 | 8.277 | 7.7653 | 7.1625 | 6.5609 | 3.855 | -2.9204 | -6.8847 | -9.7874 | 15.8041 | 15.5487 | 15.3289 | 15.0923 | 14.7913 | 14.4742 | 14.1342 | 13.7534 | 13.3014 | 12.8707 | 10.7899 | 5.4229 | 2.3252 | -0.8979 | 10.768 | 10.464 | 10.1951 | 9.9017 | 9.5072 | 9.0908 | 8.6473 | 8.1513 | 7.5646 | 6.9863 | 4.3647 | -2.0942 | -5.2726 | -7.4857
|  | TRASH GREEN | SP |  |  | 10.5582 | 10.2038 | 9.9135 | 9.6161 | 9.3074 | 9.0119 | 8.7116 | 8.352 | 7.9327 | 7.4584 | 5.5742 | -0.15694 | -4.053 | -6.0259 | 15.8256 | 15.5425 | 15.3101 | 15.071 | 14.842 | 14.6164 | 14.3803 | 14.0987 | 13.7651 | 13.3788 | 11.75 | 6.3928 | 1.3411 | -4.6176 | 10.8123 | 10.4802 | 10.2064 | 9.9241 | 9.6333 | 9.3521 | 9.0632 | 8.7159 | 8.3085 | 7.8523 | 6.0324 | 0.51083 | -3.1444 | -4.7848
MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN | MINIMUM HEADROOM | ST 84668 58036 | NO | 13.2588 | 13.1069 | 12.9385 | 12.7409 | 12.474 | 12.1739 | 11.8295 | 11.4476 | 10.9273 | 10.3604 | 7.8638 | 3.8866 | 2.8619 | 1.877 | 16.2639 | 16.1674 | 16.0584 | 15.9213 | 15.766 | 15.5784 | 15.351 | 15.0927 | 14.7164 | 14.3025 | 12.7663 | 10.1306 | 9.2668 | 8.5082 | 14.1425 | 13.9816 | 13.8026 | 13.5971 | 13.2928 | 12.9582 | 12.5848 | 12.152 | 11.4029 | 10.5518 | 7.4153 | 3.5935 | 2.6143 | 1.6724
|  | TROWBRIDGE TOWN | CT |  |  | 13.2697 | 13.1392 | 12.9921 | 12.8084 | 12.6057 | 12.3741 | 12.1119 | 11.821 | 11.4188 | 10.9702 | 9.2058 | 4.8649 | 3.2114 | 2.2554 | 16.2639 | 16.1674 | 16.0584 | 15.9213 | 15.7703 | 15.5976 | 15.4018 | 15.1844 | 14.8844 | 14.5533 | 13.3209 | 10.8833 | 9.6753 | 8.976 | 14.1974 | 14.0784 | 13.9441 | 13.7757 | 13.5525 | 13.2753 | 12.8821 | 12.4462 | 11.8508 | 11.1788 | 8.7062 | 4.5388 | 2.9728 | 2.0817
|  | TROWBRIDGE TOWN | LW |  |  | 13.2588 | 13.1069 | 12.9385 | 12.7409 | 12.474 | 12.1739 | 11.8295 | 11.4476 | 10.9273 | 10.3604 | 7.8638 | 3.8866 | 2.8619 | 2.1986 | 16.2806 | 16.1788 | 16.0646 | 15.9257 | 15.766 | 15.5784 | 15.351 | 15.0927 | 14.7164 | 14.3025 | 12.7663 | 10.1306 | 9.3823 | 8.9006 | 14.1425 | 13.9816 | 13.8026 | 13.5971 | 13.2928 | 12.9582 | 12.5848 | 12.152 | 11.4029 | 10.5518 | 7.4153 | 3.5935 | 2.6278 | 2.0086
|  | TROWBRIDGE TOWN | ST |  |  | 13.3729 | 13.3085 | 13.2404 | 13.1608 | 13.0534 | 12.9247 | 12.7722 | 12.5928 | 12.3227 | 12.0051 | 10.6511 | 5.8737 | 2.8726 | 1.877 | 16.3408 | 16.2935 | 16.2433 | 16.1844 | 16.1046 | 16.0088 | 15.895 | 15.761 | 15.5596 | 15.3226 | 14.314 | 11.5609 | 9.2668 | 8.5082 | 14.2916 | 14.234 | 14.1733 | 14.1035 | 14.0022 | 13.8844 | 13.7491 | 13.5931 | 13.2409 | 12.7658 | 10.7555 | 5.493 | 2.6143 | 1.6724
|  | TROWBRIDGE TOWN | SP |  |  | 13.387 | 13.3334 | 13.2756 | 13.2113 | 13.1348 | 13.0482 | 12.9505 | 12.8378 | 12.6767 | 12.5002 | 11.8159 | 9.569 | 6.1637 | 4.922 | 16.351 | 16.3113 | 16.2682 | 16.2201 | 16.1631 | 16.0985 | 16.0252 | 15.9404 | 15.8195 | 15.6847 | 15.1628 | 13.4683 | 11.6454 | 10.8047 | 14.3093 | 14.2634 | 14.2138 | 14.1588 | 14.0768 | 13.985 | 13.8869 | 13.7735 | 13.629 | 13.459 | 12.4898 | 9.213 | 5.797 | 4.6174
BRAMLEY (FLEE) | READING BSP | TWYFORD | MINIMUM HEADROOM | SU 78430 76339 | YES | 5.3091 | 4.7984 | 4.2685 | 3.7076 | 2.8327 | 2.0065 | 1.3411 | 0.62954 | -0.25105 | -1.1213 | -3.0297 | -5.416 | -6.1139 | -6.5851 | 8.9639 | 8.6831 | 8.3953 | 8.0892 | 7.641 | 7.2148 | 6.8576 | 6.4595 | 5.9073 | 5.3967 | 4.4644 | 3.3679 | 2.6619 | 2.088 | 6.2842 | 5.8335 | 5.3668 | 4.8712 | 4.1131 | 3.3891 | 2.7832 | 2.1246 | 1.2784 | 0.46935 | -1.2202 | -3.2816 | -3.8582 | -4.2
|  | TWYFORD | CT |  |  | 5.5667 | 5.1968 | 4.7851 | 4.3519 | 3.7043 | 3.1065 | 2.6885 | 2.2156 | 1.6674 | 0.82134 | -0.93205 | -3.9897 | -6.035 | -6.5851 | 9.0314 | 8.7955 | 8.5324 | 8.2576 | 7.8916 | 7.5476 | 7.2877 | 6.982 | 6.6156 | 6.0867 | 5.1203 | 3.6384 | 2.6619 | 2.088 | 6.493 | 6.1696 | 5.8085 | 5.4249 | 4.8618 | 4.3344 | 3.9484 | 3.5065 | 2.9907 | 2.1988 | 0.60004 | -2.0736 | -3.7516 | -4.2
|  | TWYFORD | LW |  |  | 5.3091 | 4.7984 | 4.2685 | 3.7076 | 2.8327 | 2.0065 | 1.3411 | 0.62954 | -0.25105 | -1.1213 | -3.0297 | -5.416 | -6.1139 | -6.4453 | 8.9639 | 8.6831 | 8.3953 | 8.0892 | 7.641 | 7.2148 | 6.8576 | 6.4595 | 5.9073 | 5.3967 | 4.4644 | 3.3679 | 3.0962 | 2.9728 | 6.2842 | 5.8335 | 5.3668 | 4.8712 | 4.1131 | 3.3891 | 2.7832 | 2.1246 | 1.2784 | 0.46935 | -1.2202 | -3.2816 | -3.8582 | -4.1282
|  | TWYFORD | ST |  |  | 5.7791 | 5.5579 | 5.3179 | 5.0446 | 4.6457 | 4.2919 | 4.057 | 3.801 | 3.5141 | 3.2043 | 1.8665 | -0.18417 | -1.2633 | -1.9615 | 9.1918 | 9.0561 | 8.9069 | 8.7306 | 8.4866 | 8.268 | 8.113 | 7.9388 | 7.7389 | 7.5376 | 6.5923 | 5.1882 | 4.454 | 3.8121 | 6.708 | 6.5243 | 6.3239 | 6.0887 | 5.7515 | 5.45 | 5.2344 | 4.9965 | 4.7289 | 4.4425 | 3.1714 | 1.2559 | 0.28955 | -0.32162
|  | TWYFORD | SP |  |  | 5.81 | 5.6134 | 5.418 | 5.2124 | 4.786 | 4.3958 | 4.1098 | 3.7916 | 3.4633 | 3.0789 | 1.78 | -1.1991 | -2.6239 | -3.3952 | 9.2008 | 9.0759 | 8.9499 | 8.8143 | 8.5834 | 8.3711 | 8.2145 | 8.0317 | 7.8379 | 7.6196 | 6.8184 | 4.8208 | 3.794 | 2.9673 | 6.7289 | 6.5659 | 6.4043 | 6.2325 | 5.8917 | 5.561 | 5.3054 | 5.0185 | 4.7215 | 4.3761 | 3.1723 | 0.38111 | -0.9195 | -1.606
COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET | MINIMUM HEADROOM | SP 52865 05849 | NO | 9.0444 | 8.6825 | 8.2443 | 7.7739 | 6.9547 | 6.0982 | 5.1838 | 4.214 | 3.0525 | 1.8063 | -1.596 | -5.6486 | -8.4167 | -10.1537 | 13.0946 | 12.921 | 12.6721 | 12.3964 | 12.0017 | 11.5801 | 11.1031 | 10.5862 | 9.9256 | 9.2014 | 7.4466 | 5.1536 | 2.9979 | 1.0562 | 9.8866 | 9.6253 | 9.2915 | 8.9004 | 8.1522 | 7.3679 | 6.5254 | 5.6101 | 4.4878 | 3.2763 | 0.068084 | -3.6108 | -5.8433 | -7.3321
|  | UNION STREET | CT |  |  | 9.3055 | 9.0982 | 8.8596 | 8.5156 | 7.9985 | 7.45 | 6.8627 | 6.2292 | 5.513 | 4.3151 | 0.94033 | -4.6197 | -8.4167 | -10.1537 | 13.1517 | 13.0174 | 12.8547 | 12.5854 | 12.2745 | 11.9373 | 11.5695 | 11.1642 | 10.6845 | 9.9718 | 8.0966 | 5.1536 | 2.9979 | 1.0562 | 9.8866 | 9.7836 | 9.6645 | 9.5051 | 9.0735 | 8.5463 | 7.9722 | 7.3495 | 6.6353 | 5.4743 | 2.273 | -2.6325 | -5.8433 | -7.3321
|  | UNION STREET | LW |  |  | 9.0444 | 8.6825 | 8.2443 | 7.7739 | 6.9547 | 6.0982 | 5.1838 | 4.214 | 3.0525 | 1.8063 | -1.596 | -5.6486 | -7.1172 | -7.85 | 13.0946 | 12.921 | 12.6721 | 12.3964 | 12.0017 | 11.5801 | 11.1031 | 10.5862 | 9.9256 | 9.2014 | 7.4466 | 5.3885 | 4.8188 | 4.5363 | 9.8987 | 9.6253 | 9.2915 | 8.9004 | 8.1522 | 7.3679 | 6.5254 | 5.6101 | 4.4878 | 3.2763 | 0.068084 | -3.6108 | -4.8603 | -5.4755
|  | UNION STREET | ST |  |  | 9.5052 | 9.4178 | 9.3173 | 9.2043 | 9.0002 | 8.7771 | 8.5299 | 8.2574 | 7.9251 | 7.5413 | 5.9595 | 2.0902 | -0.2089 | -1.5879 | 13.2714 | 13.2086 | 13.1317 | 13.0423 | 12.8919 | 12.7257 | 12.5364 | 12.325 | 12.0689 | 11.817 | 10.6709 | 7.8373 | 5.9063 | 4.0833 | 9.9858 | 9.9447 | 9.8973 | 9.8433 | 9.7537 | 9.6485 | 9.5242 | 9.3094 | 8.9727 | 8.5971 | 6.9959 | 1.9701 | -0.49977 | -1.0919
|  | UNION STREET | SP |  |  | 9.5456 | 9.4627 | 9.372 | 9.2716 | 9.0928 | 8.9158 | 8.7097 | 8.4854 | 8.23 | 7.8921 | 6.6776 | 3.3626 | 1.0168 | 0.048722 | 13.2841 | 13.209 | 13.1217 | 13.0252 | 12.9043 | 12.7754 | 12.632 | 12.4615 | 12.2681 | 12.036 | 11.1239 | 8.2779 | 5.2439 | 1.9516 | 9.9878 | 9.9493 | 9.9064 | 9.8577 | 9.7883 | 9.7114 | 9.6241 | 9.5207 | 9.2888 | 8.9731 | 7.7717 | 4.3837 | 0.71686 | -0.23393
EAST CLAYDON GSP | BICESTER NORTH | UPPER HEYFORD | MINIMUM HEADROOM | SP 51750 25667 | NO | 2.1735 | 1.7564 | 1.3241 | 0.86179 | 0.11193 | -0.67157 | -1.5264 | -2.4769 | -3.6686 | -4.8158 | -7.1822 | -10.0953 | -11.8658 | -13.1566 | 6.4811 | 6.2287 | 5.965 | 5.6767 | 5.2614 | 4.8214 | 4.3211 | 3.7484 | 2.9713 | 2.2411 | 0.93538 | -0.82068 | -2.4831 | -3.9061 | 3.229 | 2.8372 | 2.4304 | 1.9938 | 1.2995 | 0.57229 | -0.2265 | -1.1194 | -2.255 | -3.3433 | -5.5303 | -8.1838 | -9.6719 | -10.7259
|  | UPPER HEYFORD | CT |  |  | 2.3437 | 2.0504 | 1.7017 | 1.3486 | 0.86487 | 0.35326 | -0.17409 | -0.80291 | -1.5124 | -2.7134 | -5.1778 | -9.0973 | -11.8658 | -13.1566 | 6.4904 | 6.261 | 5.9842 | 5.701 | 5.381 | 5.0369 | 4.665 | 4.2105 | 3.6863 | 2.8785 | 1.3662 | -0.82068 | -2.4831 | -3.9061 | 3.3698 | 3.0869 | 2.7482 | 2.4033 | 1.9511 | 1.4681 | 0.96739 | 0.36647 | -0.31463 | -1.4571 | -3.7441 | -7.2689 | -9.6719 | -10.7259
|  | UPPER HEYFORD | LW |  |  | 2.1735 | 1.7564 | 1.3241 | 0.86179 | 0.11193 | -0.67157 | -1.5264 | -2.4769 | -3.6686 | -4.8158 | -7.1822 | -10.0953 | -11.1479 | -11.5978 | 6.4811 | 6.2287 | 5.965 | 5.6767 | 5.2614 | 4.8214 | 4.3211 | 3.7484 | 2.9713 | 2.2411 | 0.93538 | -0.55013 | -1.0004 | -1.1942 | 3.229 | 2.8372 | 2.4304 | 1.9938 | 1.2995 | 0.57229 | -0.2265 | -1.1194 | -2.255 | -3.3433 | -5.5303 | -8.1838 | -9.1113 | -9.502
|  | UPPER HEYFORD | ST |  |  | 2.6297 | 2.5126 | 2.3661 | 2.1862 | 1.9596 | 1.7161 | 1.4487 | 1.1517 | 0.79649 | 0.42969 | -1.3747 | -4.3421 | -5.8542 | -6.8548 | 6.7025 | 6.6024 | 6.4768 | 6.3211 | 6.1422 | 5.9477 | 5.7291 | 5.4833 | 5.1853 | 4.9044 | 3.4648 | 1.1447 | -0.17841 | -1.5255 | 3.6488 | 3.5375 | 3.397 | 3.2232 | 3.0065 | 2.7731 | 2.5158 | 2.2292 | 1.8847 | 1.5336 | -0.21895 | -3.0401 | -4.4042 | -5.2795
|  | UPPER HEYFORD | SP |  |  | 2.6504 | 2.547 | 2.4303 | 2.3105 | 2.0902 | 1.8561 | 1.6203 | 1.3336 | 1.0278 | 0.65976 | -0.73433 | -4.369 | -6.0381 | -6.7984 | 6.7032 | 6.6041 | 6.4897 | 6.3679 | 6.2121 | 6.0455 | 5.8693 | 5.6507 | 5.4085 | 5.135 | 4.046 | 1.0466 | -0.72802 | -2.4418 | 3.6662 | 3.5667 | 3.4541 | 3.3378 | 3.1325 | 2.9141 | 2.6929 | 2.4219 | 2.1315 | 1.784 | 0.4545 | -3.042 | -4.6049 | -5.2894
IVER 132KV | UPTON BSP | UPTON | MINIMUM HEADROOM | TQ 00800 79434 | YES | 12.8316 | 12.573 | 12.2637 | 11.6076 | 10.9144 | 10.3006 | 9.6384 | 8.9259 | 8.0928 | 7.2143 | 4.3268 | 0.088038 | -3.698 | -6.2648 | 19.0639 | 18.8733 | 18.6504 | 18.2103 | 17.8102 | 17.4244 | 17.0084 | 16.5489 | 16.0181 | 15.3387 | 13.006 | 8.2544 | 1.332 | -12.3931 | 12.4022 | 12.1633 | 11.8747 | 11.2841 | 10.654 | 10.0889 | 9.4709 | 8.7846 | 7.9705 | 7.0929 | 4.2193 | 0.28554 | -2.6863 | -4.7677
|  | UPTON | CT |  |  | 12.9388 | 12.7512 | 12.5273 | 11.928 | 11.4061 | 10.9681 | 10.5309 | 10.0538 | 9.5076 | 8.6464 | 5.8801 | 0.68812 | -3.698 | -6.2648 | 19.0639 | 18.8733 | 18.6504 | 18.2103 | 17.8102 | 17.4244 | 17.0084 | 16.5489 | 16.0181 | 15.3387 | 13.006 | 8.2544 | 2.6557 | -4.9818 | 12.4936 | 12.3173 | 12.1057 | 11.5634 | 11.0858 | 10.6776 | 10.2666 | 9.8182 | 9.3033 | 8.4998 | 5.8259 | 0.90986 | -2.6863 | -4.7677
|  | UPTON | LW |  |  | 12.8316 | 12.573 | 12.2637 | 11.6076 | 10.9144 | 10.3006 | 9.6384 | 8.9259 | 8.0928 | 7.2143 | 4.3268 | 0.088038 | -2.2758 | -3.9068 | 19.0956 | 18.9494 | 18.7677 | 18.3994 | 18.0367 | 17.7105 | 17.3435 | 16.936 | 16.4325 | 15.8953 | 14.101 | 11.8021 | 10.7341 | 9.9523 | 12.4022 | 12.1633 | 11.8747 | 11.2841 | 10.654 | 10.0889 | 9.4709 | 8.7846 | 7.9705 | 7.0929 | 4.2193 | 0.28554 | -1.6959 | -3.0195
|  | UPTON | ST |  |  | 13.1314 | 13.058 | 12.968 | 12.6577 | 12.4259 | 12.2608 | 12.0778 | 11.8663 | 11.6025 | 11.3169 | 10.1619 | 6.6566 | 4.2258 | 2.5881 | 19.1835 | 19.063 | 18.9242 | 18.6547 | 18.4 | 18.1704 | 17.9024 | 17.5902 | 17.2201 | 16.8553 | 15.4086 | 11.0679 | 6.0874 | -1.2031 | 12.6766 | 12.6086 | 12.5244 | 12.2543 | 12.042 | 11.8849 | 11.71 | 11.5077 | 11.2558 | 10.9847 | 9.8799 | 6.5677 | 4.3719 | 2.9465
|  | UPTON | SP |  |  | 13.1536 | 13.0772 | 12.9864 | 12.7034 | 12.5166 | 12.3842 | 12.2449 | 12.0822 | 11.884 | 11.6479 | 10.7805 | 8.1864 | 5.8193 | 4.5625 | 19.1803 | 19.0441 | 18.8811 | 18.6023 | 18.3385 | 18.0779 | 17.7707 | 17.4188 | 17.0015 | 16.5518 | 14.7852 | 9.6515 | 1.332 | -12.3931 | 12.6968 | 12.625 | 12.5391 | 12.2941 | 12.1261 | 12.0018 | 11.8701 | 11.7161 | 11.5283 | 11.3053 | 10.4809 | 8.0232 | 5.8152 | 4.6977
NURSLING GSP | VELMORE BSP | VELMORE | MINIMUM HEADROOM | SU 42935 19205 | YES | 20.6444 | 20.6168 | 20.5844 | 20.5444 | 20.501 | 20.4483 | 20.3847 | 20.3145 | 20.2144 | 20.1035 | 19.464 | 18.5023 | 18.0494 | 17.6163 | 15.346 | 15.3164 | 15.2837 | 15.2464 | 15.1963 | 15.1415 | 15.0791 | 15.0118 | 14.9199 | 14.8218 | 14.4803 | 14.0222 | 13.521 | 13.0347 | 10.9095 | 10.8817 | 10.8489 | 10.8084 | 10.7618 | 10.7074 | 10.6419 | 10.5696 | 10.466 | 10.3514 | 9.941 | 9.4671 | 9.2819 | 8.9227
|  | VELMORE | CT |  |  | 20.6444 | 20.6168 | 20.5844 | 20.5444 | 20.5021 | 20.4543 | 20.4026 | 20.3461 | 20.2705 | 20.1852 | 19.8835 | 18.8329 | 18.0494 | 17.6163 | 15.3494 | 15.3227 | 15.2921 | 15.2555 | 15.2107 | 15.1613 | 15.1079 | 15.0499 | 14.978 | 14.8916 | 14.5946 | 14.0222 | 13.521 | 13.0347 | 10.9095 | 10.8817 | 10.8489 | 10.8084 | 10.7651 | 10.7162 | 10.6632 | 10.6052 | 10.5275 | 10.4394 | 10.1287 | 9.6463 | 9.2819 | 8.9227
|  | VELMORE | LW |  |  | 20.6503 | 20.6208 | 20.587 | 20.5471 | 20.501 | 20.4483 | 20.3847 | 20.3145 | 20.2144 | 20.1035 | 19.464 | 18.5023 | 18.1167 | 17.8424 | 15.346 | 15.3164 | 15.2837 | 15.2464 | 15.1963 | 15.1415 | 15.0791 | 15.0118 | 14.9199 | 14.8218 | 14.4803 | 14.0695 | 13.9167 | 13.806 | 10.9148 | 10.8846 | 10.8501 | 10.8094 | 10.7618 | 10.7074 | 10.6419 | 10.5696 | 10.466 | 10.3514 | 9.941 | 9.4671 | 9.3288 | 9.1088
|  | VELMORE | ST |  |  | 20.6697 | 20.6572 | 20.6429 | 20.6261 | 20.6031 | 20.5763 | 20.5462 | 20.5106 | 20.4584 | 20.3965 | 20.1375 | 19.4396 | 19.084 | 18.9933 | 15.3719 | 15.3586 | 15.3438 | 15.3267 | 15.3033 | 15.2769 | 15.2473 | 15.2128 | 15.1648 | 15.1099 | 14.8895 | 14.2954 | 13.8842 | 13.5261 | 10.9358 | 10.9236 | 10.9096 | 10.8931 | 10.8701 | 10.8434 | 10.8131 | 10.7771 | 10.7238 | 10.6603 | 10.3953 | 9.6905 | 9.3455 | 9.2746
|  | VELMORE | SP |  |  | 20.672 | 20.6611 | 20.6476 | 20.6323 | 20.6146 | 20.5954 | 20.5727 | 20.5482 | 20.5141 | 20.4763 | 20.3332 | 19.8533 | 19.3736 | 19.2199 | 15.3738 | 15.3614 | 15.3465 | 15.3296 | 15.3085 | 15.2851 | 15.2577 | 15.2277 | 15.1897 | 15.147 | 14.9886 | 14.5072 | 13.9457 | 13.215 | 10.9381 | 10.9277 | 10.9146 | 10.8998 | 10.8823 | 10.8633 | 10.8407 | 10.8162 | 10.7817 | 10.7432 | 10.5981 | 10.1167 | 9.6405 | 9.5008
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR | MINIMUM HEADROOM | SZ 56148 77857 | NO | 8.0098 | 7.6374 | 7.2342 | 6.7644 | 6.1662 | 5.5246 | 4.8644 | 4.1377 | 3.3189 | 2.5348 | 1.3324 | 0.20621 | -0.036803 | -0.1763 | 7.0613 | 6.8402 | 6.6087 | 6.3606 | 6.0781 | 5.7739 | 5.4545 | 5.0986 | 4.6699 | 4.268 | 3.7325 | 3.2338 | 3.1164 | 3.0085 | 4.8956 | 4.541 | 4.1639 | 3.7567 | 3.2791 | 2.7659 | 2.2322 | 1.6413 | 0.95431 | 0.30524 | -0.6426 | -1.6165 | -1.8332 | -1.9608
|  | VENTNOR | CT |  |  | 8.2263 | 7.966 | 7.67 | 7.2765 | 6.8071 | 6.2965 | 5.7786 | 5.199 | 4.5455 | 3.8071 | 2.7692 | 1.4511 | 0.85446 | 0.66452 | 7.1112 | 6.9197 | 6.7057 | 6.4845 | 6.2427 | 5.9802 | 5.7105 | 5.4072 | 5.0555 | 4.6528 | 4.1331 | 3.5286 | 3.2164 | 3.0085 | 5.0353 | 4.7589 | 4.446 | 4.1155 | 3.7349 | 3.3207 | 2.8975 | 2.4221 | 1.8773 | 1.2528 | 0.40745 | -0.6145 | -1.0706 | -1.2196
|  | VENTNOR | LW |  |  | 8.0098 | 7.6374 | 7.2342 | 6.7644 | 6.1662 | 5.5246 | 4.8644 | 4.1377 | 3.3189 | 2.5348 | 1.3324 | 0.20621 | -0.036803 | -0.1763 | 7.0613 | 6.8402 | 6.6087 | 6.3606 | 6.0781 | 5.7739 | 5.4545 | 5.0986 | 4.6699 | 4.268 | 3.7325 | 3.2338 | 3.1164 | 3.0555 | 4.8956 | 4.541 | 4.1639 | 3.7567 | 3.2791 | 2.7659 | 2.2322 | 1.6413 | 0.95431 | 0.30524 | -0.6426 | -1.6165 | -1.8332 | -1.9608
|  | VENTNOR | ST |  |  | 8.334 | 8.1722 | 8.0002 | 7.8201 | 7.5489 | 7.2237 | 6.8965 | 6.5308 | 6.1384 | 5.7271 | 4.9071 | 3.9044 | 3.3826 | 3.0747 | 7.1826 | 7.0931 | 6.9601 | 6.8188 | 6.6431 | 6.4542 | 6.2636 | 6.0483 | 5.8155 | 5.5814 | 5.0497 | 4.4149 | 4.104 | 3.8572 | 5.1792 | 5.0157 | 4.8332 | 4.6399 | 4.3898 | 4.1205 | 3.8488 | 3.5429 | 3.2135 | 2.873 | 2.1262 | 1.2446 | 0.83158 | 0.59557
|  | VENTNOR | SP |  |  | 8.3664 | 8.2275 | 8.0862 | 7.9395 | 7.7262 | 7.4447 | 7.152 | 6.8281 | 6.4839 | 6.0874 | 5.3258 | 3.8652 | 3.0061 | 2.4713 | 7.1829 | 7.1127 | 7.0009 | 6.8808 | 6.7425 | 6.5874 | 6.4171 | 6.224 | 6.0168 | 5.793 | 5.3582 | 4.4652 | 4.0353 | 3.7584 | 5.2019 | 5.0586 | 4.9113 | 4.754 | 4.552 | 4.3285 | 4.0881 | 3.8187 | 3.5314 | 3.2047 | 2.5529 | 1.2487 | 0.56548 | 0.15929
MANNINGTON GSP | MANNINGTON BSP | VERWOOD | MINIMUM HEADROOM | SU 07716 10226 | YES | 2.9641 | 2.4421 | 1.8606 | 1.1702 | 0.07047 | -1.1059 | -2.3828 | -3.7871 | -5.559 | -7.3904 | -12.1602 | -18.3131 | -22.1461 | -25.0527 | 5.3372 | 5.1415 | 4.9338 | 4.6854 | 4.2402 | 3.5891 | 2.8622 | 2.0507 | 0.99242 | -0.10668 | -2.9235 | -6.9314 | -10.5154 | -13.9798 | 0.54324 | 0.091403 | -0.43297 | -1.0539 | -2.0564 | -3.1376 | -4.3211 | -5.6283 | -7.2836 | -8.9948 | -13.4277 | -19.0464 | -22.2415 | -24.6373
|  | VERWOOD | CT |  |  | 3.1412 | 2.7408 | 2.3163 | 1.707 | 0.90532 | 0.03863 | -0.8578 | -1.8479 | -3.0971 | -4.9147 | -9.6293 | -17.1004 | -22.1461 | -25.0527 | 5.3712 | 5.198 | 5.0139 | 4.7707 | 4.4113 | 3.8582 | 3.2681 | 2.6106 | 1.7837 | 0.65272 | -2.2912 | -6.9314 | -10.5154 | -13.9798 | 0.6521 | 0.2871 | -0.11111 | -0.68712 | -1.397 | -2.1677 | -2.9801 | -3.8989 | -5.0669 | -6.7591 | -11.1212 | -17.8621 | -22.2415 | -24.6373
|  | VERWOOD | LW |  |  | 2.9641 | 2.4421 | 1.8606 | 1.1702 | 0.07047 | -1.1059 | -2.3828 | -3.7871 | -5.559 | -7.3904 | -12.1602 | -18.3131 | -21.1178 | -22.7885 | 5.3372 | 5.1415 | 4.9338 | 4.6854 | 4.2402 | 3.5891 | 2.8622 | 2.0507 | 0.99242 | -0.10668 | -2.9235 | -6.4619 | -7.8167 | -8.6617 | 0.54324 | 0.091403 | -0.43297 | -1.0539 | -2.0564 | -3.1376 | -4.3211 | -5.6283 | -7.2836 | -8.9948 | -13.4277 | -19.0464 | -21.4418 | -22.8267
|  | VERWOOD | ST |  |  | 3.5336 | 3.3634 | 3.1903 | 2.9525 | 2.6136 | 2.2325 | 1.8213 | 1.3594 | 0.74181 | 0.060055 | -2.6463 | -8.496 | -11.9853 | -14.1822 | 5.5206 | 5.4368 | 5.3524 | 5.2431 | 5.0934 | 4.9247 | 4.7374 | 4.4888 | 4.0221 | 3.5184 | 1.4744 | -3.0468 | -6.2824 | -9.4912 | 1.0155 | 0.86152 | 0.69667 | 0.4737 | 0.15687 | -0.20042 | -0.58928 | -1.0281 | -1.6081 | -2.2328 | -4.8035 | -10.1987 | -13.2154 | -15.0618
|  | VERWOOD | SP |  |  | 3.5839 | 3.4139 | 3.247 | 3.0391 | 2.7863 | 2.5078 | 2.2113 | 1.8733 | 1.4246 | 0.8908 | -0.95934 | -6.0224 | -9.7376 | -11.4891 | 5.5333 | 5.454 | 5.3724 | 5.2727 | 5.1513 | 5.0165 | 4.8699 | 4.7041 | 4.3954 | 3.9437 | 2.3061 | -2.2831 | -7.0008 | -12.3256 | 1.059 | 0.89871 | 0.73429 | 0.53577 | 0.30031 | 0.041314 | -0.23829 | -0.56073 | -0.98309 | -1.4744 | -3.2228 | -8.0605 | -11.4238 | -12.8957
COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD | MINIMUM HEADROOM | SU 59847 89486 | NO | 8.874 | 8.124 | 7.296 | 6.679 | 5.7457 | 4.7432 | 3.6304 | 2.3932 | 0.85564 | -0.5962 | -4.0044 | -8.7936 | -11.9487 | -14.3498 | 13.3193 | 12.9622 | 12.6452 | 12.4129 | 12.1709 | 11.9197 | 11.4172 | 10.6702 | 9.6928 | 8.7782 | 6.5015 | 3.1234 | 0.83143 | -1.6921 | 10.4218 | 9.9432 | 9.4675 | 8.984 | 8.1122 | 7.1788 | 6.1362 | 4.9723 | 3.5025 | 2.1214 | -1.06 | -5.4128 | -8.0634 | -10.1106
|  | WALLINGFORD | CT |  |  | 8.874 | 8.3299 | 7.5585 | 7.0258 | 6.3633 | 5.6437 | 4.8869 | 4.0268 | 3.0296 | 1.5354 | -1.903 | -7.8111 | -11.9487 | -14.3498 | 13.3193 | 12.9622 | 12.6452 | 12.4129 | 12.1709 | 11.9213 | 11.6444 | 11.1537 | 10.4502 | 9.4825 | 7.2887 | 3.6092 | 0.83143 | -1.6921 | 10.4218 | 9.9701 | 9.5105 | 9.1261 | 8.6487 | 7.9707 | 7.2536 | 6.4355 | 5.479 | 4.0587 | 0.85585 | -4.4662 | -8.0634 | -10.1106
|  | WALLINGFORD | LW |  |  | 8.9004 | 8.124 | 7.296 | 6.679 | 5.7457 | 4.7432 | 3.6304 | 2.3932 | 0.85564 | -0.5962 | -4.0044 | -8.7936 | -11.1579 | -12.6478 | 13.3481 | 12.9864 | 12.6813 | 12.4498 | 12.193 | 11.9197 | 11.4172 | 10.6702 | 9.6928 | 8.7782 | 6.5015 | 3.1234 | 2.3195 | 1.779 | 10.4377 | 9.9432 | 9.4675 | 8.984 | 8.1122 | 7.1788 | 6.1362 | 4.9723 | 3.5025 | 2.1214 | -1.06 | -5.4128 | -7.4362 | -8.6795
|  | WALLINGFORD | ST |  |  | 9.0552 | 8.7521 | 8.4775 | 8.3189 | 8.0572 | 7.7201 | 7.3394 | 6.9173 | 6.4207 | 5.9071 | 3.3862 | -1.5195 | -4.4214 | -6.3136 | 13.4486 | 13.1703 | 12.9477 | 12.8098 | 12.6578 | 12.5046 | 12.3294 | 12.1317 | 11.8857 | 11.6265 | 10.2224 | 6.0442 | 3.8882 | 1.6781 | 10.6643 | 10.3678 | 10.1038 | 9.9215 | 9.6973 | 9.4502 | 9.1628 | 8.8317 | 8.4075 | 7.8942 | 5.7452 | 0.43049 | -2.2242 | -3.335
|  | WALLINGFORD | SP |  |  | 9.0637 | 8.7733 | 8.5144 | 8.379 | 8.2329 | 8.0587 | 7.7939 | 7.471 | 7.1087 | 6.7016 | 5.0852 | 0.32273 | -2.6065 | -4.088 | 13.4527 | 13.1813 | 12.9684 | 12.8452 | 12.7178 | 12.5961 | 12.4628 | 12.309 | 12.1325 | 11.9518 | 11.2349 | 7.2759 | 4.0642 | 0.87506 | 10.6729 | 10.3887 | 10.1435 | 9.9941 | 9.8156 | 9.6309 | 9.4247 | 9.1887 | 8.9132 | 8.5906 | 7.4144 | 2.897 | -0.075646 | -1.2386
COWLEY GSP | DRAYTON BSP | WANTAGE | MINIMUM HEADROOM | SU 41290 88304 | NO | 18.775 | 18.2177 | 17.574 | 16.9068 | 15.9457 | 14.9529 | 13.9285 | 12.8579 | 11.6327 | 10.2995 | 6.6963 | 2.6978 | 1.6073 | 0.85923 | 22.9369 | 22.6959 | 22.3884 | 22.0625 | 21.6201 | 21.1546 | 20.6583 | 20.1324 | 19.4892 | 18.7659 | 17.0046 | 15.3058 | 14.2127 | 13.0645 | 20.7064 | 20.2325 | 19.6597 | 19.0612 | 18.2188 | 17.3426 | 16.4274 | 15.4657 | 14.3466 | 13.1183 | 9.8922 | 6.3207 | 5.3623 | 4.693
|  | WANTAGE | CT |  |  | 19.4092 | 19.1724 | 18.9094 | 18.5439 | 17.9952 | 17.4205 | 16.7974 | 16.1329 | 15.4192 | 14.2801 | 11.0445 | 5.6777 | 2.1601 | 1.1291 | 23.1555 | 23.0237 | 22.8714 | 22.6218 | 22.3147 | 21.9854 | 21.6249 | 21.2333 | 20.7938 | 20.133 | 18.3318 | 15.9362 | 14.2127 | 13.0742 | 21.1577 | 20.956 | 20.7259 | 20.3743 | 19.8979 | 19.3674 | 18.7907 | 18.1722 | 17.4984 | 16.436 | 13.4769 | 8.953 | 5.8626 | 4.9402
|  | WANTAGE | LW |  |  | 18.775 | 18.2177 | 17.574 | 16.9068 | 15.9457 | 14.9529 | 13.9285 | 12.8579 | 11.6327 | 10.2995 | 6.6963 | 2.6978 | 1.6073 | 0.85923 | 22.9369 | 22.6959 | 22.3884 | 22.0625 | 21.6201 | 21.1546 | 20.6583 | 20.1324 | 19.4892 | 18.7659 | 17.0046 | 15.3058 | 14.8782 | 14.5889 | 20.7064 | 20.2325 | 19.6597 | 19.0612 | 18.2188 | 17.3426 | 16.4274 | 15.4657 | 14.3466 | 13.1183 | 9.8922 | 6.3207 | 5.3623 | 4.693
|  | WANTAGE | ST |  |  | 19.5102 | 19.3387 | 19.1579 | 18.9675 | 18.6329 | 18.2776 | 17.9172 | 17.5308 | 17.1207 | 16.6652 | 14.9792 | 11.4809 | 9.4927 | 8.155 | 23.2258 | 23.1378 | 23.0415 | 22.9359 | 22.7551 | 22.5567 | 22.3504 | 22.1188 | 21.8577 | 21.5914 | 20.501 | 18.178 | 16.9175 | 15.7267 | 21.2614 | 21.1251 | 20.9781 | 20.8196 | 20.5367 | 20.2199 | 19.8884 | 19.5296 | 19.1438 | 18.7276 | 17.1282 | 13.8291 | 12.1484 | 11.0601
|  | WANTAGE | SP |  |  | 19.587 | 19.4452 | 19.2977 | 19.1484 | 18.661 | 18.1863 | 17.6971 | 17.1799 | 16.6601 | 15.9988 | 13.8416 | 9.1761 | 6.2038 | 4.458 | 23.2529 | 23.1666 | 23.0731 | 22.976 | 22.7491 | 22.5228 | 22.285 | 22.0239 | 21.7547 | 21.4216 | 20.2553 | 17.4417 | 15.2555 | 13.0645 | 21.3174 | 21.194 | 21.0639 | 20.9314 | 20.5522 | 20.1579 | 19.7378 | 19.2877 | 18.8344 | 18.2627 | 16.3555 | 12.113 | 9.456 | 7.9183
MANNINGTON GSP | WAREHAM | WAREHAM TOWN | MINIMUM HEADROOM | SY 92036 87463 | YES | 1.4451 | 0.99387 | 0.46423 | -0.10871 | -0.88319 | -1.7274 | -2.6411 | -3.6501 | -4.9324 | -6.1482 | -8.4644 | -11.3433 | -12.661 | -13.718 | 2.6121 | 2.3535 | 2.0437 | 1.7056 | 1.2738 | 0.79849 | 0.27199 | -0.32746 | -1.1767 | -1.9679 | -3.294 | -4.8521 | -6.1849 | -7.2593 | -0.057567 | -0.488 | -0.99425 | -1.5424 | -2.2974 | -3.1171 | -4.0059 | -4.9866 | -6.2286 | -7.4062 | -9.6554 | -12.4379 | -13.7514 | -14.7835
|  | WAREHAM TOWN | CT |  |  | 1.639 | 1.3231 | 0.94624 | 0.47028 | -0.048252 | -0.61701 | -1.229 | -1.9007 | -2.7581 | -4.0108 | -6.4859 | -10.1982 | -12.661 | -13.718 | 2.677 | 2.4686 | 2.2189 | 1.9014 | 1.5761 | 1.2189 | 0.82646 | 0.36304 | -0.25337 | -1.0969 | -2.6332 | -4.729 | -6.1849 | -7.2593 | 0.13467 | -0.16257 | -0.51887 | -0.97083 | -1.4753 | -2.0256 | -2.6195 | -3.2709 | -4.0995 | -5.3133 | -7.7174 | -11.3386 | -13.7514 | -14.7835
|  | WAREHAM TOWN | LW |  |  | 1.4451 | 0.99387 | 0.46423 | -0.10871 | -0.88319 | -1.7274 | -2.6411 | -3.6501 | -4.9324 | -6.1482 | -8.4644 | -11.3433 | -12.277 | -12.7258 | 2.6121 | 2.3535 | 2.0437 | 1.7056 | 1.2738 | 0.79849 | 0.27199 | -0.32746 | -1.1767 | -1.9679 | -3.294 | -4.8521 | -5.2758 | -5.4724 | -0.057567 | -0.488 | -0.99425 | -1.5424 | -2.2974 | -3.1171 | -4.0059 | -4.9866 | -6.2286 | -7.4062 | -9.6554 | -12.4379 | -13.3369 | -13.7655
|  | WAREHAM TOWN | ST |  |  | 1.8968 | 1.7387 | 1.5456 | 1.3196 | 1.0698 | 0.78466 | 0.48307 | 0.14271 | -0.25673 | -0.6645 | -2.6669 | -5.6478 | -7.0029 | -7.9078 | 2.8431 | 2.7348 | 2.6017 | 2.4447 | 2.2754 | 2.0821 | 1.8736 | 1.6368 | 1.357 | 1.0836 | -0.38607 | -2.57 | -3.6161 | -4.6114 | 0.38476 | 0.24078 | 0.063 | -0.14648 | -0.38854 | -0.66196 | -0.95333 | -1.282 | -1.6657 | -2.0569 | -3.9804 | -6.8319 | -8.1176 | -8.9643
|  | WAREHAM TOWN | SP |  |  | 1.9377 | 1.7832 | 1.6196 | 1.4399 | 1.1966 | 0.93803 | 0.67806 | 0.37281 | 0.028039 | -0.38265 | -1.9438 | -5.8746 | -7.434 | -8.1406 | 2.86 | 2.7484 | 2.6272 | 2.4927 | 2.3387 | 2.1721 | 2.0011 | 1.7965 | 1.5634 | 1.2889 | 0.21698 | -2.8268 | -4.3937 | -5.8832 | 0.42455 | 0.28431 | 0.13525 | -0.029379 | -0.266 | -0.51441 | -0.76641 | -1.0618 | -1.3934 | -1.7898 | -3.2941 | -7.0885 | -8.608 | -9.2955
BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD | MINIMUM HEADROOM | SU 86960 71382 | YES | 0.34744 | -0.44595 | -1.139 | -1.9161 | -2.9829 | -4.0877 | -5.1024 | -6.1889 | -7.4648 | -8.789 | -11.8528 | -15.3429 | -17.332 | -18.825 | 5.2997 | 4.8318 | 4.4321 | 3.9837 | 3.4299 | 2.852 | 2.3021 | 1.7048 | 0.95978 | 0.18879 | -1.4779 | -3.3161 | -5.2903 | -6.9494 | 1.493 | 0.80401 | 0.18363 | -0.51268 | -1.4513 | -2.4279 | -3.3517 | -4.3476 | -5.5531 | -6.7992 | -9.5732 | -12.6287 | -14.2225 | -15.4505
|  | WARFIELD | CT |  |  | 0.6492 | 0.028633 | -0.48222 | -1.1218 | -1.9019 | -2.7113 | -3.4046 | -4.1738 | -5.0328 | -6.3257 | -9.3944 | -13.9869 | -17.332 | -18.825 | 5.379 | 4.9581 | 4.6106 | 4.1891 | 3.7314 | 3.2546 | 2.8254 | 2.3446 | 1.7999 | 1.0104 | -0.85308 | -3.3161 | -5.2903 | -6.9494 | 1.727 | 1.1798 | 0.71211 | 0.13525 | -0.55716 | -1.2777 | -1.9123 | -2.619 | -3.4126 | -4.6081 | -7.433 | -11.4592 | -14.2225 | -15.4505
|  | WARFIELD | LW |  |  | 0.34744 | -0.44595 | -1.139 | -1.9161 | -2.9829 | -4.0877 | -5.1024 | -6.1889 | -7.4648 | -8.789 | -11.8528 | -15.3429 | -16.5691 | -17.2748 | 5.2997 | 4.8318 | 4.4321 | 3.9837 | 3.4299 | 2.852 | 2.3021 | 1.7048 | 0.95978 | 0.18879 | -1.4779 | -3.1844 | -3.7059 | -4.0004 | 1.493 | 0.80401 | 0.18363 | -0.51268 | -1.4513 | -2.4279 | -3.3517 | -4.3476 | -5.5531 | -6.7992 | -9.5732 | -12.6287 | -13.6564 | -14.2396
|  | WARFIELD | ST |  |  | 0.93204 | 0.51742 | 0.20779 | -0.15443 | -0.58337 | -1.0304 | -1.4037 | -1.8261 | -2.292 | -2.7922 | -4.6202 | -7.9568 | -9.6286 | -10.7318 | 5.5558 | 5.2638 | 5.0536 | 4.8026 | 4.5206 | 4.2216 | 3.9588 | 3.6664 | 3.3394 | 3.0034 | 1.7242 | -0.79464 | -2.2325 | -3.7449 | 2.0207 | 1.6789 | 1.4122 | 1.0954 | 0.71375 | 0.31283 | -0.034685 | -0.41899 | -0.84484 | -1.2993 | -3.0255 | -6.1731 | -7.6826 | -8.6581
|  | WARFIELD | SP |  |  | 0.97656 | 0.58629 | 0.31254 | 0.00075441 | -0.43891 | -0.89129 | -1.2908 | -1.7139 | -2.1617 | -2.6974 | -4.3384 | -8.1661 | -10.2485 | -11.2267 | 5.5705 | 5.2857 | 5.0858 | 4.8544 | 4.5922 | 4.3142 | 4.061 | 3.7805 | 3.4757 | 3.1244 | 1.9812 | -0.91615 | -3.1391 | -5.5081 | 2.0577 | 1.7342 | 1.4987 | 1.2292 | 0.85876 | 0.47382 | 0.12127 | -0.25981 | -0.6655 | -1.1479 | -2.6791 | -6.2918 | -8.2289 | -9.1091
MELKSHAM GSP | FROME BSP | WARMINSTER | MINIMUM HEADROOM | ST 84936 44551 | YES | 8.4349 | 7.6247 | 6.6835 | 5.6692 | 4.315 | 2.8831 | 1.5425 | 0.40191 | -0.89919 | -2.1602 | -5.034 | -7.9437 | -9.522 | -10.739 | 5.9407 | 5.4161 | 4.8031 | 4.1435 | 3.3005 | 2.406 | 1.5702 | 0.85216 | 0.024823 | -0.79373 | -2.4962 | -4.0472 | -5.5752 | -6.8104 | 4.0825 | 3.3825 | 2.5668 | 1.6837 | 0.48759 | -0.77688 | -1.9681 | -3.0006 | -4.1694 | -5.3064 | -7.9319 | -10.5842 | -12.0243 | -13.1108
|  | WARMINSTER | CT |  |  | 8.6742 | 8.0014 | 7.22 | 6.3209 | 5.2215 | 4.0549 | 2.9908 | 2.1203 | 1.1973 | -0.070541 | -2.9522 | -6.8175 | -9.522 | -10.739 | 6.0126 | 5.528 | 4.9673 | 4.332 | 3.5731 | 2.768 | 2.0306 | 1.4081 | 0.74328 | -0.09871 | -1.9585 | -4.0472 | -5.5752 | -6.8104 | 4.3128 | 3.7436 | 3.0766 | 2.31 | 1.3412 | 0.31312 | -0.62777 | -1.4087 | -2.2263 | -3.3668 | -6.0291 | -9.5478 | -12.0243 | -13.1108
|  | WARMINSTER | LW |  |  | 8.4349 | 7.6247 | 6.6835 | 5.6692 | 4.315 | 2.8831 | 1.5425 | 0.40191 | -0.89919 | -2.1602 | -5.034 | -7.9437 | -8.9198 | -9.4684 | 5.9407 | 5.4161 | 4.8031 | 4.1435 | 3.3005 | 2.406 | 1.5702 | 0.85216 | 0.024823 | -0.79373 | -2.4962 | -3.9505 | -4.3597 | -4.58 | 4.0825 | 3.3825 | 2.5668 | 1.6837 | 0.48759 | -0.77688 | -1.9681 | -3.0006 | -4.1694 | -5.3064 | -7.9319 | -10.5842 | -11.4701 | -11.9717
|  | WARMINSTER | ST |  |  | 8.9446 | 8.4549 | 7.8913 | 7.2861 | 6.5045 | 5.6841 | 4.9491 | 4.368 | 3.7658 | 3.1953 | 1.2464 | -1.5668 | -2.8499 | -3.7174 | 6.1709 | 5.7866 | 5.3416 | 4.8625 | 4.2551 | 3.6155 | 3.0377 | 2.5605 | 2.0689 | 1.6191 | 0.19739 | -1.8247 | -2.8968 | -4.0403 | 4.5305 | 4.1164 | 3.6379 | 3.1227 | 2.4511 | 1.7436 | 1.1042 | 0.57923 | 0.040897 | -0.48093 | -2.1731 | -4.7249 | -5.929 | -6.7497
|  | WARMINSTER | SP |  |  | 8.9796 | 8.5087 | 7.9803 | 7.4231 | 6.6622 | 5.8697 | 5.1474 | 4.5629 | 3.9764 | 3.3792 | 1.6126 | -1.6747 | -3.2729 | -4.0415 | 6.1822 | 5.8015 | 5.369 | 4.9088 | 4.3255 | 3.712 | 3.1485 | 2.678 | 2.2035 | 1.7458 | 0.42568 | -1.9273 | -3.4938 | -5.1062 | 4.5625 | 4.1673 | 3.7193 | 3.2451 | 2.5798 | 1.8849 | 1.2491 | 0.71341 | 0.17985 | -0.36949 | -1.9328 | -4.8296 | -6.3027 | -7.0221
LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE | MINIMUM HEADROOM | SU 67988 09282 | NO | 4.1999 | 3.9525 | 3.7194 | 3.3638 | 2.753 | 2.1124 | 1.3805 | 0.59595 | -0.3123 | -1.221 | -3.43 | -5.8515 | -7.4368 | -8.5239 | 6.2527 | 5.9798 | 5.7142 | 5.4489 | 5.1647 | 4.8579 | 4.5152 | 4.1142 | 3.6875 | 3.2748 | 2.0793 | 0.77414 | 0.30016 | -0.60585 | 5.1861 | 4.8874 | 4.6091 | 4.2296 | 3.6387 | 3.0301 | 2.3977 | 1.7255 | 0.97139 | 0.22061 | -1.7863 | -3.9062 | -5.3187 | -6.3198
|  | WATERLOOVILLE | CT |  |  | 4.1999 | 3.9525 | 3.7293 | 3.4956 | 3.2246 | 2.9084 | 2.5764 | 2.0172 | 1.41 | 0.53478 | -1.6974 | -5.038 | -7.4368 | -8.5239 | 6.2527 | 5.9838 | 5.7366 | 5.4857 | 5.2197 | 4.9396 | 4.6426 | 4.3155 | 3.9932 | 3.6704 | 2.7175 | 1.3416 | 0.30016 | -0.60585 | 5.1992 | 4.9224 | 4.6657 | 4.3991 | 4.1164 | 3.8124 | 3.4945 | 3.0031 | 2.5009 | 1.7148 | -0.3493 | -3.2018 | -5.3187 | -6.3198
|  | WATERLOOVILLE | LW |  |  | 4.2065 | 3.9546 | 3.7194 | 3.3638 | 2.753 | 2.1124 | 1.3805 | 0.59595 | -0.3123 | -1.221 | -3.43 | -5.8515 | -6.7259 | -7.2129 | 6.2606 | 5.9798 | 5.7142 | 5.4489 | 5.1647 | 4.8579 | 4.5152 | 4.1142 | 3.6875 | 3.2748 | 2.0793 | 0.77414 | 0.48054 | 0.31175 | 5.1861 | 4.8874 | 4.6091 | 4.2296 | 3.6387 | 3.0301 | 2.3977 | 1.7255 | 0.97139 | 0.22061 | -1.7863 | -3.9062 | -4.7076 | -5.1626
|  | WATERLOOVILLE | ST |  |  | 4.2429 | 4.0203 | 3.8295 | 3.6493 | 3.4592 | 3.256 | 3.0421 | 2.7785 | 2.4958 | 2.2388 | 1.1809 | -1.0327 | -2.2756 | -3.1495 | 6.3015 | 6.0608 | 5.8512 | 5.6556 | 5.4481 | 5.2296 | 4.9959 | 4.7375 | 4.477 | 4.2532 | 3.4754 | 2.1468 | 1.5056 | 1.2592 | 5.2534 | 5.0245 | 4.8288 | 4.6408 | 4.4306 | 4.2025 | 3.9612 | 3.6879 | 3.4172 | 3.1708 | 2.2256 | 0.19248 | -0.87639 | -1.6871
|  | WATERLOOVILLE | SP |  |  | 4.2452 | 4.0207 | 3.8305 | 3.6497 | 3.4711 | 3.2833 | 3.0913 | 2.866 | 2.6198 | 2.3525 | 1.2057 | -1.2454 | -2.6015 | -3.2807 | 6.3029 | 6.0622 | 5.8542 | 5.6592 | 5.4623 | 5.2585 | 5.046 | 4.8095 | 4.5833 | 4.4018 | 3.8311 | 2.7452 | 1.8109 | 0.6174 | 5.2559 | 5.0264 | 4.8321 | 4.6473 | 4.4531 | 4.2403 | 4.0227 | 3.7745 | 3.5065 | 3.1848 | 2.1574 | 0.093886 | -1.1523 | -1.7316
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON | MINIMUM HEADROOM | SU 69106 94287 | YES | 8.4951 | 7.8643 | 7.2354 | 6.5109 | 5.2083 | 3.4739 | 1.3703 | -1.0814 | -3.8553 | -6.4831 | -12.6641 | -18.5913 | -20.6842 | -21.982 | 14.238 | 13.8471 | 13.446 | 12.9736 | 12.25 | 11.2822 | 10.0974 | 8.7053 | 7.028 | 5.4756 | 2.1024 | -1.3008 | -3.2053 | -4.7661 | 11.0927 | 10.5152 | 9.9341 | 9.2656 | 8.0995 | 6.5774 | 4.7356 | 2.5852 | 0.097656 | -2.2408 | -7.6116 | -12.821 | -14.5907 | -15.7242
|  | WATLINGTON | CT |  |  | 8.6379 | 8.1311 | 7.573 | 6.9367 | 5.9381 | 4.5223 | 2.8038 | 0.73792 | -1.4215 | -4.1495 | -10.4824 | -17.5911 | -20.6842 | -21.982 | 14.238 | 13.8659 | 13.446 | 12.9736 | 12.351 | 11.5009 | 10.4729 | 9.2316 | 7.9025 | 6.2475 | 2.6747 | -1.3008 | -3.2053 | -4.7661 | 11.2086 | 10.7411 | 10.2172 | 9.6234 | 8.7309 | 7.4967 | 6.0063 | 4.2073 | 2.3037 | -0.13114 | -5.6394 | -11.8656 | -14.5907 | -15.7242
|  | WATLINGTON | LW |  |  | 8.4951 | 7.8643 | 7.2354 | 6.5109 | 5.2083 | 3.4739 | 1.3703 | -1.0814 | -3.8553 | -6.4831 | -12.6641 | -18.5913 | -19.8648 | -20.2887 | 14.2436 | 13.8471 | 13.4487 | 12.9864 | 12.25 | 11.2822 | 10.0974 | 8.7053 | 7.028 | 5.4756 | 2.1024 | -1.0911 | -1.6402 | -1.8235 | 11.0927 | 10.5152 | 9.9341 | 9.2656 | 8.0995 | 6.5774 | 4.7356 | 2.5852 | 0.097656 | -2.2408 | -7.6116 | -12.821 | -13.9379 | -14.3044
|  | WATLINGTON | ST |  |  | 9.0741 | 8.841 | 8.587 | 8.259 | 7.732 | 6.9241 | 5.909 | 4.7123 | 3.4822 | 2.2101 | -2.4597 | -7.9893 | -9.9662 | -11.077 | 14.5533 | 14.3729 | 14.1689 | 13.9077 | 13.5343 | 12.9929 | 12.322 | 11.5346 | 10.7086 | 9.8822 | 6.6564 | 2.637 | 0.94585 | -0.54442 | 11.6322 | 11.429 | 11.1992 | 10.9013 | 10.4434 | 9.7647 | 8.9171 | 7.916 | 6.8705 | 5.7916 | 1.667 | -3.3401 | -5.135 | -6.1049
|  | WATLINGTON | SP |  |  | 9.1088 | 8.8964 | 8.6923 | 8.452 | 8.0292 | 7.3928 | 6.5437 | 5.5201 | 4.5169 | 3.426 | -0.075202 | -5.9246 | -7.9808 | -8.7261 | 14.5646 | 14.3905 | 14.2123 | 14.0056 | 13.7108 | 13.2912 | 12.7254 | 12.0377 | 11.3492 | 10.6091 | 8.1278 | 3.4559 | 1.2077 | -0.76104 | 11.6635 | 11.4791 | 11.2969 | 11.0843 | 10.7283 | 10.2158 | 9.5255 | 8.6859 | 7.8542 | 6.9418 | 3.9384 | -1.4703 | -3.4177 | -4.0988
AMERSHAM | LOUDWATER BSP | WELL END | MINIMUM HEADROOM | SU 88511 87957 | YES | 6.1098 | 5.7649 | 5.3524 | 4.9867 | 4.4902 | 3.9809 | 3.4558 | 2.902 | 2.2673 | 1.5677 | -0.26931 | -2.4 | -3.538 | -4.4448 | 7.2786 | 7.1317 | 6.9297 | 6.7945 | 6.6457 | 6.4693 | 6.1929 | 5.8971 | 5.5391 | 5.1421 | 4.1752 | 3.1751 | 2.4288 | 1.8008 | 6.5788 | 6.3325 | 6.0332 | 5.7915 | 5.4615 | 5.1254 | 4.7325 | 4.2524 | 3.711 | 3.1149 | 1.5054 | -0.4136 | -1.4496 | -2.279
|  | WELL END | CT |  |  | 6.342 | 6.1216 | 5.8583 | 5.604 | 5.2906 | 4.9672 | 4.6337 | 4.2814 | 3.8961 | 3.2544 | 1.5 | -1.4043 | -3.538 | -4.4448 | 7.3155 | 7.196 | 7.0223 | 6.9059 | 6.7925 | 6.6781 | 6.5674 | 6.4033 | 6.1607 | 5.7841 | 4.7964 | 3.422 | 2.4288 | 1.8008 | 6.6934 | 6.5511 | 6.3657 | 6.2152 | 6.0125 | 5.8066 | 5.6004 | 5.3834 | 5.1336 | 4.5466 | 2.9939 | 0.50238 | -1.4496 | -2.279
|  | WELL END | LW |  |  | 6.1098 | 5.7649 | 5.3524 | 4.9867 | 4.4902 | 3.9809 | 3.4558 | 2.902 | 2.2673 | 1.5677 | -0.26931 | -2.4 | -3.1131 | -3.5986 | 7.2786 | 7.1317 | 6.9297 | 6.7945 | 6.6457 | 6.4693 | 6.1929 | 5.8971 | 5.5391 | 5.1421 | 4.1752 | 3.1751 | 2.8862 | 2.6947 | 6.5788 | 6.3325 | 6.0332 | 5.7915 | 5.4615 | 5.1254 | 4.7325 | 4.2524 | 3.711 | 3.1149 | 1.5054 | -0.4136 | -1.0642 | -1.5064
|  | WELL END | ST |  |  | 6.4156 | 6.2503 | 6.0477 | 5.8925 | 5.7138 | 5.5301 | 5.3419 | 5.1434 | 4.9222 | 4.6843 | 3.7904 | 1.8515 | 0.78943 | 0.070446 | 7.3409 | 7.2411 | 7.088 | 7.0031 | 6.927 | 6.8504 | 6.7798 | 6.7044 | 6.6181 | 6.5257 | 6.0383 | 4.7676 | 4.1119 | 3.5532 | 6.729 | 6.6126 | 6.457 | 6.3593 | 6.2465 | 6.1239 | 6.0052 | 5.8801 | 5.7422 | 5.5829 | 5.0348 | 3.2192 | 2.3691 | 1.7695
|  | WELL END | SP |  |  | 6.4456 | 6.2889 | 6.1028 | 5.9676 | 5.7138 | 5.4553 | 5.2017 | 4.9366 | 4.6627 | 4.3415 | 3.3024 | 0.97463 | -0.4202 | -1.1518 | 7.3424 | 7.2488 | 7.0994 | 7.0183 | 6.9298 | 6.8421 | 6.7627 | 6.6789 | 6.5901 | 6.4893 | 5.9689 | 4.5064 | 3.4432 | 2.5103 | 6.743 | 6.6329 | 6.4867 | 6.3989 | 6.2462 | 6.0671 | 5.8944 | 5.7166 | 5.535 | 5.321 | 4.5899 | 2.6182 | 1.3912 | 0.73949
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END | MINIMUM HEADROOM | SU 57216 06147 | YES | 36.0845 | 34.9632 | 33.7892 | 32.535 | 30.6359 | 28.5951 | 26.365 | 23.8715 | 20.9359 | 18.1174 | 11.8328 | 5.3493 | 1.0919 | -2.0664 | 44.0544 | 43.3146 | 42.5495 | 41.7545 | 40.6668 | 39.4952 | 38.1547 | 36.6666 | 34.8038 | 33.0498 | 29.3902 | 25.812 | 22.5568 | 19.842 | 42.5824 | 41.5936 | 40.5805 | 39.5177 | 37.8538 | 36.0744 | 34.11 | 31.8856 | 29.2667 | 26.7601 | 21.0805 | 15.1772 | 11.2978 | 8.5587
|  | WEST END | CT |  |  | 36.4042 | 35.4981 | 34.591 | 33.4897 | 32.0334 | 30.4521 | 28.7411 | 26.8036 | 24.5753 | 21.7593 | 15.167 | 6.8396 | 1.0919 | -2.0664 | 44.1254 | 43.4499 | 42.7881 | 42.0018 | 41.0737 | 40.0727 | 38.9425 | 37.6882 | 36.191 | 34.4083 | 30.3808 | 25.812 | 22.5568 | 19.842 | 42.9139 | 42.1351 | 41.3686 | 40.4701 | 39.234 | 37.8715 | 36.3474 | 34.6404 | 32.6694 | 30.1688 | 24.2384 | 16.5744 | 11.2978 | 8.5587
|  | WEST END | LW |  |  | 36.0845 | 34.9632 | 33.7892 | 32.535 | 30.6359 | 28.5951 | 26.365 | 23.8715 | 20.9359 | 18.1174 | 11.8328 | 5.3493 | 2.5246 | 0.76372 | 44.0544 | 43.3146 | 42.5495 | 41.7545 | 40.6668 | 39.4952 | 38.1547 | 36.6666 | 34.8038 | 33.0498 | 29.3902 | 25.9458 | 24.6567 | 23.8276 | 42.5824 | 41.5936 | 40.5805 | 39.5177 | 37.8538 | 36.0744 | 34.11 | 31.8856 | 29.2667 | 26.7601 | 21.0805 | 15.1772 | 12.6686 | 11.1465
|  | WEST END | ST |  |  | 36.8843 | 36.2756 | 35.7118 | 35.124 | 34.3 | 33.3913 | 32.3751 | 31.2167 | 29.9101 | 28.7333 | 24.5434 | 18.0829 | 14.7074 | 12.4 | 44.4591 | 43.9796 | 43.5415 | 43.0997 | 42.5092 | 41.8629 | 41.113 | 40.2777 | 39.3079 | 38.4847 | 35.3761 | 30.585 | 27.9996 | 25.5666 | 43.3083 | 42.7802 | 42.3054 | 41.8339 | 41.1728 | 40.449 | 39.6145 | 38.6727 | 37.5427 | 36.5312 | 32.8775 | 27.1131 | 24.0776 | 22.0299
|  | WEST END | SP |  |  | 36.95 | 36.3522 | 35.8304 | 35.3202 | 34.6164 | 33.8796 | 33.0096 | 32.0056 | 30.8995 | 29.8469 | 26.5667 | 20.0233 | 16.5293 | 14.8083 | 44.4848 | 43.9984 | 43.5738 | 43.1709 | 42.6771 | 42.1577 | 41.514 | 40.783 | 39.9549 | 39.1893 | 36.6724 | 31.319 | 27.5946 | 23.817 | 43.3702 | 42.8585 | 42.4232 | 42.0189 | 41.4479 | 40.8585 | 40.1403 | 39.339 | 38.4306 | 37.5348 | 34.6976 | 28.952 | 25.8613 | 24.384
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE | MINIMUM HEADROOM | SU 24639 60279 | YES | 2.4342 | 1.9698 | 1.5164 | 1.0988 | 0.51952 | -0.070943 | -0.68843 | -1.3446 | -2.0177 | -2.5506 | -3.6808 | -4.8499 | -5.4154 | -6.3152 | 2.9516 | 2.732 | 2.5149 | 2.3128 | 2.0461 | 1.7663 | 1.4593 | 1.1061 | 0.70639 | 0.40407 | -0.14148 | -0.69698 | -1.341 | -2.0194 | 1.2115 | 0.79418 | 0.38136 | -0.0047559 | -0.54213 | -1.0881 | -1.6569 | -2.2572 | -2.8677 | -3.3552 | -4.4095 | -5.5013 | -6.0308 | -6.8786
|  | WEST GRAFTON VILLAGE | CT |  |  | 2.7876 | 2.5121 | 2.2431 | 2.0056 | 1.6629 | 1.3064 | 0.91385 | 0.49695 | 0.082454 | -0.43955 | -1.4204 | -2.8464 | -3.7791 | -4.1869 | 3.0471 | 2.883 | 2.7156 | 2.559 | 2.3717 | 2.1721 | 1.9413 | 1.6879 | 1.415 | 1.0824 | 0.52857 | -0.20493 | -0.71708 | -1.152 | 1.4869 | 1.2481 | 1.0082 | 0.78947 | 0.48913 | 0.1604 | -0.20413 | -0.59334 | -0.98527 | -1.4782 | -2.3825 | -3.6656 | -4.4889 | -4.8739
|  | WEST GRAFTON VILLAGE | LW |  |  | 2.4342 | 1.9698 | 1.5164 | 1.0988 | 0.51952 | -0.070943 | -0.68843 | -1.3446 | -2.0177 | -2.5506 | -3.6808 | -4.8499 | -5.1538 | -5.3819 | 2.9516 | 2.732 | 2.5149 | 2.3128 | 2.0461 | 1.7663 | 1.4593 | 1.1061 | 0.70639 | 0.40407 | -0.14148 | -0.69698 | -0.81623 | -0.89703 | 1.2115 | 0.79418 | 0.38136 | -0.0047559 | -0.54213 | -1.0881 | -1.6569 | -2.2572 | -2.8677 | -3.3552 | -4.4095 | -5.5013 | -5.7863 | -6.0011
|  | WEST GRAFTON VILLAGE | ST |  |  | 2.9458 | 2.7727 | 2.6079 | 2.4602 | 2.2492 | 2.0238 | 1.787 | 1.5331 | 1.2581 | 0.96516 | -0.2623 | -1.9397 | -2.6966 | -3.0613 | 3.163 | 3.0683 | 2.9724 | 2.881 | 2.7655 | 2.6394 | 2.5018 | 2.3502 | 2.1797 | 2.0136 | 1.218 | 0.19827 | -0.2987 | -0.7222 | 1.6414 | 1.4999 | 1.3593 | 1.2278 | 1.0453 | 0.84427 | 0.6263 | 0.39146 | 0.13524 | -0.13519 | -1.2939 | -2.8452 | -3.5238 | -3.8442
|  | WEST GRAFTON VILLAGE | SP |  |  | 2.9883 | 2.8428 | 2.7166 | 2.6158 | 2.322 | 2.0215 | 1.7134 | 1.3851 | 1.0561 | 0.63374 | -0.76806 | -3.7948 | -5.4154 | -6.3152 | 3.1757 | 3.089 | 3.009 | 2.9405 | 2.8093 | 2.6717 | 2.5283 | 2.3653 | 2.2002 | 1.9966 | 1.2658 | -0.44892 | -1.341 | -2.0194 | 1.6746 | 1.5546 | 1.4467 | 1.3566 | 1.1152 | 0.85169 | 0.56812 | 0.26455 | -0.04028 | -0.43258 | -1.7267 | -4.5098 | -6.0308 | -6.8786
AXMINSTER | YEOVIL BSP | WEST HENDFORD | MINIMUM HEADROOM | ST 55000 15442 | YES | 7.6754 | 7.1309 | 6.5369 | 5.8671 | 4.9818 | 4.0555 | 3.0508 | 1.9501 | 0.68447 | -0.48353 | -3.2259 | -6.5992 | -8.1543 | -9.4689 | 13.7124 | 13.3842 | 13.0256 | 12.6143 | 12.1231 | 11.5977 | 11.0017 | 10.3347 | 9.4937 | 8.7244 | 7.1209 | 5.2449 | 3.5335 | 2.0617 | 10.4323 | 9.9477 | 9.4179 | 8.8149 | 8.0481 | 7.2362 | 6.3356 | 5.338 | 4.1309 | 3.0098 | 0.47334 | -2.5683 | -3.7771 | -4.8606
|  | WEST HENDFORD | CT |  |  | 7.8834 | 7.4783 | 7.0002 | 6.455 | 5.8327 | 5.1811 | 4.4873 | 3.716 | 2.8902 | 1.6743 | -1.0348 | -5.3145 | -8.1543 | -9.4689 | 13.7379 | 13.4428 | 13.0939 | 12.6978 | 12.2927 | 11.8606 | 11.3841 | 10.8482 | 10.2449 | 9.4256 | 7.7152 | 5.2449 | 3.5335 | 2.0617 | 10.5604 | 10.1792 | 9.7258 | 9.2092 | 8.647 | 8.052 | 7.4066 | 6.6843 | 5.8877 | 4.7555 | 2.353 | -1.4121 | -3.7771 | -4.8606
|  | WEST HENDFORD | LW |  |  | 7.6754 | 7.1309 | 6.5369 | 5.8671 | 4.9818 | 4.0555 | 3.0508 | 1.9501 | 0.68447 | -0.48353 | -3.2259 | -6.5992 | -7.8076 | -8.372 | 13.7124 | 13.3842 | 13.0256 | 12.6143 | 12.1231 | 11.5977 | 11.0017 | 10.3347 | 9.4937 | 8.7244 | 7.1209 | 5.2782 | 4.7385 | 4.4766 | 10.4323 | 9.9477 | 9.4179 | 8.8149 | 8.0481 | 7.2362 | 6.3356 | 5.338 | 4.1309 | 3.0098 | 0.47334 | -2.5683 | -3.585 | -4.0541
|  | WEST HENDFORD | ST |  |  | 8.1834 | 7.9742 | 7.7264 | 7.4405 | 7.1232 | 6.7914 | 6.4345 | 6.0299 | 5.6 | 5.1733 | 3.2749 | -0.16967 | -1.9514 | -3.0011 | 13.9703 | 13.8162 | 13.6291 | 13.4094 | 13.1717 | 12.9193 | 12.6409 | 12.3221 | 11.9697 | 11.6376 | 10.1009 | 7.4179 | 5.8753 | 4.4713 | 10.8745 | 10.6901 | 10.4647 | 10.2 | 9.9032 | 9.5898 | 9.248 | 8.858 | 8.4338 | 8.0206 | 6.1289 | 2.9208 | 1.3795 | 0.51327
|  | WEST HENDFORD | SP |  |  | 8.2221 | 8.0351 | 7.8295 | 7.5993 | 7.3298 | 7.0495 | 6.7493 | 6.4112 | 6.0694 | 5.6835 | 4.3329 | 0.65388 | -1.3866 | -2.2887 | 13.9828 | 13.8341 | 13.6686 | 13.4799 | 13.2899 | 13.0891 | 12.8635 | 12.6009 | 12.3227 | 12.02 | 10.884 | 7.7815 | 5.6413 | 3.6505 | 10.9045 | 10.7361 | 10.5509 | 10.3402 | 10.1013 | 9.8511 | 9.576 | 9.2588 | 8.931 | 8.5655 | 7.2311 | 3.6938 | 1.8511 | 1.0861
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR | MINIMUM HEADROOM | ST 77699 22040 | YES | 17.6847 | 17.2812 | 16.7266 | 16.0986 | 15.1895 | 14.1753 | 13.0576 | 11.9229 | 10.5839 | 9.0958 | 5.3742 | 0.80176 | -2.3218 | -4.8057 | 9.2399 | 9.1349 | 8.9928 | 8.8268 | 8.5562 | 8.0124 | 7.3946 | 6.7558 | 5.9595 | 5.0186 | 2.728 | 0.01169 | -2.5432 | -4.9322 | 9.0738 | 8.7125 | 8.2135 | 7.643 | 6.8159 | 5.8962 | 4.8801 | 3.8399 | 2.615 | 1.2283 | -2.2668 | -6.4136 | -9.002 | -11.1043
|  | WEST STOUR | CT |  |  | 17.6847 | 17.5761 | 17.3114 | 16.7896 | 16.1672 | 15.4538 | 14.673 | 13.8889 | 12.9678 | 11.5227 | 7.6917 | 1.9615 | -2.3218 | -4.8057 | 9.244 | 9.1482 | 9.0219 | 8.854 | 8.6808 | 8.393 | 7.9044 | 7.4037 | 6.8025 | 5.8538 | 3.36 | 0.01169 | -2.5432 | -4.9322 | 9.2569 | 9.0561 | 8.731 | 8.2592 | 7.6992 | 7.0629 | 6.3664 | 5.6364 | 4.7727 | 3.4132 | -0.18432 | -5.3287 | -9.002 | -11.1043
|  | WEST STOUR | LW |  |  | 17.6873 | 17.2812 | 16.7266 | 16.0986 | 15.1895 | 14.1753 | 13.0576 | 11.9229 | 10.5839 | 9.0958 | 5.3742 | 0.80176 | -1.4487 | -3.0049 | 9.2399 | 9.1349 | 8.9928 | 8.8268 | 8.5562 | 8.0124 | 7.3946 | 6.7558 | 5.9595 | 5.0186 | 2.728 | 0.18911 | -0.86981 | -1.6102 | 9.0738 | 8.7125 | 8.2135 | 7.643 | 6.8159 | 5.8962 | 4.8801 | 3.8399 | 2.615 | 1.2283 | -2.2668 | -6.4136 | -8.322 | -9.5858
|  | WEST STOUR | ST |  |  | 17.7741 | 17.7228 | 17.6358 | 17.5292 | 17.4233 | 17.1253 | 16.7393 | 16.3513 | 15.8953 | 15.3869 | 13.3566 | 8.6633 | 5.993 | 4.2195 | 9.3213 | 9.2752 | 9.2083 | 9.1271 | 9.034 | 8.9189 | 8.781 | 8.6385 | 8.45 | 8.0916 | 6.5511 | 2.9199 | 0.71489 | -1.3866 | 9.3823 | 9.3268 | 9.2429 | 9.1065 | 8.8736 | 8.5888 | 8.2586 | 7.9216 | 7.5206 | 7.0409 | 5.0787 | 0.66828 | -1.666 | -3.1472
|  | WEST STOUR | SP |  |  | 17.7785 | 17.7285 | 17.6442 | 17.5445 | 17.4615 | 17.3489 | 17.1066 | 16.833 | 16.5031 | 16.0927 | 14.6314 | 10.5403 | 7.6235 | 6.1807 | 9.3266 | 9.2809 | 9.2148 | 9.1378 | 9.0638 | 8.9706 | 8.8617 | 8.7489 | 8.6027 | 8.414 | 7.1942 | 3.6231 | 0.34172 | -3.0417 | 9.4037 | 9.3563 | 9.2837 | 9.181 | 9.02 | 8.8211 | 8.5954 | 8.362 | 8.0773 | 7.7094 | 6.3015 | 2.4259 | -0.22537 | -1.4446
MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE | MINIMUM HEADROOM | SZ 07642 91485 | YES | 2.9942 | 2.7156 | 2.4169 | 2.1089 | 1.7004 | 1.2779 | 0.83228 | 0.34823 | -0.24794 | -0.7829 | -1.8809 | -3.0347 | -3.2627 | -3.3922 | 3.4312 | 3.3035 | 3.1599 | 3.0083 | 2.8079 | 2.5961 | 2.3639 | 2.1038 | 1.7596 | 1.454 | 0.93349 | 0.41604 | 0.32916 | 0.20017 | 1.7267 | 1.4738 | 1.2012 | 0.91921 | 0.54712 | 0.16156 | -0.24742 | -0.6939 | -1.2504 | -1.7487 | -2.7418 | -3.7802 | -3.9812 | -4.0942
|  | WESTBOURNE | CT |  |  | 3.2524 | 3.1159 | 2.959 | 2.7817 | 2.5379 | 2.2818 | 2.0084 | 1.696 | 1.3329 | 0.86471 | -0.063242 | -1.3918 | -2.1947 | -2.4977 | 3.5013 | 3.4172 | 3.3161 | 3.1971 | 3.0597 | 2.9129 | 2.755 | 2.5664 | 2.333 | 2.0406 | 1.5418 | 0.89416 | 0.48177 | 0.20017 | 1.9507 | 1.823 | 1.6752 | 1.5069 | 1.2809 | 1.0432 | 0.7891 | 0.49681 | 0.15368 | -0.28824 | -1.1407 | -2.3275 | -3.0342 | -3.2994
|  | WESTBOURNE | LW |  |  | 2.9942 | 2.7156 | 2.4169 | 2.1089 | 1.7004 | 1.2779 | 0.83228 | 0.34823 | -0.24794 | -0.7829 | -1.8809 | -3.0347 | -3.2627 | -3.3922 | 3.4312 | 3.3035 | 3.1599 | 3.0083 | 2.8079 | 2.5961 | 2.3639 | 2.1038 | 1.7596 | 1.454 | 0.93349 | 0.41604 | 0.32916 | 0.28385 | 1.7267 | 1.4738 | 1.2012 | 0.91921 | 0.54712 | 0.16156 | -0.24742 | -0.6939 | -1.2504 | -1.7487 | -2.7418 | -3.7802 | -3.9812 | -4.0942
|  | WESTBOURNE | ST |  |  | 3.3684 | 3.3014 | 3.2205 | 3.1323 | 2.9885 | 2.8391 | 2.6847 | 2.5164 | 2.3294 | 2.129 | 1.2734 | 0.13051 | -0.39016 | -0.68759 | 3.5753 | 3.5353 | 3.4833 | 3.4243 | 3.3415 | 3.254 | 3.1603 | 3.0553 | 2.9347 | 2.8174 | 2.2545 | 1.5216 | 1.1905 | 0.91158 | 2.0609 | 1.9993 | 1.9237 | 1.8408 | 1.7078 | 1.5693 | 1.4255 | 1.2682 | 1.0925 | 0.9061 | 0.094538 | -0.97508 | -1.4401 | -1.7004
|  | WESTBOURNE | SP |  |  | 3.4078 | 3.3561 | 3.2996 | 3.2413 | 3.1049 | 2.9593 | 2.8179 | 2.66 | 2.4932 | 2.2591 | 1.4405 | -0.48583 | -1.5297 | -2.1661 | 3.5856 | 3.5476 | 3.5048 | 3.4596 | 3.3889 | 3.3118 | 3.2356 | 3.1453 | 3.0474 | 2.9275 | 2.4677 | 1.2758 | 0.71121 | 0.33631 | 2.0951 | 2.0463 | 1.9928 | 1.9375 | 1.8131 | 1.6801 | 1.5509 | 1.4054 | 1.2513 | 1.0374 | 0.28087 | -1.5177 | -2.4596 | -3.0223
MELKSHAM GSP | FROME BSP | WESTBURY | MINIMUM HEADROOM | ST 87654 51530 | YES | 42.0579 | 41.9798 | 41.6703 | 41.081 | 40.2732 | 39.434 | 38.6269 | 37.8532 | 37.0239 | 36.1426 | 33.4195 | 30.986 | 30.1546 | 29.6216 | 35.5098 | 35.3528 | 35.1237 | 34.8555 | 34.5005 | 34.1265 | 33.7544 | 33.3857 | 32.9694 | 32.5171 | 31.1123 | 29.7403 | 27.9113 | 24.871 | 36.568 | 36.4524 | 36.2585 | 35.8824 | 35.3318 | 34.7557 | 34.1401 | 33.4941 | 32.8018 | 32.0652 | 29.6995 | 27.5076 | 26.805 | 26.3628
|  | WESTBURY | CT |  |  | 42.0579 | 41.9798 | 41.8214 | 41.615 | 41.2991 | 40.8328 | 40.2483 | 39.6681 | 39.041 | 38.2228 | 35.6131 | 32.5818 | 30.796 | 29.8812 | 35.6217 | 35.5228 | 35.3582 | 35.1405 | 34.8654 | 34.5739 | 34.2759 | 33.9703 | 33.6282 | 33.1978 | 31.7098 | 29.7403 | 28.2517 | 26.6074 | 36.568 | 36.4524 | 36.2699 | 36.0412 | 35.7944 | 35.5261 | 35.2418 | 34.886 | 34.4447 | 33.8739 | 31.6428 | 28.9433 | 27.3969 | 26.6199
|  | WESTBURY | LW |  |  | 42.0694 | 41.9835 | 41.6703 | 41.081 | 40.2732 | 39.434 | 38.6269 | 37.8532 | 37.0239 | 36.1426 | 33.4195 | 30.986 | 30.1546 | 29.6216 | 35.5098 | 35.3528 | 35.1237 | 34.8555 | 34.5005 | 34.1265 | 33.7544 | 33.3857 | 32.9694 | 32.5171 | 31.1123 | 29.7849 | 29.4108 | 29.1642 | 36.5825 | 36.4526 | 36.2585 | 35.8824 | 35.3318 | 34.7557 | 34.1401 | 33.4941 | 32.8018 | 32.0652 | 29.6995 | 27.5076 | 26.805 | 26.3628
|  | WESTBURY | ST |  |  | 42.1282 | 42.0938 | 41.9923 | 41.8616 | 41.706 | 41.5394 | 41.3642 | 41.0721 | 40.6358 | 40.1423 | 38.3525 | 35.2087 | 33.6618 | 33.5016 | 35.6814 | 35.6209 | 35.5203 | 35.3985 | 35.2323 | 35.0546 | 34.8671 | 34.6585 | 34.4098 | 34.1298 | 33.0839 | 30.9758 | 29.4861 | 27.9324 | 36.6754 | 36.6267 | 36.5292 | 36.4059 | 36.249 | 36.0755 | 35.8859 | 35.6689 | 35.3758 | 35.0319 | 33.6783 | 30.7336 | 29.4548 | 29.1809
|  | WESTBURY | SP |  |  | 42.1302 | 42.0995 | 42.0013 | 41.8767 | 41.7398 | 41.5963 | 41.4424 | 41.0279 | 40.58 | 40.049 | 38.2826 | 35.0744 | 32.7384 | 32.0386 | 35.6947 | 35.642 | 35.5499 | 35.4397 | 35.2562 | 35.0649 | 34.8625 | 34.6415 | 34.3935 | 34.1004 | 33.0828 | 30.63 | 27.9113 | 24.871 | 36.6775 | 36.6366 | 36.5448 | 36.4316 | 36.2965 | 36.1526 | 35.9985 | 35.8231 | 35.5802 | 35.2147 | 34.0028 | 31.262 | 29.137 | 28.532
NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE | MINIMUM HEADROOM | SU 41618 12009 | YES | 4.2529 | 4.0415 | 3.7895 | 3.5343 | 3.1884 | 2.8278 | 2.4324 | 1.991 | 1.4308 | 0.95529 | 0.0011882 | -1.0597 | -1.3404 | -1.525 | 4.1565 | 4.0477 | 3.9069 | 3.7626 | 3.5733 | 3.3752 | 3.1631 | 2.9165 | 2.5865 | 2.316 | 1.8942 | 1.4459 | 1.3395 | 1.2658 | 2.4542 | 2.2377 | 1.9929 | 1.7456 | 1.4047 | 1.0547 | 0.69628 | 0.30194 | -0.18702 | -0.61172 | -1.5484 | -2.5863 | -2.8426 | -3.0108
|  | WESTERN ESPLANADE | CT |  |  | 4.4631 | 4.3566 | 4.2397 | 4.0712 | 3.8624 | 3.6394 | 3.3915 | 3.1023 | 2.7643 | 2.3231 | 1.5602 | 0.23641 | -0.66653 | -1.0205 | 4.238 | 4.17 | 4.0937 | 3.9764 | 3.8475 | 3.7076 | 3.5531 | 3.3676 | 3.1433 | 2.8575 | 2.4519 | 1.8735 | 1.4787 | 1.2658 | 2.6932 | 2.5947 | 2.4884 | 2.3455 | 2.1516 | 1.9465 | 1.7176 | 1.4572 | 1.1474 | 0.73482 | -0.022506 | -1.3073 | -2.2003 | -2.5425
|  | WESTERN ESPLANADE | LW |  |  | 4.2529 | 4.0415 | 3.7895 | 3.5343 | 3.1884 | 2.8278 | 2.4324 | 1.991 | 1.4308 | 0.95529 | 0.0011882 | -1.0597 | -1.3404 | -1.525 | 4.1565 | 4.0477 | 3.9069 | 3.7626 | 3.5733 | 3.3752 | 3.1631 | 2.9165 | 2.5865 | 2.316 | 1.8942 | 1.4459 | 1.3395 | 1.2711 | 2.4542 | 2.2377 | 1.9929 | 1.7456 | 1.4047 | 1.0547 | 0.69628 | 0.30194 | -0.18702 | -0.61172 | -1.5484 | -2.5863 | -2.8426 | -3.0108
|  | WESTERN ESPLANADE | ST |  |  | 4.5311 | 4.4718 | 4.4052 | 4.3263 | 4.1934 | 4.0542 | 3.911 | 3.7566 | 3.5835 | 3.4066 | 2.6167 | 1.6975 | 1.1978 | 0.86648 | 4.2858 | 4.2503 | 4.209 | 4.1575 | 4.077 | 3.9912 | 3.9009 | 3.8018 | 3.687 | 3.5771 | 3.0455 | 2.4636 | 2.2032 | 1.9959 | 2.7505 | 2.6922 | 2.6287 | 2.5562 | 2.4309 | 2.3007 | 2.1681 | 2.0268 | 1.8724 | 1.7062 | 1.0007 | 0.098747 | -0.37652 | -0.69843
|  | WESTERN ESPLANADE | SP |  |  | 4.56 | 4.5079 | 4.4512 | 4.3957 | 4.2459 | 4.1027 | 3.9544 | 3.7955 | 3.6391 | 3.4174 | 2.6681 | 0.87188 | 0.011093 | -0.54464 | 4.2969 | 4.2614 | 4.222 | 4.1827 | 4.101 | 4.0216 | 3.9397 | 3.8484 | 3.7574 | 3.6361 | 3.196 | 2.128 | 1.7257 | 1.4658 | 2.7833 | 2.7361 | 2.6854 | 2.6358 | 2.4852 | 2.3422 | 2.1926 | 2.0363 | 1.8829 | 1.6603 | 0.94093 | -0.66552 | -1.5033 | -2.0519
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON | MINIMUM HEADROOM | SU 45207 09912 | YES | 13.9966 | 13.5184 | 12.9822 | 12.3986 | 11.3362 | 10.2108 | 9.0331 | 7.7719 | 6.3703 | 4.9063 | 0.31359 | -6.8398 | -11.4503 | -15.6949 | 19.5398 | 19.2753 | 18.9744 | 18.6388 | 18.0982 | 17.5156 | 16.8858 | 16.2024 | 15.3899 | 14.5269 | 11.7868 | 6.1081 | 0.61151 | -8.1611 | 16.056 | 15.6489 | 15.1856 | 14.6768 | 13.7356 | 12.7288 | 11.6673 | 10.5272 | 9.2444 | 7.8987 | 3.663 | -2.7665 | -6.5225 | -10.0672
|  | WESTON | CT |  |  | 14.2691 | 13.9466 | 13.5804 | 13.1328 | 12.3751 | 11.5637 | 10.7757 | 9.9203 | 8.9423 | 7.5677 | 3.3376 | -4.9786 | -11.4503 | -15.6949 | 19.582 | 19.3219 | 19.0303 | 18.6699 | 18.1662 | 17.6188 | 17.0549 | 16.4349 | 15.7077 | 14.7968 | 11.8983 | 6.1081 | 0.61151 | -5.6956 | 16.2625 | 15.9773 | 15.6506 | 15.2429 | 14.5919 | 13.8903 | 13.1994 | 12.4256 | 11.5297 | 10.275 | 6.4066 | -0.99745 | -6.5225 | -10.0672
|  | WESTON | LW |  |  | 13.9966 | 13.5184 | 12.9822 | 12.3986 | 11.3362 | 10.2108 | 9.0331 | 7.7719 | 6.3703 | 4.9063 | 0.31359 | -6.8398 | -10.9924 | -14.1887 | 19.5398 | 19.2753 | 18.9744 | 18.6388 | 18.0982 | 17.5156 | 16.8858 | 16.2024 | 15.3899 | 14.5269 | 11.7868 | 7.6952 | 5.6329 | 4.0223 | 16.056 | 15.6489 | 15.1856 | 14.6768 | 13.7356 | 12.7288 | 11.6673 | 10.5272 | 9.2444 | 7.8987 | 3.663 | -2.7665 | -6.2427 | -8.8692
|  | WESTON | ST |  |  | 14.5483 | 14.3931 | 14.2259 | 14.0388 | 13.7175 | 13.3712 | 13.0098 | 12.6101 | 12.1422 | 11.6068 | 9.6835 | 4.3176 | 0.058445 | -2.9632 | 19.7532 | 19.5922 | 19.4211 | 19.2277 | 18.9459 | 18.6395 | 18.3069 | 17.9346 | 17.4947 | 17.0255 | 15.277 | 10.4024 | 5.4989 | -0.32209 | 16.5164 | 16.3816 | 16.235 | 16.0688 | 15.7904 | 15.4887 | 15.1702 | 14.8157 | 14.3943 | 13.9156 | 12.1606 | 7.3184 | 3.7181 | 1.2765
|  | WESTON | SP |  |  | 14.614 | 14.4646 | 14.3121 | 14.1451 | 13.8789 | 13.5956 | 13.3061 | 12.9884 | 12.6276 | 12.1871 | 10.7215 | 6.3941 | 2.0506 | -0.72175 | 19.7802 | 19.6079 | 19.4243 | 19.2199 | 18.9412 | 18.6313 | 18.2925 | 17.9149 | 17.4748 | 16.977 | 15.177 | 9.9181 | 2.4177 | -8.1611 | 16.5753 | 16.4416 | 16.3049 | 16.1539 | 15.9266 | 15.682 | 15.4281 | 15.1481 | 14.8253 | 14.4371 | 13.1245 | 9.2231 | 5.4102 | 3.1351
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH | MINIMUM HEADROOM | SY 67443 79096 | YES | 14.1265 | 13.3139 | 12.3961 | 11.4118 | 10.1072 | 8.753 | 7.3777 | 5.9311 | 4.2229 | 2.4353 | -2.009 | -7.0496 | -9.326 | -11.4255 | 18.9493 | 18.4982 | 17.9546 | 17.3576 | 16.6537 | 15.9102 | 15.1512 | 14.3447 | 13.3327 | 12.2784 | 9.8442 | 7.4203 | 5.3689 | 3.5249 | 15.7528 | 15.0246 | 14.1866 | 13.2818 | 12.092 | 10.8529 | 9.5886 | 8.2551 | 6.6623 | 4.9622 | 0.90745 | -3.6427 | -5.6139 | -7.4591
|  | WEYMOUTH | CT |  |  | 14.6677 | 14.1501 | 13.5795 | 12.8348 | 11.9733 | 11.0719 | 10.1697 | 9.2006 | 8.0813 | 6.3706 | 2.0936 | -4.5273 | -9.326 | -11.4255 | 19.1216 | 18.7683 | 18.3661 | 17.8392 | 17.2952 | 16.7196 | 16.1535 | 15.5446 | 14.8267 | 13.759 | 11.1845 | 7.8317 | 5.3689 | 3.5249 | 16.2227 | 15.7474 | 15.2168 | 14.5177 | 13.7158 | 12.874 | 12.0287 | 11.1178 | 10.0571 | 8.4482 | 4.4773 | -1.3843 | -5.6139 | -7.4591
|  | WEYMOUTH | LW |  |  | 14.1265 | 13.3139 | 12.3961 | 11.4118 | 10.1072 | 8.753 | 7.3777 | 5.9311 | 4.2229 | 2.4353 | -2.009 | -7.0496 | -8.6496 | -9.6776 | 18.9493 | 18.4982 | 17.9546 | 17.3576 | 16.6537 | 15.9102 | 15.1512 | 14.3447 | 13.3327 | 12.2784 | 9.8442 | 7.4203 | 6.781 | 6.3741 | 15.7528 | 15.0246 | 14.1866 | 13.2818 | 12.092 | 10.8529 | 9.5886 | 8.2551 | 6.6623 | 4.9622 | 0.90745 | -3.6427 | -5.0568 | -5.96
|  | WEYMOUTH | ST |  |  | 14.9358 | 14.5859 | 14.2055 | 13.7781 | 13.2836 | 12.7672 | 12.2614 | 11.7333 | 11.1316 | 10.5042 | 7.9046 | 2.9682 | 0.51539 | -1.0102 | 19.308 | 19.0649 | 18.7859 | 18.4656 | 18.1229 | 17.7601 | 17.4086 | 17.0405 | 16.6251 | 16.2089 | 14.4383 | 10.9448 | 9.1494 | 7.5462 | 16.4818 | 16.1732 | 15.8287 | 15.4361 | 14.978 | 14.4977 | 14.0249 | 13.5177 | 12.9474 | 12.3581 | 9.8769 | 5.2066 | 2.9872 | 1.6439
|  | WEYMOUTH | SP |  |  | 15.0121 | 14.6836 | 14.3471 | 13.97 | 13.3928 | 12.7902 | 12.2331 | 11.6533 | 11.0283 | 10.3067 | 7.8634 | 2.1297 | -1.1028 | -2.6971 | 19.3358 | 19.0905 | 18.8242 | 18.5211 | 18.1719 | 17.8033 | 17.4706 | 17.1177 | 16.7301 | 16.2882 | 14.698 | 10.7054 | 7.7685 | 4.8864 | 16.5494 | 16.2573 | 15.9514 | 15.6037 | 15.0797 | 14.5312 | 14.0239 | 13.4934 | 12.9191 | 12.2589 | 10.0003 | 4.5692 | 1.5769 | 0.16923
COWLEY GSP | HEADINGTON BSP | WHEATLEY | MINIMUM HEADROOM | SP 60777 05379 | NO | 27.0242 | 26.429 | 25.5491 | 24.3273 | 23.1077 | 21.5727 | 20.1562 | 18.7029 | 17.1194 | 15.5343 | 10.3273 | 4.477 | 1.8686 | -0.59315 | 17.3029 | 17.0209 | 16.7197 | 16.322 | 15.881 | 15.3168 | 14.7918 | 14.2405 | 13.5845 | 12.7654 | 10.241 | 6.9065 | 3.7334 | 0.59046 | 14.0727 | 13.6479 | 12.863 | 11.8149 | 10.7114 | 9.3376 | 8.066 | 6.7562 | 5.3251 | 3.8913 | -0.48986 | -5.5142 | -7.6933 | -9.666
|  | WHEATLEY | CT |  |  | 27.1439 | 26.6918 | 26.1435 | 25.2032 | 24.274 | 23.0395 | 22.008 | 20.954 | 19.7898 | 18.3159 | 13.5544 | 6.5788 | 2.0356 | -0.59315 | 17.3101 | 17.0417 | 16.7472 | 16.3538 | 15.9374 | 15.4046 | 14.9353 | 14.4476 | 13.9029 | 13.2832 | 11.1803 | 6.9065 | 3.7334 | 0.59046 | 14.0727 | 13.7121 | 13.3263 | 12.5822 | 11.7347 | 10.6264 | 9.6969 | 8.7426 | 7.6889 | 6.3736 | 2.4089 | -3.5766 | -7.4665 | -9.666
|  | WHEATLEY | LW |  |  | 27.0242 | 26.429 | 25.5491 | 24.3273 | 23.1077 | 21.5727 | 20.1562 | 18.7029 | 17.1194 | 15.5343 | 10.3273 | 4.477 | 1.8686 | 0.22306 | 17.3029 | 17.0209 | 16.7197 | 16.322 | 15.881 | 15.3168 | 14.7918 | 14.2405 | 13.5845 | 12.7654 | 10.241 | 6.9753 | 5.6965 | 4.8476 | 14.0919 | 13.6479 | 12.863 | 11.8149 | 10.7114 | 9.3376 | 8.066 | 6.7562 | 5.3251 | 3.8913 | -0.48986 | -5.5142 | -7.6933 | -9.0279
|  | WHEATLEY | ST |  |  | 27.2803 | 26.9646 | 26.636 | 26.1855 | 25.8275 | 25.3156 | 24.8816 | 24.4367 | 23.9132 | 23.2381 | 20.8805 | 15.8864 | 12.5244 | 10.532 | 17.4272 | 17.2472 | 17.0559 | 16.7976 | 16.4929 | 16.0857 | 15.7312 | 15.3597 | 14.9287 | 14.4491 | 12.8473 | 9.707 | 7.6846 | 4.7941 | 14.2 | 13.9269 | 13.6414 | 13.2507 | 12.9099 | 12.4333 | 12.029 | 11.6122 | 11.1228 | 10.5836 | 8.604 | 3.9784 | 0.73649 | -0.26897
|  | WHEATLEY | SP |  |  | 27.2878 | 26.9843 | 26.6682 | 26.237 | 25.9086 | 25.4384 | 25.0454 | 24.6492 | 24.2083 | 23.7402 | 22.3292 | 18.6503 | 14.9298 | 12.9756 | 17.4337 | 17.263 | 17.0802 | 16.8366 | 16.5566 | 16.1843 | 15.8621 | 15.5283 | 15.161 | 14.748 | 13.4687 | 10.863 | 7.5134 | 2.7728 | 14.2069 | 13.945 | 13.6709 | 13.2981 | 12.9848 | 12.5472 | 12.1811 | 11.8102 | 11.3987 | 10.9612 | 9.639 | 6.879 | 2.6573 | 1.2162
BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH | MINIMUM HEADROOM | SU 45924 48466 | YES | 14.0652 | 13.8362 | 13.5611 | 13.2665 | 12.7117 | 12.1336 | 11.5249 | 10.7817 | 9.8786 | 8.9201 | 6.0416 | 1.6545 | -2.7612 | -5.8089 | 12.7648 | 12.6311 | 12.4142 | 12.1762 | 11.8273 | 11.4563 | 11.044 | 10.6033 | 10.0506 | 9.4451 | 7.6898 | 4.784 | 1.8036 | -1.1746 | 9.4177 | 9.1733 | 8.8441 | 8.4864 | 7.8971 | 7.2767 | 6.607 | 5.897 | 5.023 | 4.0839 | 1.3245 | -2.5387 | -6.1711 | -8.6878
|  | WHITCHURCH | CT |  |  | 14.2157 | 14.0711 | 13.908 | 13.6821 | 13.3268 | 12.9511 | 12.5451 | 12.0275 | 11.442 | 10.5071 | 7.5023 | 1.9576 | -2.7612 | -5.8089 | 12.8041 | 12.6837 | 12.5319 | 12.2834 | 11.9913 | 11.6774 | 11.3321 | 10.9577 | 10.5338 | 9.9237 | 7.9658 | 4.784 | 1.8036 | -1.1746 | 9.5388 | 9.3681 | 9.1723 | 8.8567 | 8.4388 | 7.9932 | 7.5063 | 6.983 | 6.402 | 5.4994 | 2.6427 | -2.224 | -6.1711 | -8.6878
|  | WHITCHURCH | LW |  |  | 14.0652 | 13.8362 | 13.5611 | 13.2665 | 12.7117 | 12.1336 | 11.5249 | 10.7817 | 9.8786 | 8.9201 | 6.0416 | 1.6545 | -1.2808 | -3.3975 | 12.7648 | 12.6311 | 12.4142 | 12.1762 | 11.8273 | 11.4563 | 11.044 | 10.6033 | 10.0506 | 9.4451 | 7.6898 | 5.3507 | 3.9596 | 2.8955 | 9.4177 | 9.1733 | 8.8441 | 8.4864 | 7.8971 | 7.2767 | 6.607 | 5.897 | 5.023 | 4.0839 | 1.3245 | -2.5387 | -4.9794 | -6.7022
|  | WHITCHURCH | ST |  |  | 14.3388 | 14.276 | 14.2064 | 14.1286 | 14.0048 | 13.8704 | 13.729 | 13.573 | 13.3882 | 13.1578 | 12.0701 | 8.3954 | 5.7165 | 3.5474 | 12.8871 | 12.8265 | 12.7582 | 12.6775 | 12.5339 | 12.3762 | 12.204 | 12.0104 | 11.7842 | 11.5444 | 10.5199 | 7.6132 | 5.2808 | 2.6386 | 9.6908 | 9.6183 | 9.5348 | 9.4374 | 9.2722 | 9.0912 | 8.8964 | 8.6783 | 8.4209 | 8.143 | 6.9647 | 3.5669 | 1.2893 | -0.46044
|  | WHITCHURCH | SP |  |  | 14.3641 | 14.305 | 14.2402 | 14.171 | 14.0688 | 13.9653 | 13.8585 | 13.7406 | 13.6097 | 13.4331 | 12.7146 | 9.8728 | 7.2253 | 5.5835 | 12.8968 | 12.8282 | 12.7518 | 12.653 | 12.536 | 12.4099 | 12.2719 | 12.1144 | 11.9346 | 11.697 | 10.739 | 7.8172 | 4.1918 | -0.60299 | 9.7156 | 9.6338 | 9.545 | 9.4463 | 9.3212 | 9.1914 | 9.0529 | 8.8952 | 8.7171 | 8.4992 | 7.6342 | 4.9666 | 2.6294 | 1.251
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY | MINIMUM HEADROOM | SU 52936 08794 | NO | 4.6376 | 32.0914 | 31.1635 | 30.1567 | 28.0169 | 26.0284 | 24.0315 | 22.0543 | 19.7578 | 17.309 | 10.3202 | 1.8268 | -4.4914 | -8.3212 | 11.6161 | 36.4105 | 35.8697 | 35.2722 | 34.1465 | 33.0886 | 31.9596 | 30.8105 | 29.4001 | 27.8748 | 23.6158 | 16.8453 | 10.7559 | 0.31942 | 6.7323 | 31.2674 | 30.4022 | 29.4557 | 27.5776 | 25.8031 | 23.9839 | 22.1575 | 19.9898 | 17.6635 | 11.0865 | 3.4834 | -1.4804 | -4.7741
|  | WHITELEY | CT |  |  | 5.0312 | 32.73 | 32.1584 | 31.3335 | 29.6931 | 28.2203 | 26.7598 | 25.3389 | 23.7802 | 21.4108 | 14.422 | 3.1789 | -4.4914 | -8.3212 | 11.6677 | 36.5241 | 36.1047 | 35.4812 | 34.4653 | 33.5028 | 32.4963 | 31.4787 | 30.3114 | 28.7334 | 23.9728 | 16.8453 | 10.7559 | 3.6962 | 7.0405 | 31.7797 | 31.2474 | 30.4326 | 28.9707 | 27.6294 | 26.2743 | 24.9332 | 23.4319 | 21.2045 | 14.6374 | 4.8594 | -1.4804 | -4.7741
|  | WHITELEY | LW |  |  | 4.6376 | 32.0914 | 31.1635 | 30.1567 | 28.0169 | 26.0284 | 24.0315 | 22.0543 | 19.7578 | 17.309 | 10.3202 | 1.8268 | -1.6129 | -3.6282 | 11.6161 | 36.4105 | 35.8697 | 35.2722 | 34.1465 | 33.0886 | 31.9596 | 30.8105 | 29.4001 | 27.8748 | 23.6158 | 19.0473 | 17.5886 | 16.7047 | 6.7323 | 31.2674 | 30.4022 | 29.4557 | 27.5776 | 25.8031 | 23.9839 | 22.1575 | 19.9898 | 17.6635 | 11.0865 | 3.4834 | 0.65392 | -0.98509
|  | WHITELEY | ST |  |  | 5.3799 | 33.3223 | 33.0291 | 32.7107 | 31.8529 | 31.1114 | 30.398 | 29.7047 | 28.9401 | 28.1008 | 24.9262 | 16.7678 | 12.1627 | 9.2767 | 11.7895 | 36.8796 | 36.6605 | 36.3879 | 35.7663 | 35.2003 | 34.6274 | 34.0421 | 33.3686 | 32.6483 | 29.7689 | 22.4767 | 16.8898 | 10.4196 | 7.388 | 32.3663 | 32.1056 | 31.8179 | 31.0629 | 30.389 | 29.7229 | 29.0564 | 28.3094 | 27.5113 | 24.3659 | 16.5377 | 12.4162 | 10.0768
|  | WHITELEY | SP |  |  | 5.4548 | 33.3922 | 33.1147 | 32.8155 | 32.0755 | 31.4212 | 30.8045 | 30.2128 | 29.5695 | 28.825 | 26.3336 | 19.8742 | 15.0723 | 13.0764 | 11.7956 | 36.8819 | 36.6379 | 36.3451 | 35.7941 | 35.2722 | 34.7422 | 34.1971 | 33.5829 | 32.8458 | 30.1492 | 22.5562 | 13.3069 | 0.31942 | 7.4527 | 32.4141 | 32.1585 | 31.879 | 31.2621 | 30.697 | 30.1475 | 29.6027 | 29.0007 | 28.3086 | 25.9139 | 19.5618 | 15.0988 | 13.3665
BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITELEY WOOD | MINIMUM HEADROOM | SU 52936 08794 | NO | 6.3334 | 5.8074 | 5.2309 | 4.6137 | 3.7698 | 2.8888 | 2.1355 | 1.3124 | 0.31329 | -0.67243 | -3.1606 | -5.9924 | -6.6666 | -7.0776 | 5.5161 | 5.2405 | 4.9279 | 4.5915 | 4.1709 | 3.7202 | 3.3112 | 2.8388 | 2.1847 | 1.5529 | 0.098116 | -1.5086 | -1.9148 | -2.5375 | 2.9323 | 2.4628 | 1.9424 | 1.3835 | 0.62654 | -0.16902 | -0.87171 | -1.6519 | -2.6547 | -3.6319 | -5.9187 | -8.4724 | -9.0502 | -9.3974
|  | WHITELEY WOOD | CT |  |  | 6.6268 | 6.2682 | 5.8599 | 5.399 | 4.8014 | 4.1747 | 3.6928 | 3.1498 | 2.5113 | 1.5931 | -0.63878 | -4.1245 | -6.1464 | -6.987 | 5.5622 | 5.3248 | 5.0515 | 4.7372 | 4.3902 | 4.0191 | 3.7066 | 3.3387 | 2.8748 | 2.2598 | 0.95327 | -0.94406 | -1.9148 | -2.5375 | 3.1553 | 2.8155 | 2.424 | 1.976 | 1.4248 | 0.84155 | 0.36823 | -0.17533 | -0.8333 | -1.7472 | -3.8318 | -6.8948 | -8.5548 | -9.2629
|  | WHITELEY WOOD | LW |  |  | 6.3334 | 5.8074 | 5.2309 | 4.6137 | 3.7698 | 2.8888 | 2.1355 | 1.3124 | 0.31329 | -0.67243 | -3.1606 | -5.9924 | -6.6666 | -7.0776 | 5.5161 | 5.2405 | 4.9279 | 4.5915 | 4.1709 | 3.7202 | 3.3112 | 2.8388 | 2.1847 | 1.5529 | 0.098116 | -1.5086 | -1.7767 | -1.9267 | 2.9323 | 2.4628 | 1.9424 | 1.3835 | 0.62654 | -0.16902 | -0.87171 | -1.6519 | -2.6547 | -3.6319 | -5.9187 | -8.4724 | -9.0502 | -9.3974
|  | WHITELEY WOOD | ST |  |  | 6.8051 | 6.593 | 6.3578 | 6.1022 | 5.7607 | 5.4047 | 5.1333 | 4.8342 | 4.4636 | 4.0464 | 2.3515 | -1.1013 | -2.7258 | -3.3696 | 5.7109 | 5.5844 | 5.4351 | 5.2657 | 5.0469 | 4.8172 | 4.6297 | 4.4181 | 4.1468 | 3.87 | 2.5939 | 0.17259 | -1.2743 | -1.4268 | 3.354 | 3.1712 | 2.9605 | 2.7257 | 2.408 | 2.0753 | 1.8055 | 1.5058 | 1.1294 | 0.72151 | -1.0408 | -4.3206 | -5.8208 | -6.3519
|  | WHITELEY WOOD | SP |  |  | 6.8459 | 6.6622 | 6.4642 | 6.2578 | 5.8797 | 5.4907 | 5.1818 | 4.8444 | 4.4736 | 4.0249 | 2.502 | -1.1942 | -3.5674 | -4.5976 | 5.7209 | 5.6017 | 5.4673 | 5.3238 | 5.132 | 4.9269 | 4.7683 | 4.5782 | 4.3598 | 4.1151 | 3.1895 | 0.65666 | -0.98629 | -1.8589 | 3.3857 | 3.225 | 3.0477 | 2.8607 | 2.5368 | 2.1987 | 1.923 | 1.6119 | 1.266 | 0.85592 | -0.59519 | -4.2676 | -6.4372 | -7.307
MINETY GSP | CIRENCESTER BSP | WHITEWAY | MINIMUM HEADROOM | SP 02076 03059 | NO | 1.4641 | 1.2685 | 1.0812 | 0.88732 | 0.59881 | 0.29662 | -0.030272 | -0.37318 | -0.79357 | -1.2459 | -2.3461 | -3.6495 | -4.354 | -4.8927 | 2.086 | 2.0004 | 1.9362 | 1.8746 | 1.8154 | 1.7199 | 1.5394 | 1.348 | 1.0908 | 0.81395 | 0.2091 | -0.63683 | -1.4793 | -2.4342 | 1.0496 | 0.86869 | 0.69461 | 0.51366 | 0.2487 | -0.029797 | -0.33308 | -0.65176 | -1.0479 | -1.4744 | -2.4956 | -3.6884 | -4.2556 | -4.7007
|  | WHITEWAY | CT |  |  | 1.5341 | 1.4231 | 1.292 | 1.1513 | 0.96226 | 0.7664 | 0.56206 | 0.33282 | 0.079411 | -0.34588 | -1.4259 | -3.1435 | -4.354 | -4.8927 | 2.086 | 2.0004 | 1.9362 | 1.8746 | 1.8154 | 1.7554 | 1.6643 | 1.5007 | 1.3149 | 1.0353 | 0.35582 | -0.63683 | -1.4793 | -2.343 | 1.1357 | 1.0023 | 0.87752 | 0.74277 | 0.56597 | 0.38242 | 0.18991 | -0.027001 | -0.26786 | -0.66892 | -1.6748 | -3.228 | -4.2556 | -4.7007
|  | WHITEWAY | LW |  |  | 1.4641 | 1.2685 | 1.0812 | 0.88732 | 0.59881 | 0.29662 | -0.030272 | -0.37318 | -0.79357 | -1.2459 | -2.3461 | -3.6495 | -4.1042 | -4.3176 | 2.0929 | 2.0064 | 1.943 | 1.8808 | 1.8182 | 1.7199 | 1.5394 | 1.348 | 1.0908 | 0.81395 | 0.2091 | -0.44382 | -0.62778 | -0.71258 | 1.0496 | 0.86869 | 0.69461 | 0.51366 | 0.2487 | -0.029797 | -0.33308 | -0.65176 | -1.0479 | -1.4744 | -2.4956 | -3.6884 | -4.0789 | -4.2572
|  | WHITEWAY | ST |  |  | 1.5699 | 1.5089 | 1.4623 | 1.4073 | 1.3121 | 1.2165 | 1.1088 | 0.99181 | 0.86014 | 0.71438 | 0.09173 | -1.1938 | -1.8553 | -2.2863 | 2.1165 | 2.0492 | 2.0076 | 1.9707 | 1.9345 | 1.9 | 1.8596 | 1.813 | 1.755 | 1.6893 | 1.1875 | 0.13044 | -0.56501 | -1.3648 | 1.2167 | 1.1341 | 1.0641 | 0.99143 | 0.90174 | 0.81143 | 0.70906 | 0.59763 | 0.47167 | 0.33339 | -0.26529 | -1.4878 | -2.0893 | -2.4709
|  | WHITEWAY | SP |  |  | 1.5719 | 1.5121 | 1.472 | 1.4343 | 1.3472 | 1.238 | 1.1267 | 1.0048 | 0.87126 | 0.71719 | 0.16973 | -1.2031 | -2.0026 | -2.3695 | 2.118 | 2.0517 | 2.0121 | 1.9791 | 1.9495 | 1.9221 | 1.8919 | 1.8573 | 1.8176 | 1.7125 | 1.2652 | 0.03865 | -1.0664 | -2.4342 | 1.2307 | 1.153 | 1.0933 | 1.0346 | 0.93572 | 0.83541 | 0.73278 | 0.61957 | 0.49491 | 0.35172 | -0.16239 | -1.4672 | -2.2166 | -2.5484
BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD | MINIMUM HEADROOM | SU 69235 73304 | YES | 10.1967 | 9.5942 | 8.8478 | 7.85 | 6.7083 | 5.5101 | 4.2559 | 2.8963 | 1.3981 | 0.064304 | -2.8448 | -6.1176 | -7.0479 | -7.9062 | 13.7781 | 13.2708 | 12.7869 | 12.334 | 11.8743 | 11.3882 | 10.8407 | 10.2121 | 9.3614 | 8.587 | 6.8788 | 4.9846 | 3.9579 | 3.0088 | 10.1294 | 9.6018 | 8.9388 | 8.1197 | 7.1573 | 6.1323 | 5.0389 | 3.8501 | 2.5365 | 1.3524 | -1.2801 | -4.261 | -5.0921 | -5.8614
|  | WILSON ROAD | CT |  |  | 10.1967 | 9.5996 | 9.0029 | 8.1141 | 7.1487 | 6.1358 | 5.1194 | 4.0205 | 2.8627 | 1.5236 | -1.297 | -5.1117 | -7.013 | -7.9062 | 13.7962 | 13.3124 | 12.8363 | 12.4013 | 11.9968 | 11.5725 | 11.1479 | 10.6093 | 9.9295 | 9.1531 | 7.4954 | 5.1786 | 3.9579 | 3.0088 | 10.1294 | 9.6018 | 9.0877 | 8.404 | 7.5958 | 6.7305 | 5.8614 | 4.9177 | 3.9161 | 2.7359 | 0.20804 | -3.296 | -5.0488 | -5.8614
|  | WILSON ROAD | LW |  |  | 10.22 | 9.5942 | 8.8478 | 7.85 | 6.7083 | 5.5101 | 4.2559 | 2.8963 | 1.3981 | 0.064304 | -2.8448 | -6.1176 | -7.0479 | -7.5128 | 13.7781 | 13.2708 | 12.7869 | 12.334 | 11.8743 | 11.3882 | 10.8407 | 10.2121 | 9.3614 | 8.587 | 6.8788 | 4.9846 | 4.5324 | 4.3014 | 10.1482 | 9.6054 | 8.9388 | 8.1197 | 7.1573 | 6.1323 | 5.0389 | 3.8501 | 2.5365 | 1.3524 | -1.2801 | -4.261 | -5.0921 | -5.4987
|  | WILSON ROAD | ST |  |  | 10.3977 | 9.924 | 9.47 | 9.07 | 8.7043 | 8.316 | 7.7576 | 7.0985 | 6.4222 | 5.7963 | 3.6508 | 0.14766 | -1.7695 | -2.0163 | 13.9467 | 13.5743 | 13.2251 | 12.9232 | 12.6662 | 12.397 | 12.1247 | 11.8328 | 11.5206 | 11.2063 | 9.9792 | 7.3771 | 5.8876 | 5.5533 | 10.2742 | 9.8338 | 9.4166 | 9.0562 | 8.7417 | 8.4145 | 8.0867 | 7.7383 | 7.2069 | 6.6779 | 4.8219 | 0.96368 | -0.87025 | -1.1969
|  | WILSON ROAD | SP |  |  | 10.3999 | 9.9392 | 9.4991 | 9.1185 | 8.788 | 8.4477 | 8.1013 | 7.7271 | 7.1685 | 6.6412 | 5.1222 | 1.8975 | -0.33707 | -1.0077 | 13.9546 | 13.5944 | 13.2615 | 12.9804 | 12.7561 | 12.5273 | 12.2932 | 12.0441 | 11.7888 | 11.5374 | 10.8183 | 8.4729 | 6.8796 | 5.7396 | 10.2767 | 9.8459 | 9.4418 | 9.0988 | 8.813 | 8.5215 | 8.2282 | 7.9178 | 7.6032 | 7.3012 | 6.1767 | 3.3225 | 0.50483 | -0.13205
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE | MINIMUM HEADROOM | SZ 02014 99989 | YES | 10.0721 | 9.5191 | 8.9218 | 8.2231 | 7.1751 | 6.1757 | 5.17 | 4.102 | 2.8344 | 1.5056 | -1.9116 | -6.0898 | -7.4896 | -8.3086 | 14.9399 | 14.6662 | 14.3628 | 14.0009 | 13.4978 | 13.0139 | 12.5113 | 11.9661 | 11.2679 | 10.5569 | 8.8971 | 6.9871 | 5.8164 | 4.9443 | 11.7895 | 11.2937 | 10.7505 | 10.1204 | 9.2017 | 8.3137 | 7.4061 | 6.4339 | 5.2426 | 4.012 | 0.99024 | -2.6508 | -3.8421 | -4.5282
|  | WIMBORNE | CT |  |  | 10.572 | 10.2949 | 9.9885 | 9.5309 | 8.8657 | 8.2554 | 7.6506 | 6.9833 | 6.213 | 4.9802 | 1.9575 | -3.6287 | -7.4896 | -8.3086 | 15.1088 | 14.9302 | 14.7368 | 14.4509 | 14.0857 | 13.7452 | 13.3994 | 13.0122 | 12.5508 | 11.8589 | 10.2483 | 7.6328 | 5.8164 | 4.9443 | 12.2005 | 11.9312 | 11.638 | 11.211 | 10.6078 | 10.0447 | 9.4808 | 8.8568 | 8.1314 | 6.9834 | 4.2157 | -0.53397 | -3.8421 | -4.5282
|  | WIMBORNE | LW |  |  | 10.0721 | 9.5191 | 8.9218 | 8.2231 | 7.1751 | 6.1757 | 5.17 | 4.102 | 2.8344 | 1.5056 | -1.9116 | -6.0898 | -7.332 | -8.2225 | 14.9399 | 14.6662 | 14.3628 | 14.0009 | 13.4978 | 13.0139 | 12.5113 | 11.9661 | 11.2679 | 10.5569 | 8.8971 | 6.9871 | 6.4966 | 6.1582 | 11.7895 | 11.2937 | 10.7505 | 10.1204 | 9.2017 | 8.3137 | 7.4061 | 6.4339 | 5.2426 | 4.012 | 0.99024 | -2.6508 | -3.743 | -4.5219
|  | WIMBORNE | ST |  |  | 10.7149 | 10.5198 | 10.314 | 10.0502 | 9.6575 | 9.3065 | 8.9616 | 8.586 | 8.1653 | 7.7052 | 5.8634 | 2.4157 | 0.41412 | -0.9662 | 15.2087 | 15.087 | 14.9646 | 14.806 | 14.5824 | 14.381 | 14.1766 | 13.9486 | 13.6888 | 13.4163 | 12.2644 | 10.0958 | 8.8211 | 7.7303 | 12.3415 | 12.1542 | 11.9628 | 11.7247 | 11.3722 | 11.0495 | 10.7264 | 10.3719 | 9.977 | 9.5501 | 7.8121 | 4.5973 | 2.8356 | 1.7154
|  | WIMBORNE | SP |  |  | 10.7655 | 10.5948 | 10.4293 | 10.2111 | 9.6378 | 9.0949 | 8.5695 | 8.0116 | 7.4313 | 6.7418 | 4.5077 | -0.35965 | -3.1601 | -4.7797 | 15.2276 | 15.1098 | 14.9997 | 14.8583 | 14.5825 | 14.3264 | 14.0775 | 13.8026 | 13.5069 | 13.1572 | 11.9539 | 9.0426 | 7.0651 | 5.2691 | 12.3861 | 12.2171 | 12.0583 | 11.8609 | 11.3677 | 10.9012 | 10.4482 | 9.9601 | 9.4483 | 8.8449 | 6.8486 | 2.3552 | -0.11062 | -1.464
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES | MINIMUM HEADROOM | SU 03028 12678 | YES | 20.9403 | 20.4069 | 19.8967 | 19.3222 | 18.3776 | 17.3729 | 16.3155 | 15.2435 | 13.8772 | 12.499 | 9.2253 | 4.6182 | 0.83746 | -1.8802 | 22.7504 | 22.4096 | 22.0673 | 21.6767 | 21.1351 | 20.5493 | 19.903 | 19.2219 | 18.3192 | 17.4386 | 15.5236 | 12.7818 | 10.1892 | 7.9905 | 20.3214 | 19.8112 | 19.302 | 18.7262 | 17.8445 | 16.9004 | 15.8833 | 14.8271 | 13.5088 | 12.2084 | 9.181 | 5.0673 | 1.9429 | -0.23071
|  | WIMBORNE ST GILES | CT |  |  | 21.1493 | 20.7451 | 20.3577 | 19.8944 | 19.2389 | 18.5322 | 17.7791 | 16.9647 | 16.0709 | 14.6664 | 11.2542 | 5.4203 | 0.83746 | -1.8802 | 22.7706 | 22.4518 | 22.1248 | 21.7332 | 21.2825 | 20.7929 | 20.2767 | 19.7146 | 19.076 | 18.1502 | 16.0271 | 12.7818 | 10.1892 | 7.9905 | 20.4619 | 20.053 | 19.6389 | 19.1409 | 18.5025 | 17.8091 | 17.095 | 16.3344 | 15.4893 | 14.1654 | 11.0079 | 5.8336 | 1.9429 | -0.23071
|  | WIMBORNE ST GILES | LW |  |  | 20.9403 | 20.4069 | 19.8967 | 19.3222 | 18.3776 | 17.3729 | 16.3155 | 15.2435 | 13.8772 | 12.499 | 9.2253 | 4.6182 | 2.0231 | 0.26763 | 22.7504 | 22.4096 | 22.0673 | 21.6767 | 21.1351 | 20.5493 | 19.903 | 19.2219 | 18.3192 | 17.4386 | 15.5236 | 13.071 | 11.835 | 10.9598 | 20.3214 | 19.8112 | 19.302 | 18.7262 | 17.8445 | 16.9004 | 15.8833 | 14.8271 | 13.5088 | 12.2084 | 9.181 | 5.0673 | 2.88 | 1.4336
|  | WIMBORNE ST GILES | ST |  |  | 21.4498 | 21.2354 | 21.0424 | 20.8107 | 20.5057 | 20.1705 | 19.8162 | 19.4736 | 19.1017 | 18.6731 | 16.5833 | 12.152 | 9.4076 | 7.3928 | 23.0334 | 22.8654 | 22.6969 | 22.4913 | 22.2364 | 21.9552 | 21.6473 | 21.3337 | 20.9799 | 20.6383 | 19.0084 | 15.6923 | 13.6211 | 11.6477 | 20.8161 | 20.6181 | 20.4223 | 20.1822 | 19.8689 | 19.5237 | 19.1502 | 18.7768 | 18.3599 | 17.9365 | 15.9247 | 11.8368 | 9.4912 | 7.8214
|  | WIMBORNE ST GILES | SP |  |  | 21.4819 | 21.2856 | 21.1213 | 20.9357 | 20.6338 | 20.3116 | 19.9859 | 19.6425 | 19.2995 | 18.9144 | 17.4051 | 12.8458 | 10.026 | 8.4036 | 23.0429 | 22.8757 | 22.7181 | 22.5394 | 22.3213 | 22.0844 | 21.8347 | 21.556 | 21.2597 | 20.9418 | 19.6816 | 15.9943 | 13.3316 | 10.853 | 20.8425 | 20.6541 | 20.4856 | 20.2948 | 20.0151 | 19.7152 | 19.4057 | 19.0606 | 18.7041 | 18.3108 | 16.7991 | 12.5267 | 10.0144 | 8.6633
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON | MINIMUM HEADROOM | ST 71286 27802 | YES | 13.7414 | 13.2887 | 12.7529 | 12.1719 | 11.3119 | 10.4129 | 9.46 | 8.4362 | 7.2668 | 6.0302 | 2.0235 | -3.5225 | -6.7792 | -9.559 | 19.7394 | 19.4966 | 19.1933 | 18.8577 | 18.4106 | 17.9329 | 17.4089 | 16.8358 | 16.1508 | 15.4105 | 12.9927 | 8.8127 | 4.8951 | -0.424 | 15.7364 | 15.3527 | 14.8869 | 14.378 | 13.6408 | 12.8632 | 12.0295 | 11.1277 | 10.0807 | 8.9557 | 5.2147 | 0.16866 | -2.5068 | -4.7631
|  | WINCANTON | CT |  |  | 13.9849 | 13.6753 | 13.3228 | 12.8563 | 12.2661 | 11.6505 | 11.0184 | 10.3372 | 9.573 | 8.4028 | 4.6367 | -2.0708 | -6.7792 | -9.559 | 19.7839 | 19.5575 | 19.2986 | 18.9474 | 18.5503 | 18.1272 | 17.6742 | 17.1788 | 16.6072 | 15.8362 | 13.2918 | 8.8127 | 4.8951 | 0.50964 | 15.9199 | 15.6494 | 15.3382 | 14.9126 | 14.391 | 13.8424 | 13.2726 | 12.6563 | 11.9556 | 10.911 | 7.5452 | 1.5599 | -2.5068 | -4.7631
|  | WINCANTON | LW |  |  | 13.7414 | 13.2887 | 12.7529 | 12.1719 | 11.3119 | 10.4129 | 9.46 | 8.4362 | 7.2668 | 6.0302 | 2.0235 | -3.5225 | -6.1188 | -7.7377 | 19.7394 | 19.4966 | 19.1933 | 18.8577 | 18.4106 | 17.9329 | 17.4089 | 16.8358 | 16.1508 | 15.4105 | 12.9927 | 9.8541 | 8.6235 | 7.8197 | 15.7364 | 15.3527 | 14.8869 | 14.378 | 13.6408 | 12.8632 | 12.0295 | 11.1277 | 10.0807 | 8.9557 | 5.2147 | 0.16866 | -2.0344 | -3.37
|  | WINCANTON | ST |  |  | 14.2494 | 14.1046 | 13.9413 | 13.7599 | 13.5301 | 13.2922 | 13.03 | 12.7411 | 12.3995 | 12.0137 | 10.4785 | 6.0221 | 2.9521 | 0.91575 | 19.9494 | 19.8223 | 19.6776 | 19.5141 | 19.3085 | 19.0901 | 18.8429 | 18.5668 | 18.2399 | 17.8946 | 16.5038 | 12.5282 | 8.9796 | 4.8475 | 16.1633 | 16.0421 | 15.9024 | 15.7449 | 15.5361 | 15.3177 | 15.0743 | 14.8048 | 14.4831 | 14.1259 | 12.6837 | 8.5523 | 5.9099 | 4.2614
|  | WINCANTON | SP |  |  | 14.295 | 14.1487 | 13.9903 | 13.8191 | 13.6323 | 13.4412 | 13.2405 | 13.0112 | 12.7612 | 12.4362 | 11.2493 | 7.786 | 4.6749 | 3.0023 | 19.9651 | 19.8234 | 19.6635 | 19.487 | 19.2977 | 19.0929 | 18.867 | 18.6079 | 18.3128 | 17.9462 | 16.5438 | 12.4552 | 7.0104 | -0.424 | 16.2028 | 16.0755 | 15.9365 | 15.7847 | 15.6179 | 15.4451 | 15.2621 | 15.0513 | 14.8187 | 14.5235 | 13.431 | 10.2314 | 7.4294 | 6.0416
COWLEY GSP | WITNEY BSP | WINDRUSH PARK | MINIMUM HEADROOM | SP 33366 09758 | NO | 1.7777 | 0.64912 | -0.72996 | 10.9059 | 9.3195 | 7.6905 | 5.9241 | 3.9527 | 1.5365 | -0.73273 | -6.3966 | -12.9666 | -16.5012 | -18.9363 | 3.1583 | 2.5162 | 1.7265 | 18.446 | 17.5881 | 16.6977 | 15.6832 | 14.517 | 13.0142 | 11.6087 | 8.3241 | 4.7606 | 2.1879 | 0.10217 | -1.182 | -2.1585 | -3.3493 | 12.9633 | 11.5354 | 10.0648 | 8.473 | 6.7015 | 4.5333 | 2.4776 | -2.7273 | -8.8015 | -11.8559 | -13.9851
|  | WINDRUSH PARK | CT |  |  | 2.141 | 1.2216 | 0.10878 | 11.92 | 10.7539 | 9.5608 | 8.2808 | 6.8103 | 5.1277 | 2.8697 | -2.6382 | -11.067 | -16.5012 | -18.9363 | 3.2545 | 2.6817 | 1.9954 | 18.7469 | 18.0458 | 17.2918 | 16.4703 | 15.5133 | 14.3943 | 12.9521 | 9.6264 | 4.9937 | 2.1879 | 0.10217 | -0.85167 | -1.6203 | -2.5575 | 13.9244 | 12.8915 | 11.8303 | 10.6925 | 9.3886 | 7.8942 | 5.8589 | 0.82725 | -7.0216 | -11.8559 | -13.9851
|  | WINDRUSH PARK | LW |  |  | 1.7777 | 0.64912 | -0.72996 | 10.9059 | 9.3195 | 7.6905 | 5.9241 | 3.9527 | 1.5365 | -0.73273 | -6.3966 | -12.9666 | -14.9673 | -16.1149 | 3.1583 | 2.5162 | 1.7265 | 18.446 | 17.5881 | 16.6977 | 15.6832 | 14.517 | 13.0142 | 11.6087 | 8.3241 | 4.7606 | 3.9384 | 3.4919 | -1.182 | -2.1585 | -3.3493 | 12.9633 | 11.5354 | 10.0648 | 8.473 | 6.7015 | 4.5333 | 2.4776 | -2.7273 | -8.8015 | -10.5843 | -11.5825
|  | WINDRUSH PARK | ST |  |  | 2.5856 | 2.0425 | 1.3938 | 13.7721 | 13.1477 | 12.5035 | 11.8127 | 11.034 | 10.1218 | 9.2368 | 5.5645 | -1.1812 | -4.4709 | -6.2229 | 3.5509 | 3.2024 | 2.7906 | 19.8863 | 19.4796 | 19.0549 | 18.5945 | 18.0734 | 17.4492 | 16.8278 | 14.1223 | 9.1919 | 6.696 | 4.8017 | -0.44364 | -0.87897 | -1.3935 | 15.6021 | 15.069 | 14.5139 | 13.9184 | 13.2474 | 12.455 | 11.6658 | 8.3905 | 2.2172 | -0.87567 | -2.5166
|  | WINDRUSH PARK | SP |  |  | 2.656 | 2.1334 | 1.5499 | 14.0028 | 13.3946 | 12.7866 | 12.1376 | 11.3905 | 10.5855 | 9.7509 | 6.8213 | -0.16706 | -4.0657 | -5.6543 | 3.5811 | 3.2357 | 2.8507 | 19.9794 | 19.6133 | 19.2398 | 18.8351 | 18.3645 | 17.8411 | 17.2945 | 15.2531 | 9.9116 | 6.1971 | 3.0592 | -0.37971 | -0.79221 | -1.2458 | 15.8184 | 15.2933 | 14.7649 | 14.2014 | 13.5537 | 12.8552 | 12.1113 | 9.4997 | 3.1992 | -0.42444 | -1.8989
COWLEY GSP | DRAYTON BSP | WINSMORE LANE | MINIMUM HEADROOM | SU 49513 96982 | NO | 5.3725 | 5.3339 | 5.2874 | 5.2385 | 5.1726 | 5.1041 | 5.0304 | 4.9484 | 4.8347 | 4.735 | 4.4777 | 4.181 | 4.1302 | 4.0884 | 4.1518 | 4.1315 | 4.1074 | 4.0812 | 4.0476 | 4.012 | 3.9709 | 3.9229 | 3.8564 | 3.7996 | 3.6662 | 3.5044 | 3.4814 | 3.4659 | 3.9922 | 3.9549 | 3.9146 | 3.8725 | 3.8158 | 3.7571 | 3.6946 | 3.626 | 3.5315 | 3.4488 | 3.2241 | 2.9536 | 2.9074 | 2.8713
|  | WINSMORE LANE | CT |  |  | 5.3813 | 5.3745 | 5.3655 | 5.3328 | 5.2893 | 5.2441 | 5.1877 | 5.1238 | 5.0518 | 4.9665 | 4.7697 | 4.4561 | 4.2951 | 4.2286 | 4.1609 | 4.1462 | 4.1287 | 4.1056 | 4.0791 | 4.0513 | 4.0175 | 3.9779 | 3.9314 | 3.8778 | 3.7668 | 3.6003 | 3.5231 | 3.4746 | 4.0278 | 4.0094 | 3.9885 | 3.9636 | 3.9283 | 3.8916 | 3.8455 | 3.7941 | 3.738 | 3.6706 | 3.4999 | 3.2103 | 3.06 | 2.9995
|  | WINSMORE LANE | LW |  |  | 5.3725 | 5.3339 | 5.2874 | 5.2385 | 5.1726 | 5.1041 | 5.0304 | 4.9484 | 4.8347 | 4.735 | 4.4777 | 4.181 | 4.1302 | 4.0884 | 4.1518 | 4.1315 | 4.1074 | 4.0812 | 4.0476 | 4.012 | 3.9709 | 3.9229 | 3.8564 | 3.7996 | 3.6662 | 3.5044 | 3.4814 | 3.4659 | 3.9922 | 3.9549 | 3.9146 | 3.8725 | 3.8158 | 3.7571 | 3.6946 | 3.626 | 3.5315 | 3.4488 | 3.2241 | 2.9536 | 2.9074 | 2.8713
|  | WINSMORE LANE | ST |  |  | 5.3883 | 5.3853 | 5.3821 | 5.378 | 5.3732 | 5.3507 | 5.3247 | 5.2968 | 5.2598 | 5.2195 | 5.0514 | 4.8006 | 4.6769 | 4.6194 | 4.1726 | 4.1661 | 4.1578 | 4.1472 | 4.1332 | 4.1178 | 4.1008 | 4.0821 | 4.0579 | 4.0336 | 3.9222 | 3.7568 | 3.6813 | 3.6371 | 4.0435 | 4.0352 | 4.0256 | 4.0144 | 3.9961 | 3.9764 | 3.9558 | 3.9338 | 3.9045 | 3.871 | 3.7406 | 3.5299 | 3.4158 | 3.3624
|  | WINSMORE LANE | SP |  |  | 5.3887 | 5.3855 | 5.3822 | 5.3787 | 5.3748 | 5.3698 | 5.3457 | 5.3235 | 5.2984 | 5.2576 | 5.1149 | 4.7482 | 4.5039 | 4.3646 | 4.1752 | 4.1684 | 4.1594 | 4.1509 | 4.1391 | 4.1261 | 4.1111 | 4.0968 | 4.0799 | 4.0576 | 3.9736 | 3.7437 | 3.6097 | 3.5386 | 4.0488 | 4.0424 | 4.0345 | 4.0268 | 4.0108 | 3.9936 | 3.9739 | 3.9557 | 3.936 | 3.9007 | 3.7826 | 3.4811 | 3.256 | 3.1267
MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON | MINIMUM HEADROOM | SY 84631 98138 | YES | 6.8002 | 6.3329 | 5.8317 | 5.3102 | 4.6451 | 3.9599 | 3.2455 | 2.5271 | 1.6936 | 0.88627 | -1.1497 | -3.3185 | -3.8326 | -4.1408 | 8.6543 | 8.4066 | 8.2318 | 8.0625 | 7.9148 | 7.7612 | 7.5058 | 7.1565 | 6.667 | 6.1934 | 5.0429 | 3.8651 | 3.5564 | 2.9821 | 8.506 | 8.0547 | 7.6005 | 7.1342 | 6.5298 | 5.9108 | 5.269 | 4.6241 | 3.8854 | 3.166 | 1.2666 | -0.80174 | -1.298 | -1.5989
|  | WINTERBOURNE KINGSTON | CT |  |  | 7.0684 | 6.7527 | 6.4324 | 6.0357 | 5.5727 | 5.0925 | 4.5878 | 4.0903 | 3.5442 | 2.8102 | 0.95516 | -1.7472 | -3.2275 | -3.8409 | 8.6543 | 8.4066 | 8.2318 | 8.0625 | 7.915 | 7.7719 | 7.6192 | 7.4637 | 7.2763 | 6.9889 | 5.8906 | 4.3909 | 3.5564 | 2.9821 | 8.7762 | 8.4746 | 8.1897 | 7.8526 | 7.4455 | 7.0267 | 6.5825 | 6.1196 | 5.605 | 4.9141 | 3.1861 | 0.71366 | -0.70879 | -1.3125
|  | WINTERBOURNE KINGSTON | LW |  |  | 6.8002 | 6.3329 | 5.8317 | 5.3102 | 4.6451 | 3.9599 | 3.2455 | 2.5271 | 1.6936 | 0.88627 | -1.1497 | -3.3185 | -3.8326 | -4.1408 | 8.6649 | 8.4152 | 8.2343 | 8.0687 | 7.9148 | 7.7612 | 7.5058 | 7.1565 | 6.667 | 6.1934 | 5.0429 | 3.8651 | 3.6296 | 3.4926 | 8.506 | 8.0547 | 7.6005 | 7.1342 | 6.5298 | 5.9108 | 5.269 | 4.6241 | 3.8854 | 3.166 | 1.2666 | -0.80174 | -1.298 | -1.5989
|  | WINTERBOURNE KINGSTON | ST |  |  | 7.1911 | 6.9542 | 6.7365 | 6.5207 | 6.2339 | 5.944 | 5.6426 | 5.3547 | 5.0348 | 4.7098 | 3.4096 | 0.94242 | -0.22788 | -0.80823 | 8.701 | 8.4835 | 8.3453 | 8.2297 | 8.1237 | 8.0263 | 7.9206 | 7.8151 | 7.6839 | 7.5557 | 7.0478 | 5.5748 | 4.7435 | 4.1802 | 8.8822 | 8.6406 | 8.4464 | 8.2636 | 8.0229 | 7.7757 | 7.5185 | 7.2678 | 6.9887 | 6.6969 | 5.4696 | 3.1319 | 2.0611 | 1.5485
|  | WINTERBOURNE KINGSTON | SP |  |  | 7.2368 | 7.0123 | 6.8206 | 6.6312 | 6.348 | 6.0658 | 5.7787 | 5.4982 | 5.2137 | 4.8663 | 3.6938 | 0.84675 | -0.92417 | -1.713 | 8.7035 | 8.4865 | 8.3506 | 8.2379 | 8.1454 | 8.0639 | 7.9795 | 7.8964 | 7.8029 | 7.7155 | 7.4249 | 5.6943 | 4.3364 | 3.3071 | 8.9278 | 8.7031 | 8.5343 | 8.3779 | 8.1304 | 7.883 | 7.6292 | 7.3778 | 7.1207 | 6.8008 | 5.7438 | 3.1171 | 1.478 | 0.74972
MANNINGTON GSP | REDHILL BSP | WINTON | MINIMUM HEADROOM | SZ 09349 93822 | YES | 19.1611 | 18.7253 | 18.4605 | 18.1799 | 17.7725 | 17.3168 | 16.8439 | 16.3478 | 15.7799 | 15.1461 | 13.5226 | 11.5923 | 10.4976 | 9.6914 | 20.0052 | 19.7626 | 19.6183 | 19.4646 | 19.2771 | 19.0666 | 18.8444 | 18.6099 | 18.3342 | 17.9554 | 16.9509 | 15.1665 | 13.3568 | 9.2643 | 20.0471 | 19.8079 | 19.665 | 19.4258 | 19.06 | 18.6543 | 18.2322 | 17.7887 | 17.2823 | 16.7176 | 15.2537 | 13.5019 | 12.5223 | 11.7999
|  | WINTON | CT |  |  | 19.2779 | 18.9132 | 18.7331 | 18.5082 | 18.2344 | 17.9148 | 17.6009 | 17.2727 | 16.9058 | 16.296 | 14.6729 | 12.1629 | 10.4976 | 9.6914 | 20.0341 | 19.8039 | 19.6761 | 19.5242 | 19.3675 | 19.1869 | 19.0027 | 18.807 | 18.5846 | 18.1555 | 16.9583 | 15.1665 | 13.5224 | 11.5302 | 20.0504 | 19.8253 | 19.6964 | 19.5471 | 19.4144 | 19.2031 | 18.9261 | 18.6356 | 18.3102 | 17.7685 | 16.2928 | 14.0295 | 12.5223 | 11.7999
|  | WINTON | LW |  |  | 19.1611 | 18.7253 | 18.4605 | 18.1799 | 17.7725 | 17.3168 | 16.8439 | 16.3478 | 15.7799 | 15.1461 | 13.5226 | 11.5923 | 10.8851 | 10.4672 | 20.0052 | 19.7626 | 19.6183 | 19.4646 | 19.2771 | 19.0666 | 18.8444 | 18.6099 | 18.3342 | 17.9554 | 16.9509 | 15.888 | 15.5768 | 15.393 | 20.0471 | 19.8079 | 19.665 | 19.4258 | 19.06 | 18.6543 | 18.2322 | 17.7887 | 17.2823 | 16.7176 | 15.2537 | 13.5019 | 12.8814 | 12.5172
|  | WINTON | ST |  |  | 19.5137 | 19.2591 | 19.1514 | 19.0314 | 18.8985 | 18.7406 | 18.5747 | 18.4036 | 18.2099 | 17.9954 | 17.1443 | 15.1398 | 14.0906 | 13.4503 | 20.1393 | 19.9637 | 19.8727 | 19.7731 | 19.6803 | 19.5729 | 19.4569 | 19.3333 | 19.1904 | 19.0308 | 18.414 | 16.4454 | 14.9056 | 12.9735 | 20.1397 | 19.9616 | 19.8816 | 19.7932 | 19.72 | 19.6309 | 19.5334 | 19.4258 | 19.2856 | 19.119 | 18.4791 | 16.6928 | 15.7456 | 15.1898
|  | WINTON | SP |  |  | 19.5424 | 19.2975 | 19.1963 | 19.0881 | 18.9529 | 18.8017 | 18.6471 | 18.485 | 18.3094 | 18.1013 | 17.398 | 15.5359 | 14.3397 | 13.8194 | 20.1407 | 19.9747 | 19.8817 | 19.7826 | 19.6832 | 19.5712 | 19.4513 | 19.3217 | 19.1756 | 18.9968 | 18.3647 | 16.1493 | 13.3568 | 9.2643 | 20.1459 | 19.9727 | 19.8943 | 19.8129 | 19.7511 | 19.6798 | 19.6038 | 19.5223 | 19.4248 | 19.3124 | 18.7505 | 17.0958 | 15.9784 | 15.5159
COWLEY GSP | WITNEY BSP | WITNEY TOWN | MINIMUM HEADROOM | SP 35844 09625 | NO | 8.8874 | 8.4621 | 7.9771 | 7.454 | 6.5082 | 5.5196 | 4.4714 | 3.3637 | 2.1585 | 0.85581 | -2.7626 | -7.2734 | -9.804 | -11.6733 | 8.3024 | 8.0681 | 7.7814 | 7.4608 | 6.9709 | 6.4465 | 5.8625 | 5.2332 | 4.4407 | 3.5395 | 1.2003 | -2.1017 | -5.1232 | -9.4568 | 4.7171 | 4.3195 | 3.8545 | 3.3475 | 2.477 | 1.5606 | 0.57473 | -0.47348 | -1.6603 | -2.9471 | -6.4393 | -10.6249 | -12.662 | -14.2372
|  | WITNEY TOWN | CT |  |  | 9.1844 | 8.9339 | 8.6357 | 8.2671 | 7.6725 | 7.0441 | 6.4467 | 5.8058 | 5.0669 | 3.8136 | 0.094783 | -5.745 | -9.804 | -11.6733 | 8.3614 | 8.1587 | 7.9116 | 7.5945 | 7.1932 | 6.7601 | 6.3119 | 5.8228 | 5.1939 | 4.2757 | 1.7161 | -2.1017 | -5.1232 | -8.3968 | 4.9571 | 4.7073 | 4.4051 | 4.0217 | 3.4508 | 2.8436 | 2.2526 | 1.6158 | 0.86635 | -0.36355 | -3.8067 | -9.2 | -12.662 | -14.2372
|  | WITNEY TOWN | LW |  |  | 8.8874 | 8.4621 | 7.9771 | 7.454 | 6.5082 | 5.5196 | 4.4714 | 3.3637 | 2.1585 | 0.85581 | -2.7626 | -7.2734 | -8.8809 | -9.7128 | 8.3024 | 8.0681 | 7.7814 | 7.4608 | 6.9709 | 6.4465 | 5.8625 | 5.2332 | 4.4407 | 3.5395 | 1.2003 | -1.3862 | -2.0733 | -2.4137 | 4.7171 | 4.3195 | 3.8545 | 3.3475 | 2.477 | 1.5606 | 0.57473 | -0.47348 | -1.6603 | -2.9471 | -6.4393 | -10.6249 | -12.0311 | -12.7346
|  | WITNEY TOWN | ST |  |  | 9.4384 | 9.3373 | 9.213 | 9.0713 | 8.856 | 8.6193 | 8.3611 | 8.0688 | 7.7301 | 7.3247 | 5.6604 | 1.0984 | -1.2448 | -2.6047 | 8.5325 | 8.4293 | 8.3028 | 8.1556 | 7.9575 | 7.7366 | 7.4886 | 7.2032 | 6.8656 | 6.5001 | 4.8831 | 0.89954 | -1.8526 | -4.9343 | 5.2111 | 5.1102 | 4.9836 | 4.8371 | 4.619 | 4.3775 | 4.1121 | 3.8086 | 3.4534 | 3.0441 | 1.3131 | -2.9183 | -5.0591 | -6.2917
|  | WITNEY TOWN | SP |  |  | 9.4906 | 9.3968 | 9.2935 | 9.1768 | 8.9777 | 8.7583 | 8.5344 | 8.2839 | 8.0075 | 7.6433 | 6.3545 | 2.4902 | -0.22681 | -1.2738 | 8.5535 | 8.4414 | 8.3123 | 8.1649 | 7.9812 | 7.7747 | 7.5515 | 7.2953 | 6.9957 | 6.6228 | 5.2095 | 0.97342 | -3.6229 | -9.4568 | 5.2596 | 5.1607 | 5.051 | 4.9262 | 4.732 | 4.5174 | 4.2966 | 4.0463 | 3.7642 | 3.404 | 2.1017 | -1.5697 | -4.151 | -5.1034
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM | MINIMUM HEADROOM | SU 79589 67665 | YES | 2.5571 | 2.2304 | 1.8647 | 1.4892 | 0.95241 | 0.407 | -0.15644 | -0.7771 | -1.5513 | -2.277 | -3.8529 | -5.6991 | -6.2349 | -6.6036 | 2.7435 | 2.5835 | 2.3887 | 2.1839 | 1.9117 | 1.6261 | 1.318 | 0.96249 | 0.48587 | 0.051339 | -0.68027 | -1.5057 | -1.8427 | -2.351 | 0.63844 | 0.34685 | 0.01123 | -0.33588 | -0.82049 | -1.3178 | -1.8386 | -2.4217 | -3.1684 | -3.859 | -5.2335 | -6.8227 | -7.2725 | -7.5767
|  | WOKINGHAM | CT |  |  | 2.8503 | 2.6832 | 2.4936 | 2.2495 | 1.9234 | 1.5815 | 1.2134 | 0.79005 | 0.28782 | -0.40566 | -1.78 | -4.0795 | -5.6956 | -6.3877 | 2.8313 | 2.7236 | 2.5978 | 2.4269 | 2.2316 | 2.0212 | 1.7939 | 1.5243 | 1.1896 | 0.75038 | 0.0036567 | -1.0877 | -1.8427 | -2.351 | 0.87681 | 0.71965 | 0.54024 | 0.30647 | 0.0023961 | -0.31796 | -0.66281 | -1.0619 | -1.5396 | -2.1948 | -3.4544 | -5.4755 | -6.8088 | -7.3782
|  | WOKINGHAM | LW |  |  | 2.5571 | 2.2304 | 1.8647 | 1.4892 | 0.95241 | 0.407 | -0.15644 | -0.7771 | -1.5513 | -2.277 | -3.8529 | -5.6991 | -6.2349 | -6.6036 | 2.7435 | 2.5835 | 2.3887 | 2.1839 | 1.9117 | 1.6261 | 1.318 | 0.96249 | 0.48587 | 0.051339 | -0.68027 | -1.5057 | -1.7274 | -1.8709 | 0.63844 | 0.34685 | 0.01123 | -0.33588 | -0.82049 | -1.3178 | -1.8386 | -2.4217 | -3.1684 | -3.859 | -5.2335 | -6.8227 | -7.2725 | -7.5767
|  | WOKINGHAM | ST |  |  | 2.9752 | 2.8855 | 2.7821 | 2.6625 | 2.4785 | 2.2819 | 2.0766 | 1.8533 | 1.5998 | 1.3267 | 0.14906 | -1.4767 | -2.3432 | -2.925 | 2.9142 | 2.8586 | 2.7916 | 2.7107 | 2.598 | 2.4753 | 2.3437 | 2.1979 | 2.0274 | 1.8574 | 1.0559 | -0.011078 | -0.55699 | -1.0441 | 0.99616 | 0.91323 | 0.81674 | 0.70407 | 0.53263 | 0.34889 | 0.15634 | -0.053701 | -0.29363 | -0.54917 | -1.6717 | -3.1935 | -3.9701 | -4.4841
|  | WOKINGHAM | SP |  |  | 3.0217 | 2.9452 | 2.8662 | 2.7839 | 2.583 | 2.3706 | 2.1655 | 1.9367 | 1.6989 | 1.3776 | 0.25678 | -2.4061 | -3.7183 | -4.5545 | 2.9307 | 2.8757 | 2.8171 | 2.7551 | 2.6474 | 2.5302 | 2.4174 | 2.2841 | 2.1415 | 1.9671 | 1.3024 | -0.39361 | -1.1855 | -1.8054 | 1.0371 | 0.96481 | 0.88997 | 0.81191 | 0.62871 | 0.4342 | 0.24701 | 0.036099 | -0.18386 | -0.47566 | -1.5164 | -4.0103 | -5.1959 | -5.8982
BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE | MINIMUM HEADROOM | SU 64425 81624 | YES | 3.0758 | 2.4981 | 1.8318 | 1.1279 | -0.01958 | -1.2266 | -2.5331 | -3.9399 | -5.6457 | -7.519 | -12.5106 | -19.024 | -24.9227 | -28.7263 | 4.6695 | 4.2793 | 3.8292 | 3.3547 | 2.6924 | 1.9888 | 1.2014 | 0.3409 | -0.75045 | -1.9627 | -5.0432 | -9.7268 | -13.969 | -18.1956 | -1.0429 | -1.571 | -2.1691 | -2.7976 | -3.8432 | -4.9401 | -6.1248 | -7.3987 | -8.9362 | -10.6234 | -15.1688 | -21.0472 | -26.3546 | -29.5668
|  | WOODCOTE | CT |  |  | 3.2468 | 2.7929 | 2.3367 | 1.6968 | 0.87276 | 0.0055004 | -0.90911 | -1.9049 | -3.0591 | -4.9127 | -10.1873 | -18.5829 | -24.9227 | -28.7263 | 4.6905 | 4.32 | 3.9552 | 3.4438 | 2.8694 | 2.2617 | 1.6049 | 0.88178 | 0.023852 | -1.209 | -4.6823 | -9.7268 | -13.969 | -18.1956 | -0.87933 | -1.2912 | -1.6989 | -2.2627 | -3.0038 | -3.7816 | -4.6009 | -5.4922 | -6.5223 | -8.1948 | -13.0518 | -20.6376 | -26.3546 | -29.5668
|  | WOODCOTE | LW |  |  | 3.0758 | 2.4981 | 1.8318 | 1.1279 | -0.01958 | -1.2266 | -2.5331 | -3.9399 | -5.6457 | -7.519 | -12.5106 | -19.024 | -22.4711 | -24.7688 | 4.6695 | 4.2793 | 3.8292 | 3.3547 | 2.6924 | 1.9888 | 1.2014 | 0.3409 | -0.75045 | -1.9627 | -5.0432 | -8.6164 | -10.2146 | -11.3231 | -1.0429 | -1.571 | -2.1691 | -2.7976 | -3.8432 | -4.9401 | -6.1248 | -7.3987 | -8.9362 | -10.6234 | -15.1688 | -21.0472 | -24.0259 | -25.9647
|  | WOODCOTE | ST |  |  | 3.5547 | 3.2897 | 3.0452 | 2.8122 | 2.4686 | 2.106 | 1.7024 | 1.2543 | 0.72805 | 0.1771 | -2.2781 | -8.698 | -12.455 | -15.087 | 4.8988 | 4.6544 | 4.431 | 4.2166 | 3.9163 | 3.5994 | 3.2417 | 2.842 | 2.3721 | 1.9057 | -0.173 | -5.4002 | -8.9456 | -12.7757 | -0.60139 | -0.84229 | -1.0583 | -1.2611 | -1.562 | -1.8782 | -2.231 | -2.6231 | -3.0855 | -3.5758 | -5.743 | -11.7028 | -14.9677 | -17.1542
|  | WOODCOTE | SP |  |  | 3.6009 | 3.317 | 3.0759 | 2.8418 | 2.5714 | 2.2894 | 1.9839 | 1.6403 | 1.2448 | 0.80043 | -0.94418 | -6.289 | -10.1382 | -12.011 | 4.92 | 4.6505 | 4.4147 | 4.1823 | 3.9335 | 3.6719 | 3.3807 | 3.0493 | 2.6611 | 2.2168 | 0.44958 | -4.8741 | -10.3016 | -16.7097 | -0.55969 | -0.81543 | -1.0272 | -1.2294 | -1.4668 | -1.7131 | -1.9804 | -2.2811 | -2.6276 | -3.0202 | -4.5485 | -9.4319 | -12.9329 | -14.4972
NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE | MINIMUM HEADROOM | SU 43733 15470 | YES | 1.7933 | 0.98569 | -0.17473 | -1.522 | -3.326 | -5.2154 | -7.1671 | -9.2967 | -11.8471 | -14.4788 | -20.2888 | -26.5615 | -29.3824 | -31.3247 | 2.3142 | 1.8942 | 1.2567 | 0.49952 | -0.45401 | -1.4661 | -2.5442 | -3.7339 | -5.2479 | -6.8163 | -10.0767 | -13.3555 | -15.9458 | -18.0009 | -3.6879 | -4.4018 | -5.3797 | -6.5088 | -8.0894 | -9.742 | -11.4445 | -13.2976 | -15.5684 | -17.9198 | -23.2291 | -29.0093 | -31.4452 | -33.16
|  | WOODMILL LANE | CT |  |  | 2.2861 | 1.7601 | 0.93851 | -0.16881 | -1.4883 | -2.8865 | -4.2784 | -5.8303 | -7.6344 | -10.1608 | -15.9257 | -24.0139 | -29.3824 | -31.3247 | 2.4263 | 2.0808 | 1.5618 | 0.84982 | 0.087962 | -0.72884 | -1.5828 | -2.5426 | -3.6874 | -5.2352 | -8.6856 | -13.0728 | -15.9458 | -18.0009 | -3.1853 | -3.621 | -4.2796 | -5.1602 | -6.2706 | -7.4473 | -8.6692 | -10.0326 | -11.6167 | -13.8661 | -19.0996 | -26.6628 | -31.4452 | -33.16
|  | WOODMILL LANE | LW |  |  | 1.7933 | 0.98569 | -0.17473 | -1.522 | -3.326 | -5.2154 | -7.1671 | -9.2967 | -11.8471 | -14.4788 | -20.2888 | -26.5615 | -28.6102 | -29.6975 | 2.3142 | 1.8942 | 1.2567 | 0.49952 | -0.45401 | -1.4661 | -2.5442 | -3.7339 | -5.2479 | -6.8163 | -10.0767 | -13.3555 | -14.2194 | -14.6531 | -3.6879 | -4.4018 | -5.3797 | -6.5088 | -8.0894 | -9.742 | -11.4445 | -13.2976 | -15.5684 | -17.9198 | -23.2291 | -29.0093 | -30.8252 | -31.7846
|  | WOODMILL LANE | ST |  |  | 2.6138 | 2.3243 | 1.8568 | 1.2809 | 0.54788 | -0.22467 | -1.011 | -1.8852 | -2.8894 | -3.9246 | -7.371 | -13.616 | -16.744 | -18.6483 | 2.6581 | 2.4739 | 2.1813 | 1.8153 | 1.3519 | 0.85739 | 0.3399 | -0.23916 | -0.91733 | -1.5897 | -4.0701 | -8.6421 | -11.0343 | -13.1292 | -2.9129 | -3.1501 | -3.5057 | -3.9382 | -4.5122 | -5.1184 | -5.7414 | -6.4328 | -7.2751 | -8.1683 | -11.2219 | -17.0509 | -19.8923 | -21.6803
|  | WOODMILL LANE | SP |  |  | 2.6871 | 2.4158 | 1.996 | 1.5024 | 0.74994 | -0.01489 | -0.79579 | -1.659 | -2.6017 | -3.6541 | -6.7421 | -13.6312 | -17.5328 | -19.2999 | 2.6848 | 2.492 | 2.209 | 1.877 | 1.4642 | 1.0309 | 0.57507 | 0.04926 | -0.5487 | -1.2117 | -3.2996 | -8.4359 | -12.1038 | -15.4252 | -2.8433 | -3.055 | -3.3624 | -3.7193 | -4.3398 | -4.9663 | -5.6118 | -6.3152 | -7.0805 | -7.9584 | -10.7053 | -16.9454 | -20.5668 | -22.2195
COWLEY GSP | YARNTON BSP | WOODSTOCK | MINIMUM HEADROOM | SP 44795 17462 | NO | 19.7451 | 19.3447 | 18.7649 | 18.0575 | 17.0788 | 16.0469 | 14.9418 | 13.6584 | 12.1299 | 10.7398 | 7.3427 | 3.7917 | 1.8706 | 0.51387 | 22.7311 | 22.4795 | 22.1014 | 21.6846 | 21.1648 | 20.5886 | 19.9523 | 19.1934 | 18.2258 | 17.3805 | 15.5355 | 13.4592 | 11.8271 | 10.488 | 20.8199 | 20.4405 | 19.9232 | 19.2956 | 18.4256 | 17.5048 | 16.5093 | 15.3461 | 13.9391 | 12.6739 | 9.6902 | 6.5305 | 4.8937 | 3.716
|  | WOODSTOCK | CT |  |  | 19.8546 | 19.552 | 18.9991 | 18.3807 | 17.6401 | 16.8533 | 16.0461 | 15.1154 | 14.0334 | 12.543 | 9.0204 | 4.5875 | 1.8706 | 0.51387 | 22.7311 | 22.4929 | 22.1014 | 21.6846 | 21.2287 | 20.7404 | 20.2187 | 19.6131 | 18.8983 | 17.9554 | 15.9485 | 13.4592 | 11.8271 | 10.488 | 20.9057 | 20.6118 | 20.1051 | 19.5556 | 18.908 | 18.2082 | 17.4829 | 16.6438 | 15.6622 | 14.2994 | 11.2003 | 7.2782 | 4.8937 | 3.716
|  | WOODSTOCK | LW |  |  | 19.7451 | 19.3447 | 18.7649 | 18.0575 | 17.0788 | 16.0469 | 14.9418 | 13.6584 | 12.1299 | 10.7398 | 7.3427 | 3.7917 | 2.4631 | 1.7978 | 22.7373 | 22.4795 | 22.1299 | 21.7059 | 21.1648 | 20.5886 | 19.9523 | 19.1934 | 18.2258 | 17.3805 | 15.5355 | 13.6335 | 12.9955 | 12.6615 | 20.8199 | 20.4405 | 19.9232 | 19.2956 | 18.4256 | 17.5048 | 16.5093 | 15.3461 | 13.9391 | 12.6739 | 9.6902 | 6.5305 | 5.3727 | 4.8049
|  | WOODSTOCK | ST |  |  | 20.1599 | 20.047 | 19.7716 | 19.4061 | 19.0017 | 18.5726 | 18.1197 | 17.6034 | 17.0262 | 16.4244 | 13.7063 | 10.507 | 8.9187 | 7.798 | 22.9547 | 22.855 | 22.654 | 22.3905 | 22.1085 | 21.8074 | 21.4833 | 21.1131 | 20.6945 | 20.2821 | 18.3306 | 15.9524 | 14.6628 | 13.4078 | 21.2057 | 21.0979 | 20.8581 | 20.539 | 20.1862 | 19.8099 | 19.4082 | 18.9492 | 18.4331 | 17.9006 | 15.4043 | 12.4765 | 11.1103 | 10.1624
|  | WOODSTOCK | SP |  |  | 20.1843 | 20.0895 | 19.8726 | 19.5923 | 19.2577 | 18.9092 | 18.54 | 18.0998 | 17.6093 | 17.0705 | 15.0538 | 11.3367 | 9.8286 | 9.0498 | 22.9619 | 22.8696 | 22.7022 | 22.4917 | 22.2679 | 22.0304 | 21.7686 | 21.452 | 21.0944 | 20.715 | 19.2535 | 16.2534 | 14.7815 | 13.4869 | 21.2265 | 21.1351 | 20.9505 | 20.714 | 20.4331 | 20.1385 | 19.8194 | 19.4335 | 19.001 | 18.5262 | 16.7208 | 13.1823 | 11.8102 | 11.1441
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON | MINIMUM HEADROOM | SU 44145 11242 | YES | 3.5523 | 3.4279 | 3.2934 | 3.1518 | 2.9387 | 2.7168 | 2.4793 | 2.2052 | 1.902 | 1.6183 | 0.96425 | 0.12399 | -0.2847 | -0.63959 | 4.2789 | 4.2125 | 4.1369 | 4.0547 | 3.9443 | 3.8266 | 3.6936 | 3.5285 | 3.3375 | 3.1732 | 2.8741 | 2.513 | 2.2181 | 1.9708 | 3.4115 | 3.2976 | 3.1721 | 3.0387 | 2.8452 | 2.6424 | 2.4212 | 2.1594 | 1.865 | 1.5985 | 1.0326 | 0.31891 | -0.010419 | -0.32123
|  | WOOLSTON | CT |  |  | 3.6502 | 3.5802 | 3.5016 | 3.4098 | 3.2775 | 3.1419 | 2.9923 | 2.8223 | 2.6429 | 2.35 | 1.7407 | 0.58327 | -0.2847 | -0.63959 | 4.3034 | 4.2534 | 4.1956 | 4.125 | 4.0426 | 3.9576 | 3.8582 | 3.741 | 3.6146 | 3.4255 | 3.1138 | 2.6049 | 2.2181 | 1.9708 | 3.4873 | 3.4179 | 3.3389 | 3.2447 | 3.1188 | 2.9895 | 2.8439 | 2.6757 | 2.4969 | 2.2121 | 1.6731 | 0.70621 | -0.010419 | -0.32123
|  | WOOLSTON | LW |  |  | 3.5523 | 3.4279 | 3.2934 | 3.1518 | 2.9387 | 2.7168 | 2.4793 | 2.2052 | 1.902 | 1.6183 | 0.96425 | 0.12399 | -0.17078 | -0.326 | 4.2789 | 4.2125 | 4.1369 | 4.0547 | 3.9443 | 3.8266 | 3.6936 | 3.5285 | 3.3375 | 3.1732 | 2.8741 | 2.513 | 2.3978 | 2.337 | 3.4115 | 3.2976 | 3.1721 | 3.0387 | 2.8452 | 2.6424 | 2.4212 | 2.1594 | 1.865 | 1.5985 | 1.0326 | 0.31891 | 0.075306 | -0.051962
|  | WOOLSTON | ST |  |  | 3.6977 | 3.6562 | 3.6128 | 3.5614 | 3.4912 | 3.4164 | 3.339 | 3.2519 | 3.1549 | 3.0523 | 2.597 | 1.9241 | 1.5094 | 1.2014 | 4.3441 | 4.3173 | 4.2884 | 4.2517 | 4.206 | 4.156 | 4.1026 | 4.0403 | 3.9685 | 3.8996 | 3.5563 | 3.1123 | 2.8658 | 2.6342 | 3.5394 | 3.5005 | 3.4593 | 3.4089 | 3.3419 | 3.2697 | 3.1944 | 3.1084 | 3.0113 | 2.9123 | 2.4489 | 1.8212 | 1.4734 | 1.2217
|  | WOOLSTON | SP |  |  | 3.7074 | 3.672 | 3.6375 | 3.5999 | 3.5005 | 3.4032 | 3.3022 | 3.1942 | 3.0826 | 2.9465 | 2.4863 | 1.4579 | 0.97002 | 0.67475 | 4.3462 | 4.3204 | 4.2949 | 4.2658 | 4.2144 | 4.1651 | 4.1122 | 4.0514 | 3.9879 | 3.9097 | 3.6262 | 2.9271 | 2.5967 | 2.3055 | 3.5469 | 3.5124 | 3.4792 | 3.4422 | 3.3537 | 3.268 | 3.1783 | 3.08 | 2.9786 | 2.8539 | 2.4228 | 1.4324 | 1.0071 | 0.76035
MINETY GSP | SWINDON BSP | WOOTTON BASSETT | MINIMUM HEADROOM | SU 07587 81123 | NO | 3.742 | 3.4964 | 3.2012 | 2.8816 | 2.3684 | 1.8368 | 1.261 | 0.65164 | -0.07637 | -0.86171 | -3.4099 | -7.231 | -10.5799 | -13.0966 | 18.3008 | 18.1465 | 17.958 | 17.7528 | 17.4488 | 17.1369 | 16.7886 | 16.4171 | 15.9681 | 15.4873 | 13.9323 | 11.5449 | 9.2366 | 7.0128 | 15.5288 | 15.3051 | 15.0323 | 14.7356 | 14.2603 | 13.771 | 13.237 | 12.6708 | 12.0013 | 11.29 | 8.9308 | 5.5353 | 2.7645 | 0.67078
|  | WOOTTON BASSETT | CT |  |  | 3.8352 | 3.6523 | 3.4529 | 3.1692 | 2.7838 | 2.3796 | 1.9687 | 1.5279 | 1.0314 | 0.30393 | -2.173 | -6.8179 | -10.5799 | -13.0966 | 18.3241 | 18.186 | 18.0379 | 17.8249 | 17.5607 | 17.2866 | 16.9994 | 16.6885 | 16.332 | 15.8547 | 14.2424 | 11.5449 | 9.2366 | 7.0128 | 15.6095 | 15.442 | 15.2583 | 14.9911 | 14.6294 | 14.2534 | 13.8687 | 13.4552 | 12.9873 | 12.3088 | 10.0497 | 5.9572 | 2.7645 | 0.67078
|  | WOOTTON BASSETT | LW |  |  | 3.742 | 3.4964 | 3.2012 | 2.8816 | 2.3684 | 1.8368 | 1.261 | 0.65164 | -0.07637 | -0.86171 | -3.4099 | -7.231 | -9.7011 | -11.5296 | 18.3008 | 18.1465 | 17.958 | 17.7528 | 17.4488 | 17.1369 | 16.7886 | 16.4171 | 15.9681 | 15.4873 | 13.9323 | 11.8274 | 10.6267 | 9.6951 | 15.5288 | 15.3051 | 15.0323 | 14.7356 | 14.2603 | 13.771 | 13.237 | 12.6708 | 12.0013 | 11.29 | 8.9308 | 5.5353 | 3.4804 | 1.9882
|  | WOOTTON BASSETT | ST |  |  | 3.9796 | 3.8892 | 3.7935 | 3.6922 | 3.5266 | 3.3532 | 3.1663 | 2.9661 | 2.727 | 2.4769 | 1.408 | -1.8798 | -4.3008 | -6.0819 | 18.4172 | 18.338 | 18.256 | 18.1692 | 18.0303 | 17.8886 | 17.7329 | 17.5645 | 17.3636 | 17.1607 | 16.2955 | 13.7535 | 11.7454 | 9.8022 | 15.7462 | 15.6661 | 15.5803 | 15.489 | 15.3305 | 15.1682 | 14.9919 | 14.8027 | 14.576 | 14.3404 | 13.3302 | 10.2932 | 8.1859 | 6.7332
|  | WOOTTON BASSETT | SP |  |  | 3.9968 | 3.8983 | 3.8006 | 3.7015 | 3.5744 | 3.4488 | 3.3181 | 3.1679 | 3.0004 | 2.808 | 2.0353 | -0.42657 | -2.7753 | -4.2029 | 18.4235 | 18.3337 | 18.2439 | 18.1517 | 18.0389 | 17.929 | 17.8106 | 17.6746 | 17.5208 | 17.3369 | 16.5961 | 14.324 | 11.6883 | 8.8075 | 15.7619 | 15.6728 | 15.5843 | 15.4942 | 15.3731 | 15.2571 | 15.1354 | 14.9947 | 14.8375 | 14.6573 | 13.9329 | 11.6662 | 9.5682 | 8.3706
COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD | MINIMUM HEADROOM | SU 49244 98269 | YES | 6.9831 | 6.4482 | 5.9152 | 5.3528 | 4.6808 | 3.9732 | 3.3142 | 2.6405 | 1.8667 | 1.0061 | -1.1789 | -3.7636 | -4.5544 | -5.0113 | 9.7648 | 9.4932 | 9.2166 | 8.9241 | 8.601 | 8.2518 | 7.9147 | 7.5642 | 7.1235 | 6.632 | 5.5295 | 4.3463 | 3.6434 | 3.1385 | 7.1945 | 6.7615 | 6.3203 | 5.854 | 5.3071 | 4.7111 | 4.1162 | 3.5049 | 2.7941 | 2.002 | 0.019422 | -2.2972 | -2.9897 | -3.3871
|  | WOOTTON ROAD | CT |  |  | 7.2957 | 6.9245 | 6.5635 | 6.1602 | 5.7197 | 5.2479 | 4.836 | 4.4147 | 3.9504 | 3.1749 | 1.1633 | -2.2527 | -4.4263 | -4.741 | 9.8544 | 9.6308 | 9.4086 | 9.1568 | 8.9104 | 8.6423 | 8.3965 | 8.1394 | 7.8412 | 7.3731 | 6.2498 | 4.6693 | 3.6434 | 3.1385 | 7.4102 | 7.0954 | 6.7837 | 6.4291 | 6.0549 | 5.6514 | 5.2892 | 4.9141 | 4.4889 | 3.7873 | 2.0136 | -0.95056 | -2.8596 | -3.1329
|  | WOOTTON ROAD | LW |  |  | 6.9831 | 6.4482 | 5.9152 | 5.3528 | 4.6808 | 3.9732 | 3.3142 | 2.6405 | 1.8667 | 1.0061 | -1.1789 | -3.7636 | -4.5544 | -5.0113 | 9.7648 | 9.4932 | 9.2166 | 8.9241 | 8.601 | 8.2518 | 7.9147 | 7.5642 | 7.1235 | 6.632 | 5.5295 | 4.3463 | 4.0386 | 3.8671 | 7.1945 | 6.7615 | 6.3203 | 5.854 | 5.3071 | 4.7111 | 4.1162 | 3.5049 | 2.7941 | 2.002 | 0.019422 | -2.2972 | -2.9897 | -3.3871
|  | WOOTTON ROAD | ST |  |  | 7.4194 | 7.1638 | 6.9306 | 6.6801 | 6.4154 | 6.1316 | 5.8808 | 5.6305 | 5.3551 | 5.056 | 3.9159 | 1.6373 | 0.35714 | -0.49717 | 9.9591 | 9.816 | 9.6817 | 9.5318 | 9.3758 | 9.2063 | 9.0499 | 8.8912 | 8.7085 | 8.5248 | 7.745 | 6.2126 | 5.4225 | 4.7348 | 7.5486 | 7.3473 | 7.1598 | 6.953 | 6.7276 | 6.4848 | 6.2638 | 6.0416 | 5.7915 | 5.5279 | 4.4567 | 2.3769 | 1.3108 | 0.61653
|  | WOOTTON ROAD | SP |  |  | 7.4549 | 7.2248 | 7.0234 | 6.8124 | 6.4376 | 6.0371 | 5.6694 | 5.3001 | 4.918 | 4.4791 | 3.0581 | -0.06138 | -1.8759 | -2.8812 | 9.9702 | 9.8337 | 9.71 | 9.5768 | 9.4012 | 9.2078 | 9.0281 | 8.8435 | 8.6436 | 8.4214 | 7.6432 | 5.7069 | 4.4683 | 3.4881 | 7.5724 | 7.3864 | 7.2217 | 7.0463 | 6.7632 | 6.4489 | 6.1566 | 5.8601 | 5.548 | 5.1936 | 3.9118 | 1.0497 | -0.59661 | -1.4852
BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM | MINIMUM HEADROOM | SU 82093 44312 | YES | 19.9717 | 19.3862 | 18.7979 | 18.3655 | 17.6481 | 16.868 | 15.959 | 14.9944 | 13.8574 | 12.6439 | 9.0391 | 4.5728 | 0.3588 | -2.3773 | 22.4378 | 22.1037 | 21.7459 | 21.4618 | 21.0562 | 20.6096 | 20.0563 | 19.462 | 18.7337 | 17.954 | 15.6825 | 12.3092 | 9.1927 | 5.9279 | 20.6489 | 20.1568 | 19.6365 | 19.2303 | 18.5704 | 17.8532 | 17.0136 | 16.1186 | 15.0494 | 13.9054 | 10.5279 | 6.5316 | 2.9768 | 0.75529
|  | WRECCLESHAM | CT |  |  | 20.0884 | 19.5847 | 19.1535 | 18.7636 | 18.253 | 17.6878 | 17.0075 | 16.2876 | 15.4767 | 14.3155 | 10.4872 | 4.7396 | 0.3588 | -2.3773 | 22.456 | 22.1365 | 21.8517 | 21.5458 | 21.1947 | 20.8056 | 20.3226 | 19.806 | 19.2016 | 18.4303 | 15.837 | 12.3092 | 9.1927 | 5.9279 | 20.7276 | 20.3014 | 19.9283 | 19.5477 | 19.0861 | 18.5752 | 17.9516 | 17.2793 | 16.51 | 15.4248 | 11.8453 | 6.7347 | 2.9768 | 0.75529
|  | WRECCLESHAM | LW |  |  | 19.9717 | 19.3862 | 18.7979 | 18.3655 | 17.6481 | 16.868 | 15.959 | 14.9944 | 13.8574 | 12.6439 | 9.0391 | 4.5728 | 1.9913 | 0.29939 | 22.4378 | 22.1037 | 21.7459 | 21.4618 | 21.0562 | 20.6096 | 20.0563 | 19.462 | 18.7337 | 17.954 | 15.6825 | 13.2578 | 12.037 | 11.1892 | 20.6489 | 20.1568 | 19.6365 | 19.2303 | 18.5704 | 17.8532 | 17.0136 | 16.1186 | 15.0494 | 13.9054 | 10.5279 | 6.5316 | 4.3588 | 2.9701
|  | WRECCLESHAM | ST |  |  | 20.3307 | 20.0306 | 19.7935 | 19.6788 | 19.4709 | 19.2331 | 18.8986 | 18.5454 | 18.1272 | 17.7374 | 16.1362 | 11.6918 | 9.0646 | 7.092 | 22.6185 | 22.4221 | 22.2541 | 22.1488 | 21.9712 | 21.7707 | 21.4847 | 21.1791 | 20.8085 | 20.4728 | 19.0909 | 15.4338 | 12.8428 | 9.8448 | 20.9555 | 20.7102 | 20.5085 | 20.4009 | 20.2009 | 19.9736 | 19.6584 | 19.3231 | 18.9187 | 18.5517 | 17.0141 | 12.8364 | 10.6547 | 9.081
|  | WRECCLESHAM | SP |  |  | 20.3603 | 20.0547 | 19.8177 | 19.6946 | 19.5371 | 19.3663 | 19.1112 | 18.838 | 18.5188 | 18.2047 | 17.0158 | 13.6709 | 11.0021 | 9.6251 | 22.6309 | 22.4209 | 22.2408 | 22.1175 | 21.9738 | 21.8153 | 21.5803 | 21.3242 | 21.0136 | 20.6801 | 19.3959 | 15.8289 | 11.6257 | 6.2252 | 20.9814 | 20.7251 | 20.5185 | 20.3983 | 20.2503 | 20.0905 | 19.856 | 19.6015 | 19.2959 | 19.0015 | 17.8682 | 14.6594 | 12.2146 | 11.0771
MINETY GSP | TOOTHILL BSP | WROUGHTON | MINIMUM HEADROOM | SU 14446 81504 | NO | 11.1471 | 10.7777 | 10.3582 | 9.9115 | 9.1794 | 8.4193 | 7.6045 | 6.721 | 5.6241 | 4.5324 | 2.0441 | -0.7853 | -2.2231 | -3.3212 | 15.7673 | 15.5729 | 15.3438 | 15.0949 | 14.7221 | 14.3302 | 13.8967 | 13.4189 | 12.7919 | 12.168 | 10.8333 | 9.2112 | 7.5165 | 5.9873 | 12.6926 | 12.3439 | 11.9372 | 11.5003 | 10.8189 | 10.1073 | 9.3322 | 8.4828 | 7.391 | 6.3112 | 3.9947 | 1.4742 | 0.34598 | -0.55311
|  | WROUGHTON | CT |  |  | 11.3809 | 11.1553 | 10.899 | 10.5615 | 10.0957 | 9.6043 | 9.0855 | 8.5116 | 7.8306 | 6.6897 | 4.1049 | 0.33609 | -2.2231 | -3.3212 | 15.8332 | 15.6802 | 15.5044 | 15.27 | 14.9877 | 14.6862 | 14.3602 | 13.9951 | 13.5571 | 12.9022 | 11.4048 | 9.2112 | 7.5165 | 5.9873 | 12.8731 | 12.644 | 12.3806 | 12.0245 | 11.5687 | 11.0851 | 10.5691 | 9.9931 | 9.3053 | 8.2201 | 5.8039 | 2.4608 | 0.34598 | -0.55311
|  | WROUGHTON | LW |  |  | 11.1471 | 10.7777 | 10.3582 | 9.9115 | 9.1794 | 8.4193 | 7.6045 | 6.721 | 5.6241 | 4.5324 | 2.0441 | -0.7853 | -1.7448 | -2.0889 | 15.7673 | 15.5729 | 15.3438 | 15.0949 | 14.7221 | 14.3302 | 13.8967 | 13.4189 | 12.7919 | 12.168 | 10.8333 | 9.4141 | 9.0044 | 8.8538 | 12.6926 | 12.3439 | 11.9372 | 11.5003 | 10.8189 | 10.1073 | 9.3322 | 8.4828 | 7.391 | 6.3112 | 3.9947 | 1.4742 | 0.67353 | 0.38906
|  | WROUGHTON | ST |  |  | 11.585 | 11.4929 | 11.3781 | 11.2412 | 11.0338 | 10.8096 | 10.5642 | 10.2913 | 9.9779 | 9.6336 | 8.0066 | 4.9494 | 3.5163 | 2.6187 | 15.9577 | 15.8867 | 15.7986 | 15.6927 | 15.5478 | 15.3892 | 15.2114 | 15.011 | 14.7773 | 14.5343 | 13.406 | 11.2331 | 9.8522 | 8.3753 | 13.0825 | 12.9914 | 12.8743 | 12.7321 | 12.5218 | 12.293 | 12.0401 | 11.7566 | 11.4289 | 11.0834 | 9.4371 | 6.5162 | 5.2151 | 4.4248
|  | WROUGHTON | SP |  |  | 11.6275 | 11.5448 | 11.4453 | 11.3412 | 11.1579 | 10.9665 | 10.775 | 10.5444 | 10.2981 | 9.977 | 8.7771 | 5.4732 | 3.8437 | 3.1862 | 15.9728 | 15.9008 | 15.8131 | 15.7189 | 15.5934 | 15.4578 | 15.317 | 15.1465 | 14.9566 | 14.72 | 13.8012 | 11.2706 | 9.1885 | 6.702 | 13.119 | 13.0323 | 12.9265 | 12.8155 | 12.6383 | 12.4514 | 12.2645 | 12.0346 | 11.7861 | 11.4715 | 10.2623 | 7.0276 | 5.4928 | 4.8973
AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH | MINIMUM HEADROOM | SU 88582 91845 | YES | 3.97 | 3.2442 | 2.3938 | 1.4345 | -0.060279 | -1.65 | -3.3296 | -5.1946 | -7.3003 | -9.0011 | -12.7435 | -16.9582 | -20.3532 | -22.2744 | 4.4695 | 4.0375 | 3.5222 | 2.9424 | 2.1163 | 1.2334 | 0.27891 | -0.79264 | -2.0758 | -3.1442 | -5.3317 | -8.2111 | -10.6373 | -12.7977 | 1.0242 | 0.3923 | -0.35762 | -1.2058 | -2.5175 | -3.9158 | -5.4059 | -7.0662 | -8.9789 | -10.5619 | -14.0068 | -17.822 | -20.6966 | -22.2714
|  | WYCOMBE MARSH | CT |  |  | 4.1015 | 3.4839 | 2.7658 | 1.8844 | 0.68038 | -0.60997 | -1.9355 | -3.431 | -5.0037 | -6.7736 | -10.7826 | -16.4482 | -20.3532 | -22.2744 | 4.4695 | 4.0524 | 3.5698 | 2.9752 | 2.2449 | 1.461 | 0.64127 | -0.28954 | -1.3008 | -2.4509 | -4.9657 | -8.2111 | -10.6373 | -12.7977 | 1.1324 | 0.59629 | -0.033754 | -0.81654 | -1.8676 | -2.9967 | -4.1644 | -5.4871 | -6.8981 | -8.5446 | -12.2397 | -17.3146 | -20.6966 | -22.2714
|  | WYCOMBE MARSH | LW |  |  | 3.97 | 3.2442 | 2.3938 | 1.4345 | -0.060279 | -1.65 | -3.3296 | -5.1946 | -7.3003 | -9.0011 | -12.7435 | -16.9582 | -18.6151 | -19.4748 | 4.4708 | 4.0375 | 3.5222 | 2.9424 | 2.1163 | 1.2334 | 0.27891 | -0.79264 | -2.0758 | -3.1442 | -5.3317 | -7.5526 | -8.2653 | -8.6362 | 1.0242 | 0.3923 | -0.35762 | -1.2058 | -2.5175 | -3.9158 | -5.4059 | -7.0662 | -8.9789 | -10.5619 | -14.0068 | -17.822 | -19.2585 | -19.993
|  | WYCOMBE MARSH | ST |  |  | 4.47 | 4.1246 | 3.7277 | 3.2772 | 2.6 | 1.8711 | 1.1183 | 0.27268 | -0.59546 | -1.2073 | -3.64 | -8.0632 | -10.2066 | -11.5851 | 4.7356 | 4.5007 | 4.2259 | 3.9105 | 3.4499 | 2.9529 | 2.4321 | 1.8452 | 1.2265 | 0.7719 | -1.1515 | -4.6653 | -6.6143 | -8.6134 | 1.4906 | 1.2152 | 0.89081 | 0.51827 | -0.05072 | -0.66625 | -1.3083 | -2.0331 | -2.7906 | -3.3487 | -5.6601 | -9.8407 | -11.7532 | -12.9424
|  | WYCOMBE MARSH | SP |  |  | 4.4945 | 4.1563 | 3.7976 | 3.4025 | 2.8185 | 2.2028 | 1.5344 | 0.78891 | 0.059187 | -0.49158 | -2.33 | -6.829 | -9.053 | -9.9076 | 4.74 | 4.5001 | 4.2392 | 3.949 | 3.5713 | 3.1665 | 2.7132 | 2.1972 | 1.6732 | 1.2497 | -0.26819 | -4.2456 | -7.1286 | -10.219 | 1.5122 | 1.242 | 0.9532 | 0.63291 | 0.15946 | -0.3419 | -0.89867 | -1.5249 | -2.147 | -2.6435 | -4.3588 | -8.6656 | -10.7453 | -11.5008
LOVEDEAN GSP | WYMERING BSP | WYMERING | MINIMUM HEADROOM | SU 64974 05375 | NO | 15.1258 | 14.6593 | 14.1948 | 13.686 | 12.8725 | 12.0443 | 11.1506 | 10.1376 | 8.9123 | 7.794 | 5.4862 | 2.5163 | 0.91593 | -0.41615 | 20.7869 | 20.504 | 20.2258 | 19.9114 | 19.4593 | 18.9991 | 18.4829 | 17.8756 | 17.0817 | 16.3883 | 15.167 | 13.6856 | 12.2006 | 11.0224 | 17.9271 | 17.4976 | 17.0663 | 16.5858 | 15.8341 | 15.0671 | 14.2341 | 13.2834 | 12.1169 | 11.0611 | 8.9435 | 6.2482 | 4.8204 | 3.5903
|  | WYMERING | CT |  |  | 15.3523 | 15.0315 | 14.6747 | 14.3011 | 13.7772 | 13.2474 | 12.6903 | 12.0442 | 11.2942 | 10.1223 | 7.8081 | 3.8164 | 0.91593 | -0.41615 | 20.8282 | 20.5803 | 20.3025 | 20.0088 | 19.6715 | 19.3233 | 18.9392 | 18.4843 | 17.9419 | 17.1736 | 15.8341 | 13.754 | 12.2006 | 11.0224 | 18.1365 | 17.8231 | 17.4761 | 17.113 | 16.6205 | 16.1214 | 15.5925 | 14.9759 | 14.2556 | 13.1438 | 11.0119 | 7.4326 | 4.8204 | 3.5903
|  | WYMERING | LW |  |  | 15.1258 | 14.6593 | 14.1948 | 13.686 | 12.8725 | 12.0443 | 11.1506 | 10.1376 | 8.9123 | 7.794 | 5.4862 | 2.5163 | 1.4413 | 0.80311 | 20.7869 | 20.504 | 20.2258 | 19.9114 | 19.4593 | 18.9991 | 18.4829 | 17.8756 | 17.0817 | 16.3883 | 15.167 | 13.6856 | 13.2295 | 12.9666 | 17.9271 | 17.4976 | 17.0663 | 16.5858 | 15.8341 | 15.0671 | 14.2341 | 13.2834 | 12.1169 | 11.0611 | 8.9435 | 6.2482 | 5.3027 | 4.7391
|  | WYMERING | ST |  |  | 15.6237 | 15.4767 | 15.3018 | 15.0861 | 14.8163 | 14.5517 | 14.2653 | 13.9413 | 13.5785 | 13.2029 | 11.3441 | 8.6013 | 7.1252 | 6.1067 | 21.0291 | 20.9114 | 20.7719 | 20.5969 | 20.3952 | 20.1983 | 19.9791 | 19.7275 | 19.4395 | 19.1678 | 17.7373 | 15.7462 | 14.6435 | 13.5742 | 18.3864 | 18.2484 | 18.0887 | 17.8794 | 17.6234 | 17.3715 | 17.0975 | 16.7863 | 16.4359 | 16.0776 | 14.277 | 11.6877 | 10.3649 | 9.4753
|  | WYMERING | SP |  |  | 15.6552 | 15.5294 | 15.4035 | 15.2537 | 14.9549 | 14.6755 | 14.3857 | 14.0541 | 13.7007 | 13.2767 | 11.7259 | 7.9419 | 6.257 | 5.3847 | 21.0372 | 20.926 | 20.8124 | 20.6758 | 20.48 | 20.2999 | 20.1096 | 19.8797 | 19.6302 | 19.3489 | 18.2597 | 15.421 | 14.0041 | 12.8054 | 18.4162 | 18.2982 | 18.1817 | 18.0357 | 17.7584 | 17.4997 | 17.2311 | 16.92 | 16.5877 | 16.1906 | 14.7248 | 11.1127 | 9.5547 | 8.7758
COWLEY GSP | YARNTON BSP | YARNTON | MINIMUM HEADROOM | SP 48277 12108 | NO | 17.1687 | 16.9115 | 16.5379 | 16.1387 | 15.5526 | 14.9307 | 14.284 | 13.6209 | 12.9518 | 12.3208 | 10.9001 | 9.4484 | 8.3816 | 7.7449 | 2.3913 | 2.248 | 2.0361 | 1.8107 | 1.5045 | 1.1783 | 0.83325 | 0.47741 | 0.0983 | -0.28157 | -1.0783 | -1.8919 | -2.6461 | -3.2192 | 17.8478 | 17.6126 | 17.2699 | 16.9014 | 16.3797 | 15.8239 | 15.2364 | 14.6289 | 13.98 | 13.3715 | 12.0622 | 10.7523 | 9.9299 | 9.4331
|  | YARNTON | CT |  |  | 17.2709 | 17.0746 | 16.7721 | 16.4196 | 15.9627 | 15.473 | 14.9719 | 14.4577 | 13.9295 | 13.2844 | 11.7571 | 9.7979 | 8.3816 | 7.7449 | 2.417 | 2.2903 | 2.1035 | 1.8826 | 1.6219 | 1.3424 | 1.0531 | 0.7539 | 0.45823 | 0.076066 | -0.82419 | -1.8919 | -2.6461 | -3.2192 | 17.9169 | 17.7303 | 17.4527 | 17.116 | 16.7014 | 16.255 | 15.7933 | 15.3141 | 14.8387 | 14.2402 | 12.827 | 11.0756 | 9.9299 | 9.4331
|  | YARNTON | LW |  |  | 17.1687 | 16.9115 | 16.5379 | 16.1387 | 15.5526 | 14.9307 | 14.284 | 13.6209 | 12.9518 | 12.3208 | 10.9001 | 9.4484 | 8.878 | 8.6549 | 2.3913 | 2.248 | 2.0361 | 1.8107 | 1.5045 | 1.1783 | 0.83325 | 0.47741 | 0.0983 | -0.28157 | -1.0783 | -1.8217 | -2.0607 | -2.1529 | 17.8478 | 17.6126 | 17.2699 | 16.9014 | 16.3797 | 15.8239 | 15.2364 | 14.6289 | 13.98 | 13.3715 | 12.0622 | 10.7523 | 10.28 | 10.1032
|  | YARNTON | ST |  |  | 17.3853 | 17.2778 | 17.1021 | 16.9169 | 16.6665 | 16.3967 | 16.1217 | 15.8425 | 15.5859 | 15.364 | 14.5202 | 12.8589 | 12.1314 | 11.654 | 2.4967 | 2.4224 | 2.3073 | 2.1839 | 2.0204 | 1.844 | 1.6623 | 1.4759 | 1.2988 | 1.1592 | 0.61447 | -0.55574 | -1.1194 | -1.655 | 18.0512 | 17.9538 | 17.7993 | 17.6311 | 17.396 | 17.1416 | 16.8793 | 16.61 | 16.3528 | 16.1489 | 15.3465 | 13.7787 | 13.1534 | 12.7386
|  | YARNTON | SP |  |  | 17.4024 | 17.2998 | 17.1408 | 16.9803 | 16.7578 | 16.5229 | 16.2785 | 16.0234 | 15.8012 | 15.6084 | 14.9619 | 13.3187 | 12.488 | 12.1875 | 2.5026 | 2.4269 | 2.3176 | 2.2052 | 2.0674 | 1.9196 | 1.7611 | 1.5932 | 1.4422 | 1.3102 | 0.86924 | -0.33797 | -1.1857 | -1.9632 | 18.0649 | 17.9669 | 17.8267 | 17.6822 | 17.4901 | 17.2841 | 17.0611 | 16.8222 | 16.6088 | 16.4225 | 15.7967 | 14.2289 | 13.4641 | 13.1965
BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON | MINIMUM HEADROOM | SU 53699 74307 | YES | 12.0898 | 11.5787 | 11.065 | 10.5223 | 9.798 | 9.0865 | 8.3291 | 7.5172 | 6.5655 | 5.558 | 2.9064 | -0.22331 | -1.8023 | -3.0171 | 16.8393 | 16.5358 | 16.2393 | 15.9143 | 15.5215 | 15.1281 | 14.6931 | 14.2197 | 13.622 | 12.9802 | 11.3615 | 9.5315 | 7.8871 | 6.4218 | 13.7552 | 13.3082 | 12.8492 | 12.3593 | 11.7017 | 11.0477 | 10.3458 | 9.5914 | 8.6943 | 7.7411 | 5.2514 | 2.3645 | 1.0309 | 0.010721
|  | YATTENDON | CT |  |  | 12.2638 | 11.8554 | 11.4623 | 11.0037 | 10.4857 | 9.9948 | 9.5023 | 8.9695 | 8.35 | 7.3932 | 4.7123 | 0.74326 | -1.8023 | -3.0171 | 16.8886 | 16.6151 | 16.3508 | 16.0307 | 15.7035 | 15.3853 | 15.0486 | 14.681 | 14.2403 | 13.6161 | 11.8817 | 9.5315 | 7.8871 | 6.4218 | 13.9071 | 13.5505 | 13.1989 | 12.7808 | 12.306 | 11.8491 | 11.3855 | 10.8833 | 10.2945 | 9.3934 | 6.8793 | 3.2744 | 1.0309 | 0.010721
|  | YATTENDON | LW |  |  | 12.0898 | 11.5787 | 11.065 | 10.5223 | 9.798 | 9.0865 | 8.3291 | 7.5172 | 6.5655 | 5.558 | 2.9064 | -0.22331 | -1.3097 | -1.849 | 16.8393 | 16.5358 | 16.2393 | 15.9143 | 15.5215 | 15.1281 | 14.6931 | 14.2197 | 13.622 | 12.9802 | 11.3615 | 9.5955 | 9.1063 | 8.8683 | 13.7552 | 13.3082 | 12.8492 | 12.3593 | 11.7017 | 11.0477 | 10.3458 | 9.5914 | 8.6943 | 7.7411 | 5.2514 | 2.3645 | 1.4099 | 0.94606
|  | YATTENDON | ST |  |  | 12.5174 | 12.2758 | 12.064 | 11.8415 | 11.6147 | 11.4065 | 11.1799 | 10.9326 | 10.6437 | 10.333 | 9.0239 | 5.9822 | 4.4819 | 3.5501 | 17.0411 | 16.8639 | 16.7106 | 16.5497 | 16.3893 | 16.2343 | 16.0526 | 15.8528 | 15.6154 | 15.3732 | 14.3231 | 11.902 | 10.5295 | 9.1544 | 14.1455 | 13.9438 | 13.7616 | 13.5661 | 13.3601 | 13.1652 | 12.9499 | 12.7145 | 12.4358 | 12.1415 | 10.8707 | 7.9624 | 6.6282 | 5.8188
|  | YATTENDON | SP |  |  | 12.5559 | 12.3185 | 12.1236 | 11.9291 | 11.7453 | 11.5821 | 11.4194 | 11.2229 | 11.005 | 10.7376 | 9.7714 | 7.0221 | 5.2161 | 4.4984 | 17.0584 | 16.8777 | 16.7279 | 16.5772 | 16.4443 | 16.3189 | 16.1866 | 16.0224 | 15.8346 | 15.6068 | 14.7485 | 12.2431 | 9.9654 | 7.5661 | 14.1797 | 13.9786 | 13.8103 | 13.6395 | 13.4758 | 13.3239 | 13.1719 | 12.9865 | 12.778 | 12.5281 | 11.608 | 8.9522 | 7.2549 | 6.6136
MELKSHAM GSP | CHIPPENHAM | YATTON KEYNALL | MINIMUM HEADROOM | ST 87300 75782 | YES | 27.5415 | 27.1629 | 26.7189 | 26.1547 | 25.3405 | 23.8338 | 22.2376 | 20.5675 | 18.647 | 16.6171 | 10.4619 | 3.0825 | -2.2396 | -5.5476 | 30.4855 | 30.1717 | 29.813 | 29.366 | 28.911 | 28.4338 | 27.8899 | 27.2635 | 26.5241 | 25.7109 | 21.9226 | 16.5844 | 12.1074 | 7.3261 | 29.9813 | 29.4377 | 28.7674 | 27.9263 | 26.635 | 25.2877 | 23.8808 | 22.402 | 20.6917 | 18.8795 | 13.3365 | 6.6241 | 2.0099 | -0.86286
|  | YATTON KEYNALL | CT |  |  | 27.5415 | 27.1629 | 26.7313 | 26.1732 | 25.503 | 24.7089 | 23.7486 | 22.4334 | 21.044 | 19.0585 | 13.0365 | 3.7933 | -2.2396 | -5.5476 | 30.4855 | 30.1717 | 29.813 | 29.366 | 28.911 | 28.4338 | 27.8921 | 27.3122 | 26.6789 | 25.9591 | 22.5657 | 16.5844 | 12.1074 | 7.3261 | 30.1306 | 29.6971 | 29.1924 | 28.4294 | 27.418 | 26.3628 | 25.2654 | 24.1121 | 22.8859 | 21.1186 | 15.7053 | 7.3765 | 2.0099 | -0.86286
|  | YATTON KEYNALL | LW |  |  | 27.5765 | 27.1743 | 26.7189 | 26.1547 | 25.3405 | 23.8338 | 22.2376 | 20.5675 | 18.647 | 16.6171 | 10.4619 | 3.0825 | -0.11635 | -2.0838 | 30.5218 | 30.2073 | 29.8434 | 29.4122 | 28.9561 | 28.4677 | 27.8899 | 27.2635 | 26.5241 | 25.7109 | 21.9226 | 17.4664 | 16.1754 | 15.2023 | 29.9813 | 29.4377 | 28.7674 | 27.9263 | 26.635 | 25.2877 | 23.8808 | 22.402 | 20.6917 | 18.8795 | 13.3365 | 6.6241 | 3.8848 | 2.236
|  | YATTON KEYNALL | ST |  |  | 27.7382 | 27.4824 | 27.2006 | 26.8479 | 26.421 | 25.9739 | 25.4831 | 24.9543 | 24.326 | 23.4521 | 20.0243 | 12.0142 | 8.0953 | 7.1087 | 30.6159 | 30.3834 | 30.1234 | 29.8196 | 29.4822 | 29.1302 | 28.7186 | 28.2726 | 27.784 | 27.2473 | 25.1862 | 19.8949 | 16.6479 | 12.2602 | 30.4053 | 30.1644 | 29.8904 | 29.5429 | 29.0466 | 28.5281 | 27.9754 | 27.3888 | 26.7406 | 26.0275 | 23.2916 | 16.7723 | 12.9158 | 10.7885
|  | YATTON KEYNALL | SP |  |  | 27.7533 | 27.5074 | 27.2362 | 26.9015 | 26.529 | 26.1506 | 25.7422 | 25.3106 | 24.8586 | 24.3725 | 22.3697 | 16.8258 | 11.5895 | 10.001 | 30.6232 | 30.3927 | 30.1337 | 29.8358 | 29.5316 | 29.2195 | 28.8539 | 28.4615 | 28.0655 | 27.6285 | 26.0729 | 22.3877 | 15.7342 | 7.5666 | 30.4424 | 30.2063 | 29.9414 | 29.615 | 29.2365 | 28.8478 | 28.422 | 27.9715 | 27.5128 | 26.9869 | 25.1293 | 20.5863 | 16.4851 | 14.9975
AXMINSTER | YEOVIL BSP | YEOVIL | MINIMUM HEADROOM | ST 57690 16833 | YES | 18.2818 | 16.4748 | 14.4539 | 12.2422 | 9.2826 | 6.1706 | 3.0871 | -0.10191 | -3.6075 | -7.2193 | -14.8896 | -22.9498 | -25.9569 | -27.7001 | 24.8739 | 24.192 | 23.5467 | 22.8419 | 21.9371 | 20.4322 | 18.8216 | 17.1457 | 15.2275 | 13.2288 | 9.1277 | 5.1133 | 2.3758 | 0.36274 | 18.9048 | 17.6579 | 16.3649 | 14.9645 | 12.7236 | 10.2103 | 7.5497 | 4.7815 | 1.6741 | -1.5691 | -8.3926 | -15.3923 | -17.8638 | -19.3334
|  | YEOVIL | CT |  |  | 19.05 | 17.6624 | 16.1189 | 14.282 | 11.9305 | 9.4416 | 7.0339 | 4.5435 | 1.8649 | -1.4558 | -8.6998 | -19.201 | -25.9569 | -27.7001 | 24.8739 | 24.217 | 23.6494 | 23.044 | 22.3597 | 21.5288 | 20.1793 | 18.7767 | 17.2352 | 15.3614 | 11.2398 | 5.8624 | 2.3758 | 0.36274 | 19.4431 | 18.4915 | 17.5056 | 16.3826 | 14.9215 | 12.8921 | 10.8085 | 8.6409 | 6.2784 | 3.3014 | -3.2521 | -12.2034 | -17.8638 | -19.3334
|  | YEOVIL | LW |  |  | 18.2818 | 16.4748 | 14.4539 | 12.2422 | 9.2826 | 6.1706 | 3.0871 | -0.10191 | -3.6075 | -7.2193 | -14.8896 | -22.9498 | -25.2392 | -26.7635 | 24.9043 | 24.192 | 23.5467 | 22.8419 | 21.9371 | 20.4322 | 18.8216 | 17.1457 | 15.2275 | 13.2288 | 9.1277 | 5.1133 | 4.1578 | 3.5584 | 18.9048 | 17.6579 | 16.3649 | 14.9645 | 12.7236 | 10.2103 | 7.5497 | 4.7815 | 1.6741 | -1.5691 | -8.3926 | -15.3923 | -17.2978 | -18.6349
|  | YEOVIL | ST |  |  | 19.3954 | 18.3885 | 17.353 | 16.2486 | 14.7678 | 13.207 | 11.709 | 10.1645 | 8.5229 | 6.9114 | 2.71 | -5.2174 | -9.1953 | -11.4737 | 25.025 | 24.4704 | 24.0248 | 23.5912 | 23.1044 | 22.6075 | 22.0984 | 21.5677 | 20.704 | 19.7185 | 16.923 | 11.5184 | 8.6592 | 6.4209 | 19.652 | 18.9293 | 18.2643 | 17.5824 | 16.7141 | 15.8062 | 14.9201 | 13.7836 | 12.353 | 10.9513 | 7.0099 | -0.41615 | -3.9171 | -5.78
|  | YEOVIL | SP |  |  | 19.4875 | 18.5468 | 17.6182 | 16.6465 | 15.0518 | 13.4084 | 11.7548 | 10.0733 | 8.3645 | 6.5972 | 2.1686 | -6.8347 | -12.3504 | -14.9724 | 25.0326 | 24.4849 | 24.0492 | 23.6318 | 23.1965 | 22.7363 | 22.2502 | 21.7125 | 20.9407 | 19.9281 | 17.3015 | 11.3933 | 6.8731 | 3.0133 | 19.7076 | 19.0519 | 18.4581 | 17.8631 | 16.8673 | 15.8549 | 14.8482 | 13.8247 | 12.4563 | 10.9545 | 7.0264 | -1.3455 | -6.3395 | -8.558
AXMINSTER | YEOVIL BSP | YETMINSTER | MINIMUM HEADROOM | ST 60294 10206 | YES | 3.6883 | 3.0545 | 2.4479 | 1.8401 | 0.92763 | -0.0021896 | -0.95358 | -1.8594 | -2.8134 | -3.5175 | -4.9455 | -6.5502 | -6.8881 | -8.0044 | 8.1072 | 7.7589 | 7.443 | 7.1314 | 6.6761 | 6.2142 | 5.7247 | 5.2208 | 4.6304 | 4.2022 | 3.4641 | 2.634 | 2.0954 | 1.2927 | 5.0113 | 4.5308 | 4.0813 | 3.6374 | 2.989 | 2.1575 | 1.2835 | 0.44969 | -0.41835 | -1.0628 | -2.4091 | -3.9214 | -4.2372 | -5.2692
|  | YETMINSTER | CT |  |  | 4.1965 | 3.8384 | 3.4776 | 3.1295 | 2.5385 | 1.9388 | 1.3254 | 0.72027 | 0.14352 | -0.56144 | -1.7569 | -3.6367 | -4.683 | -5.0662 | 8.2726 | 8.0203 | 7.7724 | 7.5363 | 7.1995 | 6.8601 | 6.4973 | 6.1172 | 5.7258 | 5.2485 | 4.5416 | 3.4775 | 2.8223 | 2.3056 | 5.4529 | 5.1997 | 4.9732 | 4.7536 | 4.3567 | 3.9536 | 3.4019 | 2.835 | 2.2875 | 1.6158 | 0.51498 | -1.1845 | -2.1497 | -2.5115
|  | YETMINSTER | LW |  |  | 3.6883 | 3.0545 | 2.4479 | 1.8401 | 0.92763 | -0.0021896 | -0.95358 | -1.8594 | -2.8134 | -3.5175 | -4.9455 | -6.5502 | -6.8881 | -7.0328 | 8.1072 | 7.7589 | 7.443 | 7.1314 | 6.6761 | 6.2142 | 5.7247 | 5.2208 | 4.6304 | 4.2022 | 3.4641 | 2.634 | 2.4788 | 2.4132 | 5.0113 | 4.5308 | 4.0813 | 3.6374 | 2.989 | 2.1575 | 1.2835 | 0.44969 | -0.41835 | -1.0628 | -2.4091 | -3.9214 | -4.2372 | -4.3727
|  | YETMINSTER | ST |  |  | 4.4113 | 4.186 | 3.9725 | 3.7543 | 3.3882 | 3.0181 | 2.6548 | 2.3006 | 1.9087 | 1.5072 | -0.22964 | -2.5207 | -3.4735 | -3.8881 | 8.4214 | 8.2561 | 8.1108 | 7.9628 | 7.7438 | 7.524 | 7.3022 | 7.0777 | 6.8228 | 6.5848 | 5.4381 | 3.9829 | 3.2898 | 2.7602 | 5.5618 | 5.3782 | 5.2299 | 5.0926 | 4.8603 | 4.628 | 4.3958 | 4.167 | 3.9116 | 3.5835 | 1.9414 | -0.1819 | -1.0447 | -1.4114
|  | YETMINSTER | SP |  |  | 4.474 | 4.2871 | 4.1303 | 3.9841 | 3.5374 | 3.1116 | 2.6866 | 2.2664 | 1.8366 | 1.2991 | -0.52302 | -4.5007 | -6.6662 | -8.0044 | 8.4418 | 8.2933 | 8.1728 | 8.0626 | 7.8278 | 7.6051 | 7.3787 | 7.1489 | 6.9097 | 6.633 | 5.6318 | 3.2733 | 2.0954 | 1.2927 | 5.6133 | 5.4624 | 5.3482 | 5.2449 | 4.9308 | 4.6305 | 4.3266 | 4.0268 | 3.7198 | 3.3239 | 1.6997 | -1.9624 | -4.0058 | -5.2692
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD | MINIMUM HEADROOM | SU 60592 00043 | YES | 2.2422 | 2.0591 | 1.8794 | 1.6917 | 1.4217 | 1.1431 | 0.84426 | 0.51296 | 0.099187 | -0.27222 | -1.0468 | -1.9546 | -2.2285 | -2.3535 | 2.0426 | 1.9425 | 1.845 | 1.7398 | 1.5971 | 1.4485 | 1.2827 | 1.0928 | 0.83268 | 0.60122 | 0.18805 | -0.29619 | -0.51125 | -0.81803 | 1.1948 | 1.0296 | 0.867 | 0.69832 | 0.45174 | 0.19721 | -0.072823 | -0.36845 | -0.72327 | -1.0466 | -1.7779 | -2.6382 | -2.9007 | -3.0206
|  | ZETLAND ROAD | CT |  |  | 2.3701 | 2.2625 | 2.1389 | 2.019 | 1.8547 | 1.6843 | 1.5026 | 1.2878 | 1.0469 | 0.69264 | -0.018149 | -1.1217 | -1.812 | -2.1218 | 2.0774 | 2.0012 | 1.9117 | 1.8239 | 1.7207 | 1.6128 | 1.4936 | 1.3482 | 1.1808 | 0.944 | 0.5184 | -0.10113 | -0.51125 | -0.81803 | 1.3263 | 1.2358 | 1.133 | 1.0328 | 0.88772 | 0.73733 | 0.57878 | 0.39453 | 0.19083 | -0.12148 | -0.78093 | -1.8213 | -2.495 | -2.7976
|  | ZETLAND ROAD | LW |  |  | 2.2422 | 2.0591 | 1.8794 | 1.6917 | 1.4217 | 1.1431 | 0.84426 | 0.51296 | 0.099187 | -0.27222 | -1.0468 | -1.9546 | -2.2285 | -2.3535 | 2.0426 | 1.9425 | 1.845 | 1.7398 | 1.5971 | 1.4485 | 1.2827 | 1.0928 | 0.83268 | 0.60122 | 0.18805 | -0.29619 | -0.43809 | -0.50477 | 1.1948 | 1.0296 | 0.867 | 0.69832 | 0.45174 | 0.19721 | -0.072823 | -0.36845 | -0.72327 | -1.0466 | -1.7779 | -2.6382 | -2.9007 | -3.0206
|  | ZETLAND ROAD | ST |  |  | 2.4743 | 2.4307 | 2.3749 | 2.3101 | 2.2207 | 2.1298 | 2.031 | 1.9205 | 1.7974 | 1.6662 | 1.0449 | 0.12923 | -0.34323 | -0.64339 | 2.1479 | 2.115 | 2.0719 | 2.0209 | 1.9604 | 1.8983 | 1.8285 | 1.7489 | 1.6563 | 1.5664 | 1.1109 | 0.4398 | 0.084641 | -0.22256 | 1.4127 | 1.375 | 1.3286 | 1.2756 | 1.1977 | 1.1185 | 1.0331 | 0.93865 | 0.83513 | 0.72058 | 0.20402 | -0.66643 | -1.0993 | -1.3693
|  | ZETLAND ROAD | SP |  |  | 2.4977 | 2.4661 | 2.432 | 2.3949 | 2.3243 | 2.2532 | 2.1824 | 2.0954 | 2.0064 | 1.8758 | 1.3955 | 0.13914 | -0.50866 | -0.87413 | 2.1565 | 2.1284 | 2.097 | 2.0621 | 2.0137 | 1.9651 | 1.9151 | 1.8509 | 1.7834 | 1.7002 | 1.3748 | 0.47674 | 0.04844 | -0.21851 | 1.4354 | 1.4093 | 1.3816 | 1.3515 | 1.2901 | 1.2275 | 1.1652 | 1.0912 | 1.0156 | 0.89996 | 0.48726 | -0.64987 | -1.2498 | -1.5807
[6 empty] | 12.2372 | 11.8061 | 11.2582 | 10.6558 | 9.7389 | 8.7835 | 7.7817 | 6.6433 | 5.3059 | 3.8455 | -0.58562 | -5.4548 | -9.8361 | -12.6107 | 12.0458 | 11.8135 | 11.4718 | 11.0955 | 10.6059 | 10.0876 | 9.5232 | 8.8793 | 8.105 | 7.2399 | 4.7118 | 2.0625 | -0.5362 | -2.7659 | 7.9737 | 7.5903 | 7.0838 | 6.5238 | 5.7024 | 4.8396 | 3.9216 | 2.8831 | 1.6529 | 0.29578 | -3.7466 | -8.0109 | -11.4636 | -13.7124
[6 empty] | 12.4833 | 12.1919 | 11.8618 | 11.3673 | 10.7274 | 10.0576 | 9.3496 | 8.5159 | 7.5675 | 6.122 | 1.6003 | -4.8783 | -9.8361 | -12.6107 | 12.0458 | 11.8634 | 11.6976 | 11.3307 | 10.9294 | 10.5057 | 10.0514 | 9.5244 | 8.9153 | 8.0489 | 5.3748 | 2.0625 | -0.5362 | -2.7659 | 8.1708 | 7.9035 | 7.6031 | 7.1221 | 6.5296 | 5.9052 | 5.2406 | 4.467 | 3.5824 | 2.2496 | -1.872 | -7.4119 | -11.4636 | -13.7124
[6 empty] | 12.2372 | 11.8061 | 11.2582 | 10.6558 | 9.7389 | 8.7835 | 7.7817 | 6.6433 | 5.3059 | 3.8455 | -0.58562 | -5.4548 | -7.9538 | -9.6556 | 12.0541 | 11.8135 | 11.4718 | 11.0955 | 10.6059 | 10.0876 | 9.5232 | 8.8793 | 8.105 | 7.2399 | 4.7118 | 2.25 | 1.1467 | 0.36114 | 7.9737 | 7.5903 | 7.0838 | 6.5238 | 5.7024 | 4.8396 | 3.9216 | 2.8831 | 1.6529 | 0.29578 | -3.7466 | -8.0109 | -10.0549 | -11.4353
[6 empty] | 12.638 | 12.4386 | 12.2371 | 12.0225 | 11.7207 | 11.4013 | 11.0701 | 10.6581 | 10.1774 | 9.6572 | 7.6564 | 3.5418 | 0.86088 | -1.1485 | 12.0831 | 11.9221 | 11.8093 | 11.7094 | 11.5734 | 11.3406 | 11.094 | 10.7922 | 10.4384 | 10.0745 | 8.6166 | 5.5211 | 3.5486 | 1.5951 | 8.3255 | 8.1482 | 7.9725 | 7.7844 | 7.5042 | 7.2038 | 6.8889 | 6.5027 | 6.0514 | 5.5756 | 3.7019 | -0.24631 | -2.524 | -4.1423
[6 empty] | 12.6726 | 12.4666 | 12.2666 | 12.0596 | 11.7702 | 11.4774 | 11.1599 | 10.7845 | 10.3721 | 9.8885 | 8.1561 | 4.7108 | 2.1882 | 0.75194 | 12.0844 | 11.9182 | 11.8013 | 11.6988 | 11.5767 | 11.3826 | 11.1737 | 10.9135 | 10.6265 | 10.2744 | 8.9482 | 5.9637 | 2.9825 | -0.41293 | 8.3559 | 8.1645 | 7.983 | 7.7961 | 7.5421 | 7.2812 | 6.9975 | 6.6589 | 6.2894 | 5.8569 | 4.2798 | 0.95533 | -1.3731 | -2.5653
[6 empty] | 1.1868 | 0.69236 | 0.14809 | -0.4039 | -1.2508 | -2.1255 | -3.0351 | -3.9258 | -5.006 | -6.0426 | -8.4838 | -10.7259 | -11.1352 | -11.59 | 2.4806 | 2.2734 | 2.0149 | 1.7484 | 1.3509 | 0.92843 | 0.45428 | -0.036322 | -0.6925 | -1.3178 | -2.4351 | -3.3624 | -3.5292 | -3.9652 | 0.24593 | -0.19495 | -0.68496 | -1.1827 | -1.9309 | -2.7058 | -3.5169 | -4.315 | -5.3045 | -6.2673 | -8.3705 | -10.3417 | -10.7031 | -11.0931
[6 empty] | 1.8063 | 1.6036 | 1.3771 | 1.0811 | 0.55991 | 0.010727 | -0.62812 | -1.2784 | -2.0327 | -2.9983 | -5.0322 | -7.6098 | -8.9827 | -9.4612 | 2.6671 | 2.5532 | 2.4181 | 2.2246 | 1.939 | 1.6332 | 1.2625 | 0.87225 | 0.39401 | -0.22038 | -1.335 | -2.465 | -3.0611 | -3.4019 | 0.78505 | 0.5994 | 0.3886 | 0.10551 | -0.35977 | -0.85121 | -1.4252 | -2.0142 | -2.7061 | -3.5974 | -5.4067 | -7.6539 | -8.8272 | -9.2328
[6 empty] | 1.1868 | 0.69236 | 0.14809 | -0.4039 | -1.2508 | -2.1255 | -3.0351 | -3.9258 | -5.006 | -6.0426 | -8.4838 | -10.7259 | -11.1352 | -11.4738 | 2.4806 | 2.2734 | 2.0149 | 1.7484 | 1.3509 | 0.92843 | 0.45428 | -0.036322 | -0.6925 | -1.3178 | -2.4351 | -3.3624 | -3.5292 | -3.6563 | 0.24593 | -0.19495 | -0.68496 | -1.1827 | -1.9309 | -2.7058 | -3.5169 | -4.315 | -5.3045 | -6.2673 | -8.3705 | -10.3417 | -10.7031 | -11.001
[6 empty] | 1.8966 | 1.7454 | 1.5775 | 1.4079 | 1.0384 | 0.66221 | 0.2267 | -0.22579 | -0.72126 | -1.2746 | -3.184 | -5.3218 | -6.2529 | -6.844 | 2.7463 | 2.6718 | 2.5865 | 2.4946 | 2.2932 | 2.0826 | 1.8229 | 1.5484 | 1.2375 | 0.90599 | -0.30019 | -1.5648 | -2.042 | -2.43 | 0.88016 | 0.73876 | 0.58772 | 0.43425 | 0.1121 | -0.22128 | -0.60851 | -1.0127 | -1.4577 | -1.9534 | -3.6891 | -5.6266 | -6.4497 | -6.9711
[6 empty] | 1.9856 | 1.873 | 1.7502 | 1.6265 | 1.1448 | 0.63619 | 0.082263 | -0.49405 | -1.0858 | -1.8601 | -4.13 | -8.065 | -10.3287 | -11.59 | 2.7753 | 2.7038 | 2.63 | 2.5547 | 2.3419 | 2.1092 | 1.835 | 1.5394 | 1.2263 | 0.84036 | -0.33898 | -2.5189 | -3.4369 | -3.9652 | 0.95889 | 0.84803 | 0.7354 | 0.62193 | 0.20841 | -0.23312 | -0.71768 | -1.2238 | -1.7439 | -2.4257 | -4.4256 | -8.019 | -9.9831 | -11.0931
[6 empty] | 7.8142 | 7.2795 | 6.6143 | 5.6541 | 4.0773 | 2.405 | 0.8176 | -0.83752 | -2.8164 | -4.8675 | -10.5439 | -17.6421 | -22.9543 | -26.6746 | 8.5927 | 8.2986 | 7.8892 | 7.3006 | 6.4469 | 5.5359 | 4.6404 | 3.6913 | 2.5138 | 1.258 | -2.2364 | -7.838 | -13.0697 | -20.5097 | 3.6214 | 3.142 | 2.5187 | 1.6433 | 0.25365 | -1.2256 | -2.6628 | -4.1753 | -6.0046 | -7.9246 | -13.2721 | -19.6937 | -23.8178 | -26.8466
[6 empty] | 8.123 | 7.7722 | 7.3629 | 6.5473 | 5.3563 | 4.0816 | 2.9268 | 1.7297 | 0.30388 | -1.6922 | -7.3283 | -16.3667 | -22.9543 | -26.6746 | 8.6447 | 8.3734 | 8.0488 | 7.4347 | 6.6555 | 5.8214 | 5.025 | 4.1846 | 3.1751 | 1.8752 | -1.9361 | -7.838 | -13.0697 | -18.9723 | 3.8653 | 3.5384 | 3.151 | 2.3822 | 1.3121 | 0.16471 | -0.90154 | -2.0157 | -3.349 | -5.1948 | -10.4389 | -18.3863 | -23.8178 | -26.8466
[6 empty] | 7.8142 | 7.2795 | 6.6143 | 5.6541 | 4.0773 | 2.405 | 0.8176 | -0.83752 | -2.8164 | -4.8675 | -10.5439 | -17.6421 | -21.1773 | -23.4618 | 8.5927 | 8.2986 | 7.8892 | 7.3006 | 6.4469 | 5.5359 | 4.6404 | 3.6913 | 2.5138 | 1.258 | -2.2364 | -6.2103 | -7.842 | -8.9403 | 3.6214 | 3.142 | 2.5187 | 1.6433 | 0.25365 | -1.2256 | -2.6628 | -4.1753 | -6.0046 | -7.9246 | -13.2721 | -19.6937 | -22.6122 | -24.4741
[6 empty] | 8.4242 | 8.2753 | 8.0867 | 7.7277 | 7.1386 | 6.5075 | 5.9582 | 5.3901 | 4.6833 | 3.935 | 1.4307 | -4.9222 | -8.9815 | -11.6628 | 8.8374 | 8.6936 | 8.5092 | 8.2101 | 7.7405 | 7.2389 | 6.7694 | 6.2715 | 5.6622 | 5.0434 | 2.8169 | -2.7784 | -7.489 | -13.0066 | 4.1567 | 4.0244 | 3.8499 | 3.5393 | 3.0116 | 2.4446 | 1.9336 | 1.3986 | 0.73285 | 0.047925 | -2.3511 | -8.264 | -11.8302 | -14.0827
[6 empty] | 8.4835 | 8.3301 | 8.1513 | 7.815 | 7.3561 | 6.8759 | 6.467 | 6.0431 | 5.5282 | 4.934 | 3.1528 | -1.6806 | -5.7054 | -7.7597 | 8.8589 | 8.6905 | 8.4876 | 8.1761 | 7.7749 | 7.3461 | 6.9354 | 6.4935 | 5.9633 | 5.3424 | 3.217 | -2.5439 | -10.0369 | -20.5097 | 4.2099 | 4.0606 | 3.8865 | 3.5852 | 3.1868 | 2.7676 | 2.3922 | 1.9957 | 1.5139 | 0.97061 | -0.73874 | -5.2372 | -8.8669 | -10.6041

## BSP Headroom Dem
Grid Supply Point | Bulk Supply Point | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Demand Headroom Winter MVA | [13 empty] | Demand Headroom Summer MVA | [13 empty] | Demand Headroom Spring/Autumn MVA
[5 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050
WILLESDEN GSP | ACTON LANE | MINIMUM HEADROOM | TQ2080583142 | YES | 104.5571 | 104.3941 | 104.1859 | 103.926 | 103.637 | 103.1182 | 102.3208 | 101.4173 | 100.3431 | 99.2214 | 95.4845 | 89.3997 | 83.6626 | 79.5983 | 94.0535 | 93.8505 | 93.6105 | 93.3212 | 92.9865 | 92.618 | 92.2133 | 91.782 | 91.2811 | 90.7304 | 87.5935 | 75.0925 | 50.7509 | 7.5829 | 90.6616 | 90.465 | 90.2235 | 89.9374 | 89.5466 | 89.1163 | 88.6522 | 87.7717 | 86.7586 | 85.6985 | 82.1581 | 76.5969 | 71.6602 | 68.2006
|  | CT |  |  | 104.5571 | 104.3941 | 104.1859 | 103.926 | 103.6481 | 103.3422 | 103.0215 | 102.7045 | 102.2367 | 101.2816 | 97.6919 | 89.9609 | 83.6626 | 79.5983 | 94.0535 | 93.8505 | 93.6105 | 93.3212 | 92.9865 | 92.618 | 92.2133 | 91.782 | 91.2811 | 90.7304 | 87.5935 | 77.6896 | 63.6593 | 41.9394 | 90.6893 | 90.5248 | 90.3156 | 90.0523 | 89.7301 | 89.3781 | 89.0156 | 88.6554 | 88.247 | 87.549 | 84.1709 | 77.1712 | 71.6602 | 68.2006
|  | LW |  |  | 104.5779 | 104.406 | 104.1903 | 103.9312 | 103.637 | 103.1182 | 102.3208 | 101.4173 | 100.3431 | 99.2214 | 95.4845 | 89.3997 | 85.536 | 82.8031 | 94.1465 | 94.0264 | 93.8791 | 93.7002 | 93.493 | 93.2591 | 92.9926 | 92.7145 | 92.3587 | 91.9595 | 90.5484 | 88.6183 | 86.6826 | 85.2287 | 90.6616 | 90.465 | 90.2235 | 89.9374 | 89.5466 | 89.1163 | 88.6522 | 87.7717 | 86.7586 | 85.6985 | 82.1581 | 76.5969 | 73.2589 | 70.8194
|  | ST |  |  | 104.6683 | 104.568 | 104.4406 | 104.2875 | 104.102 | 103.8942 | 103.6765 | 103.4628 | 103.2024 | 102.9077 | 101.6987 | 97.9684 | 94.4722 | 91.5154 | 94.141 | 93.9873 | 93.8106 | 93.6058 | 93.3443 | 93.0537 | 92.7304 | 92.381 | 91.9659 | 91.5204 | 89.7786 | 81.3223 | 67.8978 | 46.6695 | 90.8197 | 90.731 | 90.6196 | 90.4857 | 90.3154 | 90.1241 | 89.9216 | 89.7197 | 89.4716 | 89.179 | 87.9992 | 84.281 | 81.1955 | 78.9044
|  | SP |  |  | 104.6771 | 104.583 | 104.4613 | 104.3183 | 104.1613 | 103.9909 | 103.8155 | 103.6559 | 103.4762 | 103.2837 | 102.5598 | 100.0278 | 97.166 | 95.5168 | 94.1305 | 93.9684 | 93.7703 | 93.5434 | 93.2399 | 92.8963 | 92.51 | 92.093 | 91.6061 | 91.0596 | 87.6027 | 75.0925 | 50.7509 | 7.5829 | 90.8334 | 90.7526 | 90.6495 | 90.5288 | 90.3857 | 90.231 | 90.0701 | 89.9197 | 89.7496 | 89.5553 | 88.8415 | 86.463 | 83.6343 | 82.1091
BRAMLEY (FLEE) | ALDERSHOT BSP | MINIMUM HEADROOM | SU8597648834 | YES | 106.8256 | 102.453 | 97.688 | 92.1849 | 84.5819 | 77.0728 | 68.8815 | 60.0083 | 49.189 | 38.414 | 11.9358 | -21.0488 | -40.3178 | -55.1673 | 97.3703 | 94.805 | 91.9275 | 88.6069 | 84.4813 | 80.265 | 75.4739 | 70.162 | 63.2256 | 56.3904 | 40.5065 | 18.8933 | -0.81251 | -19.7545 | 93.4485 | 89.4723 | 85.0878 | 80.068 | 73.1493 | 66.2203 | 58.6108 | 50.314 | 40.0878 | 29.9221 | 5.2773 | -24.9363 | -41.225 | -53.4883
|  | CT |  |  | 108.294 | 104.9219 | 101.2362 | 96.5497 | 91.0273 | 85.6897 | 80.0529 | 73.8867 | 66.6956 | 56.053 | 29.7306 | -11.9534 | -40.3178 | -55.1673 | 97.4996 | 95.1023 | 92.4381 | 89.0857 | 85.5484 | 81.9683 | 78.0594 | 73.7057 | 68.4777 | 61.3969 | 44.7096 | 18.8933 | -0.81251 | -19.2362 | 94.69 | 91.5962 | 88.1727 | 83.8505 | 78.7888 | 73.8063 | 68.5154 | 62.6866 | 55.8517 | 45.8172 | 21.318 | -16.4224 | -41.225 | -53.4883
|  | LW |  |  | 106.8256 | 102.453 | 97.688 | 92.1849 | 84.5819 | 77.0728 | 68.8815 | 60.0083 | 49.189 | 38.414 | 11.9358 | -21.0488 | -34.4896 | -42.5519 | 97.3703 | 94.805 | 91.9275 | 88.6069 | 84.4813 | 80.265 | 75.4739 | 70.162 | 63.2256 | 56.3904 | 40.5065 | 21.7383 | 14.9647 | 10.8936 | 93.4485 | 89.4723 | 85.0878 | 80.068 | 73.1493 | 66.2203 | 58.6108 | 50.314 | 40.0878 | 29.9221 | 5.2773 | -24.9363 | -36.742 | -43.6951
|  | ST |  |  | 110.7617 | 109.0213 | 107.1525 | 104.8732 | 102.1094 | 99.5101 | 96.668 | 93.4957 | 89.8204 | 85.5427 | 67.3514 | 32.9289 | 14.2554 | 3.0673 | 99.2264 | 97.9247 | 96.4746 | 94.7411 | 92.6794 | 90.6302 | 88.3484 | 85.7567 | 82.7293 | 79.3305 | 64.5234 | 36.9331 | 19.3194 | 1.9847 | 97.0699 | 95.539 | 93.8541 | 91.8382 | 89.3295 | 86.8969 | 84.2238 | 81.204 | 77.699 | 73.6362 | 56.1191 | 23.4949 | 6.6083 | -3.1069
|  | SP |  |  | 111.0667 | 109.4196 | 107.7987 | 105.8722 | 103.4675 | 100.2337 | 96.896 | 93.2307 | 88.2265 | 84.6216 | 71.5936 | 37.7955 | 17.1095 | 7.7794 | 99.3295 | 98.0089 | 96.6374 | 95.0502 | 93.3169 | 90.5776 | 87.7059 | 84.497 | 79.9424 | 76.9782 | 65.7592 | 35.4598 | 9.3144 | -19.7545 | 97.3461 | 95.891 | 94.4349 | 92.7496 | 90.6151 | 87.5621 | 84.406 | 80.9013 | 76.0727 | 72.6937 | 60.3401 | 28.0799 | 8.8086 | 0.53702
BRAMLEY (FLEE) | ALTON | MINIMUM HEADROOM | SU7268539765 | YES | 30.0692 | 26.4676 | 22.8096 | 19.1 | 14.3059 | 9.3116 | 3.9159 | -2.1224 | -9.1916 | -15.6354 | -30.4846 | -48.1301 | -54.3167 | -60.7607 | 37.6792 | 35.4229 | 33.2269 | 30.9894 | 28.3226 | 25.4867 | 22.3189 | 18.6862 | 14.2251 | 10.278 | 2.0006 | -7.7377 | -15.0498 | -23.904 | 51.787 | 48.676 | 45.5639 | 42.413 | 38.4849 | 34.3641 | 29.8377 | 24.7001 | 18.3771 | 12.6941 | 0.24418 | -15.5412 | -21.1006 | -25.961
|  | CT |  |  | 31.5139 | 28.7797 | 26.0004 | 23.0306 | 19.7045 | 16.2058 | 12.4839 | 8.2489 | 3.5212 | -2.9425 | -17.1627 | -39.4195 | -54.3167 | -60.7607 | 37.9831 | 35.9632 | 34.0055 | 31.8979 | 29.8235 | 27.5891 | 25.1484 | 22.3089 | 19.06 | 14.8896 | 6.3969 | -6.1712 | -15.0498 | -21.7822 | 52.7312 | 50.2374 | 47.7574 | 45.0934 | 42.2562 | 39.2505 | 36.0142 | 32.2968 | 28.0791 | 22.2878 | 10.3762 | -7.5991 | -20.5657 | -25.961
|  | LW |  |  | 30.0692 | 26.4676 | 22.8096 | 19.1 | 14.3059 | 9.3116 | 3.9159 | -2.1224 | -9.1916 | -15.6354 | -30.4846 | -48.1301 | -54.2995 | -57.5421 | 37.6792 | 35.4229 | 33.2269 | 30.9894 | 28.3226 | 25.4867 | 22.3189 | 18.6862 | 14.2251 | 10.278 | 2.0006 | -7.7377 | -11.0399 | -12.683 | 51.787 | 48.676 | 45.5639 | 42.413 | 38.4849 | 34.3641 | 29.8377 | 24.7001 | 18.3771 | 12.6941 | 0.24418 | -15.5412 | -21.1006 | -23.8864
|  | ST |  |  | 32.9075 | 31.1358 | 29.4597 | 27.7919 | 25.9725 | 24.0523 | 21.984 | 19.7004 | 17.1192 | 14.1175 | 2.1672 | -15.3063 | -24.4511 | -29.9626 | 38.9662 | 37.5949 | 36.3643 | 35.1345 | 33.8735 | 32.5107 | 31.0159 | 29.358 | 27.4516 | 25.2334 | 16.0183 | 2.6817 | -4.8443 | -11.3847 | 54.0236 | 52.4046 | 50.9159 | 49.4346 | 47.839 | 46.1462 | 44.3087 | 42.2757 | 39.9618 | 37.2981 | 26.1787 | 10.2676 | 2.6699 | -1.6616
|  | SP |  |  | 33.1493 | 31.4825 | 30.022 | 28.6407 | 26.8429 | 23.8233 | 20.7333 | 17.4051 | 12.66 | 9.8827 | 0.51323 | -20.4582 | -31.4813 | -36.6968 | 39.0519 | 37.6961 | 36.5608 | 35.4783 | 34.3457 | 31.9667 | 29.518 | 26.8659 | 22.7987 | 20.8476 | 13.9654 | -2.4502 | -13.4335 | -23.904 | 54.2048 | 52.6501 | 51.3386 | 50.1025 | 48.6011 | 45.8739 | 43.08 | 40.052 | 35.6194 | 33.2512 | 25.056 | 5.8342 | -3.6187 | -7.7418
MELKSHAM GSP | AMESBURY | MINIMUM HEADROOM | SU1590542695 | YES | 66.4979 | 65.1508 | 63.6018 | 61.9821 | 59.765 | 57.4152 | 54.9466 | 52.3242 | 49.1445 | 46.0065 | 38.9815 | 33.0477 | 31.4962 | 30.9023 | 53.383 | 53.2289 | 52.7375 | 51.9267 | 50.8503 | 49.6962 | 48.4629 | 47.141 | 45.4924 | 43.798 | 40.1382 | 37.1381 | 36.4317 | 34.037 | 61.6226 | 60.3807 | 58.988 | 57.5133 | 55.4695 | 53.3091 | 51.0449 | 48.6437 | 45.7478 | 42.8816 | 36.337 | 30.7684 | 29.32 | 28.7705
|  | CT |  |  | 67.6608 | 66.9447 | 66.1292 | 65.0473 | 63.6266 | 62.0965 | 60.4773 | 58.7191 | 56.7483 | 53.865 | 47.2773 | 40.2479 | 36.2407 | 34.4854 | 53.383 | 53.2289 | 53.0488 | 52.809 | 52.3322 | 51.5038 | 50.6188 | 49.6502 | 48.5333 | 46.717 | 42.8849 | 38.9982 | 36.5198 | 34.4479 | 62.7535 | 62.1095 | 61.3776 | 60.4142 | 59.1211 | 57.7326 | 56.2649 | 54.6741 | 52.8862 | 50.1715 | 44.0767 | 37.5997 | 33.8248 | 32.1743
|  | LW |  |  | 66.4979 | 65.1508 | 63.6018 | 61.9821 | 59.765 | 57.4152 | 54.9466 | 52.3242 | 49.1445 | 46.0065 | 38.9815 | 33.0477 | 31.4962 | 30.9023 | 53.4109 | 53.2553 | 52.7375 | 51.9267 | 50.8503 | 49.6962 | 48.4629 | 47.141 | 45.4924 | 43.798 | 40.1382 | 37.1381 | 36.4317 | 36.1515 | 61.6226 | 60.3807 | 58.988 | 57.5133 | 55.4695 | 53.3091 | 51.0449 | 48.6437 | 45.7478 | 42.8816 | 36.337 | 30.7684 | 29.32 | 28.7705
|  | ST |  |  | 68.1632 | 67.7652 | 67.3112 | 66.8129 | 66.0371 | 65.1904 | 64.3035 | 63.3465 | 62.3116 | 61.2343 | 56.7461 | 49.0594 | 45.3928 | 42.9552 | 53.5057 | 53.4245 | 53.3323 | 53.2262 | 53.091 | 52.9319 | 52.6651 | 52.1079 | 51.4953 | 50.8738 | 48.1571 | 42.8479 | 40.3294 | 38.0005 | 63.2081 | 62.853 | 62.4496 | 62.0074 | 61.3072 | 60.5467 | 59.7513 | 58.8941 | 57.9615 | 56.9754 | 52.8559 | 45.6151 | 42.325 | 40.0951
|  | SP |  |  | 68.3177 | 67.9617 | 67.5869 | 67.1884 | 66.3407 | 65.4422 | 64.5286 | 63.5248 | 62.5126 | 61.2563 | 56.8718 | 46.3974 | 40.7479 | 37.649 | 53.5059 | 53.4191 | 53.3283 | 53.2264 | 53.1229 | 53.004 | 52.8109 | 52.2634 | 51.7005 | 51.0173 | 48.5485 | 41.9055 | 37.7112 | 34.037 | 63.3541 | 63.0426 | 62.7151 | 62.3665 | 61.5892 | 60.7697 | 59.9378 | 59.0265 | 58.1025 | 56.9425 | 52.9211 | 43.3667 | 38.0836 | 35.1684
BRAMLEY (ANDO-THAT) | ANDOVER BSP | MINIMUM HEADROOM | SU3524046643 | YES | 42.2306 | 39.4613 | 36.5895 | 33.5933 | 29.2331 | 24.3171 | 19.0999 | 13.5272 | 6.8979 | 0.30398 | -16.1556 | -35.5777 | -43.4925 | -47.8678 | 35.2206 | 33.616 | 31.9081 | 30.1062 | 27.6889 | 24.7859 | 21.6439 | 18.2529 | 11.1105 | 8.5556 | -0.32948 | -18.4317 | -31.833 | -43.5572 | 33.3569 | 30.8451 | 28.1905 | 25.4074 | 21.4082 | 16.8639 | 12.0161 | 6.8185 | 0.56824 | -5.641 | -20.924 | -38.8778 | -46.1858 | -49.6247
|  | CT |  |  | 43.837 | 41.9768 | 40.1091 | 37.9076 | 34.9507 | 31.533 | 27.9664 | 24.0375 | 19.6687 | 13.4052 | -2.1682 | -25.7087 | -41.0419 | -47.8678 | 35.7481 | 34.4443 | 33.0941 | 31.4965 | 29.5919 | 27.2752 | 24.8181 | 22.0356 | 18.8378 | 14.575 | 4.3667 | -9.8728 | -20.2511 | -28.1903 | 34.7472 | 33.036 | 31.2768 | 29.18 | 26.4267 | 23.2229 | 19.8672 | 16.1534 | 12.0001 | 6.0865 | -8.4217 | -29.8972 | -43.6836 | -49.5296
|  | LW |  |  | 42.2306 | 39.4613 | 36.5895 | 33.5933 | 29.2331 | 24.3171 | 19.0999 | 13.5272 | 6.8979 | 0.30398 | -16.1556 | -35.5777 | -43.4925 | -47.2284 | 35.2206 | 33.616 | 31.9081 | 30.1062 | 27.6889 | 24.7859 | 21.6439 | 18.2529 | 14.0533 | 9.7619 | -0.32948 | -11.929 | -17.0459 | -19.6081 | 33.3569 | 30.8451 | 28.1905 | 25.4074 | 21.4082 | 16.8639 | 12.0161 | 6.8185 | 0.56824 | -5.641 | -20.924 | -38.8778 | -46.1858 | -49.6247
|  | ST |  |  | 45.0521 | 43.9442 | 42.8391 | 41.6458 | 40.0113 | 37.9607 | 35.7822 | 33.4537 | 30.8533 | 26.9253 | 12.472 | -9.3443 | -20.6594 | -27.1129 | 36.5143 | 35.6773 | 34.8099 | 33.8699 | 32.6907 | 31.1236 | 29.4387 | 27.6275 | 25.5929 | 22.3325 | 10.5041 | -7.0746 | -16.7805 | -24.4155 | 35.915 | 34.9235 | 33.8966 | 32.7773 | 31.2543 | 29.3232 | 27.264 | 25.0563 | 22.578 | 18.8016 | 4.8277 | -16.0675 | -26.5695 | -32.3738
|  | SP |  |  | 45.3315 | 44.3043 | 43.3356 | 42.3511 | 40.6919 | 35.4655 | 31.1963 | 25.7468 | 16.6623 | 13.3789 | 2.3606 | -20.685 | -34.2004 | -40.3729 | 36.6216 | 35.7954 | 34.9684 | 34.1164 | 32.9824 | 28.2909 | 24.5453 | 19.638 | 11.1105 | 8.5556 | -0.097625 | -18.4317 | -31.833 | -43.5572 | 36.1635 | 35.2374 | 34.332 | 33.4061 | 31.885 | 26.8051 | 22.6818 | 17.3766 | 8.4391 | 5.3456 | -5.0897 | -27.089 | -39.7954 | -45.3973
MANNINGTON GSP | ARNEWOOD | MINIMUM HEADROOM | SZ2612997354 | YES | 23.9682 | 22.5257 | 20.5361 | 27.6105 | 23.9916 | 19.9448 | 15.5699 | 10.9474 | 5.5734 | 0.1345 | -12.5823 | -27.6725 | -38.6596 | -45.8173 | 26.3448 | 25.5128 | 24.2268 | 45.5918 | 43.5532 | 41.1466 | 38.4777 | 35.6097 | 31.7722 | 28.5991 | 20.9123 | 9.0915 | -1.8337 | -11.9493 | 22.621 | 21.302 | 19.4911 | 31.289 | 28.0125 | 24.3309 | 20.3202 | 16.0121 | 10.9439 | 5.7975 | -6.0728 | -19.9469 | -29.738 | -36.0989
|  | CT |  |  | 24.7615 | 23.8415 | 22.6222 | 30.0648 | 27.5191 | 24.6335 | 21.4972 | 18.161 | 14.5613 | 9.104 | -4.3403 | -24.1166 | -38.6596 | -45.8173 | 26.3735 | 25.8566 | 24.924 | 46.3118 | 44.6536 | 42.6966 | 40.5586 | 38.247 | 35.6835 | 32.0627 | 23.4764 | 12.067 | 3.0647 | -3.8772 | 23.3812 | 22.5544 | 21.4481 | 33.5715 | 31.2186 | 28.5331 | 25.6069 | 22.4722 | 19.0571 | 13.8993 | 1.3218 | -16.6106 | -29.738 | -36.0989
|  | LW |  |  | 23.9682 | 22.5257 | 20.5361 | 27.6105 | 23.9916 | 19.9448 | 15.5699 | 10.9474 | 5.5734 | 0.1345 | -12.5823 | -27.6725 | -34.8781 | -38.3701 | 26.3448 | 25.5128 | 24.2268 | 45.5918 | 43.5532 | 41.1466 | 38.4777 | 35.6097 | 32.1298 | 28.5991 | 20.9123 | 12.2792 | 8.0292 | 5.8739 | 22.621 | 21.302 | 19.4911 | 31.289 | 28.0125 | 24.3309 | 20.3202 | 16.0121 | 10.9439 | 5.7975 | -6.0728 | -19.9469 | -26.5066 | -29.6683
|  | ST |  |  | 25.5926 | 25.1914 | 24.5481 | 33.1048 | 31.8251 | 30.2412 | 28.5333 | 26.7603 | 24.8526 | 22.1409 | 11.7379 | -6.4866 | -15.6309 | -21.3231 | 26.6155 | 26.4951 | 26.1749 | 48.4853 | 47.5575 | 46.3472 | 45.0317 | 43.6472 | 42.1215 | 39.8477 | 31.0968 | 16.4581 | 8.7374 | 2.2133 | 24.1297 | 23.7701 | 23.1827 | 36.3266 | 35.2189 | 33.8208 | 32.2784 | 30.6089 | 28.7893 | 26.1709 | 16.0308 | -1.4693 | -9.8783 | -14.9551
|  | SP |  |  | 25.7381 | 25.3057 | 24.6795 | 33.3134 | 32.2448 | 28.6278 | 24.9639 | 21.1903 | 14.9257 | 12.9018 | 5.8272 | -11.4411 | -20.9633 | -24.6905 | 26.6227 | 26.4938 | 26.1716 | 48.4574 | 47.7171 | 44.4551 | 41.1381 | 37.7105 | 31.7722 | 30.1021 | 24.1077 | 9.0915 | -1.8337 | -11.9493 | 24.2668 | 23.8872 | 23.321 | 36.5392 | 35.6122 | 32.1464 | 28.6442 | 25.0191 | 18.8489 | 16.9236 | 10.1224 | -6.5739 | -15.6084 | -18.9923
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | MINIMUM HEADROOM | SU6515552705 | YES | 40.0909 | 39.7556 | 39.2663 | 38.7037 | 37.9904 | 36.4098 | 34.7689 | 33.0338 | 29.6978 | 28.8802 | 23.2532 | 15.1822 | 11.6371 | 8.7562 | 54.7268 | 54.3841 | 53.8712 | 53.3016 | 52.5769 | 51.4585 | 49.5205 | 47.5811 | 43.9966 | 43.3057 | 41.0828 | 35.1251 | 29.7667 | 24.7364 | 28.8492 | 28.225 | 27.4017 | 26.5025 | 25.1804 | 23.6929 | 22.1436 | 20.5048 | 18.2824 | 16.5467 | 11.2305 | 4.4559 | 0.58938 | -2.0183
|  | CT |  |  | 40.0909 | 39.7556 | 39.2725 | 38.72 | 38.1464 | 37.4724 | 36.8117 | 35.6359 | 34.2941 | 32.2465 | 26.6782 | 17.7463 | 11.6371 | 8.7562 | 54.7268 | 54.3883 | 53.8845 | 53.316 | 52.7183 | 52.0366 | 51.3794 | 50.6607 | 49.8961 | 48.916 | 45.6863 | 39.1608 | 36.1045 | 32.8228 | 28.9705 | 28.5836 | 27.9399 | 27.1534 | 26.1854 | 25.0894 | 23.9937 | 22.8341 | 21.5422 | 19.598 | 14.316 | 6.1313 | 0.58938 | -2.0183
|  | LW |  |  | 40.1236 | 39.7647 | 39.2663 | 38.7037 | 37.9904 | 36.4098 | 34.7689 | 33.0338 | 30.9999 | 28.8802 | 23.2532 | 15.1822 | 12.3177 | 10.9424 | 54.7382 | 54.3841 | 53.8712 | 53.3016 | 52.5769 | 51.6993 | 50.829 | 49.888 | 48.8143 | 47.6946 | 42.646 | 36.3747 | 34.2365 | 33.1262 | 28.8492 | 28.225 | 27.4017 | 26.5025 | 25.1804 | 23.6929 | 22.1436 | 20.5048 | 18.5671 | 16.5467 | 11.2305 | 4.4559 | 1.2135 | -0.23689
|  | ST |  |  | 40.296 | 40.0801 | 39.7441 | 39.376 | 38.9649 | 38.4569 | 37.9707 | 37.4682 | 36.8994 | 35.7414 | 31.7984 | 20.3821 | 14.8033 | 12.8069 | 54.8889 | 54.6512 | 54.2678 | 53.8495 | 53.4011 | 52.8702 | 52.3785 | 51.8807 | 51.3356 | 50.222 | 46.3284 | 37.3116 | 33.3116 | 31.9878 | 29.174 | 28.9541 | 28.6111 | 28.236 | 27.8186 | 27.2446 | 26.6192 | 25.9608 | 25.2214 | 23.9041 | 19.1441 | 10.6711 | 6.4967 | 4.2068
|  | SP |  |  | 40.3014 | 40.0939 | 39.7664 | 39.4158 | 39.0433 | 37.0924 | 35.183 | 33.2657 | 29.6978 | 29.0194 | 26.8355 | 19.7888 | 12.8466 | 10.8953 | 54.8901 | 54.6567 | 54.2758 | 53.8663 | 53.4493 | 51.4585 | 49.5205 | 47.5811 | 43.9966 | 43.3057 | 41.0828 | 35.1251 | 29.7667 | 24.7364 | 29.1796 | 28.9696 | 28.6359 | 28.2789 | 27.8996 | 25.9443 | 24.0168 | 21.9813 | 18.2824 | 17.4232 | 14.513 | 7.3636 | 2.8309 | 1.2726
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | MINIMUM HEADROOM | SU6515552705 | YES | 42.9661 | 41.0238 | 38.6949 | 36.116 | 32.5553 | 28.6543 | 24.4477 | 19.9508 | 14.419 | 9.0576 | -2.9967 | -18.5682 | -27.8935 | -34.03 | 39.9077 | 38.7994 | 37.4728 | 36.0446 | 34.2069 | 32.1194 | 29.8449 | 27.393 | 24.3048 | 21.331 | 14.7623 | 5.4252 | -3.7087 | -12.171 | 40.6045 | 38.8644 | 36.7685 | 34.465 | 31.4227 | 28.0531 | 24.3611 | 20.3486 | 15.2257 | 10.3138 | -0.1217 | -14.0367 | -22.0694 | -27.4655
|  | CT |  |  | 43.6081 | 42.1292 | 40.211 | 37.9909 | 35.4622 | 32.6548 | 29.7483 | 26.5845 | 22.9325 | 17.4882 | 5.1828 | -14.4933 | -27.8935 | -34.03 | 40.0667 | 39.0788 | 37.83 | 36.4414 | 34.9712 | 33.2874 | 31.5195 | 29.5791 | 27.3309 | 24.2085 | 17.1037 | 5.4252 | -3.7087 | -11.0768 | 40.9861 | 39.5844 | 37.7736 | 35.6978 | 33.4456 | 30.9268 | 28.2818 | 25.3455 | 21.9036 | 16.9195 | 6.2512 | -10.1715 | -22.0694 | -27.4655
|  | LW |  |  | 42.9661 | 41.0238 | 38.6949 | 36.116 | 32.5553 | 28.6543 | 24.4477 | 19.9508 | 14.419 | 9.0576 | -2.9967 | -18.5682 | -25.2055 | -28.3131 | 39.9077 | 38.7994 | 37.4728 | 36.0446 | 34.2069 | 32.1194 | 29.8449 | 27.393 | 24.3048 | 21.331 | 14.7623 | 6.2282 | 2.4778 | 0.63078 | 40.6045 | 38.8644 | 36.7685 | 34.465 | 31.4227 | 28.0531 | 24.3611 | 20.3486 | 15.2257 | 10.3138 | -0.1217 | -14.0367 | -19.9844 | -22.7298
|  | ST |  |  | 44.7895 | 44.0534 | 43.0493 | 41.9022 | 40.6816 | 39.2464 | 37.7117 | 36.1065 | 34.2764 | 31.893 | 22.1797 | 6.0414 | -2.5029 | -7.8479 | 40.7448 | 40.1773 | 39.4414 | 38.6502 | 37.8418 | 36.8526 | 35.791 | 34.6684 | 33.3884 | 31.6128 | 24.6461 | 12.8944 | 5.3731 | -1.6509 | 42.1479 | 41.4639 | 40.5247 | 39.4652 | 38.3257 | 36.9768 | 35.5247 | 33.9834 | 32.2144 | 29.9408 | 20.3808 | 5.1357 | -2.1774 | -6.4701
|  | SP |  |  | 44.9102 | 44.2157 | 43.3433 | 42.4111 | 41.2882 | 38.6466 | 35.9632 | 33.16 | 28.7501 | 26.8037 | 20.0219 | 3.1106 | -5.7858 | -9.6205 | 40.7849 | 40.2222 | 39.5307 | 38.8292 | 38.1048 | 35.8668 | 33.5899 | 31.2245 | 27.2764 | 25.844 | 20.8139 | 8.0386 | -1.8691 | -12.171 | 42.2444 | 41.5833 | 40.7614 | 39.9042 | 38.9079 | 36.3974 | 33.8412 | 31.1451 | 26.8376 | 25.0329 | 18.5861 | 2.2019 | -5.9406 | -9.1626
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | MINIMUM HEADROOM | SU6515552705 | YES | 79.2841 | 78.4005 | 49.9665 | 48.0932 | 45.4924 | 43.0845 | 40.5521 | 37.6834 | 34.2756 | 30.6739 | 20.5668 | 10.7217 | 4.6892 | 0.40094 | 60.0828 | 59.5658 | 31.7462 | 30.6685 | 29.261 | 27.9388 | 26.5259 | 24.9277 | 22.9771 | 20.892 | 15.0394 | 7.5045 | 1.0452 | -5.9266 | 69.6341 | 68.8408 | 40.5915 | 38.9691 | 36.7116 | 34.5871 | 32.3357 | 29.7873 | 26.7299 | 23.4866 | 14.3864 | 5.4708 | 0.59455 | -3.0617
|  | CT |  |  | 79.5855 | 78.8972 | 50.7425 | 49.0069 | 46.835 | 44.8784 | 42.8864 | 40.5939 | 37.9243 | 34.448 | 24.5201 | 12.5077 | 4.6892 | 0.40094 | 60.1311 | 59.6354 | 31.8876 | 30.7765 | 29.4707 | 28.2575 | 26.9981 | 25.5638 | 23.8784 | 21.7638 | 15.5927 | 7.5045 | 1.0452 | -5.9266 | 69.8887 | 69.2721 | 41.2795 | 39.7725 | 37.8969 | 36.176 | 34.4136 | 32.389 | 30.0152 | 26.9022 | 17.9988 | 7.2077 | 0.59455 | -3.0617
|  | LW |  |  | 79.2841 | 78.4005 | 49.9665 | 48.0932 | 45.4924 | 43.0845 | 40.5521 | 37.6834 | 34.2756 | 30.6739 | 20.5668 | 10.7217 | 6.5755 | 4.1671 | 60.0828 | 59.5658 | 31.7462 | 30.6685 | 29.261 | 27.9388 | 26.5259 | 24.9277 | 22.9771 | 20.892 | 15.0394 | 9.4523 | 7.4031 | 6.1664 | 69.6341 | 68.8408 | 40.5915 | 38.9691 | 36.7116 | 34.5871 | 32.3357 | 29.7873 | 26.7299 | 23.4866 | 14.3864 | 5.4708 | 1.9234 | -0.079587
|  | ST |  |  | 80.1403 | 79.7941 | 79.0949 | 78.1973 | 50.0404 | 48.99 | 47.906 | 46.6384 | 45.1418 | 43.5308 | 38.0216 | 28.4582 | 23.16 | 19.9058 | 60.479 | 60.1903 | 59.6803 | 59.056 | 31.2892 | 30.5436 | 29.7603 | 28.8554 | 27.7849 | 26.6448 | 22.5922 | 14.6588 | 8.6849 | 2.0654 | 70.3969 | 70.0953 | 69.5038 | 68.7522 | 40.7681 | 39.8555 | 38.9095 | 37.8038 | 36.4958 | 35.1073 | 30.2245 | 21.511 | 16.8093 | 14.0543
|  | SP |  |  | 80.2092 | 79.8595 | 79.2003 | 78.3763 | 77.4037 | 76.5712 | 75.6873 | 74.6531 | 73.4895 | 72.1869 | 68.0892 | 60.5548 | 54.9506 | 52.4084 | 60.5024 | 60.1962 | 59.6875 | 59.0809 | 58.3874 | 57.7497 | 57.0552 | 56.2477 | 55.3289 | 54.2654 | 50.6833 | 42.8275 | 33.4615 | 21.1169 | 70.4544 | 70.1384 | 69.5759 | 68.8831 | 68.0736 | 67.366 | 66.6011 | 65.6979 | 64.6816 | 63.5546 | 59.9343 | 52.9727 | 47.9824 | 45.8839
EAST CLAYDON GSP | BICESTER NORTH | MINIMUM HEADROOM | SP5972023735 | YES | 95.194 | 93.3098 | 51.8832 | 49.7855 | 46.763 | 43.6288 | 40.3965 | 36.8359 | 32.7687 | 27.4273 | 17.933 | 5.2006 | -2.6332 | -5.9261 | 75.6431 | 74.6024 | 32.9732 | 31.6375 | 29.8975 | 28.0826 | 26.1776 | 24.0612 | 21.5993 | 18.4055 | 12.653 | 5.4346 | 0.86376 | -2.7809 | 83.1944 | 81.6946 | 40.7838 | 39.2367 | 36.8823 | 34.4296 | 31.8542 | 28.9252 | 25.4203 | 20.6456 | 11.983 | 0.50896 | -6.4676 | -9.4759
|  | CT |  |  | 96.0528 | 94.6188 | 51.8832 | 49.7855 | 46.763 | 43.6288 | 40.3965 | 36.8359 | 32.7687 | 27.4273 | 17.933 | 5.2006 | -2.6332 | -5.9261 | 75.8979 | 74.9856 | 32.9732 | 31.6375 | 29.8975 | 28.0826 | 26.1776 | 24.0612 | 21.5993 | 18.4055 | 12.653 | 5.4346 | 0.86376 | -2.7809 | 84.0563 | 83.0064 | 40.7838 | 39.2367 | 36.8823 | 34.4296 | 31.8542 | 28.9252 | 25.4203 | 20.6456 | 11.983 | 0.50896 | -6.4676 | -9.4759
|  | LW |  |  | 95.194 | 93.3098 | 90.9229 | 88.4466 | 84.6475 | 80.7101 | 76.5348 | 71.9929 | 66.6994 | 61.2392 | 51.5361 | 41.3726 | 38.1982 | 36.5893 | 75.6431 | 74.6024 | 73.2542 | 71.8505 | 69.8322 | 67.7232 | 65.4407 | 62.9271 | 59.8363 | 56.6567 | 51.1294 | 45.6295 | 44.2448 | 43.5767 | 83.1944 | 81.6946 | 79.8331 | 77.8856 | 74.7824 | 71.5589 | 68.0874 | 64.2284 | 59.7934 | 55.1854 | 46.3515 | 37.134 | 34.3777 | 32.9229
|  | ST |  |  | 96.7766 | 95.9489 | 94.8269 | 93.6964 | 91.9204 | 90.0952 | 88.1753 | 86.0852 | 83.7347 | 81.1993 | 74.9246 | 64.3544 | 59.2376 | 56.4022 | 76.3866 | 75.8731 | 75.1794 | 74.4509 | 73.3319 | 72.1754 | 70.9454 | 69.5969 | 68.061 | 66.4464 | 61.8942 | 53.9887 | 49.8194 | 46.2578 | 84.593 | 84.024 | 83.2722 | 82.5064 | 81.2821 | 80.0101 | 78.6626 | 77.1877 | 75.5171 | 73.4755 | 67.6367 | 57.6675 | 53.0137 | 50.5136
|  | SP |  |  | 96.8426 | 96.022 | 95.0022 | 93.9904 | 92.1825 | 90.4 | 88.6688 | 86.7833 | 84.7211 | 82.3827 | 77.2785 | 65.8964 | 59.4277 | 56.6316 | 76.4144 | 75.8983 | 75.2576 | 74.6054 | 73.5917 | 72.5562 | 71.4752 | 70.2718 | 68.9388 | 67.4291 | 63.7752 | 54.864 | 48.2521 | 41.9505 | 84.6495 | 84.0931 | 83.4179 | 82.7421 | 81.3876 | 80.0702 | 78.8487 | 77.5265 | 76.0761 | 74.3877 | 70.043 | 59.2742 | 53.2285 | 50.6981
EALING GSP | BOSTON MANOR ROAD | MINIMUM HEADROOM | TQ1703978105 | NO | 20.6834 | 20.4024 | 20.0327 | 19.7618 | 19.3887 | 19.0691 | 18.6519 | 18.2473 | 17.7532 | 17.135 | 16.5594 | 16.0242 | 15.3559 | 14.9461 | 12.1246 | 11.9174 | 11.6814 | 11.4575 | 11.2194 | 11.0186 | 10.7727 | 10.5096 | 10.2169 | 9.8512 | 9.4614 | 9.0559 | 8.5962 | 8.3246 | 17.2058 | 16.9835 | 16.7308 | 16.4957 | 16.2388 | 16.0284 | 15.8157 | 15.4225 | 14.9322 | 14.3307 | 13.6989 | 13.116 | 12.4696 | 12.1052
|  | CT |  |  | 20.6869 | 20.4024 | 20.0327 | 19.8001 | 19.4932 | 19.2017 | 18.8998 | 18.599 | 18.2213 | 17.7722 | 17.2731 | 16.6704 | 15.9844 | 15.6227 | 12.1272 | 11.9174 | 11.6814 | 11.4575 | 11.2194 | 11.0186 | 10.7727 | 10.5096 | 10.2169 | 9.8512 | 9.4614 | 9.0559 | 8.5962 | 8.3246 | 17.2089 | 16.9843 | 16.7308 | 16.4957 | 16.2388 | 16.0284 | 15.8157 | 15.5732 | 15.239 | 14.7541 | 14.2391 | 13.6541 | 13.0021 | 12.6785
|  | LW |  |  | 20.6834 | 20.4084 | 20.1057 | 19.7618 | 19.3887 | 19.0691 | 18.6519 | 18.2473 | 17.7532 | 17.135 | 16.5594 | 16.0242 | 15.3559 | 14.9461 | 12.1246 | 11.9224 | 11.7118 | 11.4886 | 11.2547 | 11.0634 | 10.8513 | 10.6078 | 10.3299 | 9.9829 | 9.6111 | 9.2717 | 8.9086 | 8.6612 | 17.2058 | 16.9835 | 16.7526 | 16.51 | 16.2471 | 16.0377 | 15.8204 | 15.4225 | 14.9322 | 14.3307 | 13.6989 | 13.116 | 12.4696 | 12.1052
|  | ST |  |  | 20.6919 | 20.4422 | 20.1925 | 19.9477 | 19.6492 | 19.4857 | 19.2646 | 19.04 | 18.7716 | 18.5102 | 18.282 | 17.9945 | 17.6548 | 17.4212 | 12.1314 | 11.9357 | 11.7376 | 11.5477 | 11.3472 | 11.1909 | 10.998 | 10.7916 | 10.5621 | 10.324 | 10.1087 | 9.8542 | 9.5265 | 9.3262 | 17.214 | 17.0062 | 16.7978 | 16.6034 | 16.3919 | 16.2361 | 16.0744 | 15.905 | 15.7222 | 15.5253 | 15.3462 | 15.1428 | 14.8286 | 14.6452
|  | SP |  |  | 20.6914 | 20.4551 | 20.221 | 20.0007 | 19.7548 | 19.5753 | 19.3467 | 19.0767 | 18.7621 | 18.5281 | 18.1537 | 17.699 | 17.6264 | 17.3906 | 12.1321 | 11.9366 | 11.7398 | 11.5422 | 11.3433 | 11.1908 | 10.9596 | 10.7338 | 10.4834 | 10.2125 | 9.8732 | 9.4258 | 9.1456 | 8.9159 | 17.2149 | 17.0092 | 16.8039 | 16.6023 | 16.3954 | 16.2472 | 16.1071 | 15.9522 | 15.7902 | 15.6225 | 15.4238 | 15.0069 | 14.9077 | 14.7302
BOTLEY WOOD GSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU5398809673 | NO | 61.2258 | 59.7931 | 58.3636 | 56.8966 | 54.9728 | 52.9462 | 50.7169 | 48.2618 | 45.3949 | 42.7256 | 36.9319 | 30.2136 | 26.8634 | 24.3174 | 65.7718 | 65.1843 | 64.3957 | 63.5531 | 62.4989 | 61.3459 | 60.0527 | 58.6053 | 56.777 | 55.0823 | 51.7158 | 47.7991 | 44.672 | 41.9637 | 50.9637 | 49.7147 | 48.4564 | 47.1537 | 45.4413 | 43.6309 | 41.6305 | 39.4157 | 36.7725 | 34.3074 | 29.0688 | 23.011 | 20.2108 | 18.0985
|  | CT |  |  | 61.4316 | 60.1812 | 58.88 | 57.5472 | 56.0548 | 54.478 | 52.808 | 50.9424 | 48.8826 | 46.132 | 40.1506 | 31.8558 | 26.8634 | 24.3174 | 65.7927 | 65.2362 | 64.5021 | 63.6425 | 62.7119 | 61.724 | 60.6565 | 59.4501 | 58.0778 | 56.2857 | 52.64 | 47.7991 | 44.672 | 41.9637 | 51.1336 | 50.0477 | 48.8986 | 47.711 | 46.3855 | 44.9801 | 43.4872 | 41.8092 | 39.9318 | 37.3906 | 31.9814 | 24.5723 | 20.2108 | 18.0985
|  | LW |  |  | 61.2258 | 59.7931 | 58.3636 | 56.8966 | 54.9728 | 52.9462 | 50.7169 | 48.2618 | 45.3949 | 42.7256 | 36.9319 | 30.2136 | 27.7945 | 26.5733 | 65.7718 | 65.1843 | 64.3957 | 63.5531 | 62.4989 | 61.3459 | 60.0527 | 58.6053 | 56.777 | 55.0823 | 51.7158 | 47.9705 | 46.8596 | 46.2761 | 50.9637 | 49.7147 | 48.4564 | 47.1537 | 45.4413 | 43.6309 | 41.6305 | 39.4157 | 36.7725 | 34.3074 | 29.0688 | 23.011 | 20.9241 | 19.8978
|  | ST |  |  | 62.161 | 61.4057 | 60.6441 | 59.8816 | 59.0828 | 58.2307 | 57.2917 | 56.26 | 55.1578 | 54.09 | 49.813 | 43.2023 | 39.9885 | 38.0111 | 66.0045 | 65.5888 | 65.1921 | 64.8376 | 64.4618 | 63.9164 | 63.317 | 62.6183 | 61.8121 | 61.0465 | 57.8118 | 52.7299 | 49.9896 | 47.4657 | 51.8393 | 51.2255 | 50.5892 | 49.9406 | 49.2529 | 48.5141 | 47.6971 | 46.7938 | 45.8134 | 44.8577 | 40.8808 | 34.7199 | 31.8524 | 30.1624
|  | SP |  |  | 62.2184 | 61.5067 | 60.8342 | 60.2 | 59.5441 | 58.8715 | 58.1165 | 57.2571 | 56.3627 | 55.457 | 52.4407 | 45.5048 | 42.1715 | 40.7562 | 66.0144 | 65.6095 | 65.2299 | 64.901 | 64.6238 | 64.2394 | 63.7438 | 63.1793 | 62.5833 | 61.8975 | 59.4825 | 53.5038 | 49.4879 | 45.3945 | 51.8908 | 51.3169 | 50.7656 | 50.2406 | 49.6932 | 49.1285 | 48.4887 | 47.7491 | 46.9686 | 46.1656 | 43.4036 | 36.7682 | 33.7254 | 32.4831
MANNINGTON GSP | BOURNEMOUTH | MINIMUM HEADROOM | SZ0627892368 | YES | 53.5948 | 50.0141 | 45.7652 | 41.31 | 33.6097 | 25.4866 | 16.7281 | 7.306 | -3.6701 | -15.5369 | -49.2016 | -93.8894 | -122.2093 | -145.1459 | 59.0067 | 57.9853 | 56.0045 | 53.37 | 49.3539 | 44.8932 | 39.7225 | 34.101 | 27.1939 | 19.6192 | -1.5667 | -37.9262 | -72.9925 | -140.6938 | 42.9223 | 39.6491 | 35.727 | 31.5673 | 24.5493 | 17.097 | 8.7584 | -0.33245 | -10.9305 | -22.3893 | -54.9922 | -97.6663 | -122.1437 | -141.4985
|  | CT |  |  | 55.0972 | 52.4914 | 49.482 | 45.7347 | 40.0853 | 34.1132 | 27.9837 | 21.3088 | 13.6201 | 2.4578 | -30.06 | -83.0933 | -122.2093 | -145.1459 | 59.0067 | 57.9853 | 56.6876 | 53.9213 | 50.1226 | 45.8671 | 41.3199 | 36.327 | 30.4715 | 22.744 | -0.26843 | -37.9262 | -72.9925 | -113.4381 | 44.2125 | 41.8028 | 39.0079 | 35.4445 | 30.2448 | 24.7098 | 18.9911 | 12.7557 | 5.5318 | -4.8909 | -36.2389 | -87.3545 | -122.1437 | -141.4985
|  | LW |  |  | 53.5948 | 50.0141 | 45.7652 | 41.31 | 33.6097 | 25.4866 | 16.7281 | 7.306 | -3.6701 | -15.5369 | -49.2016 | -93.8894 | -115.0855 | -130.0853 | 59.2021 | 58.2186 | 56.0045 | 53.37 | 49.3539 | 44.8932 | 39.7225 | 34.101 | 27.1939 | 19.6192 | -1.5667 | -28.0263 | -38.6038 | -45.8332 | 42.9223 | 39.6491 | 35.727 | 31.5673 | 24.5493 | 17.097 | 8.7584 | -0.33245 | -10.9305 | -22.3893 | -54.9922 | -97.6663 | -116.6947 | -129.2432
|  | ST |  |  | 57.1101 | 55.8183 | 54.35 | 52.8122 | 50.2228 | 47.4376 | 44.419 | 41.0672 | 37.1215 | 32.4514 | 14.7936 | -27.122 | -52.6525 | -68.7409 | 59.6101 | 58.9563 | 58.2688 | 57.5171 | 56.3333 | 54.11 | 51.3801 | 48.3312 | 44.7365 | 40.601 | 24.6425 | -13.3828 | -44.3079 | -80.666 | 46.1346 | 44.9749 | 43.6475 | 42.2189 | 39.8523 | 37.2758 | 34.4636 | 31.3341 | 27.6286 | 23.241 | 6.4243 | -33.066 | -55.9155 | -69.727
|  | SP |  |  | 57.5068 | 56.2136 | 54.8069 | 53.3892 | 51.1597 | 47.7664 | 44.2229 | 40.3772 | 35.0926 | 31.3342 | 18.4603 | -16.4097 | -44.1712 | -57.7959 | 59.6475 | 59.0002 | 58.3092 | 57.5722 | 56.4424 | 53.2623 | 49.6556 | 45.7176 | 40.2455 | 36.2389 | 21.6359 | -18.7961 | -69.0585 | -140.6938 | 46.5047 | 45.329 | 44.0478 | 42.7229 | 40.7187 | 37.5343 | 34.1931 | 30.5648 | 25.5076 | 22.017 | 9.9184 | -23.0487 | -48.761 | -60.6655
BRAMLEY (FLEE) | BRACKNELL MAIN | MINIMUM HEADROOM | SU8607569397 | YES | 35.6683 | 32.9829 | 30.4438 | 27.5869 | 23.0953 | 18.3603 | 13.3701 | 7.7257 | 0.99954 | -5.6724 | -22.8377 | -41.2119 | -47.5134 | -52.592 | 22.7145 | 21.2423 | 19.8828 | 18.5037 | 16.2542 | 13.7382 | 11.0385 | 7.8427 | 3.9889 | 0.10866 | -10.0625 | -21.4326 | -29.4118 | -37.1731 | 25.6165 | 23.221 | 20.9395 | 18.3846 | 14.3685 | 10.156 | 5.6804 | 0.62015 | -5.4994 | -11.5993 | -27.0845 | -43.6626 | -49.1398 | -53.8009
|  | CT |  |  | 36.2444 | 33.9858 | 31.7641 | 29.2413 | 25.6562 | 21.866 | 18.0577 | 13.663 | 8.6396 | 2.0435 | -14.8127 | -36.6024 | -47.5134 | -52.592 | 22.8349 | 21.4591 | 20.1492 | 18.8272 | 16.8783 | 14.6786 | 12.3868 | 9.6564 | 6.5584 | 2.5468 | -7.9209 | -21.4326 | -29.4118 | -37.1731 | 26.173 | 24.1812 | 22.2063 | 19.9741 | 16.794 | 13.4142 | 9.9655 | 5.9684 | 1.3955 | -4.6277 | -19.7975 | -39.3055 | -49.1398 | -53.8009
|  | LW |  |  | 35.6683 | 32.9829 | 30.4438 | 27.5869 | 23.0953 | 18.3603 | 13.3701 | 7.7257 | 0.99954 | -5.6724 | -22.8377 | -41.2119 | -46.253 | -48.5641 | 22.7145 | 21.2423 | 19.8828 | 18.5037 | 16.2542 | 13.7382 | 11.0385 | 7.8427 | 3.9889 | 0.10866 | -10.0625 | -20.6481 | -23.0488 | -24.1906 | 25.6165 | 23.221 | 20.9395 | 18.3846 | 14.3685 | 10.156 | 5.6804 | 0.62015 | -5.4994 | -11.5993 | -27.0845 | -43.6626 | -48.0727 | -50.0495
|  | ST |  |  | 37.6161 | 36.2602 | 34.9898 | 33.5653 | 31.5459 | 29.4268 | 27.2458 | 24.7387 | 21.8711 | 18.8635 | 7.3659 | -10.597 | -18.6557 | -22.9314 | 23.3415 | 22.3014 | 21.3569 | 20.4601 | 19.3533 | 18.2564 | 17.04 | 15.3748 | 13.4989 | 11.5745 | 3.8484 | -10.1989 | -18.0422 | -25.3053 | 27.4095 | 26.2372 | 25.1269 | 23.8977 | 22.1885 | 20.4158 | 18.5521 | 16.3335 | 13.7664 | 11.0956 | 0.60304 | -16.0594 | -23.3966 | -27.1116
|  | SP |  |  | 37.7523 | 36.4732 | 35.348 | 34.1545 | 32.4723 | 30.7354 | 28.9147 | 26.7853 | 24.4623 | 21.9213 | 13.4297 | -3.5457 | -12.8309 | -16.4982 | 23.3786 | 22.3702 | 21.4651 | 20.6285 | 19.6292 | 18.6549 | 17.6312 | 16.2877 | 14.6826 | 12.9625 | 6.8247 | -7.6241 | -19.7087 | -32.6288 | 27.5357 | 26.4371 | 25.4592 | 24.4378 | 23.029 | 21.598 | 20.0607 | 18.2562 | 16.2472 | 14.0168 | 6.4323 | -9.4632 | -18.2068 | -21.5119
BRAMLEY (FLEE) | BRACKNELL RESERVE | MINIMUM HEADROOM | SU8607569397 | YES | 57.3756 | 55.2666 | 53.1897 | 50.846 | 47.1491 | 43.3814 | 39.1351 | 34.4829 | 28.9512 | 23.7769 | 11.8096 | -3.5143 | -12.7819 | -18.8365 | 49.2303 | 47.8867 | 46.5441 | 44.9765 | 42.7749 | 40.5643 | 37.9914 | 35.1176 | 31.4974 | 28.1522 | 21.0179 | 11.9056 | 3.8885 | -2.9243 | 50.057 | 48.2515 | 46.4858 | 44.4846 | 41.189 | 37.8843 | 34.2183 | 30.2405 | 25.4593 | 20.5564 | 9.396 | -4.6738 | -12.556 | -18.1212
|  | CT |  |  | 57.9575 | 56.321 | 54.6964 | 52.6944 | 50.021 | 47.3059 | 44.3271 | 41.0081 | 37.3396 | 32.0428 | 19.8239 | 0.28729 | -12.7819 | -18.8365 | 49.3097 | 48.0683 | 46.813 | 45.2363 | 43.3863 | 41.5398 | 39.4715 | 37.1352 | 34.4908 | 30.9496 | 23.2194 | 11.9056 | 3.8885 | -2.9243 | 50.7314 | 49.3614 | 48.0245 | 46.3741 | 44.0595 | 41.7606 | 39.2742 | 36.5179 | 33.0354 | 28.0208 | 16.64 | -1.028 | -12.556 | -18.1212
|  | LW |  |  | 57.3756 | 55.2666 | 53.1897 | 50.846 | 47.1491 | 43.3814 | 39.1351 | 34.4829 | 28.9512 | 23.7769 | 11.8096 | -3.5143 | -9.222 | -12.0903 | 49.2303 | 47.8867 | 46.5441 | 44.9765 | 42.7749 | 40.5643 | 37.9914 | 35.1176 | 31.4974 | 28.1522 | 21.0179 | 12.4967 | 9.9431 | 8.6492 | 50.057 | 48.2515 | 46.4858 | 44.4846 | 41.189 | 37.8843 | 34.2183 | 30.2405 | 25.4593 | 20.5564 | 9.396 | -4.6738 | -9.6496 | -12.0891
|  | ST |  |  | 59.1576 | 58.2705 | 57.4449 | 56.4425 | 55.0797 | 53.7728 | 52.2694 | 50.6282 | 48.8088 | 47.068 | 39.0288 | 24.7878 | 17.2504 | 12.3712 | 50.1812 | 49.4686 | 48.783 | 47.929 | 46.8312 | 45.8059 | 44.6238 | 43.3232 | 41.856 | 40.4988 | 34.0618 | 22.9115 | 16.4163 | 10.0517 | 51.6859 | 50.9302 | 50.2441 | 49.3943 | 48.2322 | 47.1709 | 45.9657 | 44.6581 | 43.2163 | 41.775 | 34.4912 | 20.9847 | 14.2257 | 10.0213
|  | SP |  |  | 59.2983 | 58.4172 | 57.684 | 56.8105 | 55.4827 | 54.2338 | 52.8818 | 51.3369 | 49.7618 | 48.0754 | 42.0492 | 26.5053 | 18.288 | 14.6995 | 50.2456 | 49.5097 | 48.8604 | 48.0666 | 47.0659 | 46.1601 | 45.1638 | 44.0127 | 42.7942 | 41.4719 | 36.4747 | 23.0469 | 13.1981 | 2.9274 | 51.8176 | 51.0865 | 50.4811 | 49.7397 | 48.5434 | 47.4817 | 46.3502 | 45.0717 | 43.7813 | 42.3607 | 37.4214 | 22.682 | 14.9812 | 11.7899
EALING GSP | BRIDGE ROAD | MINIMUM HEADROOM | TQ1484575785 | NO | 58.651 | 16.7323 | 15.2065 | 13.4398 | 10.909 | 8.205 | 5.3576 | 2.2809 | -0.70312 | -3.6666 | -12.5349 | -24.0937 | -31.2912 | -36.8432 | 52.7396 | 1.0253 | 0.10623 | -1.076 | -2.49 | -4.0208 | -5.6285 | -7.3927 | -9.1559 | -11.3288 | -18.352 | -31.1291 | -51.1941 | -91.0167 | 51.181 | -0.80131 | -2.1446 | -3.7144 | -5.9668 | -8.3844 | -10.9519 | -13.7245 | -16.4715 | -19.2396 | -27.5385 | -38.0315 | -43.9697 | -48.6521
|  | CT |  |  | 59.079 | 17.4251 | 16.2291 | 14.6672 | 12.6928 | 10.5736 | 8.4488 | 6.122 | 3.9999 | 1.18 | -7.4554 | -21.5251 | -31.2912 | -36.8432 | 52.7396 | 1.0253 | 0.10623 | -1.076 | -2.49 | -4.0208 | -5.6285 | -7.3927 | -9.1559 | -11.3288 | -18.352 | -31.1291 | -45.6682 | -65.965 | 51.5007 | -0.24844 | -1.2823 | -2.6673 | -4.3989 | -6.2957 | -8.2133 | -10.3095 | -12.2648 | -14.8806 | -22.92 | -35.5499 | -43.9697 | -48.6521
|  | LW |  |  | 58.651 | 16.7323 | 15.2065 | 13.4398 | 10.909 | 8.205 | 5.3576 | 2.2809 | -0.70312 | -3.6666 | -12.5349 | -24.0937 | -29.646 | -33.0245 | 52.7574 | 1.1283 | 0.27069 | -0.74074 | -2.0903 | -3.5451 | -5.1105 | -6.7995 | -8.5611 | -10.3919 | -15.8724 | -22.444 | -25.0802 | -26.7678 | 51.181 | -0.80131 | -2.1446 | -3.7144 | -5.9668 | -8.3844 | -10.9519 | -13.7245 | -16.4715 | -19.2396 | -27.5385 | -38.0315 | -42.7313 | -45.51
|  | ST |  |  | 59.7454 | 18.5233 | 17.9055 | 17.1625 | 16.1918 | 15.1422 | 14.0435 | 12.8198 | 11.7404 | 10.7196 | 6.9025 | -3.2876 | -9.783 | -14.0202 | 53.1285 | 1.6592 | 1.0627 | 0.34912 | -0.56992 | -1.5703 | -2.6571 | -3.8646 | -5.0475 | -6.2103 | -10.6298 | -22.9801 | -36.5187 | -56.2093 | 52.113 | 0.75524 | 0.24102 | -0.3954 | -1.251 | -2.1818 | -3.1681 | -4.2637 | -5.2594 | -6.2058 | -9.8289 | -19.3264 | -24.9123 | -28.3841
|  | SP |  |  | 59.8399 | 18.6131 | 18.0305 | 17.3469 | 16.5916 | 15.7843 | 14.9171 | 13.9394 | 13.1495 | 12.3391 | 9.5798 | 1.8149 | -4.8952 | -8.2434 | 53.1403 | 1.6312 | 0.99212 | 0.24182 | -0.66206 | -1.6677 | -2.7944 | -4.0615 | -5.3161 | -6.7588 | -12.1307 | -27.1112 | -51.1941 | -91.0167 | 52.1968 | 0.82631 | 0.33849 | -0.24905 | -0.90292 | -1.6092 | -2.3844 | -3.2592 | -3.9881 | -4.7388 | -7.3466 | -14.6466 | -20.7879 | -23.583
BRAMLEY (FLEE) | BURGHFIELD MAIN | MINIMUM HEADROOM | SU6942870520 | YES | 59.5554 | 57.5118 | 55.0788 | 52.3672 | 48.5224 | 44.6752 | 40.531 | 36.1757 | 30.8273 | 25.2964 | 10.3142 | -8.1631 | -20.1927 | -28.4498 | 32.9566 | 31.7544 | 30.2306 | 28.4902 | 26.2971 | 24.1024 | 21.642 | 19.044 | 15.6594 | 12.1874 | 3.1717 | -8.1069 | -18.8221 | -28.7663 | 32.9778 | 31.141 | 29.0043 | 26.5912 | 23.0582 | 19.524 | 15.7181 | 11.7318 | 6.8618 | 1.74 | -12.1554 | -28.8745 | -39.2364 | -46.254
|  | CT |  |  | 60.5631 | 59.1253 | 57.4772 | 55.2489 | 52.5179 | 49.8275 | 46.9665 | 43.9469 | 40.372 | 35.0134 | 20.2292 | -3.1991 | -20.1927 | -28.4498 | 33.2181 | 32.1529 | 30.9201 | 29.2172 | 27.3728 | 25.5485 | 23.5441 | 21.4222 | 18.8316 | 15.295 | 5.6833 | -8.1069 | -18.8221 | -28.7663 | 34.0079 | 32.7672 | 31.3184 | 29.319 | 26.8347 | 24.3883 | 21.712 | 18.8737 | 15.4907 | 10.4633 | -3.2496 | -24.2675 | -39.2364 | -46.254
|  | LW |  |  | 59.5554 | 57.5118 | 55.0788 | 52.3672 | 48.5224 | 44.6752 | 40.531 | 36.1757 | 30.8273 | 25.2964 | 10.3142 | -8.1631 | -16.2115 | -21.4484 | 32.9566 | 31.7544 | 30.2306 | 28.4902 | 26.2971 | 24.1024 | 21.642 | 19.044 | 15.6594 | 12.1874 | 3.1717 | -6.8371 | -10.5156 | -12.9418 | 32.9778 | 31.141 | 29.0043 | 26.5912 | 23.0582 | 19.524 | 15.7181 | 11.7318 | 6.8618 | 1.74 | -12.1554 | -28.8745 | -35.9631 | -40.3315
|  | ST |  |  | 61.4887 | 60.6218 | 59.618 | 58.4402 | 56.9773 | 55.5905 | 54.0497 | 52.4624 | 50.5644 | 48.6217 | 40.1755 | 22.8339 | 12.6849 | 5.9438 | 33.8113 | 33.1368 | 32.3643 | 31.417 | 30.3048 | 29.2274 | 27.9947 | 26.7203 | 25.1736 | 23.6548 | 16.8729 | 3.2385 | -5.9375 | -15.4179 | 34.7733 | 34.0127 | 33.1435 | 32.1212 | 30.858 | 29.616 | 28.218 | 26.7866 | 25.0687 | 23.2917 | 15.2671 | -0.94047 | -9.8841 | -15.5779
|  | SP |  |  | 61.6371 | 60.7731 | 59.8355 | 58.7437 | 57.2247 | 55.8086 | 54.3043 | 52.7456 | 50.9961 | 49.0406 | 41.7399 | 24.6471 | 13.6135 | 7.8819 | 33.863 | 33.1672 | 32.3822 | 31.442 | 30.3618 | 29.3527 | 28.2298 | 27.058 | 25.6918 | 24.1377 | 18.0337 | 3.0331 | -11.2313 | -28.3889 | 34.915 | 34.1797 | 33.3819 | 32.4467 | 31.0783 | 29.8012 | 28.418 | 26.9951 | 25.3951 | 23.6027 | 16.9503 | 1.0315 | -8.9966 | -13.9045
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MINIMUM HEADROOM | SU6942870520 | YES | 60.5936 | 58.2181 | 55.6253 | 52.9198 | 49.1435 | 45.3146 | 41.5456 | 37.3999 | 32.4585 | 27.6162 | 16.1813 | 0.66266 | -7.4041 | -14.5653 | 53.2453 | 52.3721 | 50.8852 | 49.3381 | 47.3381 | 45.2858 | 43.1857 | 40.8058 | 37.7837 | 34.8995 | 28.8491 | 21.1914 | 13.7423 | 7.3366 | 52.9995 | 50.9147 | 48.6635 | 46.3264 | 42.9568 | 39.5361 | 36.1671 | 32.5003 | 28.2266 | 23.8138 | 13.2164 | -0.83803 | -7.6929 | -13.849
|  | CT |  |  | 61.8792 | 60.2337 | 58.3811 | 56.3284 | 53.7238 | 51.1001 | 48.6444 | 45.8946 | 42.7946 | 38.0723 | 27.0865 | 7.576 | -7.4041 | -14.5653 | 53.2453 | 52.6979 | 51.6472 | 50.2337 | 48.648 | 47.0263 | 45.4299 | 43.6027 | 41.4831 | 38.4863 | 32.083 | 21.7981 | 13.7423 | 7.3366 | 54.3187 | 52.9583 | 51.4355 | 49.7658 | 47.5285 | 45.2707 | 43.1511 | 40.7119 | 37.9282 | 33.654 | 23.5575 | 5.4959 | -7.6929 | -13.849
|  | LW |  |  | 60.5936 | 58.2181 | 55.6253 | 52.9198 | 49.1435 | 45.3146 | 41.5456 | 37.3999 | 32.4585 | 27.6162 | 16.1813 | 0.66266 | -6.5395 | -11.2454 | 53.2997 | 52.3721 | 50.8852 | 49.3381 | 47.3381 | 45.2858 | 43.1857 | 40.8058 | 37.7837 | 34.8995 | 28.8491 | 21.1914 | 17.9415 | 15.7162 | 52.9995 | 50.9147 | 48.6635 | 46.3264 | 42.9568 | 39.5361 | 36.1671 | 32.5003 | 28.2266 | 23.8138 | 13.2164 | -0.83803 | -6.9642 | -10.8878
|  | ST |  |  | 62.3687 | 61.8684 | 60.7771 | 59.6331 | 58.1638 | 56.7118 | 55.3923 | 53.9382 | 52.2982 | 50.5843 | 43.065 | 29.4145 | 20.9997 | 14.9199 | 53.5198 | 53.1391 | 52.7555 | 52.4089 | 51.5645 | 50.5904 | 49.6602 | 48.6156 | 47.4088 | 46.229 | 40.7392 | 31.0121 | 24.769 | 18.6779 | 55.1033 | 54.2849 | 53.3962 | 52.483 | 51.2794 | 50.0794 | 48.9635 | 47.7406 | 46.3706 | 44.8887 | 38.2876 | 25.7556 | 18.4345 | 13.1239
|  | SP |  |  | 62.375 | 61.8911 | 61.2015 | 60.2725 | 58.6386 | 57.0545 | 55.5995 | 53.9839 | 52.3022 | 50.3384 | 43.3964 | 26.3651 | 16.4024 | 10.3864 | 53.5232 | 53.1476 | 52.784 | 52.4629 | 51.8375 | 50.9078 | 50.0287 | 49.0088 | 47.918 | 46.6753 | 42.0037 | 29.6369 | 20.8933 | 12.1213 | 55.2693 | 54.5365 | 53.8068 | 53.0816 | 51.6623 | 50.2753 | 48.9654 | 47.5338 | 46.0477 | 44.2936 | 38.2393 | 23.1769 | 14.2837 | 9.0239
BRAMLEY (FLEE) | CAMBERLEY MAIN | MINIMUM HEADROOM | SU8607569397 | YES | 31.9914 | 28.9847 | 25.6691 | 22.1623 | 16.9715 | 11.1277 | 4.7032 | -2.343 | -10.7395 | -18.1737 | -35.2904 | -58.5288 | -72.6578 | -82.8765 | 35.2482 | 33.2871 | 31.0926 | 28.8202 | 25.8046 | 22.2634 | 18.2818 | 13.7914 | 8.1384 | 3.2537 | -7.1133 | -24.8345 | -41.5901 | -58.159 | 28.0639 | 25.2687 | 22.1607 | 18.9061 | 14.1481 | 8.7668 | 2.8257 | -3.7544 | -11.7051 | -18.7213 | -34.5486 | -55.9383 | -68.1126 | -76.9267
|  | CT |  |  | 32.6693 | 30.2367 | 27.3559 | 24.2762 | 20.4691 | 16.0939 | 11.4126 | 6.3006 | 0.59139 | -7.2562 | -24.4651 | -52.8612 | -72.6578 | -82.8765 | 35.2562 | 33.4155 | 31.2157 | 28.917 | 26.3773 | 23.3715 | 20.0917 | 16.4269 | 12.2481 | 6.8867 | -4.1337 | -21.9009 | -35.5908 | -47.1821 | 28.6205 | 26.3355 | 23.599 | 20.7077 | 17.192 | 13.1369 | 8.7855 | 3.9834 | -1.422 | -8.8366 | -24.7156 | -50.4927 | -68.1126 | -76.9267
|  | LW |  |  | 31.9914 | 28.9847 | 25.6691 | 22.1623 | 16.9715 | 11.1277 | 4.7032 | -2.343 | -10.7395 | -18.1737 | -35.2904 | -58.5288 | -69.3996 | -75.4674 | 35.2482 | 33.2871 | 31.0926 | 28.8202 | 25.8046 | 22.2634 | 18.2818 | 13.7914 | 8.1384 | 3.2537 | -7.1133 | -21.1291 | -27.5613 | -31.1731 | 28.0639 | 25.2687 | 22.1607 | 18.9061 | 14.1481 | 8.7668 | 2.8257 | -3.7544 | -11.7051 | -18.7213 | -34.5486 | -55.9383 | -65.7057 | -71.0614
|  | ST |  |  | 34.4968 | 33.2467 | 31.7413 | 30.1558 | 28.2636 | 25.9265 | 23.3765 | 20.7079 | 17.7027 | 13.7317 | -2.8582 | -27.5668 | -41.1272 | -49.1887 | 36.5728 | 35.5564 | 34.3098 | 33.0355 | 31.5791 | 29.728 | 27.7042 | 25.5468 | 23.0832 | 19.7203 | 5.7618 | -14.7329 | -27.1926 | -38.0189 | 30.3954 | 29.2513 | 27.8402 | 26.3856 | 24.6491 | 22.4885 | 20.1316 | 17.6353 | 14.7947 | 10.9859 | -5.0631 | -28.5786 | -40.985 | -48.0714
|  | SP |  |  | 34.6703 | 33.4967 | 32.207 | 30.9555 | 29.3601 | 24.5229 | 19.5377 | 14.3767 | 5.8942 | 2.9138 | -7.8512 | -33.5824 | -47.3682 | -53.4452 | 36.6388 | 35.6358 | 34.4951 | 33.4138 | 32.2094 | 27.7735 | 23.205 | 18.4522 | 10.3692 | 7.8051 | -1.612 | -24.8345 | -41.5901 | -58.159 | 30.5539 | 29.4771 | 28.2711 | 27.1387 | 25.7029 | 21.0424 | 16.2477 | 11.2558 | 2.9346 | 0.11004 | -10.1538 | -34.9529 | -47.9312 | -53.3863
BRAMLEY (FLEE) | CAMBERLEY RESERVE | MINIMUM HEADROOM | SU8658459452 | YES | 52.2611 | 49.8454 | 47.118 | 44.3233 | 40.5614 | 36.1562 | 31.3929 | 26.3394 | 20.3863 | 13.9847 | -0.87384 | -18.6957 | -30.9159 | -38.9131 | -2.3961 | -4.0168 | -5.962 | -8.0235 | -10.315 | -13.0413 | -16.105 | -19.4726 | -23.9087 | -28.329 | -37.6215 | -49.961 | -59.9884 | -69.6137 | -5.5564 | -7.9182 | -10.6595 | -13.4818 | -17.0276 | -21.1754 | -25.7656 | -30.7118 | -36.9653 | -43.1916 | -56.4881 | -71.977 | -80.4874 | -86.5691
|  | CT |  |  | 52.7506 | 50.7002 | 48.3576 | 45.8402 | 43.0391 | 39.6359 | 36.0705 | 32.2648 | 27.8899 | 21.5056 | 6.3583 | -16.0437 | -30.9159 | -38.9131 | -2.3961 | -4.0168 | -5.8963 | -8.0235 | -10.0898 | -12.5361 | -15.1756 | -18.0518 | -21.5175 | -26.0194 | -36.0618 | -49.961 | -59.9884 | -69.6137 | -5.3091 | -7.4027 | -9.8217 | -12.5169 | -15.3232 | -18.6864 | -22.2722 | -26.1613 | -30.7813 | -36.996 | -50.5796 | -69.0845 | -80.4874 | -86.5691
|  | LW |  |  | 52.2611 | 49.8454 | 47.118 | 44.3233 | 40.5614 | 36.1562 | 31.3929 | 26.3394 | 20.3863 | 13.9847 | -0.87384 | -18.6957 | -26.4281 | -31.0889 | -2.3514 | -4.0105 | -5.962 | -7.9923 | -10.315 | -13.0413 | -16.105 | -19.4726 | -23.9087 | -28.329 | -37.6215 | -48.0475 | -51.6844 | -53.9496 | -5.5564 | -7.9182 | -10.6595 | -13.4818 | -17.0276 | -21.1754 | -25.7656 | -30.7118 | -36.9653 | -43.1916 | -56.4881 | -71.977 | -78.0764 | -81.7406
|  | ST |  |  | 53.804 | 52.6775 | 51.3857 | 50.0947 | 48.7847 | 47.1094 | 45.2831 | 43.3362 | 41.0773 | 38.6511 | 29.3431 | 10.7825 | 1.1662 | -4.5258 | -1.4935 | -2.4059 | -3.52 | -4.6859 | -5.9085 | -7.4036 | -9.048 | -10.8259 | -12.902 | -14.9748 | -23.0939 | -38.3401 | -47.8311 | -56.7941 | -4.0803 | -5.1614 | -6.4679 | -7.8002 | -9.2403 | -11.0397 | -13.016 | -15.1487 | -17.6329 | -20.1635 | -29.8205 | -47.4218 | -56.1123 | -60.9613
|  | SP |  |  | 53.9165 | 52.8553 | 51.6984 | 50.5648 | 49.5436 | 48.2459 | 46.8442 | 45.3409 | 43.664 | 41.8351 | 36.2552 | 18.9159 | 8.4727 | 4.0737 | -1.4541 | -2.3738 | -3.4248 | -4.5065 | -5.4735 | -6.6549 | -7.9786 | -9.4527 | -11.1167 | -12.9362 | -19.025 | -35.3362 | -49.579 | -65.2019 | -3.9826 | -5.0368 | -6.209 | -7.3762 | -8.4555 | -9.799 | -11.2945 | -12.9542 | -14.8131 | -16.8015 | -23.1542 | -39.8341 | -49.6323 | -53.5463
IVER 132KV | CHALVEY BSP | MINIMUM HEADROOM | SU9666979364 | NO | 59.3699 | 56.8859 | 53.7561 | 50.4132 | 46.0061 | 41.0949 | 36.1321 | 30.7103 | 24.5534 | 18.6158 | 3.4741 | -15.1767 | -26.6679 | -34.9115 | 46.5845 | 45.0805 | 43.3499 | 41.4171 | 39.1638 | 36.6975 | 34.1416 | 31.0956 | 27.358 | 23.6447 | 12.7771 | -5.1907 | -28.641 | -71.0627 | 49.0623 | 46.828 | 44.0212 | 40.997 | 36.9389 | 32.6034 | 28.1758 | 23.3196 | 17.7438 | 12.2924 | -1.7602 | -18.8383 | -28.3725 | -35.2087
|  | CT |  |  | 59.8503 | 57.6887 | 55.0306 | 51.8777 | 48.1853 | 44.2754 | 40.4267 | 36.0923 | 31.3392 | 25.6145 | 10.7159 | -11.672 | -26.6679 | -34.9115 | 46.6323 | 45.0991 | 43.3825 | 41.4171 | 39.1638 | 36.7333 | 34.2839 | 31.2379 | 27.8308 | 23.8433 | 12.7771 | -5.1907 | -22.4764 | -44.4788 | 49.5354 | 47.6186 | 45.2716 | 42.4362 | 39.0771 | 35.4923 | 31.9903 | 28.1241 | 23.8504 | 18.6234 | 4.8473 | -15.4236 | -28.3725 | -35.2087
|  | LW |  |  | 59.3699 | 56.8859 | 53.7561 | 50.4132 | 46.0061 | 41.0949 | 36.1321 | 30.7103 | 24.5534 | 18.6158 | 3.4741 | -15.1767 | -23.7816 | -28.5469 | 46.5845 | 45.0805 | 43.3499 | 41.5236 | 39.2045 | 36.6975 | 34.1416 | 31.0956 | 27.358 | 23.6447 | 14.085 | 2.7987 | -1.9065 | -4.6009 | 49.0623 | 46.828 | 44.0212 | 40.997 | 36.9389 | 32.6034 | 28.1758 | 23.3196 | 17.7438 | 12.2924 | -1.7602 | -18.8383 | -26.3632 | -30.4307
|  | ST |  |  | 60.9755 | 59.668 | 58.13 | 56.5181 | 54.4647 | 52.2864 | 50.1516 | 47.7949 | 45.1632 | 42.3282 | 33.3355 | 14.744 | 4.1988 | -2.1977 | 47.2409 | 46.1591 | 45.0287 | 43.8557 | 42.4348 | 40.8819 | 39.301 | 37.528 | 35.5266 | 33.1627 | 24.4405 | 5.3708 | -11.2098 | -32.2622 | 50.6394 | 49.5563 | 48.2463 | 46.8569 | 45.0445 | 43.1054 | 41.1833 | 39.055 | 36.6618 | 34.0475 | 25.5017 | 8.081 | -1.3941 | -6.8918
|  | SP |  |  | 61.1145 | 59.8274 | 58.3822 | 56.9013 | 55.2964 | 52.5171 | 49.7244 | 46.7436 | 42.4754 | 40.3347 | 34.205 | 19.1931 | 8.0429 | 3.0537 | 47.2648 | 46.1826 | 45.0506 | 43.8885 | 42.5896 | 40.0751 | 37.4907 | 34.7121 | 30.5938 | 28.3576 | 20.5432 | -0.65963 | -28.641 | -71.0627 | 50.7742 | 49.6874 | 48.4545 | 47.1782 | 45.7969 | 43.2324 | 40.6227 | 37.8326 | 33.7581 | 31.7965 | 26.0123 | 11.6703 | 1.3881 | -2.8208
LOVEDEAN GSP | CHICHESTER & HUNSTON | MINIMUM HEADROOM | SU9219807420 | NO | 160.5889 | 153.6154 | 145.8325 | 137.2746 | 125.2627 | 112.5182 | 99.3325 | 85.1255 | 68.6636 | 51.9951 | 8.8739 | -35.9793 | -63.2902 | -82.7034 | 140.7106 | 136.5591 | 131.8294 | 126.6417 | 120.1123 | 113.0169 | 105.4467 | 97.2203 | 87.2331 | 77.0049 | 52.1223 | 24.5247 | -0.92768 | -26.1157 | 135.9592 | 129.8482 | 122.8247 | 115.0792 | 104.4347 | 93.0525 | 81.1256 | 68.265 | 53.1518 | 37.7813 | -1.3573 | -41.8393 | -63.6997 | -79.7131
|  | CT |  |  | 163.2993 | 157.84 | 152.0672 | 144.5241 | 135.4524 | 125.7677 | 115.8476 | 105.1012 | 93.2811 | 76.8928 | 32.9321 | -24.134 | -63.2902 | -82.7034 | 141.3132 | 137.5578 | 133.7081 | 128.5888 | 122.9932 | 116.9244 | 110.5867 | 103.666 | 95.8364 | 85.3998 | 58.2357 | 24.5247 | -0.92768 | -24.4407 | 138.078 | 133.2925 | 128.2247 | 121.4622 | 113.4031 | 104.7504 | 95.8098 | 86.0908 | 75.2789 | 60.1868 | 20.2124 | -30.8616 | -63.6997 | -79.7131
|  | LW |  |  | 160.5889 | 153.6154 | 145.8325 | 137.2746 | 125.2627 | 112.5182 | 99.3325 | 85.1255 | 68.6636 | 51.9951 | 8.8739 | -35.9793 | -54.4207 | -64.8448 | 140.7106 | 136.5591 | 131.8294 | 126.6417 | 120.1123 | 113.0169 | 105.4467 | 97.2203 | 87.2331 | 77.0049 | 52.1223 | 27.6238 | 18.5991 | 13.4491 | 135.9592 | 129.8482 | 122.8247 | 115.0792 | 104.4347 | 93.0525 | 81.1256 | 68.265 | 53.1518 | 37.7813 | -1.3573 | -41.8393 | -57.507 | -66.2205
|  | ST |  |  | 166.182 | 162.8644 | 159.6298 | 156.0312 | 151.0839 | 145.7197 | 140.2692 | 134.3926 | 127.9574 | 120.7838 | 93.1298 | 45.5981 | 22.0033 | 7.3588 | 143.3539 | 140.9418 | 138.6036 | 136.0263 | 132.6119 | 128.838 | 124.9112 | 120.6457 | 115.8631 | 110.4981 | 89.2876 | 51.5394 | 29.3523 | 7.2642 | 140.9884 | 138.2132 | 135.4608 | 132.4049 | 128.1371 | 123.459 | 118.6405 | 113.4207 | 107.6156 | 101.0939 | 75.504 | 30.8564 | 9.5985 | -3.1446
|  | SP |  |  | 166.6635 | 163.4501 | 160.4584 | 157.1789 | 153.1736 | 146.8499 | 140.3553 | 133.4607 | 124.0985 | 118.2056 | 97.6593 | 53.6038 | 27.6161 | 16.2583 | 143.5271 | 141.0345 | 138.7341 | 136.2713 | 133.5111 | 128.405 | 123.0649 | 117.3552 | 109.1121 | 104.4686 | 87.6172 | 47.9801 | 13.3719 | -26.1157 | 141.4044 | 138.6589 | 136.1266 | 133.4107 | 130.0682 | 124.4046 | 118.5161 | 112.2419 | 103.4667 | 98.1993 | 79.5956 | 37.9985 | 13.8229 | 3.7965
CHICKERELL GSP | CHICKERELL BSP | MINIMUM HEADROOM | SY6547980511 | NO | 26.466 | 22.7583 | 18.1224 | 13.181 | 6.0885 | -1.6074 | -9.6443 | -18.0582 | -28.5783 | -39.54 | -69.2462 | -105.4925 | -119.0479 | -130.0268 | 25.4775 | 23.5264 | 20.992 | 18.1293 | 14.408 | 10.138 | 5.5852 | 0.80672 | -5.4858 | -12.2012 | -29.581 | -50.775 | -73.6331 | -103.0813 | 24.1588 | 21.0295 | 17.2732 | 13.1482 | 7.0289 | 0.33906 | -6.5823 | -13.7749 | -22.5445 | -31.8494 | -59.0024 | -91.5302 | -104.0124 | -114.1789
|  | CT |  |  | 28.6497 | 26.1795 | 23.2172 | 19.2784 | 14.2698 | 8.7464 | 3.006 | -3.0652 | -10.4789 | -20.8295 | -50.0089 | -94.436 | -119.0479 | -130.0268 | 26.1679 | 24.5931 | 22.7176 | 20.0294 | 16.9966 | 13.4707 | 9.7598 | 5.7026 | 0.66278 | -5.9572 | -24.3311 | -50.775 | -68.8522 | -85.8094 | 26.3787 | 24.4651 | 22.1823 | 19.1327 | 15.0457 | 10.4694 | 5.7167 | 0.73268 | -5.5124 | -15.0663 | -41.7709 | -81.3667 | -104.0124 | -114.1789
|  | LW |  |  | 26.466 | 22.7583 | 18.1224 | 13.181 | 6.0885 | -1.6074 | -9.6443 | -18.0582 | -28.5783 | -39.54 | -69.2462 | -105.4925 | -117.8353 | -124.7461 | 25.4775 | 23.5264 | 20.992 | 18.1293 | 14.408 | 10.138 | 5.5852 | 0.80672 | -5.4858 | -12.2012 | -29.581 | -49.7472 | -56.6423 | -60.5004 | 24.1588 | 21.0295 | 17.2732 | 13.1482 | 7.0289 | 0.33906 | -6.5823 | -13.7749 | -22.5445 | -31.8494 | -59.0024 | -91.5302 | -102.85 | -109.1692
|  | ST |  |  | 30.1616 | 28.7384 | 27.071 | 25.2133 | 22.5283 | 19.4186 | 16.2073 | 12.8095 | 8.614 | 3.1918 | -16.6206 | -53.8431 | -71.4809 | -81.8392 | 27.1133 | 26.1712 | 25.0668 | 23.6946 | 21.8934 | 19.6559 | 17.3006 | 14.8044 | 11.7277 | 7.5451 | -7.9846 | -37.2075 | -54.0423 | -70.1212 | 27.5741 | 26.506 | 25.2852 | 23.795 | 21.7345 | 19.2483 | 16.6737 | 13.9781 | 10.6746 | 6.0158 | -11.226 | -45.8352 | -61.8943 | -71.0043
|  | SP |  |  | 30.5362 | 29.1657 | 27.6381 | 25.9663 | 23.3923 | 17.5495 | 11.6708 | 5.5993 | -4.1545 | -8.8801 | -24.7576 | -59.9767 | -80.4366 | -89.5761 | 27.2546 | 26.2778 | 25.1742 | 23.8287 | 22.1581 | 17.1886 | 12.1405 | 6.9278 | -1.8461 | -5.4556 | -17.9404 | -47.7122 | -73.6331 | -103.0813 | 27.9311 | 26.9752 | 25.9219 | 24.6326 | 22.5288 | 17.1556 | 11.7424 | 6.2201 | -2.8323 | -6.8657 | -20.0139 | -51.7961 | -70.8363 | -78.9714
MELKSHAM GSP | CHIPPENHAM | MINIMUM HEADROOM | ST9275574305 | NO | 29.5819 | 25.5615 | 21.1999 | 16.5982 | 10.7817 | 4.979 | -1.1972 | -7.8912 | -15.8943 | -23.8295 | -42.7366 | -64.4848 | -71.2619 | -78.9858 | 22.0415 | 19.8886 | 17.5386 | 14.9938 | 11.8976 | 8.836 | 5.4583 | 1.5836 | -3.3685 | -8.2386 | -18.8194 | -29.8234 | -39.553 | -48.8512 | 22.9892 | 19.4875 | 15.6951 | 11.6915 | 6.4204 | 1.1836 | -4.3723 | -10.4104 | -17.7056 | -24.9485 | -42.506 | -62.4089 | -68.3963 | -74.9548
|  | CT |  |  | 31.7204 | 28.9324 | 25.8373 | 22.311 | 18.4839 | 14.7222 | 10.7279 | 6.2625 | 1.2459 | -6.3686 | -24.537 | -52.1026 | -70.967 | -78.9858 | 22.7888 | 21.0574 | 19.1066 | 16.7535 | 14.3744 | 11.9616 | 9.3117 | 6.2974 | 2.8159 | -2.1392 | -13.3235 | -28.6711 | -39.553 | -48.8512 | 25.1611 | 22.8728 | 20.3275 | 17.4246 | 14.0257 | 10.5919 | 6.959 | 2.9134 | -1.704 | -8.8848 | -25.7587 | -51.1435 | -67.9136 | -74.9548
|  | LW |  |  | 29.5819 | 25.5615 | 21.1999 | 16.5982 | 10.7817 | 4.979 | -1.1972 | -7.8912 | -15.8943 | -23.8295 | -42.7366 | -64.4848 | -71.2619 | -74.333 | 22.0415 | 19.8886 | 17.5386 | 14.9938 | 11.8976 | 8.836 | 5.4583 | 1.5836 | -3.3685 | -8.2386 | -18.8194 | -29.8234 | -32.5842 | -33.8171 | 22.9892 | 19.4875 | 15.6951 | 11.6915 | 6.4204 | 1.1836 | -4.3723 | -10.4104 | -17.7056 | -24.9485 | -42.506 | -62.4089 | -68.3963 | -71.0874
|  | ST |  |  | 33.4737 | 31.872 | 30.1087 | 28.1998 | 26.139 | 24.1755 | 22.0539 | 19.725 | 17.1077 | 14.3597 | 2.362 | -19.327 | -30.0361 | -36.5264 | 23.7918 | 22.7208 | 21.5494 | 20.2506 | 18.8853 | 17.6169 | 16.165 | 14.5308 | 12.6605 | 10.7491 | 1.7254 | -14.6687 | -23.794 | -32.6422 | 26.6061 | 25.3156 | 23.8995 | 22.3497 | 20.5578 | 18.8561 | 17.0374 | 15.0596 | 12.802 | 10.291 | -0.80403 | -21.3587 | -31.0685 | -36.7766
|  | SP |  |  | 33.8348 | 32.3637 | 30.8718 | 29.3054 | 27.2123 | 25.2436 | 23.2416 | 21.001 | 18.6246 | 15.7196 | 5.4407 | -19.8132 | -33.7997 | -40.3513 | 23.9309 | 22.8951 | 21.8272 | 20.6675 | 19.3381 | 18.1171 | 16.8523 | 15.4114 | 13.7892 | 11.8488 | 4.6104 | -15.1321 | -29.7255 | -44.768 | 26.9544 | 25.8095 | 24.6413 | 23.395 | 21.5031 | 19.7209 | 17.9137 | 15.9388 | 13.8503 | 11.2494 | 2.0587 | -21.3862 | -34.3949 | -40.2736
MANNINGTON GSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ1569893141 | YES | 51.2027 | 49.307 | 46.7889 | 43.9957 | 39.4781 | 34.7077 | 29.5972 | 24.1404 | 17.9915 | 11.3867 | -6.8422 | -30.7901 | -51.4948 | -64.7265 | 46.9773 | 45.8873 | 44.357 | 42.6385 | 40.2118 | 37.5508 | 34.6021 | 31.2577 | 27.212 | 22.7866 | 11.4827 | -7.4738 | -25.3768 | -56.4733 | 50.2425 | 48.4854 | 46.08 | 43.3972 | 39.2583 | 34.8312 | 30.0135 | 24.8462 | 18.839 | 12.3317 | -4.8375 | -26.6034 | -43.169 | -53.9967
|  | CT |  |  | 52.0791 | 50.7456 | 49.0528 | 46.6729 | 43.5593 | 40.2594 | 36.7625 | 32.9787 | 28.8711 | 22.112 | 2.9418 | -27.6059 | -51.4948 | -64.7265 | 47.1097 | 46.085 | 44.8131 | 43.0012 | 40.913 | 38.6216 | 36.0778 | 33.2157 | 30.0047 | 25.4107 | 12.3618 | -7.4738 | -25.3768 | -44.4429 | 50.9156 | 49.6252 | 47.9898 | 45.5999 | 42.6336 | 39.4492 | 36.043 | 32.3499 | 28.3086 | 21.9494 | 4.0287 | -23.358 | -43.169 | -53.9967
|  | LW |  |  | 51.2027 | 49.307 | 46.7889 | 43.9957 | 39.4781 | 34.7077 | 29.5972 | 24.1404 | 17.9915 | 11.3867 | -6.8422 | -30.7901 | -43.5148 | -51.6333 | 46.9773 | 45.8873 | 44.357 | 42.6385 | 40.2118 | 37.5508 | 34.6021 | 31.2577 | 27.212 | 22.7866 | 11.4827 | -2.047 | -8.4362 | -12.5433 | 50.2425 | 48.4854 | 46.08 | 43.3972 | 39.2583 | 34.8312 | 30.0135 | 24.8462 | 18.839 | 12.3317 | -4.8375 | -26.6034 | -37.455 | -44.1533
|  | ST |  |  | 53.1348 | 52.5166 | 51.7048 | 50.7653 | 49.4368 | 47.9672 | 46.3578 | 44.6023 | 42.7247 | 40.2694 | 30.1346 | 6.0515 | -7.8836 | -17.4144 | 47.8 | 47.2322 | 46.5177 | 45.6895 | 44.5591 | 43.2639 | 41.8213 | 40.2421 | 38.4906 | 36.2673 | 26.9878 | 5.9269 | -9.5484 | -27.2217 | 51.9838 | 51.4098 | 50.6529 | 49.7637 | 48.4603 | 46.9922 | 45.367 | 43.5947 | 41.6439 | 39.1805 | 29.1951 | 6.4963 | -5.8094 | -13.8867
|  | SP |  |  | 53.3341 | 52.6817 | 51.8996 | 51.0291 | 49.969 | 47.6557 | 45.2699 | 42.6988 | 38.8693 | 37.0406 | 30.3392 | 10.1916 | -3.9894 | -10.7084 | 47.8709 | 47.2237 | 46.4532 | 45.5921 | 44.603 | 42.2965 | 39.8784 | 37.2808 | 33.3187 | 31.3046 | 23.6565 | 1.3947 | -23.5513 | -56.4733 | 52.1663 | 51.5281 | 50.7766 | 49.9361 | 48.9307 | 46.6487 | 44.2827 | 41.7261 | 37.8683 | 36.0414 | 29.2683 | 10.1246 | -2.9095 | -8.6391
IVER 132KV | CIPPENHAM | MINIMUM HEADROOM | SU9626679634 | NO | 84.485 | 83.6903 | 82.7865 | 81.7828 | 80.1018 | 78.2416 | 76.2029 | 73.9816 | 71.4239 | 68.6535 | 61.2481 | 52.6593 | 48.425 | 45.4776 | 68.6791 | 68.2727 | 67.8104 | 67.2869 | 66.4805 | 65.5776 | 64.5651 | 63.4521 | 61.8282 | 59.9818 | 55.2598 | 48.4577 | 42.7624 | 33.9455 | 75.7835 | 75.0236 | 74.1524 | 73.1763 | 71.6261 | 69.9084 | 67.9994 | 65.9008 | 63.414 | 60.7043 | 53.594 | 45.5539 | 42.3801 | 39.9673
|  | CT |  |  | 84.8881 | 84.357 | 83.7023 | 82.9124 | 81.7804 | 80.4983 | 79.1616 | 77.6888 | 76.0015 | 73.327 | 66.0672 | 55.1519 | 48.425 | 45.4776 | 68.7557 | 68.3863 | 67.943 | 67.4116 | 66.7376 | 65.975 | 65.1533 | 64.1979 | 62.8708 | 60.9762 | 55.8577 | 48.4577 | 42.7624 | 36.5311 | 76.0859 | 75.5443 | 74.8765 | 74.0621 | 72.9733 | 71.7482 | 70.4502 | 69.0127 | 67.3448 | 64.7473 | 57.8019 | 48.0031 | 42.3801 | 39.9673
|  | LW |  |  | 84.485 | 83.6903 | 82.7865 | 81.7828 | 80.1018 | 78.2416 | 76.2029 | 73.9816 | 71.4239 | 68.6535 | 61.2481 | 52.6593 | 49.8673 | 48.8073 | 68.6791 | 68.2727 | 67.8104 | 67.2869 | 66.4805 | 65.5776 | 64.5651 | 63.4521 | 61.8282 | 59.9818 | 55.2598 | 50.1792 | 48.9659 | 48.5034 | 75.7835 | 75.0236 | 74.1524 | 73.1763 | 71.6261 | 69.9084 | 67.9994 | 65.9008 | 63.414 | 60.7043 | 53.594 | 45.5539 | 43.1927 | 42.3184
|  | ST |  |  | 85.4262 | 85.2156 | 84.9404 | 84.6057 | 84.163 | 83.6255 | 83.009 | 82.3109 | 81.4699 | 80.5271 | 76.7865 | 68.5285 | 64.2417 | 61.7454 | 69.0492 | 68.8544 | 68.6201 | 68.3413 | 67.9994 | 67.5947 | 67.1273 | 66.5965 | 65.9595 | 65.2701 | 62.0253 | 54.1966 | 48.837 | 42.7699 | 76.6321 | 76.4151 | 76.1342 | 75.7898 | 75.3421 | 74.8085 | 74.1936 | 73.4935 | 72.6423 | 71.7148 | 67.8685 | 59.5202 | 55.6448 | 53.6012
|  | SP |  |  | 85.5119 | 85.31 | 85.0683 | 84.7869 | 84.4074 | 83.9482 | 83.4425 | 82.8638 | 82.1927 | 81.3878 | 78.6486 | 71.4556 | 66.3155 | 64.4645 | 69.0752 | 68.8724 | 68.6334 | 68.3589 | 68.0353 | 67.6503 | 67.2154 | 66.7188 | 66.1364 | 65.4442 | 62.8203 | 54.389 | 45.3175 | 33.9455 | 76.7117 | 76.4945 | 76.238 | 75.9405 | 75.571 | 75.1326 | 74.6418 | 74.0755 | 73.411 | 72.6264 | 69.8702 | 62.3751 | 57.399 | 55.6995
MINETY GSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP0268900364 | YES | -112.08 | -168.7665 | -171.94 | -175.3036 | -180.1388 | -185.1865 | -190.4267 | -196.0397 | -202.4365 | -208.7771 | -225.1806 | -243.3322 | -249.2492 | -253.2169 | -110.0211 | -165.0911 | -166.7254 | -168.4667 | -170.8346 | -173.3704 | -176.102 | -179.1244 | -182.8503 | -186.5392 | -194.6982 | -203.2823 | -208.5401 | -214.6052 | -131.7352 | -188.0975 | -190.9432 | -193.9544 | -198.2638 | -202.7634 | -207.5311 | -212.6995 | -218.7554 | -224.6851 | -239.3071 | -255.2953 | -260.3281 | -263.6565
|  | CT |  |  | -109.5572 | -164.9232 | -166.7723 | -168.8833 | -171.935 | -175.1703 | -178.525 | -182.2071 | -186.3916 | -192.4075 | -207.3026 | -229.8468 | -244.0122 | -249.2676 | -109.687 | -163.9473 | -165.0759 | -166.5643 | -168.3573 | -170.2707 | -172.3177 | -174.6469 | -177.4088 | -181.1548 | -189.4385 | -200.7722 | -208.5401 | -214.6052 | -129.5404 | -184.7495 | -186.5211 | -188.5628 | -191.3728 | -194.3566 | -197.4832 | -200.9512 | -204.8942 | -210.5705 | -223.8974 | -243.6961 | -255.6777 | -260.0957
|  | LW |  |  | -112.08 | -168.7665 | -171.94 | -175.3036 | -180.1388 | -185.1865 | -190.4267 | -196.0397 | -202.4365 | -208.7771 | -225.1806 | -243.3322 | -249.2492 | -253.2169 | -110.0211 | -165.0911 | -166.7254 | -168.4667 | -170.8346 | -173.3704 | -176.102 | -179.1244 | -182.8503 | -186.5392 | -194.6982 | -203.2823 | -205.8835 | -207.6557 | -131.7352 | -188.0975 | -190.9432 | -193.9544 | -198.2638 | -202.7634 | -207.5311 | -212.6995 | -218.7554 | -224.6851 | -239.3071 | -255.2953 | -260.3281 | -263.6565
|  | ST |  |  | 4.3733 | 3.1722 | -110.9946 | -165.8436 | -167.5943 | -169.451 | -171.3739 | -173.4283 | -175.6718 | -178.1112 | -187.8163 | -203.9257 | -213.3429 | -219.8128 | 3.5856 | 3.0838 | -110.29 | -164.4297 | -165.4855 | -166.6122 | -167.8569 | -169.2339 | -170.7885 | -172.3482 | -179.1727 | -190.4022 | -196.9848 | -203.2872 | -15.6465 | -16.708 | -130.7381 | -185.4366 | -186.9924 | -188.6958 | -190.4773 | -192.3971 | -194.5207 | -196.7792 | -206.1243 | -221.2091 | -229.2154 | -234.6215
|  | SP |  |  | 4.6954 | 3.6714 | 2.7322 | 1.7556 | -0.52154 | -2.8622 | -5.2236 | -7.7359 | -10.3276 | -13.4783 | -23.6072 | -45.0658 | -57.8537 | -65.5775 | 3.5874 | 3.087 | 2.7195 | 2.3656 | 1.3418 | 0.11463 | -1.1552 | -2.5516 | -4.0681 | -5.8371 | -12.0231 | -26.6588 | -36.5783 | -46.3069 | -15.3627 | -16.2713 | -17.098 | -17.9473 | -19.933 | -21.9685 | -24.0289 | -26.2695 | -28.5981 | -31.4069 | -40.6672 | -60.7117 | -72.2045 | -78.9558
EALING GSP | COPLEY DENE | MINIMUM HEADROOM | TQ1745580805 | NO | 18.2937 | 17.6031 | 16.9514 | 16.2468 | 14.9836 | 13.6175 | 12.1654 | 10.6037 | 8.7826 | 6.7925 | 0.45615 | -8.1237 | -14.0063 | -18.0262 | 17.8094 | 17.2907 | 16.7732 | 16.1838 | 15.3962 | 14.5355 | 13.6303 | 12.6344 | 11.4971 | 9.9865 | 4.7473 | -6.3045 | -28.1156 | -66.6665 | 17.1966 | 16.5831 | 15.9894 | 15.3393 | 14.2299 | 13.0228 | 11.7249 | 10.2573 | 8.536 | 6.6654 | 0.71557 | -7.1448 | -11.913 | -15.2465
|  | CT |  |  | 18.4962 | 17.9455 | 17.4349 | 16.8492 | 15.9698 | 15.012 | 14.0772 | 13.0673 | 11.9187 | 10.0663 | 4.0195 | -6.6422 | -14.0063 | -18.0262 | 17.8094 | 17.2907 | 16.7732 | 16.1838 | 15.3962 | 14.5355 | 13.6303 | 12.6344 | 11.4971 | 9.9865 | 4.7473 | -6.3045 | -19.5665 | -39.0005 | 17.342 | 16.8389 | 16.3574 | 15.7966 | 15.0018 | 14.1337 | 13.2704 | 12.333 | 11.2544 | 9.5671 | 3.9709 | -5.6548 | -11.913 | -15.2465
|  | LW |  |  | 18.2937 | 17.6031 | 16.9514 | 16.2468 | 14.9836 | 13.6175 | 12.1654 | 10.6037 | 8.7826 | 6.7925 | 0.45615 | -8.1237 | -11.8736 | -13.917 | 17.8987 | 17.5148 | 17.1548 | 16.758 | 16.0882 | 15.3619 | 14.5767 | 13.7312 | 12.7457 | 11.6719 | 8.0711 | 3.1478 | 1.4218 | 0.42612 | 17.1966 | 16.5831 | 15.9894 | 15.3393 | 14.2299 | 13.0228 | 11.7249 | 10.2573 | 8.536 | 6.6654 | 0.71557 | -7.1448 | -10.3514 | -12.0424
|  | ST |  |  | 19.0491 | 18.8141 | 18.6175 | 18.4043 | 18.0927 | 17.7388 | 17.3427 | 16.9049 | 16.3657 | 15.7521 | 13.2002 | 5.7733 | 1.1212 | -1.7083 | 18.1205 | 17.7781 | 17.4392 | 17.0631 | 16.5737 | 16.0304 | 15.413 | 14.7222 | 13.9099 | 13.0417 | 9.6423 | -0.66262 | -13.2963 | -32.2906 | 17.8634 | 17.655 | 17.4688 | 17.2631 | 16.9644 | 16.6263 | 16.2439 | 15.8194 | 15.2932 | 14.7063 | 12.2394 | 5.1911 | 1.0637 | -1.2862
|  | SP |  |  | 19.1106 | 18.8694 | 18.6768 | 18.4748 | 18.2333 | 17.9583 | 17.6653 | 17.3418 | 16.9494 | 16.4762 | 14.7033 | 9.2638 | 4.5808 | 2.5534 | 18.1139 | 17.7393 | 17.3448 | 16.9085 | 16.3498 | 15.7093 | 14.9845 | 14.1695 | 13.2082 | 12.0419 | 7.5605 | -5.4553 | -28.1156 | -66.6665 | 17.9198 | 17.7009 | 17.5152 | 17.3172 | 17.0865 | 16.8253 | 16.544 | 16.2307 | 15.8479 | 15.3952 | 13.6856 | 8.4381 | 4.007 | 2.2135
FAWLEY GSP | COWES & WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ5053594332 | YES | 106.1889 | 101.7302 | 95.9641 | 69.3518 | 60.4428 | 50.9626 | 40.9942 | 30.5487 | 18.52 | 5.8072 | -30.2625 | -69.4071 | -83.8573 | -91.7808 | 98.6265 | 96.3136 | 93.1031 | 69.2022 | 64.647 | 59.6109 | 54.1495 | 48.3593 | 41.4366 | 33.8243 | 12.9686 | -7.3758 | -14.4714 | -39.3614 | 94.6207 | 90.6094 | 85.4146 | 59.4015 | 51.3875 | 42.8064 | 33.7267 | 24.1812 | 13.1006 | 1.1895 | -32.0631 | -67.3288 | -80.3143 | -87.3985
|  | CT |  |  | 109.4714 | 106.8225 | 103.4485 | 98.5799 | 92.5826 | 86.1094 | 79.1774 | 71.8344 | 63.6554 | 51.6232 | 16.2806 | -34.6672 | -70.0381 | -85.0274 | 98.6265 | 97.58 | 95.7018 | 92.5201 | 88.9412 | 84.9546 | 80.6511 | 76.052 | 70.6664 | 63.1605 | 41.2112 | 12.7004 | -9.1199 | -27.9426 | 97.4791 | 95.0629 | 92.0831 | 87.5862 | 82.11 | 76.1593 | 69.763 | 62.9632 | 55.3331 | 44.1581 | 11.4779 | -33.8999 | -65.2709 | -78.5433
|  | LW |  |  | 106.1889 | 101.7302 | 95.9641 | 69.3518 | 60.4428 | 50.9626 | 40.9942 | 30.5487 | 18.52 | 5.8072 | -30.2625 | -69.4071 | -83.8573 | -91.7808 | 98.663 | 96.3136 | 93.1031 | 69.2022 | 64.647 | 59.6109 | 54.1495 | 48.3593 | 41.4366 | 33.8243 | 12.9686 | -7.3758 | -14.4714 | -18.3067 | 94.6207 | 90.6094 | 85.4146 | 59.4015 | 51.3875 | 42.8064 | 33.7267 | 24.1812 | 13.1006 | 1.1895 | -32.0631 | -67.3288 | -80.3143 | -87.3985
|  | ST |  |  | 110.9865 | 109.3575 | 107.414 | 105.316 | 102.2155 | 98.6477 | 94.8725 | 90.8589 | 86.4091 | 80.8199 | 59.6593 | 17.6006 | -3.6127 | -15.9617 | 99.1635 | 98.4455 | 97.7209 | 96.7871 | 94.7259 | 92.3044 | 89.6964 | 86.8904 | 83.7131 | 79.5369 | 63.4769 | 30.5904 | 11.7128 | -5.6993 | 98.9234 | 97.4724 | 95.8026 | 93.9895 | 91.2202 | 87.9938 | 84.5228 | 80.8117 | 76.6632 | 71.4149 | 51.3654 | 11.3406 | -8.0988 | -19.0611
|  | SP |  |  | 111.4409 | 109.8861 | 108.0938 | 106.1431 | 102.9764 | 96.8332 | 90.5788 | 84.0743 | 74.4503 | 69.3681 | 51.8937 | 12.6834 | -12.3797 | -22.9141 | 99.1889 | 98.4486 | 97.706 | 96.8462 | 94.9123 | 89.9848 | 84.9264 | 79.6478 | 71.2303 | 67.5532 | 54.4213 | 22.2641 | -7.3248 | -39.3614 | 99.3276 | 97.9195 | 96.3748 | 94.7241 | 91.9354 | 86.1642 | 80.2739 | 74.1288 | 64.8606 | 60.1974 | 44.035 | 6.956 | -16.5402 | -26.0173
COWLEY GSP | COWLEY LOCAL (2 X 45) | MINIMUM HEADROOM | SP5617503067 | NO | 88.3939 | 87.2649 | 86.3041 | 85.0394 | 83.1857 | 80.8553 | 78.3455 | 75.5727 | 72.3634 | 69.1085 | 59.8066 | 49.1835 | 45.8751 | 44.1339 | 67.1227 | 66.4721 | 65.9129 | 65.2016 | 64.2568 | 63.0814 | 61.7952 | 60.3679 | 58.644 | 56.9017 | 52.423 | 47.4006 | 45.4297 | 44.0895 | 77.6398 | 76.6805 | 75.8657 | 74.8191 | 73.2701 | 71.3455 | 69.2729 | 66.9822 | 64.343 | 61.6617 | 53.9163 | 45.0297 | 42.0115 | 40.4222
|  | CT |  |  | 88.6826 | 87.7254 | 86.9841 | 85.8702 | 84.3484 | 82.3577 | 80.2097 | 77.8151 | 75.1658 | 71.9116 | 62.3375 | 50.198 | 45.8751 | 44.1339 | 67.1672 | 66.5515 | 66.0658 | 65.366 | 64.526 | 63.4589 | 62.3066 | 61.0236 | 59.5849 | 57.8071 | 53.0091 | 47.4006 | 45.4297 | 44.0895 | 77.9383 | 77.15 | 76.541 | 75.6507 | 74.421 | 72.8226 | 71.0894 | 69.1507 | 67.0041 | 64.3351 | 56.408 | 45.9818 | 42.0115 | 40.4222
|  | LW |  |  | 88.3939 | 87.2649 | 86.3041 | 85.0394 | 83.1857 | 80.8553 | 78.3455 | 75.5727 | 72.3634 | 69.1085 | 59.8066 | 49.1835 | 47.2048 | 46.3911 | 67.1227 | 66.4721 | 65.9129 | 65.2016 | 64.2568 | 63.0814 | 61.7952 | 60.3679 | 58.644 | 56.9017 | 52.423 | 47.4919 | 46.6781 | 46.3935 | 77.6398 | 76.6805 | 75.8657 | 74.8191 | 73.2701 | 71.3455 | 69.2729 | 66.9822 | 64.343 | 61.6617 | 53.9163 | 45.0297 | 43.2473 | 42.5055
|  | ST |  |  | 89.0541 | 88.3982 | 87.9361 | 87.2944 | 86.3482 | 85.093 | 83.7541 | 82.2743 | 80.6621 | 79.0178 | 72.7194 | 64.0246 | 61.7733 | 60.4706 | 67.4357 | 67.0141 | 66.707 | 66.295 | 65.7119 | 64.9548 | 64.1446 | 63.2509 | 62.2722 | 61.3106 | 57.471 | 52.0989 | 50.6118 | 49.3418 | 78.2385 | 77.7035 | 77.3308 | 76.845 | 76.151 | 75.245 | 74.2725 | 73.1924 | 72.0085 | 70.7854 | 65.824 | 58.444 | 56.4818 | 55.3359
|  | SP |  |  | 89.1006 | 88.4618 | 88.0405 | 87.4774 | 86.6535 | 85.5934 | 84.3879 | 83.0705 | 81.6794 | 80.1806 | 74.8777 | 66.1266 | 63.5716 | 62.5166 | 67.4481 | 67.0223 | 66.7283 | 66.3555 | 65.886 | 65.2832 | 64.5641 | 63.7654 | 62.9132 | 62.0093 | 58.7244 | 52.8489 | 50.6979 | 48.8962 | 78.2839 | 77.7694 | 77.4349 | 77.0175 | 76.41 | 75.6537 | 74.791 | 73.8517 | 72.8611 | 71.7751 | 67.8652 | 60.3561 | 58.0544 | 57.1128
COWLEY GSP | COWLEY LOCAL (2 X 90) | MINIMUM HEADROOM | SP5617503067 | NO | 49.2721 | 47.0274 | 44.7419 | 41.7833 | 37.5618 | 33.0011 | 28.0027 | 22.9583 | 16.8264 | 10.5998 | -7.6548 | -28.7637 | -43.8531 | -54.1707 | 38.6712 | 37.2483 | 35.8 | 34.0113 | 31.6447 | 29.0971 | 26.2728 | 23.3754 | 19.7508 | 16.072 | 5.0574 | -13.4603 | -30.2661 | -60.078 | 38.8703 | 36.8328 | 34.7707 | 32.2477 | 28.4799 | 24.384 | 19.9054 | 15.3532 | 9.8357 | 4.2162 | -12.2423 | -31.2952 | -44.1776 | -52.7734
|  | CT |  |  | 50.0709 | 48.2503 | 46.4808 | 43.9003 | 40.6912 | 37.1859 | 33.3962 | 29.5914 | 25.1401 | 18.9986 | 0.95138 | -25.4897 | -43.8531 | -54.1707 | 38.726 | 37.3095 | 35.9398 | 34.0463 | 31.8401 | 29.4549 | 26.8546 | 24.1558 | 20.9746 | 16.9575 | 5.0574 | -13.4603 | -30.2661 | -50.1188 | 39.5478 | 37.978 | 36.481 | 34.3105 | 31.4499 | 28.3403 | 24.995 | 21.606 | 17.6458 | 12.1138 | -4.1155 | -28.266 | -44.1776 | -52.7734
|  | LW |  |  | 49.2721 | 47.0274 | 44.7419 | 41.7833 | 37.5618 | 33.0011 | 28.0027 | 22.9583 | 16.8264 | 10.5998 | -7.6548 | -28.7637 | -37.8421 | -43.9128 | 38.6712 | 37.2483 | 35.8 | 34.0113 | 31.6447 | 29.0971 | 26.2728 | 23.3754 | 19.7508 | 16.072 | 5.5307 | -5.8974 | -10.1545 | -13.0435 | 38.8703 | 36.8328 | 34.7707 | 32.2477 | 28.4799 | 24.384 | 19.9054 | 15.3532 | 9.8357 | 4.2162 | -12.2423 | -31.2952 | -39.1828 | -44.2505
|  | ST |  |  | 51.0587 | 49.9835 | 49.0671 | 47.7987 | 46.0818 | 44.1987 | 42.0982 | 39.9961 | 37.4577 | 34.8393 | 25.248 | 6.0747 | -4.9575 | -12.1052 | 39.431 | 38.4528 | 37.5481 | 36.4015 | 34.9587 | 33.4025 | 31.6689 | 29.8567 | 27.6862 | 25.5045 | 17.5576 | 0.39817 | -14.6387 | -33.4531 | 40.5416 | 39.6084 | 38.7789 | 37.7055 | 36.3037 | 34.777 | 32.9986 | 31.1851 | 28.9855 | 26.69 | 18.3425 | 0.69533 | -9.0414 | -15.0648
|  | SP |  |  | 51.3903 | 50.3613 | 49.4997 | 48.2554 | 46.7194 | 45.0726 | 43.214 | 41.3867 | 39.2351 | 36.8939 | 29.1744 | 13.0804 | 1.8937 | -3.6891 | 39.5225 | 38.5077 | 37.5585 | 36.3957 | 35.015 | 33.5236 | 31.8348 | 30.069 | 27.974 | 25.663 | 17.6819 | -1.1538 | -24.9709 | -60.078 | 40.835 | 39.93 | 39.1512 | 38.1773 | 36.8967 | 35.5522 | 34.0091 | 32.439 | 30.5882 | 28.5513 | 21.9168 | 7.3733 | -2.8089 | -7.5613
BRAMLEY (FLEE) | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU7827550779 | YES | 48.3947 | -56.4977 | -81.7247 | -84.6892 | -89.1662 | -93.7553 | -98.7174 | -104.2852 | -111.1109 | -117.5816 | -132.3793 | -150.6776 | -160.3961 | -168.3304 | 42.9033 | -60.9496 | -85.1382 | -87.0189 | -89.5669 | -92.1913 | -95.1368 | -98.5244 | -102.965 | -107.0713 | -115.6239 | -125.9678 | -135.5412 | -143.6699 | 43.091 | -61.5817 | -86.6078 | -89.3717 | -93.4871 | -97.7169 | -102.3275 | -107.5237 | -113.9789 | -120.0688 | -133.7261 | -150.4588 | -158.5382 | -165.0335
|  | CT |  |  | 49.3374 | -54.9095 | -79.5962 | -82.0168 | -85.1557 | -88.3547 | -91.6657 | -95.5047 | -99.9289 | -106.5269 | -121.2413 | -144.5738 | -160.3961 | -168.3304 | 43.0399 | -60.6636 | -84.7989 | -86.6354 | -88.7192 | -90.8519 | -93.1458 | -95.8451 | -99.0217 | -103.3938 | -112.4916 | -125.9678 | -135.5412 | -143.6699 | 43.8841 | -60.2197 | -84.7813 | -87.0776 | -89.9955 | -92.9768 | -96.0885 | -99.7102 | -103.9068 | -110.1262 | -123.7111 | -144.7788 | -158.5382 | -165.0335
|  | LW |  |  | 48.3947 | -56.4977 | -81.7247 | -84.6892 | -89.1662 | -93.7553 | -98.7174 | -104.2852 | -111.1109 | -117.5816 | -132.3793 | -150.6776 | -157.444 | -161.1931 | 42.9033 | -60.9496 | -85.1382 | -87.0189 | -89.5669 | -92.1913 | -95.1368 | -98.5244 | -102.965 | -107.0713 | -115.6239 | -125.6701 | -128.7685 | -130.4943 | 43.091 | -61.5817 | -86.6078 | -89.3717 | -93.4871 | -97.7169 | -102.3275 | -107.5237 | -113.9789 | -120.0688 | -133.7261 | -150.4588 | -156.3702 | -159.5814
|  | ST |  |  | 50.9752 | 49.774 | 26.172 | 24.9089 | 23.3387 | 21.756 | 20.0559 | 18.1378 | 15.9142 | 13.5971 | 3.0469 | -14.6344 | -24.1209 | -30.0579 | 44.2175 | 43.2578 | 19.8838 | 18.8588 | 17.6637 | 16.4558 | 15.1266 | 13.618 | 11.845 | 10.1127 | 1.9139 | -11.7743 | -19.8203 | -27.3772 | 45.4743 | 44.3816 | 20.8677 | 19.6892 | 18.229 | 16.7524 | 15.152 | 13.344 | 11.2369 | 9.0592 | -1.0544 | -17.7755 | -26.3138 | -31.4567
|  | SP |  |  | 51.1402 | 50.0195 | 26.6133 | 25.6231 | 24.1699 | 22.7482 | 21.2898 | 19.5741 | 17.6853 | 15.4937 | 7.5356 | -12.4324 | -23.102 | -28.0665 | 44.2692 | 43.3229 | 20.0396 | 19.1629 | 18.12 | 17.0947 | 16.0126 | 14.7062 | 13.2414 | 11.6016 | 5.3694 | -11.1954 | -22.648 | -33.8438 | 45.6216 | 44.5987 | 21.2691 | 20.3516 | 19.0244 | 17.725 | 16.3826 | 14.7903 | 13.032 | 10.995 | 3.5054 | -15.5914 | -25.5288 | -29.9458
IVER 132KV | DENHAM | MINIMUM HEADROOM | TQ0173587553 | NO | 57.4166 | 34.2632 | 32.5643 | 30.6855 | 27.7002 | 24.4659 | 20.7681 | 16.5437 | 11.4552 | 6.953 | -3.2075 | -15.9521 | -20.6778 | -23.1637 | 51.6579 | 29.1988 | 28.1689 | 26.9687 | 25.3288 | 23.4435 | 21.2142 | 18.5798 | 15.1755 | 12.29 | 6.4355 | -0.33256 | -2.4104 | -3.5368 | 56.2719 | 33.2554 | 31.6959 | 29.9548 | 27.3104 | 24.4081 | 21.0291 | 17.0463 | 12.1689 | 7.8976 | -1.5226 | -13.0754 | -17.1736 | -19.2815
|  | CT |  |  | 57.9734 | 56.7556 | 55.2712 | 53.8037 | 51.8596 | 49.6932 | 47.1908 | 44.4011 | 41.2042 | 36.3353 | 25.9375 | 9.4931 | -1.2471 | -6.3818 | 51.6917 | 50.7231 | 49.5309 | 48.3449 | 47.0467 | 45.5654 | 43.7925 | 41.7815 | 39.4008 | 36.1331 | 29.6828 | 20.144 | 13.1863 | 6.8028 | 56.6525 | 55.4732 | 54.0295 | 52.6035 | 50.8153 | 48.802 | 46.4584 | 43.829 | 40.7661 | 36.2225 | 26.8405 | 12.0941 | 2.6932 | -1.7388
|  | LW |  |  | 57.4166 | 34.2632 | 32.5643 | 30.6855 | 27.7002 | 24.4659 | 20.7681 | 16.5437 | 11.4552 | 6.953 | -3.2075 | -15.9521 | -20.6778 | -23.1637 | 51.6579 | 29.1988 | 28.1689 | 26.9687 | 25.3288 | 23.4435 | 21.2142 | 18.5798 | 15.1755 | 12.29 | 6.4355 | -0.33256 | -2.4104 | -3.5368 | 56.2719 | 33.2554 | 31.6959 | 29.9548 | 27.3104 | 24.4081 | 21.0291 | 17.0463 | 12.1689 | 7.8976 | -1.5226 | -13.0754 | -17.1736 | -19.2815
|  | ST |  |  | 59.2386 | 58.7582 | 58.1171 | 57.3682 | 56.4925 | 55.4691 | 54.2391 | 52.8408 | 51.1658 | 49.4674 | 41.2124 | 28.9404 | 22.5607 | 18.3285 | 52.5568 | 52.1597 | 51.646 | 51.0144 | 50.304 | 49.4613 | 48.4552 | 47.2977 | 45.8775 | 44.5583 | 37.883 | 28.3422 | 22.5492 | 16.515 | 57.8894 | 57.4299 | 56.8104 | 56.084 | 55.2474 | 54.2545 | 53.0721 | 51.7196 | 50.0666 | 48.4379 | 40.3659 | 28.9972 | 23.5619 | 20.0958
|  | SP |  |  | 59.3127 | 58.9005 | 58.4488 | 57.9278 | 57.1365 | 56.2381 | 55.2221 | 53.9926 | 52.5829 | 50.97 | 44.8028 | 30.211 | 23.472 | 20.3306 | 52.5696 | 52.1956 | 51.7738 | 51.2872 | 50.6941 | 50.0001 | 49.2125 | 48.2222 | 47.0432 | 45.7415 | 40.622 | 28.0494 | 19.8445 | 10.8983 | 57.953 | 57.5554 | 57.1188 | 56.6133 | 55.8741 | 55.032 | 54.0899 | 52.9264 | 51.5598 | 50.0364 | 44.1451 | 30.2157 | 24.1796 | 21.5544
COWLEY GSP | DRAYTON BSP | MINIMUM HEADROOM | SU4653592295 | YES | 123.0719 | 114.197 | 104.5835 | 94.4549 | 86.4058 | 77.3712 | 67.9747 | 58.2991 | 47.3363 | 36.9245 | 13.7333 | -10.946 | -22.8229 | -31.5043 | 89.9512 | 81.8573 | 73.2713 | 64.4311 | 59.8136 | 54.6265 | 49.148 | 43.542 | 36.9479 | 30.6313 | 17.1364 | 3.0633 | -9.5033 | -20.0032 | 109.276 | 100.0165 | 90.0417 | 79.6144 | 72.651 | 64.6943 | 56.3678 | 47.7423 | 37.6722 | 28.0294 | 7.0197 | -14.9617 | -24.9839 | -32.641
|  | CT |  |  | 124.6488 | 116.6978 | 108.0864 | 98.6141 | 92.1593 | 84.8535 | 77.4428 | 69.7882 | 61.4271 | 51.2181 | 28.0786 | -3.1492 | -22.8229 | -31.5043 | 90.3585 | 82.5104 | 74.2205 | 65.5132 | 61.3706 | 56.7351 | 51.9926 | 47.121 | 41.7672 | 35.3851 | 21.0961 | 3.0633 | -9.5033 | -20.0032 | 110.2485 | 101.6357 | 92.4281 | 82.5059 | 76.9527 | 70.6806 | 64.2539 | 57.3716 | 49.7622 | 40.2971 | 19.1612 | -7.9318 | -24.9839 | -32.641
|  | LW |  |  | 123.0719 | 114.197 | 104.5835 | 94.4549 | 86.4058 | 77.3712 | 67.9747 | 58.2991 | 47.3363 | 36.9245 | 13.7333 | -10.946 | -19.5866 | -23.9257 | 89.9512 | 81.8573 | 73.2713 | 64.4311 | 59.8136 | 54.6265 | 49.148 | 43.542 | 36.9479 | 30.6313 | 17.1364 | 3.6475 | -0.69962 | -2.8465 | 109.276 | 100.0165 | 90.0417 | 79.6144 | 72.651 | 64.6943 | 56.3678 | 47.7423 | 37.6722 | 28.0294 | 7.0197 | -14.9617 | -22.427 | -26.272
|  | ST |  |  | 126.1975 | 119.498 | 112.4278 | 105.1673 | 101.2719 | 96.7627 | 92.1049 | 87.4326 | 82.4199 | 77.2878 | 61.7495 | 37.1901 | 25.0212 | 17.9993 | 90.8178 | 84.0441 | 76.8669 | 69.3405 | 66.4426 | 63.1853 | 59.8749 | 56.6002 | 53.0754 | 49.3298 | 37.3639 | 18.3094 | 7.5398 | -2.3436 | 111.9445 | 104.5988 | 96.8996 | 88.9934 | 85.4705 | 81.4776 | 77.3693 | 73.2101 | 68.703 | 64.0876 | 49.1493 | 25.6912 | 15.0848 | 9.242
|  | SP |  |  | 126.4632 | 119.8923 | 113.0546 | 106.1145 | 102.4986 | 97.4271 | 92.1354 | 86.8399 | 80.2711 | 75.7331 | 63.3197 | 39.0152 | 25.2601 | 19.4778 | 90.8311 | 84.0675 | 77.0539 | 69.6799 | 67.0323 | 63.0186 | 58.9014 | 54.8217 | 49.4959 | 46.2144 | 36.6258 | 16.308 | 0.51114 | -15.5555 | 112.1577 | 104.8787 | 97.377 | 89.7691 | 86.6864 | 82.172 | 77.4552 | 72.6941 | 66.6405 | 62.6376 | 51.1916 | 27.3854 | 14.4615 | 9.3449
EALING GSP | EALING | MINIMUM HEADROOM | TQ1844579506 | NO | 10.79 | 10.0348 | 8.9594 | 7.9271 | 6.4145 | 4.7712 | 3.1108 | 1.3401 | -0.41434 | -2.1814 | -7.7225 | -15.669 | -21.6419 | -25.7337 | 19.7309 | 19.493 | 19.1615 | 18.7177 | 17.9227 | 17.0094 | 16.0344 | 14.9758 | 13.9029 | 12.5866 | 8.3438 | 0.13653 | -9.4182 | -30.4854 | 14.2004 | 13.5597 | 12.6411 | 11.7361 | 10.4009 | 8.9477 | 7.462 | 5.8749 | 4.2666 | 2.6285 | -2.5246 | -9.7102 | -14.6578 | -18.0958
|  | CT |  |  | 10.9551 | 10.3144 | 9.3651 | 8.4219 | 7.2421 | 5.948 | 4.7197 | 3.3997 | 2.1667 | 0.40493 | -5.0011 | -14.6685 | -21.6419 | -25.7337 | 19.7309 | 19.493 | 19.1615 | 18.7177 | 17.9227 | 17.0094 | 16.0344 | 14.9758 | 13.9029 | 12.5866 | 8.3438 | 0.13653 | -8.6918 | -20.6786 | 14.3172 | 13.7659 | 12.9584 | 12.1359 | 11.1226 | 9.981 | 8.8838 | 7.7034 | 6.575 | 4.9539 | -0.029281 | -8.6695 | -14.6578 | -18.0958
|  | LW |  |  | 10.79 | 10.0348 | 8.9594 | 7.9271 | 6.4145 | 4.7712 | 3.1108 | 1.3401 | -0.41434 | -2.1814 | -7.7225 | -15.669 | -19.7439 | -22.326 | 19.797 | 19.6116 | 19.3413 | 19.006 | 18.3022 | 17.4802 | 16.5976 | 15.6018 | 14.5564 | 13.4831 | 10.0814 | 5.5653 | 3.6422 | 2.3555 | 14.2004 | 13.5597 | 12.6411 | 11.7361 | 10.4009 | 8.9477 | 7.462 | 5.8749 | 4.2666 | 2.6285 | -2.5246 | -9.7102 | -13.142 | -15.2593
|  | ST |  |  | 11.3974 | 11.0624 | 10.5387 | 10.0612 | 9.4844 | 8.8356 | 8.2043 | 7.5171 | 6.8901 | 6.2707 | 3.9385 | -2.6646 | -7.3546 | -10.3969 | 19.8294 | 19.6498 | 19.3911 | 19.1221 | 18.8118 | 18.4128 | 17.8074 | 17.147 | 16.4832 | 15.7683 | 13.0345 | 5.3912 | -2.9363 | -14.2759 | 14.7313 | 14.4598 | 14.0347 | 13.6351 | 13.1364 | 12.5688 | 12.0044 | 11.3882 | 10.8082 | 10.2375 | 8.0383 | 1.921 | -2.0938 | -4.5314
|  | SP |  |  | 11.4495 | 11.1168 | 10.631 | 10.187 | 9.7112 | 9.183 | 8.6539 | 8.0784 | 7.586 | 7.0978 | 5.4105 | 0.64049 | -3.6984 | -5.9427 | 19.8281 | 19.6416 | 19.373 | 19.0912 | 18.7768 | 18.3177 | 17.6682 | 16.954 | 16.2354 | 15.4773 | 12.3813 | 3.6902 | -9.4182 | -30.4854 | 14.7783 | 14.5048 | 14.1125 | 13.7411 | 13.3397 | 12.882 | 12.4121 | 11.8958 | 11.4418 | 10.9936 | 9.4119 | 4.909 | 0.9233 | -0.97183
EALING GSP | EALING (D) | MINIMUM HEADROOM | TQ1844579505 | NO | 58.5899 | 57.071 | 55.3831 | 53.7608 | 51.2158 | 48.4819 | 45.5999 | 42.5359 | 39.3485 | 36.0464 | 25.0607 | 8.1446 | -3.3977 | -13.137 | 61.0823 | 60.2787 | 59.0814 | 57.8177 | 56.2553 | 54.5509 | 52.7538 | 50.778 | 48.5802 | 45.9149 | 36.756 | 16.3182 | -22.7795 | -90.3561 | 47.4333 | 46.1863 | 44.7726 | 43.4011 | 41.3608 | 39.1611 | 36.6028 | 33.8338 | 30.8523 | 27.7472 | 17.5339 | 2.2942 | -6.7884 | -14.6626
|  | CT |  |  | 59.1482 | 57.9618 | 56.6242 | 55.2881 | 53.4695 | 51.4996 | 49.5929 | 47.5358 | 45.3462 | 42.1754 | 31.8363 | 11.8869 | -3.3977 | -13.137 | 61.1048 | 60.2787 | 59.0814 | 57.8177 | 56.2553 | 54.5509 | 52.7538 | 50.778 | 48.5802 | 45.9149 | 36.756 | 16.3182 | -8.6895 | -44.2441 | 47.7943 | 46.7805 | 45.6287 | 44.4435 | 42.9205 | 41.2625 | 39.6186 | 37.8387 | 35.9012 | 33.1832 | 23.7031 | 5.9099 | -6.7884 | -14.6626
|  | LW |  |  | 58.5899 | 57.071 | 55.3831 | 53.7608 | 51.2158 | 48.4819 | 45.5999 | 42.5359 | 39.3485 | 36.0464 | 25.0607 | 8.1446 | -1.2022 | -7.8225 | 61.0823 | 60.4469 | 59.7229 | 58.8165 | 57.5239 | 56.1312 | 54.6089 | 52.9786 | 51.1483 | 49.2301 | 42.8614 | 33.1825 | 28.6313 | 25.2752 | 47.4333 | 46.1863 | 44.7726 | 43.4011 | 41.3608 | 39.1611 | 36.6028 | 33.8338 | 30.8523 | 27.7472 | 17.5339 | 2.2942 | -5.5271 | -10.9408
|  | ST |  |  | 60.0467 | 59.4389 | 58.782 | 58.2023 | 57.4638 | 56.6352 | 55.7517 | 54.7754 | 53.7006 | 52.5331 | 47.9171 | 34.0653 | 23.7511 | 16.871 | 61.4574 | 60.9553 | 60.3209 | 59.4989 | 58.475 | 57.3417 | 56.0794 | 54.6673 | 53.0649 | 51.4205 | 45.0661 | 26.3155 | 2.5091 | -31.905 | 48.6027 | 48.0936 | 47.5343 | 47.025 | 46.3687 | 45.6292 | 44.8339 | 43.9508 | 42.9566 | 41.8927 | 37.6188 | 25.0026 | 16.2596 | 10.7621
|  | SP |  |  | 60.1791 | 59.5939 | 58.9857 | 58.4586 | 57.8678 | 57.2192 | 56.5168 | 55.743 | 54.9466 | 54.023 | 50.6892 | 40.1873 | 29.8794 | 23.8883 | 61.4644 | 60.9482 | 60.1826 | 59.2607 | 58.1107 | 56.8074 | 55.3263 | 53.6616 | 51.773 | 49.6064 | 41.3344 | 17.3835 | -22.7795 | -90.3561 | 48.7158 | 48.2135 | 47.6876 | 47.2159 | 46.6944 | 46.1212 | 45.4883 | 44.7862 | 44.0475 | 43.213 | 40.157 | 30.5005 | 21.2655 | 16.268
LALEHAM | EAST BEDFONT 11 | MINIMUM HEADROOM | TQ0840573836 | NO | 7.3024 | 6.8995 | 6.2153 | 5.4248 | 4.3845 | 3.2798 | 2.1061 | 0.83049 | -0.46071 | -1.726 | -5.3997 | -10.0732 | -13.8329 | -16.4551 | 5.5082 | 5.2696 | 4.9051 | 4.4763 | 3.9135 | 3.3131 | 2.666 | 1.9653 | 1.248 | 0.53461 | -1.5441 | -5.5398 | -9.4144 | -16.681 | 6.9728 | 6.6176 | 6.0591 | 5.4064 | 4.4919 | 3.5078 | 2.4581 | 1.3203 | 0.13861 | -1.047 | -4.4874 | -8.6787 | -11.879 | -14.1532
|  | CT |  |  | 7.4449 | 7.1355 | 6.6181 | 5.8821 | 5.0339 | 4.1366 | 3.1979 | 2.1613 | 1.2063 | -0.019258 | -3.705 | -9.5418 | -13.8329 | -16.4551 | 5.5414 | 5.3174 | 4.9995 | 4.5612 | 4.0391 | 3.4847 | 2.8964 | 2.2503 | 1.6353 | 0.87461 | -1.501 | -5.5398 | -9.4144 | -13.9346 | 7.1156 | 6.851 | 6.4358 | 5.8447 | 5.1021 | 4.3134 | 3.4649 | 2.527 | 1.6436 | 0.50219 | -2.9366 | -8.1384 | -11.879 | -14.1532
|  | LW |  |  | 7.3024 | 6.8995 | 6.2153 | 5.4248 | 4.3845 | 3.2798 | 2.1061 | 0.83049 | -0.46071 | -1.726 | -5.3997 | -10.0732 | -12.6822 | -14.4237 | 5.5082 | 5.2696 | 4.9051 | 4.4763 | 3.9135 | 3.3131 | 2.666 | 1.9653 | 1.248 | 0.53461 | -1.5441 | -4.1012 | -5.3676 | -6.2515 | 6.9728 | 6.6176 | 6.0591 | 5.4064 | 4.4919 | 3.5078 | 2.4581 | 1.3203 | 0.13861 | -1.047 | -4.4874 | -8.6787 | -10.8664 | -12.2928
|  | ST |  |  | 7.6511 | 7.4737 | 7.1764 | 6.8306 | 6.3842 | 5.9133 | 5.4149 | 4.8618 | 4.3747 | 3.9322 | 2.2397 | -2.3067 | -5.1242 | -7.0655 | 5.6498 | 5.4947 | 5.2867 | 5.0448 | 4.7447 | 4.4192 | 4.0513 | 3.6463 | 3.2715 | 2.9065 | 1.5159 | -2.2794 | -5.7344 | -9.9657 | 7.2958 | 7.148 | 6.9298 | 6.671 | 6.3296 | 5.9455 | 5.5228 | 5.0362 | 4.5889 | 4.1762 | 2.5686 | -1.647 | -4.0743 | -5.6706
|  | SP |  |  | 7.6798 | 7.4895 | 7.201 | 6.8707 | 6.5279 | 6.1712 | 5.7839 | 5.3479 | 4.9922 | 4.6489 | 3.4594 | -0.013146 | -2.9014 | -4.4 | 5.6579 | 5.4928 | 5.2809 | 5.0372 | 4.7744 | 4.4949 | 4.1675 | 3.802 | 3.4727 | 3.0887 | 1.6916 | -2.3311 | -8.1629 | -16.681 | 7.3222 | 7.1681 | 6.961 | 6.7194 | 6.4628 | 6.1818 | 5.8594 | 5.4939 | 5.1722 | 4.8539 | 3.7315 | 0.50976 | -2.0726 | -3.3045
LALEHAM | EAST BEDFONT A | MINIMUM HEADROOM | TQ0840573835 | NO | 4.6599 | 3.4478 | 1.6105 | -0.69148 | 13.2083 | 10.109 | 6.8381 | 3.2459 | -0.47992 | -4.0608 | -14.4192 | -29.1401 | -41.7776 | -51.1307 | -1.1535 | -1.8604 | -2.9026 | -4.2016 | 29.1604 | 27.4869 | 25.6874 | 23.6273 | 21.2917 | 19.044 | 12.2343 | -0.24245 | -12.7586 | -36.8148 | -2.7268 | -3.8351 | -5.5205 | -7.6238 | 15.576 | 12.7422 | 9.7167 | 6.3936 | 2.8561 | -0.5999 | -10.3944 | -23.4642 | -33.8495 | -41.6022
|  | CT |  |  | 5.107 | 4.1733 | 2.7077 | 0.61236 | 15.1009 | 12.6109 | 10.0308 | 7.1683 | 4.3681 | 0.86806 | -9.5669 | -27.4905 | -41.7776 | -51.1307 | -1.0792 | -1.7645 | -2.7487 | -4.0859 | 29.3709 | 27.7917 | 26.1158 | 24.0582 | 21.9468 | 19.5186 | 12.2343 | -0.24245 | -12.7586 | -27.4384 | -2.361 | -3.2293 | -4.5619 | -6.5094 | 17.1949 | 14.8862 | 12.4729 | 9.8026 | 7.1273 | 3.7798 | -5.9804 | -21.8202 | -33.8495 | -41.6022
|  | LW |  |  | 4.6599 | 3.4478 | 1.6105 | -0.69148 | 13.2083 | 10.109 | 6.8381 | 3.2459 | -0.47992 | -4.0608 | -14.4192 | -29.1401 | -38.3475 | -45.0384 | -1.1535 | -1.8604 | -2.9026 | -4.2016 | 29.1604 | 27.4869 | 25.6874 | 23.6273 | 21.2917 | 19.044 | 12.6999 | 4.6982 | 0.17243 | -3.2366 | -2.7268 | -3.8351 | -5.5205 | -7.6238 | 15.576 | 12.7422 | 9.7167 | 6.3936 | 2.8561 | -0.5999 | -10.3944 | -23.4642 | -31.136 | -36.5976
|  | ST |  |  | 5.6564 | 5.081 | 4.1588 | 2.9784 | 18.5505 | 17.1386 | 15.6479 | 13.9848 | 12.3807 | 10.9416 | 5.606 | -7.1517 | -16.3413 | -23.0186 | -0.78958 | -1.2919 | -2.0089 | -2.9015 | 31.0338 | 29.9358 | 28.7511 | 27.4519 | 26.1564 | 24.9347 | 19.9785 | 8.5936 | -2.4391 | -16.0525 | -1.8166 | -2.3338 | -3.1442 | -4.1842 | 20.5131 | 19.2015 | 17.8018 | 16.2458 | 14.7122 | 13.3369 | 8.1013 | -3.6199 | -11.4264 | -16.8672
|  | SP |  |  | 5.7538 | 5.1864 | 4.3021 | 3.1971 | 18.9787 | 17.7871 | 16.5113 | 15.0999 | 13.7943 | 12.6243 | 8.6582 | -1.337 | -10.2375 | -15.7625 | -0.75992 | -1.2724 | -1.9992 | -2.8873 | 31.1013 | 30.0485 | 28.8945 | 27.6338 | 26.3897 | 25.1045 | 20.1657 | 7.6311 | -9.9622 | -36.8148 | -1.7241 | -2.2463 | -3.0287 | -4.0026 | 20.9161 | 19.8335 | 18.6531 | 17.3493 | 16.1173 | 15.0046 | 11.1596 | 1.8123 | -5.8614 | -10.2655
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | MINIMUM HEADROOM | SU5644404017 | NO | 75.0982 | 21.2289 | 17.7183 | -1.419 | -6.6079 | -12.4045 | -18.6992 | -25.3687 | -33.2559 | -41.555 | -63.7919 | -91.5348 | -111.4292 | -125.2469 | 54.2189 | 2.2855 | 1.1249 | -15.487 | -17.0437 | -18.9915 | -21.1667 | -23.4894 | -26.4703 | -31.8986 | -45.9046 | -64.139 | -80.7681 | -96.4329 | 23.4199 | -30.1652 | -33.3364 | -52.1233 | -57.0492 | -62.5519 | -68.5 | -74.7971 | -82.1368 | -89.859 | -110.3135 | -135.2802 | -152.325 | -164.2244
|  | CT |  |  | 75.867 | 22.5414 | 19.8322 | 1.041 | -2.8968 | -7.3528 | -12.078 | -17.1232 | -22.8074 | -30.941 | -53.1512 | -86.9423 | -111.4292 | -125.2469 | 54.2189 | 2.3232 | 1.2276 | -15.4008 | -16.8252 | -18.5785 | -20.4826 | -22.5129 | -24.7608 | -27.983 | -43.2708 | -64.139 | -80.7681 | -96.4329 | 24.2695 | -28.7461 | -31.1358 | -49.5176 | -53.1509 | -57.2749 | -61.6388 | -66.2996 | -71.6402 | -79.2831 | -100.1242 | -130.8845 | -152.325 | -164.2244
|  | LW |  |  | 75.0982 | 21.2289 | 17.7183 | -1.419 | -6.6079 | -12.4045 | -18.6992 | -25.3687 | -33.2559 | -41.555 | -63.7919 | -91.5348 | -105.7854 | -114.872 | 54.2199 | 2.2855 | 1.1249 | -15.487 | -17.0437 | -18.9915 | -21.1667 | -23.4894 | -26.4703 | -31.8986 | -45.9046 | -61.9875 | -69.7415 | -74.7268 | 23.4199 | -30.1652 | -33.3364 | -52.1233 | -57.0492 | -62.5519 | -68.5 | -74.7971 | -82.1368 | -89.859 | -110.3135 | -135.2802 | -147.7211 | -155.4818
|  | ST |  |  | 77.3699 | 76.0234 | 74.502 | 21.9047 | 19.8369 | 17.3516 | 14.6389 | 11.773 | 8.5782 | 4.3453 | -11.9795 | -40.8661 | -56.0066 | -65.8131 | 54.6688 | 53.9882 | 53.2328 | 1.4696 | 0.49067 | -0.80114 | -2.2318 | -3.7538 | -5.4491 | -8.1909 | -17.6914 | -38.1504 | -52.7538 | -66.739 | 25.651 | 24.5447 | 23.2747 | -29.0626 | -30.8679 | -33.1041 | -35.6359 | -38.3268 | -41.3453 | -45.3511 | -60.9711 | -88.1637 | -101.7562 | -110.2905
|  | SP |  |  | 77.5625 | 76.2149 | 74.7931 | 73.2903 | 71.6308 | 67.2199 | 62.6339 | 57.8745 | 50.3194 | 47.1345 | 35.7974 | 10.2222 | -5.5988 | -13.0353 | 54.6972 | 54.0202 | 53.2805 | 52.4677 | 51.5936 | 48.0113 | 44.3174 | 40.5355 | 34.0331 | 32.029 | 25.3298 | 6.143 | -15.4871 | -39.8679 | 25.8401 | 24.753 | 23.5883 | 22.3398 | 20.8944 | 16.6705 | 12.2535 | 7.6504 | 0.25248 | -2.7358 | -13.4625 | -37.9676 | -52.6164 | -59.0981
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | MINIMUM HEADROOM | SU5644404017 | NO | 37.1052 | 36.0314 | 34.6781 | 32.9796 | 30.1039 | 27.0561 | 23.9783 | 20.6913 | 16.7272 | 12.5652 | 1.4222 | -12.8666 | -24.5261 | -32.6129 | 32.9096 | 32.3133 | 31.4533 | 30.38 | 28.8111 | 27.1286 | 25.3873 | 23.533 | 21.1872 | 18.6376 | 11.8062 | 1.7008 | -7.9495 | -18.2762 | 37.9712 | 36.9602 | 35.6151 | 33.9524 | 31.3258 | 28.5207 | 25.6406 | 22.5865 | 18.8252 | 14.8415 | 4.3531 | -8.4491 | -17.5634 | -24.1267
|  | CT |  |  | 37.7105 | 37.01 | 36.1447 | 34.7375 | 32.6968 | 30.4278 | 28.2361 | 25.919 | 23.1372 | 19.0474 | 7.7074 | -10.6719 | -24.5261 | -32.6129 | 33.0436 | 32.4998 | 31.8127 | 30.7135 | 29.3626 | 27.9057 | 26.4497 | 24.892 | 22.9907 | 20.3684 | 12.8459 | 1.7008 | -7.9495 | -18.2762 | 38.4127 | 37.7032 | 36.8187 | 35.3447 | 33.3919 | 31.2863 | 29.2125 | 27.006 | 24.3268 | 20.4543 | 9.8165 | -6.1821 | -17.5634 | -24.1267
|  | LW |  |  | 37.1052 | 36.0314 | 34.6781 | 32.9796 | 30.1039 | 27.0561 | 23.9783 | 20.6913 | 16.7272 | 12.5652 | 1.4222 | -12.8666 | -20.5133 | -25.6643 | 32.9096 | 32.3133 | 31.4533 | 30.38 | 28.8111 | 27.1286 | 25.3873 | 23.533 | 21.1872 | 18.6376 | 11.8062 | 3.9679 | 0.44894 | -2.0346 | 37.9712 | 36.9602 | 35.6151 | 33.9524 | 31.3258 | 28.5207 | 25.6406 | 22.5865 | 18.8252 | 14.8415 | 4.3531 | -8.4491 | -14.7299 | -18.9145
|  | ST |  |  | 38.3568 | 38.0666 | 37.6687 | 37.0819 | 36.1716 | 35.1833 | 34.2411 | 33.1824 | 31.8597 | 30.4323 | 25.0778 | 11.7265 | 3.3047 | -2.4341 | 33.4403 | 33.1784 | 32.8187 | 32.305 | 31.5491 | 30.7298 | 29.9092 | 29.0213 | 27.9418 | 26.8186 | 22.3985 | 11.3649 | 2.9884 | -6.2257 | 39.0879 | 38.8019 | 38.4022 | 37.8327 | 36.9286 | 35.9435 | 34.9682 | 33.9176 | 32.63 | 31.2783 | 25.9508 | 13.4335 | 6.0988 | 1.3184
|  | SP |  |  | 38.4661 | 38.1816 | 37.8139 | 37.2919 | 36.608 | 35.8849 | 35.2113 | 34.4812 | 33.5391 | 32.422 | 28.6403 | 17.9237 | 9.5968 | 5.2204 | 33.4776 | 33.1901 | 32.8015 | 32.2894 | 31.6681 | 30.9994 | 30.325 | 29.5782 | 28.6904 | 27.6055 | 23.6609 | 12.4753 | -0.50436 | -17.5747 | 39.1856 | 38.8764 | 38.4866 | 37.9683 | 37.3144 | 36.6199 | 35.9367 | 35.1803 | 34.2775 | 33.2228 | 29.503 | 19.2322 | 11.7343 | 8.077
BRAMLEY (FLEE) | FERNHURST | MINIMUM HEADROOM | SU7268539765 | YES | 36.8394 | 32.6076 | 27.8108 | 22.7456 | 15.8832 | 8.8321 | 1.9354 | -5.6044 | -14.335 | -22.2647 | -40.6102 | -60.5276 | -66.3249 | -69.766 | 43.4529 | 41.2901 | 38.7511 | 36.0255 | 32.4958 | 28.8224 | 25.089 | 20.8952 | 15.6818 | 10.9089 | 0.83751 | -9.3759 | -15.0315 | -23.5028 | 60.7521 | 57.301 | 53.3535 | 49.1632 | 43.5731 | 37.8075 | 32.063 | 25.6931 | 18.1622 | 11.075 | -4.6808 | -22.7198 | -27.5754 | -30.4033
|  | CT |  |  | 39.9246 | 37.4241 | 34.3355 | 30.8436 | 26.3635 | 21.6971 | 17.21 | 12.1536 | 6.7077 | -0.97071 | -17.8567 | -42.373 | -58.0313 | -65.1911 | 44.4885 | 42.9255 | 40.9542 | 38.6904 | 36.0539 | 33.2694 | 30.4412 | 27.0629 | 23.3176 | 18.3255 | 8.0261 | -5.6055 | -15.0315 | -23.265 | 62.9997 | 60.8599 | 58.2061 | 55.1179 | 51.3201 | 47.339 | 43.4119 | 38.8974 | 33.9595 | 27.102 | 13.0112 | -6.7888 | -20.3682 | -26.2323
|  | LW |  |  | 36.8394 | 32.6076 | 27.8108 | 22.7456 | 15.8832 | 8.8321 | 1.9354 | -5.6044 | -14.335 | -22.2647 | -40.6102 | -60.5276 | -66.3249 | -69.766 | 43.4529 | 41.2901 | 38.7511 | 36.0255 | 32.4958 | 28.8224 | 25.089 | 20.8952 | 15.6818 | 10.9089 | 0.83751 | -9.3759 | -11.767 | -13.1051 | 60.7521 | 57.301 | 53.3535 | 49.1632 | 43.5731 | 37.8075 | 32.063 | 25.6931 | 18.1622 | 11.075 | -4.6808 | -22.7198 | -27.5754 | -30.4033
|  | ST |  |  | 41.7021 | 40.3148 | 38.5236 | 36.5295 | 33.8985 | 31.1588 | 28.5513 | 25.665 | 22.4561 | 19.0404 | 4.5925 | -15.9597 | -26.0377 | -32.0152 | 45.6222 | 44.7491 | 43.5744 | 42.2367 | 40.5814 | 38.831 | 37.1014 | 35.161 | 32.9522 | 30.7049 | 20.5104 | 5.8796 | -2.1218 | -9.7607 | 64.6237 | 63.4863 | 61.9899 | 60.2996 | 58.0928 | 55.7867 | 53.5603 | 51.0791 | 48.2145 | 45.2515 | 31.993 | 13.9441 | 6.0048 | 1.3401
|  | SP |  |  | 42.1487 | 40.9653 | 39.521 | 37.9927 | 35.0415 | 32.0767 | 29.2585 | 26.1577 | 22.9211 | 18.8393 | 4.7771 | -25.2375 | -41.4036 | -49.7992 | 45.7862 | 44.9716 | 43.9355 | 42.813 | 41.1111 | 39.3612 | 37.6636 | 35.7338 | 33.6622 | 31.1687 | 22.1784 | 1.8583 | -11.1465 | -23.5028 | 64.9621 | 63.9649 | 62.7519 | 61.4572 | 59.0745 | 56.6767 | 54.3865 | 51.8225 | 49.1362 | 45.7883 | 33.9798 | 7.8136 | -5.9026 | -13.142
LOVEDEAN GSP | FORT WIDLEY | MINIMUM HEADROOM | SU6497405375 | NO | 35.0384 | 33.669 | 32.1217 | 30.4642 | 27.9751 | 25.1322 | 22.0632 | 18.6659 | 14.724 | 10.8641 | 2.0999 | -8.0929 | -15.6924 | -21.2864 | 37.9564 | 37.096 | 36.1194 | 35.0922 | 33.717 | 32.0995 | 30.283 | 28.2801 | 25.7992 | 23.3982 | 18.4196 | 12.7446 | 7.3198 | 1.2945 | 34.4566 | 33.2628 | 31.9419 | 30.4868 | 28.2609 | 25.7203 | 22.9645 | 19.9366 | 16.4212 | 12.9873 | 5.0859 | -4.169 | -11.0805 | -15.8823
|  | CT |  |  | 35.4521 | 34.3622 | 33.1846 | 31.7161 | 29.8172 | 27.6055 | 25.2358 | 22.5826 | 19.6107 | 15.7487 | 6.496 | -6.1997 | -15.6924 | -21.2864 | 38.0283 | 37.2424 | 36.4118 | 35.3762 | 34.1935 | 32.8011 | 31.2581 | 29.5572 | 27.5711 | 25.13 | 19.5882 | 12.7446 | 7.3198 | 2.7654 | 34.8845 | 33.9623 | 32.9422 | 31.6719 | 30.0005 | 28.0524 | 25.9499 | 23.6149 | 20.9881 | 17.5569 | 9.1687 | -2.3916 | -11.0805 | -15.8823
|  | LW |  |  | 35.0384 | 33.669 | 32.1217 | 30.4642 | 27.9751 | 25.1322 | 22.0632 | 18.6659 | 14.724 | 10.8641 | 2.0999 | -8.0929 | -13.5822 | -17.1844 | 37.9564 | 37.096 | 36.1194 | 35.0922 | 33.717 | 32.0995 | 30.283 | 28.2801 | 25.7992 | 23.3982 | 18.4196 | 12.9458 | 10.076 | 8.1867 | 34.4566 | 33.2628 | 31.9419 | 30.4868 | 28.2609 | 25.7203 | 22.9645 | 19.9366 | 16.4212 | 12.9873 | 5.0859 | -4.169 | -9.0733 | -12.2038
|  | ST |  |  | 36.0518 | 35.3488 | 34.6364 | 33.8818 | 32.8357 | 31.549 | 30.1437 | 28.5641 | 26.8398 | 24.9221 | 18.0661 | 7.5323 | 1.6788 | -2.3627 | 38.4477 | 37.9175 | 37.3869 | 36.8344 | 36.0952 | 35.1724 | 34.1382 | 32.9955 | 31.7133 | 30.2583 | 24.8685 | 16.7742 | 12.2015 | 8.0833 | 35.3764 | 34.7789 | 34.1977 | 33.6061 | 32.7321 | 31.6372 | 30.4209 | 29.0731 | 27.5828 | 25.8835 | 19.7145 | 9.8983 | 4.7334 | 1.2934
|  | SP |  |  | 36.1313 | 35.4336 | 34.7726 | 34.1113 | 33.2138 | 31.2366 | 29.0998 | 26.8006 | 23.4159 | 21.8581 | 16.838 | 6.4654 | 0.65052 | -2.3929 | 38.476 | 37.9277 | 37.4104 | 36.9012 | 36.291 | 34.6243 | 32.8122 | 30.8888 | 27.8752 | 26.6865 | 22.6829 | 13.9064 | 7.6227 | 1.2945 | 35.4515 | 34.8681 | 34.3361 | 33.8263 | 33.0758 | 31.2623 | 29.2924 | 27.2038 | 24.0245 | 22.6735 | 18.2859 | 8.6544 | 3.3778 | 0.7875
MELKSHAM GSP | FROME BSP | MINIMUM HEADROOM | ST7885048051 | NO | 26.784 | 22.9332 | 18.5987 | 14.1271 | 8.1999 | 1.8336 | -4.6004 | -11.4308 | -19.2732 | -27.4061 | -48.5083 | -73.7677 | -83.8626 | -92.7616 | 21.8044 | 20.8764 | 19.8058 | 18.6243 | 15.648 | 12.0508 | 8.2896 | 4.2167 | -5.6362 | -8.7389 | -19.1693 | -42.3168 | -58.6839 | -73.2397 | 18.3313 | 14.9178 | 11.0796 | 7.0805 | 1.743 | -4.0447 | -9.943 | -16.2278 | -23.5226 | -31.1023 | -50.4881 | -73.5431 | -82.8706 | -90.5757
|  | CT |  |  | 29.5568 | 27.1524 | 24.4702 | 21.1399 | 17.1114 | 12.7329 | 8.3569 | 3.6411 | -1.5362 | -9.0725 | -29.1165 | -60.868 | -83.0463 | -92.7616 | 21.8044 | 20.8764 | 19.8058 | 18.6243 | 17.483 | 15.5189 | 12.5597 | 9.3174 | 5.6431 | 0.68075 | -11.785 | -29.26 | -42.3461 | -51.8691 | 20.8587 | 18.6986 | 16.2734 | 13.236 | 9.578 | 5.5594 | 1.5089 | -2.8733 | -7.7289 | -14.7393 | -33.2051 | -61.9172 | -81.8315 | -90.5757
|  | LW |  |  | 26.784 | 22.9332 | 18.5987 | 14.1271 | 8.1999 | 1.8336 | -4.6004 | -11.4308 | -19.2732 | -27.4061 | -48.5083 | -73.7677 | -83.8626 | -89.7692 | 21.8844 | 20.957 | 19.8527 | 18.715 | 15.648 | 12.0508 | 8.2896 | 4.2167 | -0.72323 | -5.8539 | -17.9535 | -31.9015 | -38.0441 | -41.4613 | 18.3313 | 14.9178 | 11.0796 | 7.0805 | 1.743 | -4.0447 | -9.943 | -16.2278 | -23.5226 | -31.1023 | -50.4881 | -73.5431 | -82.8706 | -88.2907
|  | ST |  |  | 30.5473 | 28.9291 | 27.1497 | 25.2073 | 22.7327 | 19.9339 | 17.1504 | 14.205 | 11.0906 | 6.4974 | -9.8551 | -37.0132 | -50.623 | -59.0291 | 22.1381 | 21.4155 | 20.5876 | 19.7619 | 18.8982 | 17.7462 | 16.5947 | 15.3643 | 13.7697 | 10.052 | -3.4658 | -24.7276 | -36.044 | -45.0996 | 21.7611 | 20.3747 | 18.8332 | 17.1294 | 14.9083 | 12.3534 | 9.7819 | 7.0497 | 4.1261 | -0.26031 | -15.9342 | -41.2846 | -54.2873 | -61.8843
|  | SP |  |  | 30.9694 | 29.4322 | 27.8149 | 26.0979 | 22.9567 | 15.6684 | 8.4637 | 1.076 | -10.5671 | -15.1873 | -29.8356 | -60.2067 | -77.2772 | -85.4676 | 22.1509 | 21.4256 | 20.6073 | 19.8022 | 19.0235 | 14.1482 | 9.3035 | 4.3792 | -5.6362 | -8.7389 | -19.1693 | -42.3168 | -58.6839 | -73.2397 | 22.1468 | 20.8418 | 19.4123 | 17.9123 | 15.1383 | 8.2112 | 1.3343 | -5.7264 | -17.0594 | -21.3299 | -34.9379 | -63.4149 | -79.3676 | -86.798
MINETY GSP | GALILEO | MINIMUM HEADROOM | SU 10596 83733 | YES | 34.715 | 34.5796 | 34.3791 | 34.1587 | 33.813 | 33.447 | 33.0567 | 32.6412 | 32.122 | 31.5804 | 30.3196 | 28.4149 | 26.6342 | 25.282 | 28.3918 | 28.3274 | 28.223 | 28.1067 | 27.9342 | 27.7504 | 27.5513 | 27.3377 | 27.0702 | 26.7839 | 26.0972 | 24.8476 | 23.4838 | 21.9957 | 28.9111 | 28.8201 | 28.6333 | 28.4271 | 28.1089 | 27.7712 | 27.4085 | 27.021 | 26.5296 | 26.0165 | 24.8507 | 23.1659 | 21.7161 | 20.5858
|  | CT |  |  | 34.7735 | 34.682 | 34.5363 | 34.3446 | 34.0967 | 33.8372 | 33.5694 | 33.278 | 32.9283 | 32.3908 | 31.0495 | 28.6661 | 26.6342 | 25.282 | 28.4091 | 28.358 | 28.2704 | 28.1585 | 28.0204 | 27.8754 | 27.7232 | 27.5568 | 27.3602 | 27.0651 | 26.293 | 24.8476 | 23.4838 | 22.1095 | 28.9477 | 28.8954 | 28.7731 | 28.5912 | 28.3603 | 28.1184 | 27.867 | 27.5925 | 27.26 | 26.7525 | 25.5116 | 23.4109 | 21.7161 | 20.5858
|  | LW |  |  | 34.715 | 34.5796 | 34.3791 | 34.1587 | 33.813 | 33.447 | 33.0567 | 32.6412 | 32.122 | 31.5804 | 30.3196 | 28.4149 | 27.1362 | 26.2014 | 28.3918 | 28.3274 | 28.223 | 28.1067 | 27.9342 | 27.7504 | 27.5513 | 27.3377 | 27.0702 | 26.7839 | 26.0972 | 25.1008 | 24.4882 | 24.0326 | 28.9111 | 28.8201 | 28.6333 | 28.4271 | 28.1089 | 27.7712 | 27.4085 | 27.021 | 26.5296 | 26.0165 | 24.8507 | 23.1659 | 22.096 | 21.3291
|  | ST |  |  | 34.8829 | 34.8524 | 34.7814 | 34.7015 | 34.5935 | 34.4742 | 34.3466 | 34.2034 | 34.0395 | 33.8694 | 33.067 | 31.245 | 30.0048 | 29.0411 | 28.4699 | 28.4503 | 28.4034 | 28.3505 | 28.2822 | 28.207 | 28.1252 | 28.033 | 27.9273 | 27.8081 | 27.2783 | 25.9959 | 24.8891 | 23.6528 | 29.0459 | 29.0448 | 28.9941 | 28.9331 | 28.8319 | 28.7194 | 28.5981 | 28.4611 | 28.303 | 28.1444 | 27.3725 | 25.7043 | 24.6572 | 23.8791
|  | SP |  |  | 34.8983 | 34.8708 | 34.8077 | 34.7425 | 34.6517 | 34.5597 | 34.461 | 34.3475 | 34.2235 | 34.0794 | 33.503 | 31.7496 | 30.5577 | 29.8079 | 28.4774 | 28.4593 | 28.4141 | 28.3662 | 28.307 | 28.2456 | 28.1786 | 28.1017 | 28.0169 | 27.8968 | 27.4255 | 26.0108 | 24.3243 | 21.9957 | 29.0614 | 29.0713 | 29.0254 | 28.9662 | 28.884 | 28.801 | 28.7119 | 28.6057 | 28.4892 | 28.3563 | 27.8128 | 26.1594 | 25.1294 | 24.5169
WILLESDEN GSP | GREENFORD | MINIMUM HEADROOM | TQ 14695 83785 | NO | 25.2031 | 24.4563 | 23.4965 | 22.4306 | 20.8871 | 19.2363 | 17.4772 | 15.4955 | 13.1792 | 10.9018 | 4.3535 | -3.1293 | -9.8422 | -13.5966 | 33.1221 | 32.7143 | 32.2567 | 31.5644 | 30.7101 | 29.7911 | 28.7927 | 27.6661 | 26.3386 | 24.802 | 19.7485 | 11.9302 | 2.3769 | -20.8594 | 28.3791 | 27.7566 | 26.9469 | 26.0409 | 24.6838 | 23.2317 | 21.682 | 19.9416 | 17.8528 | 15.7503 | 9.6672 | 2.8829 | -2.8742 | -6.0716
|  | CT |  |  | 25.3483 | 24.7067 | 23.9775 | 22.9613 | 21.7475 | 20.449 | 19.0589 | 17.4772 | 15.711 | 13.4568 | 6.6429 | -3.0869 | -9.8422 | -13.5966 | 33.1221 | 32.7143 | 32.2567 | 31.5644 | 30.7101 | 29.7911 | 28.7927 | 27.6661 | 26.3836 | 24.802 | 19.7485 | 11.9302 | 3.619 | -7.5456 | 28.5182 | 27.9948 | 27.3919 | 26.537 | 25.4906 | 24.3693 | 23.1541 | 21.7366 | 20.1418 | 18.0781 | 11.7788 | 3.0503 | -2.8742 | -6.0716
|  | LW |  |  | 25.2031 | 24.4563 | 23.4965 | 22.4306 | 20.8871 | 19.2363 | 17.4772 | 15.4955 | 13.1792 | 10.9018 | 4.3535 | -3.1293 | -6.6764 | -8.5615 | 33.1328 | 32.7561 | 32.2782 | 31.6712 | 30.8093 | 29.8781 | 28.8599 | 27.7102 | 26.3386 | 24.9404 | 20.8921 | 16.732 | 15.1026 | 14.1774 | 28.3791 | 27.7566 | 26.9469 | 26.0409 | 24.6838 | 23.2317 | 21.682 | 19.9416 | 17.8528 | 15.7503 | 9.6672 | 2.8829 | -0.14837 | -1.7118
|  | ST |  |  | 25.7391 | 25.3846 | 24.9968 | 24.5733 | 23.9933 | 23.3687 | 22.7051 | 21.9044 | 21.0077 | 20.2294 | 17.4927 | 10.4179 | 6.3719 | 3.5847 | 33.2785 | 33.0501 | 32.7589 | 32.4389 | 32.0135 | 31.5448 | 30.9411 | 30.2284 | 29.4233 | 28.6477 | 25.7581 | 18.0373 | 10.435 | -0.21987 | 28.8698 | 28.6068 | 28.315 | 27.9914 | 27.5281 | 27.0265 | 26.4885 | 25.839 | 25.0782 | 24.3797 | 21.8135 | 15.1495 | 11.6354 | 9.2839
|  | SP |  |  | 25.7795 | 25.4063 | 25.0168 | 24.5943 | 24.1526 | 23.6793 | 23.1635 | 22.5448 | 21.8698 | 21.2611 | 19.3013 | 14.3741 | 10.5725 | 9.0017 | 33.277 | 33.034 | 32.719 | 32.3735 | 31.98 | 31.5463 | 31.0104 | 30.353 | 29.612 | 28.7002 | 25.3755 | 16.3457 | 2.3769 | -20.8594 | 28.9068 | 28.6295 | 28.338 | 28.0176 | 27.6764 | 27.3092 | 26.9031 | 26.417 | 25.8826 | 25.3432 | 23.5147 | 18.7963 | 15.2619 | 13.9467
LOVEDEAN GSP | HAVANT | MINIMUM HEADROOM | SU7055105721 | NO | 24.2168 | 21.5409 | 17.9128 | 14.0135 | 8.4218 | 2.2035 | -4.4872 | -11.6471 | -20.4078 | -29.4345 | -51.6049 | -77.7122 | -98.5227 | -112.1999 | 30.8058 | 29.1604 | 26.8837 | 24.4142 | 21.1847 | 17.5143 | 13.47 | 9.0626 | 3.3685 | -2.5258 | -16.1955 | -33.9505 | -49.3055 | -63.8981 | 33.7994 | 31.5573 | 28.6082 | 25.4211 | 20.4665 | 14.8781 | 8.8708 | 2.4256 | -5.4522 | -13.5986 | -33.8744 | -57.6863 | -76.3744 | -88.0234
|  | CT |  |  | 24.96 | 22.8475 | 20.0852 | 16.5263 | 12.3786 | 7.6891 | 2.719 | -2.6517 | -8.8664 | -18.0738 | -41.4135 | -74.8189 | -98.5227 | -112.1999 | 30.887 | 29.3622 | 27.4368 | 24.8814 | 22.1202 | 18.9681 | 15.591 | 11.8757 | 7.4496 | 1.2722 | -13.9266 | -33.9505 | -49.3055 | -63.8981 | 34.5832 | 32.891 | 30.7071 | 27.8643 | 24.1988 | 20.0435 | 15.6379 | 10.8577 | 5.3109 | -2.9857 | -24.2403 | -55.0208 | -76.3744 | -88.0234
|  | LW |  |  | 24.2168 | 21.5409 | 17.9128 | 14.0135 | 8.4218 | 2.2035 | -4.4872 | -11.6471 | -20.4078 | -29.4345 | -51.6049 | -77.7122 | -90.3432 | -98.0959 | 30.8058 | 29.1604 | 26.8837 | 24.4142 | 21.1847 | 17.5143 | 13.47 | 9.0626 | 3.3685 | -2.5258 | -16.1955 | -30.7771 | -36.7756 | -40.6543 | 33.7994 | 31.5573 | 28.6082 | 25.4211 | 20.4665 | 14.8781 | 8.8708 | 2.4256 | -5.4522 | -13.5986 | -33.8744 | -57.6863 | -68.8257 | -75.4169
|  | ST |  |  | 26.5594 | 25.5008 | 24.0667 | 22.5126 | 20.4677 | 18.0301 | 15.4311 | 12.6352 | 9.3847 | 5.9864 | -8.0027 | -34.8696 | -49.5822 | -59.6517 | 32.0066 | 31.1916 | 30.1322 | 28.9569 | 27.388 | 25.5084 | 23.484 | 21.2686 | 18.6436 | 15.971 | 4.7204 | -16.6058 | -29.7344 | -43.1632 | 35.9092 | 35.1054 | 34.0566 | 32.9079 | 31.315 | 29.3864 | 27.2123 | 24.7872 | 21.932 | 18.8962 | 6.432 | -18.3487 | -31.2575 | -39.751
|  | SP |  |  | 26.729 | 25.6453 | 24.3071 | 22.9297 | 21.3609 | 19.502 | 17.5148 | 15.3257 | 12.8634 | 10.0636 | 0.017454 | -24.2047 | -38.5474 | -45.5176 | 32.064 | 31.18 | 30.1275 | 29.0146 | 27.7814 | 26.2943 | 24.6862 | 22.8662 | 20.7634 | 18.3012 | 9.1787 | -13.5644 | -33.4302 | -56.9656 | 36.0698 | 35.2728 | 34.3217 | 33.3343 | 32.1159 | 30.6497 | 29.0863 | 27.2131 | 25.0673 | 22.59 | 13.7032 | -8.4074 | -21.472 | -27.3723
NORTH HYDE GSP | HAYES | MINIMUM HEADROOM | TQ0953579555 | NO | 23.6228 | 22.972 | 22.0785 | 21.2961 | 20.0085 | 18.6246 | 17.1343 | 15.5712 | 13.6891 | 11.6653 | 5.3233 | -2.4885 | -8.5938 | -12.2796 | 30.3484 | 29.8096 | 29.392 | 29.0274 | 28.4636 | 27.8548 | 27.201 | 26.5116 | 25.6691 | 24.7509 | 20.6653 | 12.9694 | 4.4549 | -15.5961 | 25.8057 | 24.7978 | 23.9601 | 23.1836 | 21.9898 | 20.7017 | 19.3058 | 17.8383 | 16.0506 | 14.1091 | 8.0836 | 1.0268 | -3.7909 | -6.8091
|  | CT |  |  | 23.6228 | 23.0291 | 22.6721 | 22.2266 | 21.3079 | 20.2795 | 19.1908 | 18.0527 | 16.7812 | 14.8191 | 8.4754 | -1.6249 | -8.5938 | -12.2796 | 30.4201 | 29.9109 | 29.5471 | 29.1859 | 28.701 | 28.1731 | 27.6072 | 27.0051 | 26.3257 | 25.1891 | 20.6653 | 12.9694 | 5.2337 | -4.5785 | 25.9963 | 25.1149 | 24.5602 | 23.8826 | 23.0405 | 22.0848 | 21.0466 | 19.9535 | 18.7169 | 16.886 | 10.9611 | 1.977 | -3.7909 | -6.8091
|  | LW |  |  | 23.6459 | 22.972 | 22.0785 | 21.2961 | 20.0085 | 18.6246 | 17.1343 | 15.5712 | 13.6891 | 11.6653 | 5.3233 | -2.4885 | -5.9826 | -7.9084 | 30.3484 | 29.8096 | 29.392 | 29.0274 | 28.4636 | 27.8548 | 27.201 | 26.5116 | 25.6691 | 24.7509 | 21.0823 | 16.7753 | 15.1459 | 14.1871 | 25.8057 | 24.7978 | 23.9601 | 23.1836 | 21.9898 | 20.7017 | 19.3058 | 17.8383 | 16.0506 | 14.1091 | 8.0836 | 1.0268 | -1.8739 | -3.4557
|  | ST |  |  | 23.8189 | 23.3406 | 23.101 | 22.9451 | 22.7332 | 22.4881 | 22.2245 | 21.9353 | 21.5328 | 20.8784 | 18.1565 | 10.4606 | 6.0612 | 3.2575 | 30.6603 | 30.3166 | 30.0889 | 29.9115 | 29.657 | 29.3746 | 29.0673 | 28.7279 | 28.3201 | 27.8332 | 25.9297 | 18.4643 | 11.2801 | 1.7696 | 26.5543 | 26.0218 | 25.7263 | 25.5018 | 25.1241 | 24.6961 | 24.2353 | 23.7272 | 23.133 | 22.5192 | 19.9379 | 12.7264 | 8.8018 | 6.4095
|  | SP |  |  | 23.8313 | 23.3577 | 23.1219 | 22.9699 | 22.8012 | 22.6103 | 22.4165 | 22.2081 | 21.9668 | 21.6407 | 19.7322 | 14.0405 | 9.4793 | 7.4749 | 30.6798 | 30.3411 | 30.1091 | 29.9247 | 29.676 | 29.4023 | 29.1044 | 28.7813 | 28.4131 | 27.8878 | 25.7036 | 17.2462 | 4.4549 | -15.5961 | 26.6087 | 26.072 | 25.7665 | 25.5299 | 25.2299 | 24.9053 | 24.5602 | 24.1861 | 23.7807 | 23.2967 | 21.4732 | 16.156 | 11.9402 | 10.2134
COWLEY GSP | HEADINGTON BSP | MINIMUM HEADROOM | SP5444008085 | YES | 39.3398 | 37.1859 | 34.8452 | 31.8347 | 27.6792 | 23.4547 | 19.8002 | 15.8786 | 11.5509 | 7.1057 | -4.2684 | -17.4567 | -24.5594 | -30.9797 | 43.4914 | 42.1797 | 40.7511 | 38.9295 | 36.6725 | 34.3204 | 32.2383 | 29.9257 | 27.2226 | 24.4597 | 17.6953 | 9.4833 | 1.501 | -6.9073 | 40.6508 | 38.7288 | 36.6251 | 33.9508 | 30.3065 | 26.5693 | 23.2641 | 19.6802 | 15.649 | 11.5222 | 1.0363 | -10.7454 | -16.3988 | -21.7328
|  | CT |  |  | 40.3312 | 38.7389 | 36.9807 | 34.4821 | 31.2559 | 27.972 | 25.3717 | 22.5396 | 19.4827 | 15.1653 | 4.1615 | -12.5556 | -24.5594 | -30.9797 | 43.6844 | 42.487 | 41.1898 | 39.4095 | 37.4044 | 35.3018 | 33.5414 | 31.5644 | 29.3883 | 26.5648 | 19.4612 | 9.4833 | 1.501 | -6.667 | 41.4541 | 40.0055 | 38.4019 | 36.1424 | 33.2981 | 30.3716 | 27.9922 | 25.3718 | 22.5187 | 18.5585 | 8.5505 | -6.3187 | -16.3988 | -21.7328
|  | LW |  |  | 39.3398 | 37.1859 | 34.8452 | 31.8347 | 27.6792 | 23.4547 | 19.8002 | 15.8786 | 11.5509 | 7.1057 | -4.2684 | -17.4567 | -23.3002 | -27.3564 | 43.4914 | 42.1797 | 40.7511 | 38.9295 | 36.6725 | 34.3204 | 32.2383 | 29.9257 | 27.2226 | 24.4597 | 17.6953 | 10.713 | 8.1234 | 6.267 | 40.6508 | 38.7288 | 36.6251 | 33.9508 | 30.3065 | 26.5693 | 23.2641 | 19.6802 | 15.649 | 11.5222 | 1.0363 | -10.7454 | -15.6363 | -18.9988
|  | ST |  |  | 41.0113 | 39.9239 | 38.8035 | 37.2816 | 35.3795 | 33.4236 | 31.9025 | 30.2459 | 28.4606 | 26.493 | 20.1233 | 7.1636 | -0.28229 | -4.7964 | 44.2152 | 43.3811 | 42.5213 | 41.3775 | 39.9923 | 38.5359 | 37.3398 | 36.0088 | 34.5549 | 33.0502 | 27.8613 | 17.4522 | 10.151 | 2.5679 | 42.1507 | 41.2067 | 40.2312 | 38.9211 | 37.2596 | 35.5298 | 34.1389 | 32.6096 | 30.948 | 29.1494 | 23.2055 | 11.5533 | 4.9076 | 0.97007
|  | SP |  |  | 41.155 | 40.1395 | 39.1258 | 37.7756 | 35.924 | 34.0031 | 32.4925 | 30.8311 | 29.1466 | 27.1663 | 21.5546 | 9.2385 | 0.45548 | -4.0107 | 44.2542 | 43.421 | 42.5866 | 41.5153 | 40.2711 | 38.9292 | 37.8177 | 36.5448 | 35.2191 | 33.6938 | 28.9536 | 17.7407 | 6.5073 | -6.9073 | 42.2738 | 41.3843 | 40.5035 | 39.3553 | 37.7985 | 36.1546 | 34.8209 | 33.3284 | 31.8104 | 30.0344 | 24.8218 | 13.4591 | 5.6386 | 1.7724
COWLEY GSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU8473392200 | YES | 20.1771 | 17.3285 | 14.2876 | 11.0725 | 6.2527 | 1.0173 | -4.5583 | -10.6984 | -18.0014 | -25.0148 | -42.0963 | -63.8921 | -73.5769 | -83.3688 | 24.5914 | 23.929 | 23.2415 | 22.0269 | 19.9904 | 17.6199 | 15.0845 | 12.3324 | 9.0218 | 4.6394 | -5.4339 | -23.9666 | -46.3634 | -73.8814 | 16.9401 | 14.3339 | 11.4932 | 8.4922 | 4.0636 | -0.77246 | -5.9772 | -11.7286 | -18.6408 | -25.2663 | -41.158 | -61.1988 | -69.6691 | -77.1692
|  | CT |  |  | 21.8178 | 19.9199 | 17.8305 | 15.4304 | 12.249 | 8.7353 | 4.9965 | 0.87398 | -3.7495 | -10.6626 | -27.1176 | -54.0828 | -73.5769 | -83.3688 | 24.5914 | 23.929 | 23.2415 | 22.4588 | 21.6516 | 20.0356 | 18.1121 | 16.013 | 13.2862 | 8.4986 | -2.6058 | -20.7182 | -36.5908 | -52.8872 | 18.3106 | 16.5412 | 14.5711 | 12.2831 | 9.3146 | 6.0104 | 2.4751 | -1.4367 | -5.8506 | -12.3971 | -27.735 | -52.2098 | -68.9879 | -77.1692
|  | LW |  |  | 20.1771 | 17.3285 | 14.2876 | 11.0725 | 6.2527 | 1.0173 | -4.5583 | -10.6984 | -18.0014 | -25.0148 | -42.0963 | -63.8921 | -73.5669 | -79.2364 | 24.7237 | 24.0988 | 23.3354 | 22.0269 | 19.9904 | 17.6199 | 15.0845 | 12.3324 | 9.0218 | 4.6394 | -5.4339 | -18.0035 | -23.3776 | -26.4763 | 16.9401 | 14.3339 | 11.4932 | 8.4922 | 4.0636 | -0.77246 | -5.9772 | -11.7286 | -18.6408 | -25.2663 | -41.158 | -61.1988 | -69.6691 | -74.5093
|  | ST |  |  | 23.3785 | 22.4415 | 21.4164 | 20.2984 | 18.7728 | 16.9709 | 15.036 | 12.8934 | 10.4272 | 7.0228 | -6.8306 | -30.5876 | -43.3304 | -50.9877 | 25.0298 | 24.6311 | 24.2508 | 23.8431 | 23.3588 | 22.638 | 21.8371 | 20.9421 | 19.6354 | 17.2577 | 7.4407 | -13.3278 | -27.8498 | -43.4986 | 19.8135 | 18.9673 | 18.021 | 16.9731 | 15.5436 | 13.8343 | 11.9897 | 9.9412 | 7.5742 | 4.2999 | -9.1206 | -31.7189 | -43.3341 | -50.07
|  | SP |  |  | 23.6424 | 22.7934 | 21.951 | 21.0786 | 19.5818 | 15.7686 | 11.8799 | 7.79 | 1.2219 | -1.7109 | -12.0516 | -37.7482 | -53.1072 | -60.4129 | 25.0309 | 24.636 | 24.2653 | 23.8822 | 23.4569 | 20.6895 | 17.8748 | 14.9341 | 9.0875 | 7.095 | -0.51633 | -23.9666 | -46.3634 | -73.8814 | 20.0504 | 19.2766 | 18.4969 | 17.6785 | 16.304 | 12.6068 | 8.8346 | 4.8619 | -1.5867 | -4.3525 | -14.1683 | -38.649 | -52.9444 | -59.463
IVER 66KV | HILLINGDON | MINIMUM HEADROOM | TQ0744082847 | NO | 7.94 | 6.9938 | 5.8592 | 4.86 | 3.281 | 1.604 | -0.231 | -2.2015 | -4.6546 | -7.3207 | -14.2939 | -22.5889 | -29.6622 | -33.37 | 20.7127 | 20.0516 | 19.2293 | 18.4838 | 17.5123 | 16.4691 | 15.2808 | 13.9839 | 12.2765 | 10.4348 | 5.9993 | -1.3793 | -7.7975 | -19.4962 | 10.8148 | 9.9316 | 8.837 | 7.8331 | 6.3332 | 4.7315 | 2.9513 | 1.0272 | -1.4247 | -4.0646 | -10.6365 | -18.2438 | -23.9194 | -26.9288
|  | CT |  |  | 8.153 | 7.3742 | 6.5095 | 5.5978 | 4.4954 | 3.3115 | 2.0241 | 0.62795 | -0.97974 | -3.7699 | -11.2216 | -22.0815 | -29.6622 | -33.37 | 20.7127 | 20.0521 | 19.3292 | 18.5056 | 17.6363 | 16.699 | 15.6666 | 14.5319 | 13.1858 | 11.2195 | 5.9993 | -1.3793 | -7.7975 | -15.1368 | 10.9728 | 10.2333 | 9.4016 | 8.4498 | 7.3529 | 6.1712 | 4.8796 | 3.4719 | 1.824 | -0.82234 | -7.8241 | -17.6451 | -23.9194 | -26.9288
|  | LW |  |  | 7.94 | 6.9938 | 5.8592 | 4.86 | 3.281 | 1.604 | -0.231 | -2.2015 | -4.6546 | -7.3207 | -14.2939 | -22.5889 | -25.9827 | -27.5425 | 20.7219 | 20.0516 | 19.2293 | 18.4838 | 17.5123 | 16.4691 | 15.2808 | 13.9839 | 12.2765 | 10.4348 | 6.0399 | 1.3679 | -0.13939 | -0.87093 | 10.8148 | 9.9316 | 8.837 | 7.8331 | 6.3332 | 4.7315 | 2.9513 | 1.0272 | -1.4247 | -4.0646 | -10.6365 | -18.2438 | -21.1782 | -22.4747
|  | ST |  |  | 8.6401 | 8.1873 | 7.7091 | 7.3585 | 6.9191 | 6.438 | 5.8961 | 5.2893 | 4.5708 | 3.8077 | 0.26532 | -8.4043 | -12.7782 | -15.5952 | 21.0733 | 20.6422 | 20.1907 | 19.8197 | 19.3564 | 18.8539 | 18.2844 | 17.6438 | 16.8879 | 16.1279 | 12.7224 | 4.815 | -0.93239 | -7.9958 | 11.473 | 11.0616 | 10.6185 | 10.2662 | 9.805 | 9.2996 | 8.7267 | 8.0826 | 7.3159 | 6.5317 | 2.9227 | -5.3422 | -9.2519 | -11.659
|  | SP |  |  | 8.6992 | 8.2272 | 7.7572 | 7.4248 | 7.0896 | 6.735 | 6.3566 | 5.919 | 5.4133 | 4.831 | 2.576 | -4.7296 | -9.0739 | -10.6501 | 21.0959 | 20.6262 | 20.1511 | 19.7648 | 19.3699 | 18.9484 | 18.4848 | 17.9493 | 17.3239 | 16.5526 | 13.5122 | 4.6363 | -5.3759 | -19.4962 | 11.529 | 11.0881 | 10.6463 | 10.3077 | 9.9618 | 9.5975 | 9.2053 | 8.7477 | 8.2134 | 7.6088 | 5.2239 | -1.8554 | -5.9932 | -7.37
EALING GSP | IRONBRIDGE | MINIMUM HEADROOM | TQ1426580175 | NO | 13.6917 | 13.1797 | 12.3733 | 11.3522 | 9.8745 | 8.2749 | 6.5682 | 4.7694 | 3.0168 | 1.2516 | -4.0667 | -10.735 | -16.3763 | -19.7784 | 21.4449 | 21.1225 | 20.6715 | 20.0359 | 19.286 | 18.2079 | 17.0232 | 15.7634 | 14.5657 | 13.1391 | 8.6697 | 0.74112 | -12.9958 | -38.7559 | 16.2147 | 15.7399 | 14.9981 | 14.0652 | 12.723 | 11.2763 | 9.715 | 8.0638 | 6.4145 | 4.7613 | -0.21845 | -6.2842 | -10.7232 | -13.4867
|  | CT |  |  | 13.8437 | 13.4335 | 12.7799 | 11.8207 | 10.6261 | 9.341 | 7.9819 | 6.5413 | 5.2468 | 3.478 | -1.8018 | -10.2309 | -16.3763 | -19.7784 | 21.4449 | 21.1225 | 20.6715 | 20.0359 | 19.286 | 18.2079 | 17.0232 | 15.7634 | 14.5657 | 13.1391 | 8.6697 | 0.74112 | -8.6213 | -21.7123 | 16.3371 | 15.9527 | 15.3597 | 14.4773 | 13.3858 | 12.208 | 10.9549 | 9.6283 | 8.4198 | 6.7736 | 1.8644 | -5.6679 | -10.7232 | -13.4867
|  | LW |  |  | 13.6917 | 13.1797 | 12.3733 | 11.3522 | 9.8745 | 8.2749 | 6.5682 | 4.7694 | 3.0168 | 1.2516 | -4.0667 | -10.735 | -13.9496 | -15.8414 | 21.4793 | 21.1973 | 20.7853 | 20.2151 | 19.4979 | 18.7061 | 17.6199 | 16.4642 | 15.3223 | 14.1807 | 10.7587 | 6.95 | 5.4502 | 4.5233 | 16.2147 | 15.7399 | 14.9981 | 14.0652 | 12.723 | 11.2763 | 9.715 | 8.0638 | 6.4145 | 4.7613 | -0.21845 | -6.2842 | -9.0118 | -10.5503
|  | ST |  |  | 14.1225 | 13.8927 | 13.4898 | 12.9366 | 12.2417 | 11.4769 | 10.6554 | 9.7931 | 9.0737 | 8.3935 | 5.8554 | 0.076085 | -3.7477 | -6.254 | 21.5445 | 21.2844 | 20.9169 | 20.4013 | 19.7899 | 19.1073 | 18.3543 | 17.5923 | 16.7308 | 15.8978 | 12.8079 | 5.3033 | -3.4488 | -16.2039 | 16.6037 | 16.39 | 16.0339 | 15.5394 | 14.9072 | 14.2076 | 13.4509 | 12.6581 | 11.9851 | 11.3459 | 8.9317 | 3.5358 | 0.16324 | -1.94
|  | SP |  |  | 14.1542 | 13.912 | 13.511 | 12.978 | 12.3739 | 11.7186 | 10.997 | 10.2534 | 9.6769 | 9.1179 | 7.2231 | 3.0298 | -0.39627 | -2.0376 | 21.5404 | 21.2723 | 20.8894 | 20.3609 | 19.7317 | 19.0256 | 18.2406 | 17.2751 | 16.3209 | 15.2992 | 11.5597 | 2.2229 | -12.9958 | -38.7559 | 16.6332 | 16.4053 | 16.0493 | 15.5727 | 15.0283 | 14.4346 | 13.7743 | 13.0955 | 12.5612 | 12.0373 | 10.2444 | 6.3102 | 3.1873 | 1.8067
FAWLEY GSP | LANGLEY BSP | MINIMUM HEADROOM | SU4515801418 | YES | 31.59 | 31.0102 | 30.2304 | 29.3761 | 27.7794 | 25.9752 | 24.0911 | 22.0141 | 19.4184 | 16.5967 | 9.2857 | 1.4875 | -3.5945 | -6.1994 | 26.9332 | 26.8009 | 26.5991 | 26.2994 | 25.4006 | 24.238 | 22.9876 | 21.5772 | 19.7042 | 17.6607 | 13.0782 | 8.6844 | 5.7109 | 3.493 | 21.3607 | 20.7976 | 20.0097 | 19.1414 | 17.6133 | 15.8878 | 14.0729 | 12.0649 | 9.5075 | 6.7333 | -0.060197 | -7.0817 | -11.2207 | -13.4023
|  | CT |  |  | 31.9218 | 31.5593 | 31.0996 | 30.3862 | 29.2775 | 27.982 | 26.6327 | 25.1131 | 23.2671 | 20.4467 | 12.7348 | 2.4129 | -3.5945 | -6.1994 | 26.9332 | 26.8009 | 26.6007 | 26.2994 | 25.8617 | 24.8818 | 23.8601 | 22.6925 | 21.2303 | 19.1841 | 14.1212 | 8.6844 | 5.7109 | 3.493 | 21.6276 | 21.2539 | 20.7775 | 20.0091 | 18.9022 | 17.6203 | 16.2879 | 14.7853 | 12.941 | 10.1802 | 2.9482 | -6.1308 | -11.2207 | -13.4023
|  | LW |  |  | 31.59 | 31.0102 | 30.2304 | 29.3761 | 27.7794 | 25.9752 | 24.0911 | 22.0141 | 19.4184 | 16.5967 | 9.2857 | 1.4875 | -0.90893 | -1.7154 | 26.9618 | 26.8251 | 26.5991 | 26.3192 | 25.4006 | 24.238 | 22.9876 | 21.5772 | 19.7042 | 17.6607 | 13.0782 | 8.8243 | 7.8875 | 7.5637 | 21.3607 | 20.7976 | 20.0097 | 19.1414 | 17.6133 | 15.8878 | 14.0729 | 12.0649 | 9.5075 | 6.7333 | -0.060197 | -7.0817 | -9.1233 | -9.8019
|  | ST |  |  | 32.2706 | 32.1201 | 31.9044 | 31.6399 | 31.1023 | 30.4396 | 29.7743 | 28.991 | 28.0472 | 26.9616 | 22.4858 | 14.8113 | 11.6 | 9.4197 | 27.05 | 26.9894 | 26.8757 | 26.7238 | 26.4139 | 26.0317 | 25.6824 | 25.2432 | 24.5664 | 23.6825 | 19.8268 | 13.7145 | 11.2821 | 9.1907 | 21.9865 | 21.831 | 21.6074 | 21.3316 | 20.7754 | 20.1012 | 19.4277 | 18.6383 | 17.6911 | 16.6409 | 12.1748 | 4.6684 | 1.7619 | -0.066807
|  | SP |  |  | 32.3328 | 32.1746 | 31.9675 | 31.7239 | 31.2749 | 30.7274 | 30.2313 | 29.5756 | 28.8251 | 27.9045 | 24.4875 | 17.3944 | 14.0362 | 12.9162 | 27.0543 | 26.9881 | 26.8702 | 26.7178 | 26.4433 | 26.1036 | 25.8052 | 25.4194 | 24.9788 | 24.4218 | 21.3737 | 14.7297 | 10.7866 | 7.0324 | 22.0426 | 21.8689 | 21.6466 | 21.3863 | 20.9332 | 20.3914 | 19.8993 | 19.2523 | 18.5169 | 17.6326 | 14.2911 | 7.0645 | 3.8696 | 2.854
IVER 132KV | LONGFORD | MINIMUM HEADROOM | TQ0383076784 | NO | 80.8945 | 80.517 | 79.9313 | 79.2305 | 78.3936 | 77.4247 | 76.2663 | 74.9535 | 73.2979 | 71.299 | 64.3287 | 55.7628 | 54.1989 | 53.344 | 58.4523 | 58.1767 | 57.9054 | 57.604 | 57.2109 | 56.775 | 56.2729 | 55.567 | 54.6417 | 53.5192 | 48.2661 | 42.1787 | 41.1413 | 40.5148 | 74.869 | 74.4892 | 74.0646 | 73.5948 | 72.94 | 72.2296 | 71.0789 | 69.6557 | 67.9109 | 65.8102 | 58.7207 | 50.5637 | 49.1093 | 48.3128
|  | CT |  |  | 80.8945 | 80.5219 | 80.0184 | 79.3835 | 78.6625 | 77.8573 | 76.9632 | 75.9731 | 74.8174 | 73.3357 | 68.3077 | 59.6213 | 56.4446 | 54.8897 | 58.4683 | 58.2328 | 57.9983 | 57.7268 | 57.4073 | 57.0595 | 56.5836 | 56.0244 | 55.3577 | 54.5273 | 51.1996 | 44.7711 | 42.948 | 41.9772 | 74.9408 | 74.6464 | 74.3338 | 73.9169 | 73.4164 | 72.8765 | 72.2057 | 71.1811 | 70.0215 | 68.4508 | 63.1839 | 54.2586 | 51.3166 | 49.8798
|  | LW |  |  | 80.9321 | 80.517 | 79.9313 | 79.2305 | 78.3936 | 77.4247 | 76.2663 | 74.9535 | 73.2979 | 71.299 | 64.3287 | 55.7628 | 54.1989 | 53.344 | 58.4523 | 58.1767 | 57.9054 | 57.604 | 57.2109 | 56.775 | 56.2729 | 55.567 | 54.6417 | 53.5192 | 48.2661 | 42.1787 | 41.1413 | 40.5148 | 74.869 | 74.4892 | 74.0646 | 73.5948 | 72.94 | 72.2296 | 71.0789 | 69.6557 | 67.9109 | 65.8102 | 58.7207 | 50.5637 | 49.1093 | 48.3128
|  | ST |  |  | 81.1772 | 80.9884 | 80.8103 | 80.616 | 80.3547 | 79.9842 | 79.4932 | 78.9129 | 78.133 | 77.1109 | 73.0293 | 62.0114 | 56.6261 | 55.2412 | 58.6321 | 58.4959 | 58.3799 | 58.2601 | 58.1035 | 57.9293 | 57.7258 | 57.4898 | 57.1753 | 56.5979 | 54.267 | 46.2053 | 42.0365 | 40.97 | 75.1865 | 75.0332 | 74.8852 | 74.7253 | 74.4965 | 74.2457 | 73.9565 | 73.628 | 73.2042 | 72.3928 | 68.4685 | 57.8018 | 52.4698 | 51.0863
|  | SP |  |  | 81.1944 | 81.0274 | 80.8707 | 80.7052 | 80.5089 | 80.2898 | 79.9622 | 79.5708 | 79.0859 | 78.4724 | 76.353 | 68.7672 | 61.2509 | 59.1368 | 58.6722 | 58.5459 | 58.4409 | 58.3356 | 58.2151 | 58.0843 | 57.9411 | 57.7775 | 57.5762 | 57.3239 | 56.1846 | 51.4403 | 45.585 | 43.9163 | 75.2817 | 75.1306 | 74.9979 | 74.8577 | 74.6914 | 74.5093 | 74.3154 | 74.0912 | 73.8171 | 73.4831 | 71.6729 | 64.2914 | 56.8683 | 54.839
AMERSHAM | LOUDWATER BSP | MINIMUM HEADROOM | SU9064791105 | NO | 16.1506 | 13.5467 | -32.2579 | 81.9049 | 77.9697 | 73.8834 | 69.4462 | 64.5962 | 58.7156 | 53.1139 | 40.6935 | 25.3655 | 16.5033 | 9.9127 | 12.2076 | 11.1071 | -33.0161 | 82.8288 | 81.2101 | 79.531 | 77.7122 | 75.6109 | 71.7751 | 68.172 | 60.9231 | 51.7095 | 43.0748 | 35.3756 | 15.2247 | 12.8956 | -32.6329 | 81.7635 | 78.1605 | 74.3998 | 70.2851 | 65.7591 | 60.182 | 54.8761 | 43.3278 | 29.3076 | 21.7586 | 16.261
|  | CT |  |  | 17.0165 | 15.0047 | -30.2272 | 84.4072 | 81.6634 | 78.8036 | 75.7889 | 72.4634 | 68.6705 | 62.9121 | 50.0215 | 30.0377 | 16.5033 | 9.9127 | 12.5216 | 11.607 | -32.3497 | 83.6254 | 82.4305 | 81.1858 | 79.8717 | 78.0778 | 75.3333 | 71.4693 | 63.3171 | 51.7095 | 43.0748 | 35.3756 | 15.9582 | 14.1531 | -30.8712 | 83.9296 | 81.3913 | 78.732 | 75.9081 | 72.773 | 69.1584 | 63.7024 | 51.7018 | 33.6676 | 21.7586 | 16.261
|  | LW |  |  | 16.1506 | 13.5467 | -32.2579 | 81.9049 | 77.9697 | 73.8834 | 69.4462 | 64.5962 | 58.7156 | 53.1139 | 40.6935 | 25.3655 | 19.6726 | 16.7419 | 12.2076 | 11.1071 | -33.0161 | 82.8288 | 81.2101 | 79.531 | 77.7122 | 75.6109 | 71.7751 | 68.172 | 60.9231 | 52.6256 | 50.0925 | 48.7885 | 15.2247 | 12.8956 | -32.6329 | 81.7635 | 78.1605 | 74.3998 | 70.2851 | 65.7591 | 60.182 | 54.8761 | 43.3278 | 29.3076 | 24.3198 | 21.7975
|  | ST |  |  | 18.4362 | 17.3724 | 16.1789 | 132.0032 | 87.7049 | 86.292 | 84.7535 | 83.086 | 81.2167 | 79.3053 | 70.5569 | 55.1213 | 47.2844 | 42.2562 | 13.0736 | 12.5308 | 11.9649 | 128.4093 | 84.831 | 84.179 | 83.4653 | 82.6852 | 81.8024 | 80.8548 | 74.8272 | 62.624 | 55.5249 | 48.3061 | 17.3339 | 16.4389 | 15.4075 | 131.3535 | 87.1619 | 85.8522 | 84.4143 | 82.8441 | 81.0606 | 79.245 | 70.772 | 56.1048 | 49.0467 | 44.6763
|  | SP |  |  | 18.5918 | 17.5851 | 16.5659 | 132.617 | 131.4205 | 130.1692 | 128.8699 | 127.404 | 125.8476 | 124.0377 | 117.3486 | 99.7468 | 91.0063 | 87.2859 | 13.1279 | 12.6075 | 12.0928 | 128.6056 | 128.0352 | 127.4357 | 126.8023 | 126.0969 | 125.3329 | 124.4048 | 120.7002 | 105.6045 | 94.7717 | 83.0406 | 17.4741 | 16.6257 | 15.7578 | 131.919 | 130.8429 | 129.7084 | 128.5223 | 127.1648 | 125.7059 | 124.0069 | 117.6427 | 100.7496 | 92.5563 | 89.2251
MANNINGTON GSP | LYTCHETT | MINIMUM HEADROOM | SY9783994358 | YES | 55.4444 | 27.8153 | 18.9536 | 18.1366 | 17.1799 | 14.2798 | 10.208 | 5.7351 | 0.18529 | -5.4721 | -18.3809 | -37.2308 | -49.2141 | -58.1381 | 50.7829 | 23.2485 | 14.2751 | 12.7764 | 10.6766 | 8.1025 | 5.3301 | 2.2461 | -1.6556 | -5.4812 | -13.8508 | -24.6327 | -35.6523 | -47.2617 | 46.7033 | 17.9185 | 7.7162 | 5.5417 | 2.1405 | -1.6963 | -5.7087 | -10.0621 | -15.2417 | -20.4281 | -33.2766 | -50.3793 | -60.7801 | -68.5988
|  | CT |  |  | 55.4444 | 27.8153 | 18.9672 | 18.1366 | 17.2488 | 16.0388 | 14.8057 | 12.503 | 8.5365 | 2.9628 | -9.8357 | -31.4225 | -49.2141 | -58.1381 | 50.7829 | 23.2485 | 14.4881 | 13.6304 | 11.8875 | 9.7746 | 7.5486 | 5.0388 | 2.1084 | -1.7718 | -10.5523 | -23.9352 | -34.2407 | -42.2343 | 47.7386 | 19.5652 | 10.085 | 8.4135 | 6.1135 | 3.4432 | 0.66278 | -2.4128 | -5.8943 | -10.9418 | -23.4822 | -45.0202 | -60.7801 | -68.5988
|  | LW |  |  | 55.5061 | 27.8482 | 18.9536 | 18.1377 | 17.1799 | 14.2798 | 10.208 | 5.7351 | 0.18529 | -5.4721 | -18.3809 | -37.2308 | -46.2778 | -51.8493 | 50.8542 | 23.3206 | 14.2751 | 12.7764 | 10.6766 | 8.1025 | 5.3301 | 2.2461 | -1.6556 | -5.4812 | -13.8508 | -24.6327 | -29.7976 | -32.8953 | 46.7033 | 17.9185 | 7.7162 | 5.5417 | 2.1405 | -1.6963 | -5.7087 | -10.0621 | -15.2417 | -20.4281 | -33.2766 | -50.3793 | -58.4724 | -63.3664
|  | ST |  |  | 55.7925 | 28.3734 | 19.7803 | 19.3009 | 18.6999 | 17.79 | 16.8739 | 15.8755 | 14.7303 | 12.6503 | 3.6012 | -15.4774 | -25.3291 | -31.272 | 51.0597 | 23.6921 | 15.1338 | 14.7009 | 14.1639 | 13.3036 | 12.1616 | 10.6499 | 8.905 | 6.2622 | -3.7249 | -19.3697 | -28.2885 | -35.6198 | 48.5351 | 20.878 | 11.9917 | 11.1642 | 9.9755 | 8.4474 | 6.8768 | 5.1719 | 3.2833 | 0.37113 | -10.2326 | -27.7377 | -37.7378 | -43.8799
|  | SP |  |  | 55.8141 | 28.3972 | 19.8139 | 19.3664 | 18.8488 | 15.4868 | 18.2723 | 14.858 | 8.5916 | 7.3226 | 1.8304 | -18.2765 | -29.2771 | -34.307 | 51.0711 | 23.7004 | 15.1423 | 14.7262 | 14.2544 | 10.9172 | 13.5722 | 9.6281 | 2.8158 | 0.83546 | -6.2305 | -23.2572 | -35.6523 | -47.2617 | 48.7082 | 21.0978 | 12.2998 | 11.6032 | 10.3614 | 6.236 | 8.2557 | 4.0056 | -3.1099 | -5.4669 | -13.3276 | -31.1023 | -41.6797 | -46.727
BRAMLEY (FLEE) | MAIDENHEAD BSP | MINIMUM HEADROOM | SU8648579800 | YES | 49.7115 | 47.7805 | 45.4656 | 42.8561 | 39.1849 | 35.1982 | 30.9834 | 26.1199 | 20.2987 | 14.408 | 0.47487 | -14.4258 | -22.1075 | -28.1738 | 41.8775 | 40.8747 | 39.7111 | 38.4045 | 36.6361 | 34.7114 | 32.6554 | 30.0471 | 26.6613 | 23.2454 | 15.2988 | 4.9197 | -4.4498 | -14.1683 | 42.8103 | 41.1473 | 39.2118 | 37.0424 | 33.843 | 30.3894 | 26.7563 | 22.6093 | 17.5169 | 12.1055 | -0.49443 | -13.9941 | -20.7393 | -25.9811
|  | CT |  |  | 50.3882 | 48.916 | 47.0317 | 44.8102 | 42.1187 | 39.1429 | 36.1346 | 32.5869 | 28.4834 | 22.5594 | 8.4452 | -10.2012 | -22.1075 | -28.1738 | 42.0514 | 41.144 | 40.0481 | 38.7786 | 37.3104 | 35.6916 | 34.0233 | 31.7543 | 29.1114 | 25.4797 | 16.648 | 4.9197 | -4.4498 | -14.1683 | 43.5296 | 42.3214 | 40.8176 | 39.0507 | 36.7926 | 34.3077 | 31.8096 | 28.6421 | 24.8896 | 19.4481 | 6.6797 | -10.0395 | -20.7393 | -25.9811
|  | LW |  |  | 49.7115 | 47.7805 | 45.4656 | 42.8561 | 39.1849 | 35.1982 | 30.9834 | 26.1199 | 20.2987 | 14.408 | 0.47487 | -14.4258 | -19.9572 | -22.671 | 41.8775 | 40.8747 | 39.7111 | 38.4045 | 36.6361 | 34.7114 | 32.6554 | 30.0471 | 26.6613 | 23.2454 | 15.2988 | 7.1207 | 4.5497 | 3.2384 | 42.8103 | 41.1473 | 39.2118 | 37.0424 | 33.843 | 30.3894 | 26.7563 | 22.6093 | 17.5169 | 12.1055 | -0.49443 | -13.9941 | -18.8015 | -21.1014
|  | ST |  |  | 51.5751 | 50.8613 | 49.9192 | 48.7835 | 47.4229 | 45.8983 | 44.32 | 42.451 | 40.2456 | 37.8936 | 28.7318 | 14.4339 | 7.2467 | 2.5418 | 42.6531 | 42.1267 | 41.5005 | 40.7702 | 39.9278 | 38.991 | 38.0015 | 36.8391 | 35.4674 | 34.0152 | 27.4165 | 15.563 | 7.6861 | -1.3788 | 44.5016 | 43.9246 | 43.2123 | 42.3659 | 41.3189 | 40.1521 | 38.9338 | 37.4979 | 35.8002 | 33.8307 | 25.377 | 11.9775 | 5.556 | 1.5015
|  | SP |  |  | 51.7052 | 51.0391 | 50.2161 | 49.2888 | 48.1568 | 46.8671 | 45.5727 | 43.9791 | 42.2028 | 40.129 | 33.196 | 18.3497 | 10.2884 | 6.6389 | 42.6908 | 42.1727 | 41.5745 | 40.9119 | 40.1723 | 39.3347 | 38.4645 | 37.4138 | 36.2236 | 34.8149 | 29.4566 | 15.6572 | 3.2238 | -12.3645 | 44.6231 | 44.1001 | 43.494 | 42.8226 | 41.9459 | 40.9488 | 39.9509 | 38.7369 | 37.3923 | 35.7826 | 29.7337 | 15.6462 | 8.1433 | 4.9202
MANNINGTON GSP | MANNINGTON BSP | MINIMUM HEADROOM | SU0759205256 | YES | 64.8757 | 61.3566 | 56.9215 | 52.3259 | 45.9415 | 38.6397 | 30.3877 | 21.1584 | 10.278 | -0.11581 | -25.8915 | -56.7457 | -71.809 | -83.6412 | 57.0581 | 55.6456 | 53.7869 | 51.9345 | 49.2689 | 46.0345 | 39.7597 | 32.1156 | 18.4461 | 15.3283 | 5.2685 | -22.0812 | -41.1309 | -56.0794 | 66.1755 | 63.0799 | 59.0784 | 54.9531 | 49.0591 | 42.3136 | 34.7477 | 26.3146 | 16.4066 | 6.9383 | -16.8729 | -45.6536 | -59.014 | -69.6781
|  | CT |  |  | 66.6163 | 64.1449 | 60.9762 | 57.2013 | 52.6856 | 47.4147 | 41.3358 | 34.4173 | 26.6394 | 16.4276 | -8.786 | -46.2407 | -71.809 | -83.6412 | 57.522 | 56.4014 | 54.8646 | 53.2256 | 51.1058 | 48.5294 | 45.5867 | 42.264 | 38.3052 | 31.5482 | 15.6498 | -6.6453 | -22.1455 | -33.0731 | 67.8878 | 65.7072 | 62.9036 | 59.5714 | 55.4351 | 50.6012 | 45.0706 | 38.7959 | 31.7474 | 22.4919 | -0.64518 | -35.7802 | -59.014 | -69.6781
|  | LW |  |  | 64.8757 | 61.3566 | 56.9215 | 52.3259 | 45.9415 | 38.6397 | 30.3877 | 21.1584 | 10.278 | -0.11581 | -25.8915 | -56.7457 | -69.5917 | -76.5195 | 57.0581 | 55.6456 | 53.7869 | 51.9345 | 49.2689 | 46.0345 | 42.3701 | 38.2802 | 31.8463 | 25.1555 | 9.5595 | -9.0062 | -17.1392 | -21.4768 | 66.1755 | 63.0799 | 59.0784 | 54.9531 | 49.0591 | 42.3136 | 34.7477 | 26.3146 | 16.4066 | 6.9383 | -16.8729 | -45.6536 | -57.5565 | -63.946
|  | ST |  |  | 68.2025 | 66.8016 | 64.9391 | 63.0319 | 60.4893 | 57.3181 | 53.6562 | 49.4979 | 44.8698 | 38.3874 | 14.454 | -20.8059 | -38.108 | -47.5497 | 58.1249 | 57.4037 | 56.3598 | 55.3689 | 53.9581 | 52.1234 | 50.0112 | 47.6092 | 44.9143 | 40.4098 | 24.8262 | -3.1582 | -17.5417 | -27.7897 | 69.2309 | 68.0709 | 66.4857 | 64.8285 | 62.5041 | 59.598 | 56.2822 | 52.5289 | 48.3398 | 42.2774 | 20.1391 | -13.0013 | -29.3118 | -38.3187
|  | SP |  |  | 68.5384 | 67.2061 | 65.5182 | 63.883 | 61.3784 | 53.0113 | 44.2433 | 34.9822 | 19.6347 | 14.5373 | -2.6617 | -38.3495 | -57.8202 | -65.9486 | 58.2312 | 57.5505 | 56.5645 | 55.6568 | 54.2672 | 47.1336 | 39.7597 | 32.1156 | 18.4461 | 15.3283 | 5.2685 | -22.0812 | -41.1309 | -56.0794 | 69.5499 | 68.4851 | 67.0408 | 65.6351 | 63.3222 | 55.1816 | 46.7124 | 37.8136 | 22.8414 | 18.1449 | 2.3944 | -30.4096 | -48.8981 | -56.3984
BOTLEY WOOD GSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU4761512025 | NO | 7.2678 | 3.1543 | -1.3732 | 55.1905 | 48.4589 | 41.3697 | 33.6577 | 25.4456 | 15.4797 | 5.225 | -21.3969 | -56.1913 | -83.8905 | -104.1974 | 15.4317 | 13.1146 | 10.5939 | 68.9549 | 65.2876 | 61.4033 | 56.9836 | 52.0067 | 45.671 | 39.1346 | 23.1607 | 0.80322 | -20.9624 | -42.1041 | -2.546 | -6.0259 | -9.8125 | 47.4643 | 41.5164 | 35.2914 | 28.5818 | 21.4717 | 12.5466 | 3.2815 | -20.986 | -52.404 | -76.9118 | -94.0261
|  | CT |  |  | 8.6931 | 5.5077 | 2.305 | 59.5097 | 54.7463 | 49.7134 | 44.2602 | 38.4381 | 31.7849 | 21.6533 | -5.9039 | -50.1338 | -83.8905 | -104.1974 | 15.8439 | 13.7919 | 11.71 | 70.072 | 67.0595 | 63.871 | 60.1617 | 56.0961 | 51.3203 | 44.6009 | 26.7656 | 0.80322 | -20.9624 | -42.1041 | -1.0858 | -3.6515 | -6.2466 | 51.7263 | 47.6842 | 43.4385 | 38.8494 | 33.7342 | 27.7806 | 18.6375 | -6.4429 | -46.8015 | -76.9118 | -94.0261
|  | LW |  |  | 7.2678 | 3.1543 | -1.3732 | 55.1905 | 48.4589 | 41.3697 | 33.6577 | 25.4456 | 15.4797 | 5.225 | -21.3969 | -56.1913 | -74.968 | -87.2763 | 15.4317 | 13.1146 | 10.5939 | 68.9549 | 65.2876 | 61.4033 | 56.9836 | 52.0067 | 45.671 | 39.1346 | 23.1607 | 4.4637 | -4.4086 | -10.5458 | -2.546 | -6.0259 | -9.8125 | 47.4643 | 41.5164 | 35.2914 | 28.5818 | 21.4717 | 12.5466 | 3.2815 | -20.986 | -52.404 | -68.7027 | -78.9761
|  | ST |  |  | 10.7589 | 8.9747 | 7.2761 | 66.7141 | 64.4961 | 62.125 | 59.5105 | 56.7045 | 53.4566 | 50.1387 | 35.3318 | 1.0709 | -19.4497 | -34.2296 | 17.0171 | 15.7401 | 14.5312 | 74.41 | 72.9059 | 71.234 | 69.2868 | 67.1662 | 64.6743 | 62.1799 | 50.2412 | 23.3452 | 5.2182 | -14.0575 | 0.62453 | -0.75671 | -2.0771 | 57.6972 | 55.9169 | 54.0303 | 51.9406 | 49.6918 | 47.072 | 44.2986 | 31.3539 | 0.079169 | -17.6457 | -29.9268
|  | SP |  |  | 11.0697 | 9.2867 | 7.6978 | 67.3083 | 65.432 | 63.5503 | 61.5095 | 59.2522 | 56.7489 | 53.879 | 42.8765 | 11.591 | -9.7935 | -21.3139 | 17.1337 | 15.8187 | 14.6132 | 74.5279 | 73.2243 | 71.8915 | 70.3165 | 68.5456 | 66.5276 | 64.0879 | 54.3734 | 25.5087 | -2.8333 | -37.0691 | 0.9155 | -0.42697 | -1.631 | 58.309 | 56.7645 | 55.2351 | 53.5705 | 51.733 | 49.6829 | 47.2826 | 38.0916 | 10.066 | -9.1104 | -18.7031
MELKSHAM GSP | NORRINGTON | MINIMUM HEADROOM | ST8833564965 | NO | 83.4008 | 75.1353 | -87.0089 | -96.2815 | -111.2483 | -118.622 | -126.5017 | -134.9489 | -145.4487 | -156.2782 | -180.2094 | -206.9149 | -216.6978 | -221.3231 | 70.4652 | 62.7504 | -98.5765 | -107.031 | -121.4645 | -126.2258 | -131.4168 | -137.019 | -144.2307 | -151.6938 | -167.4492 | -184.3654 | -190.4339 | -193.3683 | 52.6351 | 43.725 | -118.7089 | -128.1916 | -144.798 | -151.6869 | -158.8223 | -166.296 | -174.938 | -183.8715 | -207.0139 | -235.4498 | -246.6097 | -251.9153
|  | CT |  |  | 85.3748 | 78.3302 | 70.8532 | 62.4948 | 49.6482 | 44.521 | 39.1052 | 33.2141 | 26.3443 | 15.8633 | -8.7039 | -42.0258 | -63.8847 | -73.6216 | 71.2596 | 64.0266 | 56.4436 | 48.0809 | 34.5342 | 30.7503 | 26.7109 | 22.3025 | 17.0778 | 9.5814 | -7.7755 | -30.7227 | -47.9427 | -62.4159 | 55.256 | 47.8056 | 40.0596 | 31.8903 | 17.7396 | 13.4107 | 8.9239 | 4.1741 | -1.1048 | -9.488 | -31.6818 | -68.9113 | -94.865 | -106.5217
|  | LW |  |  | 83.4008 | 75.1353 | -87.0089 | -96.2815 | -111.2483 | -118.622 | -126.5017 | -134.9489 | -145.4487 | -156.2782 | -180.2094 | -206.9149 | -216.6978 | -221.3231 | 70.4652 | 62.7504 | -98.5765 | -107.031 | -121.4645 | -126.2258 | -131.4168 | -137.019 | -144.2307 | -151.6938 | -167.4492 | -184.3654 | -190.4339 | -193.3683 | 52.6351 | 43.725 | -118.7089 | -128.1916 | -144.798 | -151.6869 | -158.8223 | -166.296 | -174.938 | -183.8715 | -207.0139 | -235.4498 | -246.6097 | -251.9153
|  | ST |  |  | 87.457 | 81.7474 | 75.804 | 69.7986 | 59.2516 | 56.5063 | 53.5935 | 50.4634 | 46.911 | 42.4963 | 24.083 | -8.0883 | -22.8674 | -31.6921 | 72.6472 | 66.29 | 59.7504 | 53.1645 | 41.1889 | 39.0404 | 36.6348 | 34.0443 | 31.0665 | 27.3365 | 11.8215 | -15.5658 | -30.5744 | -44.5012 | 56.7831 | 50.359 | 43.8026 | 37.2472 | 25.1606 | 22.9275 | 20.6138 | 18.1992 | 15.4976 | 11.6206 | -2.8711 | -30.9193 | -47.978 | -58.914
|  | SP |  |  | 87.8172 | 82.1414 | 76.3732 | 70.6174 | 60.3213 | 58.7505 | 54.0518 | 49.0955 | 41.4889 | 37.6975 | 23.9883 | -10.5867 | -28.5235 | -35.9352 | 72.8059 | 66.4281 | 59.9405 | 53.4492 | 41.6745 | 40.6112 | 36.4145 | 31.9764 | 24.8487 | 21.6829 | 9.9362 | -20.7267 | -43.597 | -66.9181 | 57.2084 | 50.9406 | 44.6191 | 38.3304 | 26.2091 | 24.8602 | 20.3855 | 15.8302 | 8.6859 | 5.2764 | -6.1786 | -33.3352 | -50.6759 | -58.8563
NORTH HYDE GSP | NORTH HYDE (D) | MINIMUM HEADROOM | TQ1035578925 | NO | 60.8796 | 52.0859 | 43.1979 | 34.2403 | 24.8179 | 23.4722 | 22.0604 | 20.5902 | 18.8001 | 16.928 | 11.0192 | 1.0242 | -9.5522 | -16.8558 | 56.5559 | 46.0864 | 35.555 | 24.9389 | 14.2075 | 13.5524 | 12.7376 | 11.8872 | 10.9764 | 9.788 | 5.6827 | -3.1555 | -13.1691 | -35.1566 | 51.1254 | 40.3443 | 29.4084 | 18.3985 | 7.0214 | 5.7295 | 4.3386 | 2.9037 | 1.2215 | -0.55248 | -6.0938 | -14.7057 | -23.2461 | -29.3021
|  | CT |  |  | 61.0673 | 52.3935 | 43.698 | 34.8226 | 25.716 | 24.694 | 23.5816 | 22.4078 | 21.1346 | 19.2511 | 13.2227 | 1.0242 | -9.5522 | -16.8558 | 56.5559 | 46.0864 | 35.555 | 24.9389 | 14.2075 | 13.5524 | 12.7376 | 11.8872 | 10.9764 | 9.788 | 5.6827 | -3.1555 | -13.1691 | -25.7224 | 51.248 | 40.5565 | 29.8384 | 18.8565 | 7.7235 | 6.7149 | 5.6165 | 4.4613 | 3.2498 | 1.4923 | -4.0995 | -14.5459 | -23.2461 | -29.3021
|  | LW |  |  | 60.8796 | 52.0859 | 43.1979 | 34.2403 | 24.8179 | 23.4722 | 22.0604 | 20.5902 | 18.8001 | 16.928 | 11.0192 | 1.1854 | -5.9971 | -11.4115 | 56.5893 | 46.0948 | 35.5574 | 24.9884 | 14.2344 | 13.6445 | 12.9858 | 12.1958 | 11.2704 | 10.2951 | 7.1083 | 1.7978 | -1.6795 | -4.4426 | 51.1254 | 40.3443 | 29.4084 | 18.3985 | 7.0214 | 5.7295 | 4.3386 | 2.9037 | 1.2215 | -0.55248 | -6.0938 | -14.7057 | -20.5581 | -24.946
|  | ST |  |  | 61.3871 | 52.9367 | 44.4979 | 36.0399 | 27.4584 | 26.9975 | 26.5156 | 26.0349 | 25.5219 | 24.9685 | 22.5924 | 14.5817 | 8.0838 | 3.0191 | 56.6749 | 46.2895 | 35.9134 | 25.5117 | 15.0021 | 14.6663 | 14.3013 | 13.7823 | 13.1933 | 12.588 | 10.2042 | 2.6653 | -5.9867 | -17.7043 | 51.604 | 41.1379 | 30.6727 | 20.18 | 9.5265 | 9.0331 | 8.5083 | 7.9745 | 7.4012 | 6.8321 | 4.4572 | -2.8763 | -8.2778 | -12.3443
|  | SP |  |  | 61.4249 | 52.9765 | 44.5465 | 36.106 | 27.6107 | 27.2516 | 26.8675 | 26.4944 | 26.1251 | 25.7074 | 24.1087 | 18.1771 | 12.2991 | 8.2974 | 56.6736 | 46.284 | 35.8985 | 25.4864 | 14.971 | 14.6255 | 14.18 | 13.6063 | 12.9762 | 12.256 | 9.501 | 0.8732 | -12.9747 | -35.1566 | 51.6368 | 41.1491 | 30.6713 | 20.1766 | 9.6366 | 9.2773 | 8.8727 | 8.4706 | 8.0678 | 7.6267 | 5.924 | 0.39532 | -4.6504 | -7.866
NORTH HYDE GSP | NORTH HYDE 11 | MINIMUM HEADROOM | TQ1035578926 | NO | 33.2528 | 20.9987 | -5.4116 | -26.2326 | -37.9137 | -39.4011 | -40.9865 | -42.6566 | -44.6691 | -46.8493 | -53.5667 | -63.3286 | -72.4466 | -78.4713 | 31.3911 | 16.5665 | -16.0343 | -41.1796 | -54.3645 | -54.8125 | -55.5772 | -56.5998 | -57.76 | -59.284 | -64.4723 | -74.4168 | -88.2243 | -116.5577 | 26.9345 | 11.4471 | -21.7237 | -47.3247 | -61.4038 | -62.7505 | -64.1976 | -65.7656 | -67.6782 | -69.7549 | -76.0055 | -84.7382 | -92.1731 | -97.2193
|  | CT |  |  | 33.2528 | 20.9987 | -5.3161 | -25.5872 | -36.9158 | -38.0478 | -39.2631 | -40.5532 | -42.0256 | -44.1988 | -50.912 | -62.9642 | -72.4466 | -78.4713 | 31.3911 | 16.5665 | -16.0343 | -41.1796 | -54.3645 | -54.8125 | -55.5772 | -56.5998 | -57.76 | -59.284 | -64.4723 | -74.4168 | -85.5799 | -100.4369 | 27.1182 | 11.7569 | -21.2188 | -46.7377 | -60.5164 | -61.5758 | -62.7245 | -63.9464 | -65.3211 | -67.3416 | -73.5561 | -84.2005 | -92.1731 | -97.2193
|  | LW |  |  | 33.2824 | 21.0117 | -5.4116 | -26.2326 | -37.9137 | -39.4011 | -40.9865 | -42.6566 | -44.6691 | -46.8493 | -53.5667 | -63.3286 | -69.1356 | -73.2596 | 31.4546 | 16.6663 | -15.9086 | -40.9917 | -54.1191 | -54.5119 | -55.1753 | -56.1166 | -57.2713 | -58.5495 | -62.634 | -68.1506 | -70.9796 | -73.0759 | 26.9345 | 11.4471 | -21.7237 | -47.3247 | -61.4038 | -62.7505 | -64.1976 | -65.7656 | -67.6782 | -69.7549 | -76.0055 | -84.7382 | -89.5741 | -92.93
|  | ST |  |  | 33.4445 | 21.3282 | -4.8487 | -24.9281 | -35.4561 | -35.7745 | -36.1091 | -36.4682 | -36.9183 | -37.4156 | -40.5441 | -49.4362 | -55.5851 | -59.8805 | 31.542 | 16.8282 | -15.6647 | -40.6571 | -53.7184 | -54.0349 | -54.3759 | -54.7477 | -55.203 | -55.7045 | -58.8886 | -68.2589 | -78.5489 | -92.7445 | 27.5163 | 12.6143 | -19.9814 | -45.0146 | -58.1749 | -58.5776 | -59.0402 | -59.5897 | -60.2603 | -60.9712 | -63.9255 | -72.0872 | -77.3887 | -80.9245
|  | SP |  |  | 33.4609 | 21.3509 | -4.8162 | -24.8871 | -35.3632 | -35.6205 | -35.8829 | -36.1558 | -36.4719 | -36.8027 | -38.5658 | -45.2361 | -51.0789 | -54.4218 | 31.5449 | 16.8277 | -15.6725 | -40.676 | -53.7323 | -54.0472 | -54.3856 | -54.7515 | -55.1813 | -56.0964 | -59.7881 | -70.685 | -88.2243 | -116.5577 | 27.5677 | 12.6913 | -19.8721 | -44.8872 | -57.9598 | -58.2786 | -58.6117 | -59.0024 | -59.4633 | -59.9908 | -62.0115 | -68.1157 | -73.2849 | -76.0264
IVER 66KV | NORTHOLT | MINIMUM HEADROOM | TQ1155583245 | NO | 23.1732 | 22.6046 | 21.8123 | 20.9335 | 19.4051 | 17.7863 | 16.028 | 14.1511 | 11.9016 | 9.4486 | 1.6757 | -9.0171 | -18.6865 | -24.8159 | 22.3365 | 22.0279 | 21.548 | 21.006 | 20.2208 | 19.376 | 18.4186 | 17.3825 | 16.1035 | 14.6855 | 9.4307 | -0.17422 | -9.5705 | -28.195 | 21.8334 | 21.3456 | 20.6905 | 19.966 | 18.6152 | 17.1585 | 15.5658 | 13.8671 | 11.8133 | 9.5073 | 2.2243 | -7.4298 | -15.7778 | -20.9968
|  | CT |  |  | 23.3965 | 22.9828 | 22.4929 | 21.6875 | 20.596 | 19.4281 | 18.174 | 16.8196 | 15.2971 | 12.8339 | 4.9571 | -8.6093 | -18.6865 | -24.8159 | 22.3429 | 22.029 | 21.6572 | 21.031 | 20.3022 | 19.5128 | 18.644 | 17.6915 | 16.5988 | 15.0152 | 9.4307 | -0.17422 | -9.5705 | -21.0444 | 22.0591 | 21.7205 | 21.3211 | 20.6859 | 19.7445 | 18.6997 | 17.5778 | 16.313 | 14.8743 | 12.5775 | 5.2496 | -6.8786 | -15.7778 | -20.9968
|  | LW |  |  | 23.1732 | 22.6046 | 21.8123 | 20.9335 | 19.4051 | 17.7863 | 16.028 | 14.1511 | 11.9016 | 9.4486 | 1.6757 | -9.0171 | -14.8521 | -18.5436 | 22.3365 | 22.0279 | 21.548 | 21.006 | 20.2208 | 19.376 | 18.4186 | 17.3825 | 16.1035 | 14.6855 | 10.0613 | 4.0924 | 1.3469 | -0.5012 | 21.8334 | 21.3456 | 20.6905 | 19.966 | 18.6152 | 17.1585 | 15.5658 | 13.8671 | 11.8133 | 9.5073 | 2.2243 | -7.4298 | -12.3556 | -15.3894
|  | ST |  |  | 23.7968 | 23.6239 | 23.423 | 23.1874 | 22.7867 | 22.3533 | 21.8597 | 21.3158 | 20.6573 | 19.9498 | 16.9139 | 7.552 | 1.1861 | -3.2833 | 22.5838 | 22.4104 | 22.2109 | 21.9776 | 21.6047 | 21.2004 | 20.734 | 20.2159 | 19.6 | 18.9751 | 16.0863 | 7.1767 | -1.2941 | -11.9909 | 22.4009 | 22.2706 | 22.1191 | 21.9404 | 21.6325 | 21.2987 | 20.9173 | 20.4609 | 19.887 | 19.2417 | 16.3582 | 7.6675 | 2.1379 | -1.5679
|  | SP |  |  | 23.8561 | 23.6479 | 23.4158 | 23.1617 | 22.8706 | 22.5608 | 22.2287 | 21.8459 | 21.4055 | 20.8793 | 18.799 | 12.2922 | 6.6128 | 3.6536 | 22.6033 | 22.3834 | 22.1316 | 21.8521 | 21.5231 | 21.1624 | 20.7589 | 20.2943 | 19.7564 | 19.0855 | 15.9898 | 6.4541 | -7.2594 | -28.195 | 22.4528 | 22.3019 | 22.1326 | 21.9463 | 21.7247 | 21.4879 | 21.2336 | 20.9394 | 20.56 | 20.0991 | 18.1747 | 12.1243 | 7.0246 | 4.5907
COWLEY GSP | OXFORD (OSNEY) BSP | MINIMUM HEADROOM | SP 50148 05901 | YES | 29.9404 | 28.0073 | 25.6859 | 23.1196 | 19.2847 | 15.0823 | 10.6902 | 5.8644 | 0.40462 | -4.6216 | -17.8817 | -34.5412 | -45.6627 | -54.1076 | 40.3145 | 39.1921 | 37.8172 | 36.1733 | 34.1806 | 31.8964 | 29.4427 | 26.705 | 23.404 | 20.3446 | 12.3032 | -2.4547 | -16.1236 | -40.1617 | 27.7787 | 26.5089 | 24.4318 | 22.0693 | 18.6481 | 14.9148 | 10.9669 | 6.6158 | 1.5667 | -3.0909 | -15.3637 | -30.3781 | -39.4177 | -46.609
|  | CT |  |  | 30.6728 | 29.2032 | 27.3568 | 25.2065 | 22.3448 | 19.1789 | 16.0092 | 12.4379 | 8.5329 | 3.629 | -9.3075 | -30.2171 | -45.6627 | -54.1076 | 40.3467 | 39.2203 | 37.8366 | 36.1733 | 34.2621 | 32.1339 | 29.9253 | 27.4223 | 24.6287 | 21.3003 | 12.3032 | -2.4547 | -16.1236 | -32.7151 | 27.9251 | 27.1988 | 25.8812 | 23.8777 | 21.3094 | 18.4696 | 15.6123 | 12.3955 | 8.8489 | 4.314 | -7.6369 | -26.3191 | -39.4177 | -46.609
|  | LW |  |  | 29.9404 | 28.0073 | 25.6859 | 23.1196 | 19.2847 | 15.0823 | 10.6902 | 5.8644 | 0.40462 | -4.6216 | -17.8817 | -34.5412 | -42.311 | -47.4947 | 40.3145 | 39.1921 | 37.8172 | 36.2423 | 34.1806 | 31.8964 | 29.4427 | 26.705 | 23.404 | 20.3446 | 12.4716 | 3.3442 | -0.17409 | -2.597 | 27.7787 | 26.5089 | 24.4318 | 22.0693 | 18.6481 | 14.9148 | 10.9669 | 6.6158 | 1.5667 | -3.0909 | -15.3637 | -30.3781 | -36.7788 | -41.008
|  | ST |  |  | 31.8256 | 31.08 | 30.1379 | 29.0664 | 27.6405 | 26.0063 | 24.3092 | 22.3708 | 20.2191 | 18.3023 | 11.1521 | -4.7419 | -14.3337 | -20.3632 | 41.1098 | 40.4457 | 39.6315 | 38.653 | 37.4662 | 36.11 | 34.671 | 33.0283 | 31.1935 | 29.549 | 23.1286 | 8.2824 | -4.3334 | -19.5899 | 28.3787 | 27.9361 | 27.4052 | 26.756 | 26.0408 | 24.7727 | 23.2539 | 21.5261 | 19.5959 | 17.8792 | 11.1714 | -3.6681 | -12.143 | -17.2232
|  | SP |  |  | 31.941 | 31.2269 | 30.3786 | 29.4398 | 28.2142 | 26.816 | 25.3448 | 23.6527 | 21.9048 | 20.2322 | 14.7819 | 0.5844 | -9.7919 | -14.978 | 41.1249 | 40.4383 | 39.6176 | 38.6541 | 37.5684 | 36.3174 | 34.9511 | 33.3693 | 31.6604 | 29.9683 | 23.9205 | 7.4127 | -12.2951 | -40.1617 | 28.4063 | 27.9845 | 27.4828 | 26.8833 | 26.2718 | 25.52 | 24.2446 | 22.7604 | 21.2101 | 19.7396 | 14.7378 | 1.445 | -8.0124 | -12.4531
WILLESDEN GSP | PERIVALE | MINIMUM HEADROOM | TQ1755582965 | NO | 31.8543 | 57.2197 | 56.9347 | 56.6191 | 56.0401 | 55.4266 | 54.7726 | 54.0735 | 53.2349 | 52.3285 | 49.2954 | 44.9638 | 41.0756 | 38.6306 | 24.5326 | 57.9988 | 57.8433 | 57.6402 | 57.376 | 57.0685 | 56.7274 | 56.3585 | 55.8953 | 55.3905 | 53.6068 | 49.6515 | 45.7774 | 38.1989 | 28.1953 | 55.5743 | 55.2964 | 54.9868 | 54.4421 | 53.8625 | 53.2378 | 52.5663 | 51.7527 | 50.8702 | 47.9757 | 44.1302 | 40.8395 | 38.7972
|  | CT |  |  | 31.9519 | 57.3852 | 57.1892 | 56.9267 | 56.5348 | 56.1177 | 55.6758 | 55.201 | 54.6509 | 53.7706 | 50.7787 | 45.2006 | 41.0756 | 38.6306 | 24.5326 | 57.9988 | 57.8433 | 57.6402 | 57.376 | 57.0912 | 56.7815 | 56.4436 | 56.0418 | 55.4935 | 53.6068 | 49.6515 | 45.7774 | 41.1312 | 28.277 | 55.7159 | 55.5246 | 55.2575 | 54.8778 | 54.4724 | 54.0403 | 53.574 | 53.0299 | 52.1815 | 49.3342 | 44.3688 | 40.8395 | 38.7972
|  | LW |  |  | 31.8543 | 57.2197 | 56.9347 | 56.6191 | 56.0401 | 55.4266 | 54.7726 | 54.0735 | 53.2349 | 52.3285 | 49.2954 | 44.9638 | 42.6261 | 41.0901 | 24.5327 | 58.0048 | 57.846 | 57.6662 | 57.3784 | 57.0685 | 56.7274 | 56.3585 | 55.8953 | 55.3905 | 53.7159 | 51.4909 | 50.3741 | 49.6031 | 28.1953 | 55.5743 | 55.2964 | 54.9868 | 54.4421 | 53.8625 | 53.2378 | 52.5663 | 51.7527 | 50.8702 | 47.9757 | 44.1302 | 42.1709 | 40.9377
|  | ST |  |  | 32.1057 | 57.6363 | 57.5539 | 57.4597 | 57.3154 | 57.1522 | 56.9702 | 56.7634 | 56.499 | 56.1843 | 54.9021 | 50.8324 | 48.1394 | 46.3539 | 24.614 | 58.1497 | 58.0621 | 57.9621 | 57.8211 | 57.6623 | 57.4818 | 57.276 | 57.0173 | 56.7269 | 55.5599 | 51.9803 | 48.4328 | 44.0442 | 28.4314 | 55.9675 | 55.8896 | 55.7989 | 55.6564 | 55.4943 | 55.3117 | 55.1027 | 54.8367 | 54.5299 | 53.2651 | 49.4352 | 47.1359 | 45.6707
|  | SP |  |  | 32.1286 | 57.6626 | 57.5829 | 57.5003 | 57.3814 | 57.2491 | 57.1089 | 56.9528 | 56.7643 | 56.5364 | 55.6864 | 52.9925 | 50.3741 | 49.0768 | 24.6164 | 58.1509 | 58.0543 | 57.9495 | 57.8106 | 57.6527 | 57.477 | 57.2785 | 57.0382 | 56.7416 | 55.6057 | 51.9294 | 46.3446 | 38.1989 | 28.453 | 55.9886 | 55.9098 | 55.8282 | 55.7148 | 55.5871 | 55.4508 | 55.2974 | 55.1115 | 54.8878 | 54.0461 | 51.4341 | 49.2238 | 48.2072
MANNINGTON GSP | POOLE PS (HAMWORTHY) | MINIMUM HEADROOM | SZ0021890892 | YES | 44.3742 | 43.5225 | 42.5114 | 41.7176 | 40.1592 | 38.3402 | 36.4869 | 34.5685 | 32.4024 | 30.1273 | 24.1018 | 17.0827 | 11.7885 | 8.5519 | 31.1635 | 30.8765 | 30.5572 | 30.2519 | 29.8371 | 28.7844 | 27.1327 | 25.4739 | 22.4535 | 21.8162 | 19.8945 | 15.796 | 9.0412 | 1.1331 | 27.2369 | 26.5346 | 25.6819 | 24.9781 | 23.6312 | 22.0388 | 20.4008 | 18.6971 | 16.7601 | 14.6304 | 9.1727 | 2.8329 | -1.8856 | -4.7176
|  | CT |  |  | 44.5641 | 43.8388 | 43.0037 | 42.3053 | 41.0562 | 39.5747 | 38.0824 | 36.5393 | 34.8473 | 32.6255 | 26.5246 | 17.9266 | 11.7885 | 8.5519 | 31.1635 | 30.8765 | 30.5572 | 30.2519 | 29.8371 | 29.2719 | 28.69 | 28.0905 | 27.4196 | 26.6948 | 24.0213 | 18.2602 | 13.3542 | 8.6606 | 27.4008 | 26.8106 | 26.1196 | 25.4971 | 24.424 | 23.1331 | 21.8215 | 20.4578 | 18.9564 | 16.9219 | 11.4202 | 3.6254 | -1.8856 | -4.7176
|  | LW |  |  | 44.3742 | 43.5225 | 42.5114 | 41.7176 | 40.1592 | 38.3402 | 36.4869 | 34.5685 | 32.4024 | 30.1273 | 24.1018 | 17.0827 | 13.4723 | 11.3741 | 31.1902 | 30.895 | 30.5654 | 30.2659 | 29.8403 | 29.2373 | 28.5926 | 27.9195 | 27.1218 | 26.2248 | 22.9632 | 18.9614 | 17.1024 | 15.8011 | 27.2369 | 26.5346 | 25.6819 | 24.9781 | 23.6312 | 22.0388 | 20.4008 | 18.6971 | 16.7601 | 14.6304 | 9.1727 | 2.8329 | -0.42554 | -2.2768
|  | ST |  |  | 44.8383 | 44.394 | 43.912 | 43.5832 | 42.9218 | 42.0766 | 41.2242 | 40.3538 | 39.3987 | 37.9408 | 33.5066 | 25.74 | 21.5046 | 19.0394 | 31.2821 | 31.0754 | 30.8519 | 30.6729 | 30.3642 | 29.9076 | 29.4375 | 28.9543 | 28.4142 | 27.4034 | 24.1632 | 18.4114 | 15.3523 | 10.9368 | 27.6601 | 27.3308 | 26.9651 | 26.6923 | 26.1511 | 25.4358 | 24.7035 | 23.9502 | 23.1193 | 21.7929 | 17.6502 | 10.5483 | 6.6426 | 4.4508
|  | SP |  |  | 44.8863 | 44.4615 | 44.0124 | 43.711 | 43.1368 | 41.1679 | 39.1906 | 37.2081 | 33.8443 | 32.834 | 29.9328 | 23.9406 | 19.5312 | 17.7989 | 31.2916 | 31.0895 | 30.87 | 30.6979 | 30.4256 | 28.7844 | 27.1327 | 25.4739 | 22.4535 | 21.8162 | 19.8945 | 15.796 | 9.0412 | 1.1331 | 27.704 | 27.3909 | 27.0543 | 26.8054 | 26.3505 | 24.5091 | 22.6479 | 20.7766 | 17.5296 | 16.6399 | 14.0012 | 8.4975 | 4.6502 | 3.1624
LOVEDEAN GSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ6341099735 | NO | 22.9785 | 20.5402 | 17.9239 | 14.9232 | 10.0065 | 4.714 | -0.47689 | -6.0395 | -12.6246 | -19.5591 | -42.2927 | -73.296 | -92.8351 | -106.8209 | 4.2102 | 2.4345 | 0.60381 | -1.7103 | -4.7822 | -8.127 | -11.5103 | -15.2471 | -19.5899 | -24.841 | -43.3925 | -82.2707 | -159.8385 | -295.168 | 12.9984 | 10.9355 | 8.6817 | 6.0954 | 1.9618 | -2.5098 | -6.9656 | -11.7658 | -17.5149 | -23.6175 | -44.0667 | -71.768 | -87.5039 | -98.8524
|  | CT |  |  | 23.7101 | 21.8249 | 19.9559 | 17.3283 | 13.5656 | 9.4858 | 5.7134 | 1.6334 | -3.1575 | -9.8846 | -31.8304 | -68.8263 | -92.8351 | -106.8209 | 4.2102 | 2.4345 | 0.60381 | -1.7103 | -4.7822 | -8.127 | -11.5103 | -15.2471 | -19.5899 | -24.841 | -43.3925 | -82.2707 | -128.7467 | -196.48 | 13.6296 | 11.9781 | 10.3065 | 7.9793 | 4.7669 | 1.2747 | -2.0145 | -5.5859 | -9.8015 | -15.6329 | -34.6955 | -67.3001 | -87.5039 | -98.8524
|  | LW |  |  | 22.9785 | 20.5402 | 17.9239 | 14.9232 | 10.0065 | 4.714 | -0.47689 | -6.0395 | -12.6246 | -19.5591 | -42.2927 | -73.296 | -86.6395 | -95.3101 | 4.4749 | 3.1564 | 1.7632 | 0.14766 | -2.3429 | -5.029 | -7.7128 | -10.6058 | -14.1079 | -17.8327 | -30.1617 | -47.1234 | -53.6156 | -57.9467 | 12.9984 | 10.9355 | 8.6817 | 6.0954 | 1.9618 | -2.5098 | -6.9656 | -11.7658 | -17.5149 | -23.6175 | -44.0667 | -71.768 | -83.0698 | -90.2541
|  | ST |  |  | 24.8474 | 23.8511 | 22.9387 | 21.8264 | 20.1581 | 18.3191 | 16.6331 | 14.7508 | 12.3696 | 9.7018 | -0.32683 | -24.7415 | -40.0102 | -49.8911 | 4.8551 | 3.572 | 2.2747 | 0.76958 | -1.3023 | -3.5763 | -5.9405 | -8.6048 | -11.7553 | -15.0544 | -27.4017 | -62.3242 | -106.4302 | -172.5515 | 14.7044 | 13.8879 | 13.1152 | 12.1653 | 10.7074 | 9.0825 | 7.5519 | 5.8388 | 3.7027 | 1.3505 | -7.642 | -29.6954 | -42.6671 | -50.6898
|  | SP |  |  | 25.0366 | 24.0469 | 23.1563 | 22.1081 | 20.8246 | 19.414 | 18.0887 | 16.6416 | 14.8839 | 12.8142 | 5.349 | -12.8145 | -27.567 | -35.2937 | 4.8221 | 3.443 | 1.9604 | 0.26354 | -2.1146 | -4.8109 | -7.7426 | -11.0409 | -14.9319 | -19.2734 | -35.8349 | -81.9328 | -159.8385 | -295.168 | 14.8811 | 14.0633 | 13.3043 | 12.4089 | 11.3039 | 10.0609 | 8.8598 | 7.541 | 5.9368 | 4.0671 | -2.6481 | -19.2383 | -32.5312 | -38.9631
BRAMLEY (FLEE) | PYESTOCK BSP | MINIMUM HEADROOM | SU8298354548 | YES | 42.6725 | 30.8653 | 19.0077 | 7.1461 | -5.0494 | -5.8493 | -6.6942 | -7.6031 | -8.781 | -9.9946 | -12.291 | -15.3325 | -17.9572 | -19.5865 | 45.6664 | 31.0998 | 16.4508 | 1.802 | -12.9123 | -13.4262 | -13.9905 | -14.6134 | -15.5664 | -16.4337 | -17.7744 | -20.3282 | -22.6248 | -25.3703 | 43.0525 | 28.3666 | 13.5988 | -1.1631 | -16.2143 | -17.0161 | -17.8778 | -18.817 | -20.1446 | -21.3731 | -23.5152 | -26.2779 | -28.3201 | -29.6022
|  | CT |  |  | 42.7977 | 31.0864 | 19.3127 | 7.5329 | -4.3877 | -4.9032 | -5.4146 | -5.984 | -6.7593 | -8.0853 | -10.7153 | -14.7813 | -17.9572 | -19.5865 | 45.6664 | 31.0998 | 16.4508 | 1.802 | -12.8929 | -13.3238 | -13.7738 | -14.2864 | -14.9916 | -15.9528 | -17.7264 | -20.3282 | -22.6248 | -25.0692 | 43.1214 | 28.5109 | 13.8024 | -0.9041 | -15.7214 | -16.2781 | -16.8415 | -17.4777 | -18.3438 | -19.6353 | -22.1017 | -25.7489 | -28.3201 | -29.6022
|  | LW |  |  | 42.6725 | 30.8653 | 19.0077 | 7.1461 | -5.0494 | -5.8493 | -6.6942 | -7.6031 | -8.781 | -9.9946 | -12.291 | -15.3325 | -16.6991 | -17.4931 | 45.6906 | 31.1223 | 16.488 | 1.8611 | -12.9123 | -13.4262 | -13.9905 | -14.6134 | -15.5664 | -16.4337 | -17.7744 | -19.3942 | -19.9973 | -20.3473 | 43.0525 | 28.3666 | 13.5988 | -1.1631 | -16.2143 | -17.0161 | -17.8778 | -18.817 | -20.1446 | -21.3731 | -23.5152 | -26.2779 | -27.4562 | -28.1009
|  | ST |  |  | 43.0601 | 31.5159 | 19.9267 | 8.3332 | -3.3067 | -3.522 | -3.7584 | -4.0188 | -4.3239 | -4.6612 | -6.566 | -9.8478 | -11.4794 | -12.6114 | 45.8946 | 31.4747 | 16.989 | 2.5031 | -12.0244 | -12.269 | -12.5413 | -12.8434 | -13.2023 | -13.5541 | -15.3277 | -18.234 | -20.1928 | -22.501 | 43.4293 | 29.0158 | 14.5257 | 0.037853 | -14.5076 | -14.7678 | -15.0549 | -15.3715 | -15.7474 | -16.137 | -18.1453 | -21.2843 | -22.7963 | -23.7727
|  | SP |  |  | 43.0808 | 31.5477 | 19.9821 | 8.4335 | -3.147 | -3.3125 | -3.467 | -3.6544 | -3.8784 | -4.1464 | -5.2153 | -9.0817 | -10.5975 | -11.2815 | 45.8956 | 31.4732 | 16.9953 | 2.5397 | -11.9374 | -12.1452 | -12.3499 | -12.6009 | -12.8948 | -13.2245 | -14.574 | -18.4695 | -21.4011 | -25.3703 | 43.4453 | 29.0389 | 14.5738 | 0.14 | -14.3323 | -14.5324 | -14.718 | -14.9496 | -15.2236 | -15.5374 | -16.828 | -20.5553 | -21.9943 | -22.6165
BRAMLEY (FLEE) | READING BSP | MINIMUM HEADROOM | SU7459173788 | YES | 83.9915 | 80.5694 | 76.8556 | 72.7104 | 65.8438 | 58.3228 | 50.2193 | 41.3196 | 30.4209 | 19.5785 | -7.543 | -41.1728 | -64.1475 | -80.9605 | 65.0728 | 63.3217 | 61.3707 | 58.5949 | 54.894 | 50.6004 | 45.8117 | 40.4525 | 33.4625 | 26.5942 | 10.7167 | -17.371 | -43.3822 | -90.6471 | 56.9657 | 53.7743 | 50.2939 | 46.4068 | 40.1247 | 33.2322 | 25.7484 | 17.4971 | 7.2624 | -2.8978 | -27.7982 | -58.2773 | -77.4068 | -91.1681
|  | CT |  |  | 85.2489 | 82.7348 | 79.8602 | 76.4455 | 71.6436 | 66.2877 | 60.7292 | 54.5601 | 47.3684 | 36.3581 | 8.6725 | -33.689 | -64.1475 | -80.9605 | 65.2962 | 63.6426 | 61.4004 | 58.5949 | 55.2473 | 51.4715 | 47.396 | 42.8197 | 37.3832 | 29.8051 | 11.2916 | -17.371 | -43.3822 | -72.2387 | 58.0173 | 55.6279 | 52.8815 | 49.6197 | 45.1846 | 40.2377 | 35.0633 | 29.3034 | 22.5469 | 12.2371 | -13.1703 | -51.1541 | -77.4068 | -91.1681
|  | LW |  |  | 83.9915 | 80.5694 | 76.8556 | 72.7104 | 65.8438 | 58.3228 | 50.2193 | 41.3196 | 30.4209 | 19.5785 | -7.543 | -41.1728 | -56.9359 | -66.0709 | 65.0728 | 63.3217 | 61.3707 | 58.7233 | 54.894 | 50.6004 | 45.8117 | 40.4525 | 33.4625 | 26.5942 | 10.7167 | -7.9402 | -15.7676 | -20.4954 | 56.9657 | 53.7743 | 50.2939 | 46.4068 | 40.1247 | 33.2322 | 25.7484 | 17.4971 | 7.2624 | -2.8978 | -27.7982 | -58.2773 | -71.904 | -79.6046
|  | ST |  |  | 87.5751 | 86.4769 | 85.2005 | 83.6389 | 81.4209 | 78.8265 | 76.0267 | 72.8958 | 69.2306 | 64.9998 | 46.4694 | 13.2161 | -5.895 | -18.4944 | 66.4868 | 65.5567 | 64.5443 | 63.3436 | 61.7531 | 59.5069 | 57.0225 | 54.2261 | 50.9447 | 47.2889 | 31.3285 | 1.2486 | -22.1054 | -49.5876 | 60.2689 | 59.2465 | 58.0454 | 56.577 | 54.5336 | 52.1441 | 49.542 | 46.6228 | 43.1765 | 39.2292 | 21.6118 | -9.558 | -26.536 | -37.2608
|  | SP |  |  | 87.7965 | 86.7432 | 85.6526 | 84.4085 | 82.4875 | 79.2118 | 75.8455 | 72.0808 | 66.8994 | 63.3057 | 49.8913 | 17.003 | -2.5805 | -12.2143 | 66.5287 | 65.5793 | 64.5729 | 63.4317 | 61.9518 | 58.9843 | 55.7287 | 52.0878 | 46.9478 | 43.4324 | 29.9248 | -5.5489 | -41.6096 | -90.6471 | 60.4674 | 59.4765 | 58.4478 | 57.2691 | 55.5513 | 52.4944 | 49.3376 | 45.798 | 40.8515 | 37.5292 | 25.0554 | -6.1757 | -24.1698 | -32.4844
BRAMLEY (FLEE) | READING TOWN BSP | MINIMUM HEADROOM | SU7154074122 | YES | 57.8379 | 55.658 | 52.9718 | 50.1789 | 46.4118 | 42.5079 | 38.5397 | 34.4003 | 29.8326 | 25.1413 | 11.3534 | -4.1791 | -13.4559 | -20.81 | 45.575 | 44.1976 | 42.6164 | 40.9404 | 38.9069 | 36.7859 | 34.5379 | 32.1876 | 29.6584 | 27.0169 | 18.8587 | 5.4605 | -7.1224 | -31.3725 | 54.8619 | 52.8842 | 50.4951 | 47.9921 | 44.6886 | 41.2407 | 37.6413 | 33.8486 | 29.5977 | 25.1982 | 12.5611 | -1.3188 | -8.7129 | -14.8994
|  | CT |  |  | 58.4277 | 56.6169 | 54.2991 | 51.8392 | 48.8571 | 45.7722 | 42.8093 | 39.7167 | 36.3949 | 31.865 | 18.3412 | -0.63975 | -13.4559 | -20.81 | 45.7046 | 44.3731 | 42.7743 | 40.9404 | 38.9925 | 36.9812 | 34.9061 | 32.7187 | 30.4578 | 27.6224 | 18.8587 | 5.4605 | -7.1224 | -22.4572 | 55.3024 | 53.6233 | 51.5347 | 49.2895 | 46.6461 | 43.8937 | 41.1623 | 38.2782 | 35.1844 | 30.9633 | 18.6047 | 2.0943 | -8.7129 | -14.8994
|  | LW |  |  | 57.8379 | 55.658 | 52.9718 | 50.1789 | 46.4118 | 42.5079 | 38.5397 | 34.4003 | 29.8326 | 25.1413 | 11.3534 | -4.1791 | -11.3672 | -15.9299 | 45.575 | 44.1976 | 42.6164 | 40.965 | 38.9069 | 36.7859 | 34.5379 | 32.1876 | 29.6584 | 27.0169 | 19.177 | 11.0259 | 7.6362 | 5.3749 | 54.8619 | 52.8842 | 50.4951 | 47.9921 | 44.6886 | 41.2407 | 37.6413 | 33.8486 | 29.5977 | 25.1982 | 12.5611 | -1.3188 | -7.2143 | -10.9124
|  | ST |  |  | 59.439 | 58.3089 | 56.8836 | 55.4359 | 53.7991 | 52.1261 | 50.441 | 48.6812 | 46.8052 | 44.8112 | 37.1919 | 23.2975 | 14.7063 | 9.2055 | 46.1245 | 45.077 | 43.8914 | 42.6841 | 41.4621 | 40.0939 | 38.6146 | 37.0467 | 35.4637 | 33.8106 | 27.5493 | 15.5056 | 3.8622 | -10.878 | 56.3132 | 55.2962 | 54.062 | 52.7857 | 51.3278 | 49.8237 | 48.2412 | 46.5576 | 44.7896 | 42.935 | 35.6884 | 22.4275 | 14.9717 | 10.5519
|  | SP |  |  | 59.5356 | 58.4437 | 57.1241 | 55.805 | 54.4186 | 53.0167 | 51.5756 | 50.0762 | 48.5762 | 46.9046 | 41.035 | 29.5691 | 20.686 | 16.1023 | 46.144 | 45.1043 | 43.9324 | 42.7438 | 41.5618 | 40.2522 | 38.8035 | 37.2598 | 35.7396 | 34.0437 | 27.8787 | 14.6701 | -3.9815 | -31.3725 | 56.3983 | 55.4061 | 54.2708 | 53.1158 | 51.9216 | 50.6961 | 49.3588 | 47.9292 | 46.5295 | 44.9815 | 39.4833 | 28.2844 | 20.0791 | 16.2173
MANNINGTON GSP | REDHILL BSP | MINIMUM HEADROOM | SZ0851296149 | YES | 53.5797 | 51.6398 | 49.4058 | 46.9396 | 43.0853 | 39.0047 | 34.8342 | 30.4288 | 25.1851 | 19.4531 | 4.6894 | -14.1708 | -33.6792 | -44.7718 | 48.5489 | 47.2908 | 45.7976 | 44.1614 | 41.9544 | 39.5948 | 37.0937 | 34.4426 | 30.9658 | 27.0747 | 17.7871 | 4.7061 | -7.2011 | -18.4182 | 51.1831 | 49.4364 | 47.3702 | 45.0901 | 41.581 | 37.8573 | 34.001 | 29.9192 | 25.0229 | 19.6408 | 5.7438 | -11.1805 | -27.6678 | -37.1131
|  | CT |  |  | 54.1329 | 52.5812 | 51.0143 | 48.7622 | 45.9477 | 42.9606 | 39.9475 | 36.7492 | 33.1393 | 27.4147 | 11.0906 | -13.97 | -33.6792 | -44.7718 | 48.6566 | 47.4889 | 46.3013 | 44.5957 | 42.7108 | 40.7046 | 38.6217 | 36.4046 | 33.6744 | 29.7656 | 19.0567 | 4.7061 | -7.2011 | -18.4182 | 51.6602 | 50.2601 | 48.8184 | 46.7108 | 44.1244 | 41.3762 | 38.5666 | 35.58 | 32.1897 | 26.8503 | 11.552 | -10.6011 | -27.6678 | -37.1131
|  | LW |  |  | 53.5797 | 51.6398 | 49.4058 | 46.9396 | 43.0853 | 39.0047 | 34.8342 | 30.4288 | 25.1851 | 19.4531 | 4.6894 | -14.1708 | -24.5798 | -31.1926 | 48.5489 | 47.2908 | 45.7976 | 44.1614 | 41.9544 | 39.5948 | 37.0937 | 34.4426 | 30.9658 | 27.0747 | 17.7871 | 7.5887 | 2.8451 | -0.31409 | 51.1831 | 49.4364 | 47.3702 | 45.0901 | 41.581 | 37.8573 | 34.001 | 29.9192 | 25.0229 | 19.6408 | 5.7438 | -11.1805 | -19.8703 | -25.3806
|  | ST |  |  | 54.9943 | 54.0344 | 53.1156 | 52.1241 | 50.7901 | 49.3523 | 47.9282 | 46.4242 | 44.7254 | 42.9805 | 35.8284 | 16.8806 | 6.0894 | -1.8152 | 49.2338 | 48.4432 | 47.6699 | 46.8474 | 45.7758 | 44.623 | 43.4342 | 42.1799 | 40.7575 | 39.3486 | 33.2124 | 18.2015 | 8.6923 | -1.4685 | 52.4845 | 51.6457 | 50.8187 | 49.9293 | 48.7124 | 47.398 | 46.0642 | 44.6525 | 43.0512 | 41.4174 | 34.6003 | 16.8196 | 7.4104 | 0.75033
|  | SP |  |  | 55.1293 | 54.1332 | 53.2222 | 52.2712 | 51.1515 | 49.9863 | 48.8657 | 47.6638 | 46.3549 | 44.931 | 39.7817 | 24.2824 | 13.5906 | 8.4015 | 49.2894 | 48.4378 | 47.6275 | 46.7884 | 45.8845 | 44.9291 | 43.9644 | 42.9231 | 41.7702 | 40.4336 | 35.4016 | 20.279 | 5.2607 | -12.6157 | 52.6084 | 51.7275 | 50.9021 | 50.0462 | 49.0452 | 48.0022 | 46.9719 | 45.8607 | 44.6457 | 43.3212 | 38.4572 | 23.791 | 14.0367 | 9.668
NURSLING GSP | ROWNHAMS | MINIMUM HEADROOM | SU3723416928 | NO | -39.4049 | -42.3454 | -96.9024 | -100.5582 | -106.0272 | -112.3363 | -119.274 | -126.7248 | -135.9611 | -145.2255 | -168.8596 | -197.1797 | -209.6659 | -216.4366 | -33.0588 | -34.9217 | -88.2387 | -90.5805 | -93.8341 | -97.7523 | -102.0726 | -106.6584 | -112.3012 | -117.9138 | -133.0114 | -151.0598 | -161.6678 | -178.968 | -30.3196 | -33.1418 | -87.4833 | -90.8764 | -96.2475 | -102.3939 | -109.2251 | -116.5031 | -125.3262 | -134.2101 | -157.7932 | -186.6256 | -199.4289 | -206.0916
|  | CT |  |  | -27.6612 | -29.909 | -83.5064 | -86.6907 | -90.7143 | -95.4609 | -100.6388 | -106.2543 | -112.6378 | -121.8914 | -145.7131 | -179.3797 | -202.1676 | -215.8027 | -21.9331 | -23.5578 | -76.5115 | -78.7687 | -81.4356 | -84.6906 | -88.2445 | -92.0421 | -96.3383 | -102.6559 | -118.4417 | -142.4956 | -161.6678 | -178.968 | -18.2181 | -20.2072 | -73.5431 | -76.2558 | -80.0449 | -84.6039 | -89.5592 | -94.8791 | -100.8675 | -109.6967 | -133.2696 | -169.0094 | -193.1314 | -205.0456
|  | LW |  |  | -39.4049 | -42.3454 | -96.9024 | -100.5582 | -106.0272 | -112.3363 | -119.274 | -126.7248 | -135.9611 | -145.2255 | -168.8596 | -197.1797 | -209.6659 | -216.4366 | -33.0588 | -34.9217 | -88.2387 | -90.5805 | -93.8341 | -97.7523 | -102.0726 | -106.6584 | -112.3012 | -117.9138 | -133.0114 | -151.0598 | -159.1777 | -163.6392 | -30.3196 | -33.1418 | -87.4833 | -90.8764 | -96.2475 | -102.3939 | -109.2251 | -116.5031 | -125.3262 | -134.2101 | -157.7932 | -186.6256 | -199.4289 | -206.0916
|  | ST |  |  | -26.04 | -27.2602 | -28.7151 | -30.2037 | -32.301 | -35.0028 | -37.9507 | -41.0719 | -44.6457 | -49.496 | -69.1979 | -100.9102 | -116.8754 | -126.5205 | -20.9693 | -21.9856 | -23.2468 | -24.5077 | -26.0733 | -28.1646 | -30.4528 | -32.8414 | -35.5614 | -39.5192 | -54.6339 | -80.927 | -97.4509 | -113.7526 | -16.8631 | -17.9692 | -19.3163 | -20.668 | -22.4899 | -24.8646 | -27.4431 | -30.1986 | -33.4719 | -38.0857 | -56.2352 | -86.8328 | -102.5344 | -111.9089
|  | SP |  |  | -25.8333 | -27.069 | -28.4311 | -29.7581 | -31.6358 | -37.4297 | -43.4366 | -49.5962 | -59.7256 | -63.4816 | -77.3812 | -108.1978 | -125.174 | -132.449 | -20.8851 | -21.9274 | -23.175 | -24.3877 | -25.8483 | -31.2041 | -36.742 | -42.3728 | -51.9428 | -55.1178 | -66.6045 | -93.5625 | -118.0662 | -146.324 | -16.6378 | -17.7002 | -18.9325 | -20.1184 | -21.8701 | -27.5038 | -33.322 | -39.2074 | -49.024 | -52.575 | -65.4273 | -94.3042 | -111.1164 | -118.2199
MANNINGTON GSP | SALISBURY | MINIMUM HEADROOM | SU1106531365 | YES | 60.8637 | 58.0873 | 54.8826 | 51.5926 | 46.8257 | 41.7738 | 36.5015 | 30.6665 | 23.612 | 16.7164 | 0.87028 | -15.3489 | -20.759 | -24.6472 | 55.0674 | 53.6122 | 51.8329 | 50.0615 | 47.6603 | 44.9786 | 42.1046 | 38.8468 | 34.5142 | 30.2713 | 21.4289 | 12.9907 | 3.4896 | -8.1242 | 59.5881 | 57.0708 | 54.1495 | 51.208 | 46.8844 | 42.2664 | 37.5129 | 32.2359 | 25.6896 | 19.2819 | 4.694 | -10.072 | -14.8501 | -18.1028
|  | CT |  |  | 62.9636 | 61.302 | 59.3568 | 56.9594 | 53.8914 | 50.5758 | 47.0567 | 43.009 | 38.2778 | 31.5979 | 16.2228 | -4.4153 | -18.4946 | -24.6472 | 55.7426 | 54.6329 | 53.295 | 51.7475 | 49.8269 | 47.677 | 45.3698 | 42.6444 | 39.3781 | 35.0778 | 25.3862 | 12.9907 | 3.4896 | -6.0665 | 61.548 | 60.0866 | 58.3531 | 56.3491 | 53.5727 | 50.4702 | 47.2481 | 43.5622 | 39.2873 | 33.2193 | 19.0486 | -0.28057 | -12.7002 | -18.1028
|  | LW |  |  | 60.8637 | 58.0873 | 54.8826 | 51.5926 | 46.8257 | 41.7738 | 36.5015 | 30.6665 | 23.612 | 16.7164 | 0.87028 | -15.3489 | -20.759 | -22.8759 | 55.0674 | 53.6122 | 51.8329 | 50.0615 | 47.6603 | 44.9786 | 42.1046 | 38.8468 | 34.5142 | 30.2713 | 21.4289 | 13.0963 | 10.8554 | 9.9511 | 59.5881 | 57.0708 | 54.1495 | 51.208 | 46.8844 | 42.2664 | 37.5129 | 32.2359 | 25.6896 | 19.2819 | 4.694 | -10.072 | -14.8501 | -16.7028
|  | ST |  |  | 64.1357 | 63.2129 | 62.1313 | 61.0211 | 59.4282 | 57.6359 | 55.7714 | 53.584 | 51.0966 | 48.5996 | 38.6904 | 20.6199 | 11.3871 | 6.0991 | 56.4465 | 55.7599 | 54.9128 | 54.0999 | 53.0167 | 51.7479 | 50.4812 | 48.9608 | 47.1444 | 45.4046 | 37.9328 | 23.8444 | 15.1366 | 5.9894 | 62.5651 | 61.73 | 60.7213 | 59.7451 | 58.3076 | 56.6767 | 55.0563 | 53.1776 | 50.9538 | 48.6776 | 39.6809 | 22.9318 | 14.383 | 9.4077
|  | SP |  |  | 64.4588 | 63.6287 | 62.6964 | 61.7669 | 60.0699 | 58.218 | 56.3829 | 54.2397 | 51.9545 | 49.2826 | 40.3802 | 19.2803 | 7.5862 | 1.9094 | 56.5566 | 55.8738 | 55.0561 | 54.3071 | 53.213 | 51.9499 | 50.7279 | 49.2595 | 47.6545 | 45.8568 | 39.3368 | 22.2843 | 8.3442 | -8.1242 | 62.8609 | 62.1174 | 61.2519 | 60.4685 | 58.8951 | 57.1595 | 55.5005 | 53.5862 | 51.5577 | 49.1649 | 41.0432 | 21.8316 | 10.945 | 5.6332
MANNINGTON GSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST8560523325 | YES | 53.3122 | 49.8941 | 46.0555 | 41.9372 | 36.5451 | 30.9339 | 24.3457 | 18.0463 | 10.5787 | 3.1321 | -15.0068 | -34.9259 | -40.18 | -43.2334 | 50.9009 | 48.9881 | 46.864 | 44.5863 | 41.8594 | 38.9993 | 35.1068 | 31.6247 | 27.1706 | 22.7449 | 13.187 | 3.1329 | -0.075577 | -5.0188 | 55.5584 | 52.3448 | 48.8873 | 45.1914 | 40.3395 | 35.2857 | 29.0765 | 23.2861 | 16.3746 | 9.4757 | -7.0602 | -25.1658 | -29.9471 | -32.7137
|  | CT |  |  | 55.8773 | 53.8234 | 51.6734 | 48.7713 | 45.2797 | 41.577 | 36.8737 | 32.4748 | 27.4674 | 20.5869 | 4.0799 | -20.1768 | -35.1073 | -41.1926 | 51.8396 | 50.4386 | 49.0186 | 47.0795 | 45.0052 | 42.7963 | 39.6336 | 36.8678 | 33.6256 | 29.3507 | 19.7112 | 7.2051 | -0.075577 | -5.0188 | 58.0198 | 56.1338 | 54.1776 | 51.5854 | 48.4243 | 45.0836 | 40.5744 | 36.5385 | 31.9705 | 25.6824 | 10.4106 | -12.0816 | -25.383 | -30.8156
|  | LW |  |  | 53.3122 | 49.8941 | 46.0555 | 41.9372 | 36.5451 | 30.9339 | 24.3457 | 18.0463 | 10.5787 | 3.1321 | -15.0068 | -34.9259 | -40.18 | -43.2334 | 50.9009 | 48.9881 | 46.864 | 44.5863 | 41.8594 | 38.9993 | 35.1068 | 31.6247 | 27.1706 | 22.7449 | 13.187 | 3.1329 | 0.70463 | -0.73703 | 55.5584 | 52.3448 | 48.8873 | 45.1914 | 40.3395 | 35.2857 | 29.0765 | 23.2861 | 16.3746 | 9.4757 | -7.0602 | -25.1658 | -29.9471 | -32.7137
|  | ST |  |  | 56.7781 | 55.3252 | 53.8752 | 52.2613 | 50.1126 | 47.8559 | 44.7916 | 42.169 | 39.2461 | 36.2431 | 24.4535 | 4.319 | -5.0622 | -10.3843 | 52.4225 | 51.3981 | 50.4164 | 49.3432 | 48.052 | 46.7021 | 44.4487 | 42.7471 | 40.8204 | 38.8861 | 30.8745 | 17.2369 | 11.1193 | 6.5419 | 58.8333 | 57.4921 | 56.1711 | 54.7306 | 52.806 | 50.795 | 47.7949 | 45.3871 | 42.713 | 39.9376 | 29.1797 | 10.4937 | 1.4984 | -3.5948
|  | SP |  |  | 57.1657 | 55.8182 | 54.5334 | 53.1554 | 50.6645 | 48.1279 | 44.835 | 41.9621 | 38.9736 | 35.4227 | 23.4878 | -2.5556 | -16.7987 | -24.7826 | 52.576 | 51.5623 | 50.6263 | 49.6432 | 48.2999 | 46.9301 | 44.699 | 42.9989 | 41.2037 | 39.1725 | 32.0999 | 15.2657 | 5.587 | -1.9851 | 59.1992 | 57.9664 | 56.8059 | 55.5878 | 53.3192 | 51.0228 | 47.781 | 45.1156 | 42.3507 | 39.0761 | 28.1304 | 4.0395 | -9.1594 | -16.3194
IVER 132KV | SLOUGH | MINIMUM HEADROOM | SU95578175 | NO | 37.4541 | 36.2979 | 34.9861 | 33.4608 | 22.8031 | 11.8719 | -3.2643 | -6.4066 | -10.2148 | -14.0474 | -24.723 | -39.7103 | -50.6298 | -58.1017 | 17.8084 | 17.2577 | 16.6701 | 15.999 | 4.7278 | -6.7328 | -23.3628 | -24.7972 | -26.8351 | -28.301 | -34.1309 | -44.2074 | -53.4925 | -66.5136 | 27.2071 | 26.092 | 24.7998 | 23.3019 | 10.7719 | -2.0383 | -20.1266 | -23.1877 | -26.9779 | -30.7757 | -40.8248 | -54.5577 | -63.4076 | -69.5978
|  | CT |  |  | 37.8927 | 37.0449 | 36.1015 | 34.7856 | 24.8557 | 14.6982 | 0.45466 | -1.7493 | -4.2951 | -8.2941 | -19.033 | -37.2238 | -50.6298 | -58.1017 | 17.9267 | 17.4529 | 16.9538 | 16.3089 | 5.269 | -5.9321 | -22.2552 | -23.3693 | -24.6547 | -26.4621 | -32.6601 | -44.2074 | -53.3281 | -61.8746 | 27.5327 | 26.6761 | 25.714 | 24.3616 | 12.4489 | 0.30265 | -16.9925 | -19.2128 | -21.7982 | -25.5808 | -35.6189 | -52.087 | -63.4076 | -69.5978
|  | LW |  |  | 37.4541 | 36.2979 | 34.9861 | 33.4608 | 22.8031 | 11.8719 | -3.2643 | -6.4066 | -10.2148 | -14.0474 | -24.723 | -39.7103 | -47.4026 | -51.9393 | 17.8084 | 17.2577 | 16.6701 | 15.999 | 4.7278 | -6.7328 | -23.3628 | -24.7972 | -26.5356 | -28.301 | -34.1309 | -43.1469 | -47.4221 | -50.0056 | 27.2071 | 26.092 | 24.7998 | 23.3019 | 10.7719 | -2.0383 | -20.1266 | -23.1877 | -26.9779 | -30.7757 | -40.8248 | -54.5577 | -61.2917 | -65.1598
|  | ST |  |  | 38.6326 | 38.2491 | 37.8312 | 37.2835 | 28.3662 | 19.2791 | 6.0996 | 5.0743 | 3.8324 | 2.0543 | -5.3239 | -20.5879 | -29.4712 | -35.1597 | 18.2602 | 17.9943 | 17.7346 | 17.4253 | 6.815 | -3.9343 | -19.8085 | -20.4297 | -21.1772 | -22.436 | -27.1284 | -38.1808 | -46.4504 | -54.2518 | 28.2929 | 27.9121 | 27.4893 | 26.9409 | 15.9856 | 4.8569 | -11.4089 | -12.4728 | -13.7653 | -15.5569 | -22.9624 | -37.394 | -45.3519 | -50.2203
|  | SP |  |  | 38.7451 | 38.3652 | 37.9856 | 37.5152 | 28.7538 | 18.6459 | 4.4787 | 2.4691 | -0.97547 | -2.2277 | -6.824 | -20.191 | -29.3347 | -33.6502 | 18.2985 | 18.0338 | 17.7815 | 17.4934 | 6.9437 | -4.9466 | -21.9468 | -23.691 | -26.8351 | -27.7401 | -30.9793 | -41.5066 | -53.4925 | -66.5136 | 28.3984 | 28.0081 | 27.6153 | 27.1404 | 16.3552 | 4.2212 | -13.0116 | -15.042 | -18.512 | -19.7754 | -24.4745 | -37.3067 | -45.7794 | -49.5211
NURSLING GSP | SOUTHAMPTON (2 X 60) | MINIMUM HEADROOM | SU4143512045 | NO | 26.3392 | 24.8473 | 23.18 | 21.6329 | 19.6145 | 17.714 | 15.8083 | 13.6271 | 11.1655 | 8.805 | 1.4516 | -9.4269 | -16.0277 | -22.237 | 25.846 | 25.1919 | 24.4735 | 23.8268 | 22.7151 | 21.516 | 20.2714 | 18.7735 | 17.0767 | 15.2828 | 9.2903 | -4.377 | -33.138 | -84.0318 | 21.4305 | 20.3531 | 19.1514 | 18.1249 | 16.7809 | 15.4855 | 14.0019 | 12.1827 | 10.1273 | 8.1737 | 1.9791 | -7.271 | -12.6613 | -17.6948
|  | CT |  |  | 26.8542 | 25.6438 | 24.268 | 22.9265 | 21.3112 | 19.8351 | 18.4406 | 16.7987 | 15.012 | 12.8434 | 6.1847 | -6.5844 | -16.0277 | -22.237 | 25.846 | 25.1919 | 24.4735 | 23.8268 | 22.7151 | 21.516 | 20.2714 | 18.7735 | 17.0767 | 15.2828 | 9.2903 | -3.8818 | -20.6786 | -46.2475 | 21.7612 | 20.874 | 19.8655 | 19.0154 | 17.9642 | 16.9798 | 16.0404 | 14.8632 | 13.5666 | 11.8669 | 6.3495 | -4.7057 | -12.6613 | -17.6948
|  | LW |  |  | 26.3392 | 24.8473 | 23.18 | 21.6329 | 19.6145 | 17.714 | 15.8083 | 13.6271 | 11.1655 | 8.805 | 1.4516 | -9.4269 | -15.5509 | -20.0594 | 25.8831 | 25.3006 | 24.6673 | 24.1319 | 23.3476 | 22.4997 | 21.625 | 20.5063 | 19.1974 | 17.8795 | 13.6646 | 7.7406 | 4.8474 | 2.6109 | 21.4305 | 20.3531 | 19.1514 | 18.1249 | 16.7809 | 15.4855 | 14.0019 | 12.1827 | 10.1273 | 8.1737 | 1.9791 | -7.271 | -12.1682 | -15.6261
|  | ST |  |  | 27.4701 | 26.7936 | 26.0751 | 25.5576 | 24.8857 | 24.2066 | 23.5455 | 22.6969 | 21.712 | 20.715 | 17.3444 | 8.6864 | 2.0239 | -2.5037 | 26.0913 | 25.618 | 25.1141 | 24.6879 | 24.178 | 23.6745 | 22.8297 | 21.7036 | 20.403 | 19.1562 | 14.6407 | 2.213 | -13.8126 | -38.3103 | 22.2263 | 21.7276 | 21.1964 | 20.8053 | 20.3425 | 19.9205 | 19.4961 | 18.8667 | 18.1069 | 17.3417 | 14.7 | 8.0731 | 3.2523 | -0.17135
|  | SP |  |  | 27.554 | 26.9409 | 26.2989 | 25.8563 | 25.3659 | 24.8498 | 24.3354 | 23.6609 | 22.9206 | 22.1234 | 19.6321 | 12.8747 | 6.1387 | 1.8723 | 26.0902 | 25.6191 | 25.1017 | 24.6582 | 24.0983 | 23.4176 | 22.3082 | 20.9514 | 19.3845 | 17.7824 | 11.9041 | -4.377 | -33.138 | -84.0318 | 22.2859 | 21.8345 | 21.3583 | 21.0228 | 20.6608 | 20.343 | 20.0248 | 19.5262 | 18.9589 | 18.381 | 16.5611 | 11.756 | 6.7985 | 3.4666
NURSLING GSP | SOUTHAMPTON (2 X 90) | MINIMUM HEADROOM | SU4143512045 | NO | 44.7403 | 42.9636 | 40.9418 | 38.4784 | 35.3355 | 31.3395 | 27.3515 | 23.1958 | 18.4287 | 13.5231 | -1.9003 | -23.3655 | -38.2924 | -49.7721 | 42.683 | 42.151 | 41.5809 | 40.8489 | 40.0624 | 36.4531 | 31.6586 | 26.7996 | 17.603 | 15.8336 | 10.0791 | -6.8782 | -30.6631 | -60.9049 | 28.8737 | 27.3069 | 25.4505 | 23.1975 | 20.3437 | 16.698 | 12.9949 | 9.1072 | 2.8615 | -0.17378 | -14.7484 | -34.3292 | -46.6561 | -56.4686
|  | CT |  |  | 45.4957 | 44.1699 | 42.6823 | 40.593 | 38.3204 | 35.2787 | 32.4007 | 29.3868 | 26.0172 | 21.2923 | 6.4011 | -18.9744 | -38.2924 | -49.7721 | 42.683 | 42.151 | 41.5809 | 40.8489 | 40.0624 | 38.8094 | 37.5694 | 36.2483 | 34.723 | 32.2516 | 23.5693 | 5.4496 | -11.5014 | -29.9567 | 29.4413 | 28.2283 | 26.8515 | 24.8556 | 22.6984 | 19.8334 | 17.0751 | 14.1621 | 10.8711 | 6.4521 | -7.4471 | -29.9512 | -46.6561 | -56.4686
|  | LW |  |  | 44.7403 | 42.9636 | 40.9418 | 38.4784 | 35.3355 | 31.3395 | 27.3515 | 23.1958 | 18.4287 | 13.5231 | -1.9003 | -23.3655 | -36.3222 | -44.4131 | 42.7645 | 42.2495 | 41.6953 | 41.0159 | 40.249 | 38.9428 | 37.4522 | 35.3089 | 32.8387 | 30.283 | 22.2693 | 9.4321 | 1.4975 | -3.4972 | 28.8737 | 27.3069 | 25.4505 | 23.1975 | 20.3437 | 16.698 | 12.9949 | 9.1072 | 4.5662 | -0.17378 | -14.7484 | -34.3292 | -45.5952 | -52.5261
|  | ST |  |  | 46.3525 | 45.6789 | 44.9547 | 44.0121 | 43.0424 | 41.4535 | 39.9279 | 38.3261 | 36.4278 | 32.9549 | 21.1006 | -1.2357 | -15.6928 | -24.5734 | 42.9515 | 42.5914 | 42.2243 | 41.7724 | 41.2129 | 40.1865 | 39.1788 | 38.1004 | 36.8251 | 34.0561 | 24.9733 | 7.5969 | -8.9939 | -25.9719 | 30.2985 | 29.7223 | 29.0824 | 28.2461 | 27.2619 | 25.7002 | 24.1787 | 22.5666 | 20.6625 | 17.2475 | 5.5556 | -16.0714 | -29.0716 | -36.5478
|  | SP |  |  | 46.4739 | 45.8367 | 45.1664 | 44.3263 | 43.5838 | 38.4285 | 33.3325 | 28.1685 | 18.6439 | 16.401 | 9.0076 | -7.9713 | -22.0963 | -29.1493 | 42.9589 | 42.6027 | 42.2348 | 41.7911 | 41.2764 | 36.4531 | 31.6586 | 26.7996 | 17.603 | 15.8336 | 10.0791 | -6.8782 | -30.6631 | -60.9049 | 30.4062 | 29.8392 | 29.2318 | 28.4795 | 27.7383 | 22.6286 | 17.5528 | 12.385 | 2.8615 | 0.6667 | -6.6511 | -23.2304 | -36.564 | -42.6938
EALING GSP | SOUTHFIELD ROAD | MINIMUM HEADROOM | TQ2054579745 | NO | 12.0376 | 30.1994 | 30.1552 | 30.1076 | 30.0322 | 29.9502 | 29.8665 | 29.776 | 29.6805 | 29.5816 | 29.2267 | 28.3371 | 27.2964 | 26.4124 | 21.114 | 36.2926 | 36.2681 | 36.2411 | 36.2103 | 36.1739 | 36.1306 | 36.0823 | 36.0268 | 35.9652 | 35.7239 | 34.3486 | 31.5596 | 26.6053 | 14.7658 | 29.9315 | 29.8914 | 29.8481 | 29.7781 | 29.7019 | 29.6237 | 29.539 | 29.4493 | 29.3562 | 29.0241 | 28.2544 | 27.4558 | 26.7584
|  | CT |  |  | 12.0431 | 30.2104 | 30.1702 | 30.125 | 30.0654 | 30.0009 | 29.9393 | 29.8727 | 29.8016 | 29.703 | 29.3583 | 28.3738 | 27.2964 | 26.4124 | 21.114 | 36.2926 | 36.2681 | 36.2411 | 36.2103 | 36.1757 | 36.138 | 36.0965 | 36.0503 | 36.0036 | 35.7796 | 34.7592 | 32.847 | 30.0164 | 14.7711 | 29.9422 | 29.906 | 29.8649 | 29.8101 | 29.7507 | 29.6938 | 29.6321 | 29.566 | 29.4729 | 29.1503 | 28.308 | 27.4558 | 26.7584
|  | LW |  |  | 12.0376 | 30.1994 | 30.1552 | 30.1076 | 30.0322 | 29.9502 | 29.8665 | 29.776 | 29.6805 | 29.5816 | 29.2267 | 28.3371 | 27.4538 | 26.683 | 21.1263 | 36.3179 | 36.3083 | 36.2981 | 36.2862 | 36.2734 | 36.2601 | 36.2458 | 36.2292 | 36.2125 | 36.1499 | 35.9029 | 35.5619 | 35.2672 | 14.7658 | 29.9315 | 29.8914 | 29.8481 | 29.7781 | 29.7019 | 29.6237 | 29.539 | 29.4493 | 29.3562 | 29.0241 | 28.2544 | 27.5526 | 26.9405
|  | ST |  |  | 12.0882 | 30.2706 | 30.2489 | 30.2252 | 30.1958 | 30.1625 | 30.1306 | 30.0944 | 30.0562 | 30.0151 | 29.8389 | 29.1854 | 28.5057 | 27.9462 | 21.1221 | 36.3031 | 36.2813 | 36.2575 | 36.2297 | 36.1977 | 36.1629 | 36.1241 | 36.0806 | 36.0383 | 35.8743 | 35.1417 | 33.3767 | 30.6737 | 14.8148 | 30.0004 | 29.9821 | 29.962 | 29.9365 | 29.9074 | 29.8793 | 29.8471 | 29.8128 | 29.7755 | 29.6163 | 29.038 | 28.4541 | 27.9835
|  | SP |  |  | 12.0903 | 30.2725 | 30.2523 | 30.2295 | 30.2065 | 30.1793 | 30.1509 | 30.1212 | 30.089 | 30.0558 | 29.9203 | 29.3931 | 28.7611 | 28.24 | 21.1201 | 36.2992 | 36.2742 | 36.2462 | 36.2128 | 36.1739 | 36.1306 | 36.0823 | 36.0268 | 35.9652 | 35.7239 | 34.3486 | 31.5596 | 26.6053 | 14.8168 | 30.0022 | 29.9854 | 29.9662 | 29.9468 | 29.9236 | 29.899 | 29.8731 | 29.8447 | 29.815 | 29.695 | 29.2369 | 28.6961 | 28.2597
LALEHAM | STAINES | MINIMUM HEADROOM | TQ0454572135 | NO | 244.7181 | 240.7907 | 236.1554 | 231.2895 | 224.6731 | 217.3941 | 209.6105 | 201.4951 | 192.3135 | 182.8745 | 156.4303 | 126.6694 | 110.9239 | 98.8128 | 205.8527 | 204.066 | 202.2973 | 200.4926 | 197.6089 | 193.6949 | 189.4508 | 184.9915 | 179.7434 | 174.2457 | 158.7443 | 139.0992 | 122.7569 | 106.6231 | 228.7628 | 225.3488 | 221.3048 | 217.0542 | 211.1639 | 204.7121 | 197.795 | 190.5523 | 182.2912 | 173.7353 | 149.6306 | 122.428 | 108.5083 | 98.22
|  | CT |  |  | 245.662 | 242.4099 | 238.6186 | 234.2221 | 228.9574 | 223.1176 | 217.0577 | 210.7798 | 204.0813 | 195.0669 | 169.2965 | 133.3638 | 110.9239 | 98.8128 | 205.9244 | 204.2433 | 202.5743 | 200.8046 | 198.6647 | 195.2061 | 191.5671 | 187.7566 | 183.547 | 178.1042 | 162.0793 | 139.0992 | 122.7569 | 106.6231 | 229.7357 | 226.8893 | 223.6238 | 219.8319 | 215.2152 | 210.118 | 204.8156 | 199.2933 | 193.3272 | 185.1813 | 161.821 | 128.6923 | 108.5083 | 98.22
|  | LW |  |  | 244.7181 | 240.7907 | 236.1554 | 231.2895 | 224.6731 | 217.3941 | 209.6105 | 201.4951 | 192.3135 | 182.8745 | 156.4303 | 126.6694 | 115.0336 | 108.0213 | 205.8527 | 204.066 | 202.2973 | 200.4926 | 197.6089 | 193.6949 | 189.4508 | 184.9915 | 179.7434 | 174.2457 | 158.7443 | 141.2486 | 135.7061 | 132.2259 | 228.7628 | 225.3488 | 221.3048 | 217.0542 | 211.1639 | 204.7121 | 197.795 | 190.5523 | 182.2912 | 173.7353 | 149.6306 | 122.428 | 112.2171 | 106.2844
|  | ST |  |  | 247.5888 | 245.6699 | 243.5462 | 241.3744 | 238.5862 | 235.4557 | 232.1332 | 228.693 | 225.0528 | 221.3028 | 205.6827 | 174.5591 | 157.957 | 148.7898 | 206.6459 | 205.4441 | 204.3707 | 203.3516 | 202.1461 | 200.8312 | 199.4071 | 197.4135 | 194.8388 | 192.1403 | 181.108 | 157.2674 | 141.4826 | 126.6681 | 231.3683 | 229.7959 | 228.1204 | 226.3533 | 224.035 | 221.4515 | 218.6843 | 215.7834 | 212.6179 | 209.2665 | 195.4017 | 167.1736 | 152.2027 | 144.1952
|  | SP |  |  | 247.8336 | 245.9747 | 244.005 | 242.0659 | 239.7264 | 237.1306 | 234.332 | 231.4456 | 228.5779 | 225.4977 | 214.1757 | 187.4019 | 168.5141 | 160.4425 | 206.7092 | 205.5378 | 204.4996 | 203.5368 | 202.4676 | 201.3206 | 200.0844 | 198.6781 | 196.5083 | 194.0656 | 185.0341 | 162.2046 | 137.685 | 110.4779 | 231.5946 | 230.0998 | 228.5566 | 227.0053 | 225.0808 | 222.9721 | 220.6768 | 218.2781 | 215.8185 | 213.0973 | 203.2 | 179.3437 | 162.0307 | 155.0549
MINETY GSP | STRATTON (2 X 60) | MINIMUM HEADROOM | SU1699888837 | NO | 10.8825 | 7.8772 | 4.4288 | 0.91934 | -3.8064 | -8.6551 | -13.5573 | -18.9117 | -25.2419 | -31.5181 | -45.9916 | -61.5062 | -67.2349 | -70.9342 | 9.5813 | 7.9615 | 6.0859 | 4.1691 | 1.7434 | -0.82313 | -3.5034 | -6.5504 | -10.4039 | -14.1434 | -22.0367 | -30.2654 | -36.873 | -42.943 | 2.7619 | 0.16535 | -2.8248 | -5.8973 | -10.0537 | -14.3586 | -18.7509 | -23.5591 | -29.2934 | -35.0126 | -48.0119 | -62.0459 | -67.2084 | -70.3584
|  | CT |  |  | 12.3251 | 10.0821 | 7.4402 | 4.563 | 1.0758 | -2.4972 | -6.0499 | -10.013 | -14.6136 | -20.6431 | -34.8122 | -53.2721 | -65.613 | -70.9342 | 9.8901 | 8.4928 | 6.8654 | 5.038 | 3.0396 | 0.92307 | -1.2432 | -3.6807 | -6.6053 | -10.305 | -18.6801 | -29.2694 | -36.873 | -42.943 | 4.0411 | 2.1643 | -0.05055 | -2.521 | -5.5977 | -8.7852 | -11.9849 | -15.5616 | -19.7505 | -25.2857 | -38.1074 | -54.686 | -65.6288 | -70.3584
|  | LW |  |  | 10.8825 | 7.8772 | 4.4288 | 0.91934 | -3.8064 | -8.6551 | -13.5573 | -18.9117 | -25.2419 | -31.5181 | -45.9916 | -61.5062 | -67.2349 | -70.1447 | 9.5813 | 7.9615 | 6.0859 | 4.1691 | 1.7434 | -0.82313 | -3.5034 | -6.5504 | -10.4039 | -14.1434 | -22.0367 | -30.2654 | -33.3627 | -34.9543 | 2.7619 | 0.16535 | -2.8248 | -5.8973 | -10.0537 | -14.3586 | -18.7509 | -23.5591 | -29.2934 | -35.0126 | -48.0119 | -62.0459 | -67.2084 | -69.8153
|  | ST |  |  | 34.9998 | 33.6446 | 10.6149 | 9.0439 | 7.0111 | 4.9012 | 2.8084 | 0.48466 | -2.1024 | -5.0458 | -15.7604 | -31.4294 | -39.5445 | -44.723 | 32.2692 | 31.4403 | 8.9836 | 7.9745 | 6.6996 | 5.3235 | 3.9246 | 2.3592 | 0.58943 | -1.4732 | -9.3892 | -21.1398 | -27.8302 | -33.9601 | 26.6399 | 25.5515 | 2.8191 | 1.5466 | -0.13438 | -1.9141 | -3.6971 | -5.7436 | -8.05 | -10.72 | -20.6927 | -35.4397 | -42.8235 | -47.4354
|  | SP |  |  | 35.2218 | 33.9739 | 32.6009 | 31.2685 | 29.2163 | 26.0407 | 22.8834 | 19.4851 | 14.8202 | 11.9774 | 2.8651 | -15.7183 | -25.6411 | -30.6427 | 32.3388 | 31.517 | 30.6155 | 29.7226 | 28.58 | 26.2569 | 23.9137 | 21.4 | 17.6347 | 15.7979 | 9.6039 | -4.5023 | -14.1154 | -23.4303 | 26.837 | 25.8399 | 24.7656 | 23.7216 | 21.9994 | 19.1331 | 16.2671 | 13.1994 | 8.8882 | 6.3865 | -1.816 | -19.295 | -28.4854 | -32.9804
MINETY GSP | STRATTON (2 X 90) | MINIMUM HEADROOM | SU1699888838 | YES | 49.5392 | 48.4823 | 47.1126 | 45.6868 | 43.37 | 40.6898 | 37.7945 | 34.7755 | 31.1297 | 27.2655 | 15.7931 | 0.32981 | -13.3958 | -22.0631 | 35.1911 | 34.7205 | 34.1063 | 33.4393 | 32.6105 | 30.8569 | 27.9578 | 25.0541 | 19.7751 | 18.5245 | 14.0149 | 1.8784 | -11.1139 | -25.8249 | 39.874 | 38.943 | 37.727 | 36.4644 | 34.3665 | 31.8866 | 29.2464 | 26.4935 | 23.1773 | 19.6796 | 9.1985 | -4.7544 | -16.9099 | -24.4094
|  | CT |  |  | 49.8085 | 48.9858 | 48.029 | 46.7369 | 44.9987 | 42.9651 | 40.7527 | 38.4403 | 35.8116 | 32.0117 | 20.2807 | 1.2157 | -13.3958 | -22.0631 | 35.1911 | 34.7205 | 34.1063 | 33.4393 | 32.6105 | 31.5073 | 30.3381 | 29.1388 | 27.2526 | 24.6765 | 16.6958 | 4.7056 | -5.4356 | -14.6229 | 40.1216 | 39.405 | 38.552 | 37.4182 | 35.851 | 33.9659 | 31.9514 | 29.8468 | 27.4583 | 24.0274 | 13.3809 | -3.9021 | -16.9099 | -24.4094
|  | LW |  |  | 49.5392 | 48.4823 | 47.1126 | 45.6868 | 43.37 | 40.6898 | 37.7945 | 34.7755 | 31.1297 | 27.2655 | 15.7931 | 0.32981 | -9.0239 | -14.9199 | 35.2471 | 34.7688 | 34.125 | 33.4807 | 32.6365 | 31.4663 | 29.8893 | 28.0167 | 25.5841 | 23.0166 | 15.5219 | 6.1795 | 0.73518 | -2.7593 | 39.874 | 38.943 | 37.727 | 36.4644 | 34.3665 | 31.8866 | 29.2464 | 26.4935 | 23.1773 | 19.6796 | 9.1985 | -4.7544 | -12.9277 | -17.8792
|  | ST |  |  | 50.4688 | 49.9934 | 49.413 | 48.8453 | 47.9335 | 46.7629 | 45.474 | 44.1473 | 42.58 | 40.2367 | 31.4264 | 14.6765 | 4.1259 | -2.6135 | 35.4304 | 35.1001 | 34.6522 | 34.243 | 33.6234 | 32.7357 | 31.789 | 30.8217 | 29.6537 | 27.7453 | 20.8432 | 7.6293 | -1.8518 | -10.2878 | 40.7148 | 40.3125 | 39.8009 | 39.3056 | 38.4857 | 37.3806 | 36.2005 | 34.9844 | 33.5494 | 31.3379 | 23.1227 | 7.9705 | -1.3454 | -7.0715
|  | SP |  |  | 50.6463 | 50.1494 | 49.5601 | 49.0038 | 48.2433 | 45.1899 | 42.0727 | 38.9078 | 33.3609 | 31.7728 | 25.9565 | 13.3256 | 3.8189 | -0.88586 | 35.4454 | 35.1178 | 34.6739 | 34.2764 | 33.7208 | 30.8569 | 27.9578 | 25.0541 | 19.7751 | 18.5245 | 14.0149 | 1.8784 | -11.1139 | -25.8249 | 40.8784 | 40.4618 | 39.9468 | 39.4655 | 38.7777 | 35.768 | 32.7326 | 29.6537 | 24.2066 | 22.7301 | 17.376 | 6.1377 | -2.1726 | -6.0161
MINETY GSP | SWINDON BSP | MINIMUM HEADROOM | SP1245387050 | NO | 42.3384 | 40.0793 | 24.7035 | 22.1125 | 18.0917 | 13.6115 | 8.813 | 3.5928 | -2.7781 | -9.4868 | -27.5392 | -50.9807 | -67.28 | -77.9738 | 41.9219 | 40.4655 | 26.0195 | 24.392 | 22.2033 | 19.5817 | 16.5989 | 13.2681 | 8.9084 | 4.3523 | -7.1294 | -26.0691 | -43.2522 | -72.5465 | 57.8688 | 55.6959 | 40.3992 | 37.8731 | 34.1089 | 29.8819 | 25.3009 | 20.3751 | 14.1411 | 7.5945 | -9.4242 | -30.9253 | -44.3774 | -53.7118
|  | CT |  |  | 43.2474 | 41.5622 | 26.8906 | 24.7302 | 21.9763 | 18.8252 | 15.4425 | 11.7652 | 7.3943 | 0.65597 | -17.5621 | -46.6379 | -67.28 | -77.9738 | 42.0551 | 40.6674 | 26.3803 | 24.6731 | 22.7626 | 20.3972 | 17.8528 | 14.9447 | 11.4617 | 6.7432 | -5.9758 | -26.0691 | -43.2522 | -61.6616 | 58.592 | 56.9066 | 42.2592 | 40.0572 | 37.3824 | 34.2385 | 30.9258 | 27.3063 | 23.0259 | 16.6732 | -0.35295 | -26.5661 | -44.3774 | -53.7118
|  | LW |  |  | 42.3384 | 40.0793 | 24.7035 | 22.1125 | 18.0917 | 13.6115 | 8.813 | 3.5928 | -2.7781 | -9.4868 | -27.5392 | -50.9807 | -62.3809 | -68.4829 | 41.9219 | 40.4655 | 26.0195 | 24.392 | 22.2033 | 19.5817 | 16.5989 | 13.2681 | 8.9084 | 4.3523 | -7.1294 | -21.2813 | -27.6768 | -31.2717 | 57.8688 | 55.6959 | 40.3992 | 37.8731 | 34.1089 | 29.8819 | 25.3009 | 20.3751 | 14.1411 | 7.5945 | -9.4242 | -30.9253 | -40.7842 | -46.0138
|  | ST |  |  | 44.4298 | 43.5355 | 42.6617 | 41.7641 | 27.7492 | 26.2946 | 24.7037 | 22.9523 | 20.8389 | 17.4428 | 4.3015 | -21.7505 | -36.2727 | -44.6903 | 42.83 | 41.9451 | 41.125 | 40.2757 | 26.3739 | 25.0462 | 23.5744 | 21.9468 | 19.9123 | 16.8297 | 4.9149 | -18.4845 | -35.1545 | -52.3675 | 59.7845 | 58.8868 | 58.033 | 57.1427 | 43.1162 | 41.6491 | 40.0341 | 38.2342 | 35.9927 | 32.6447 | 19.7327 | -5.109 | -18.3653 | -25.7107
|  | SP |  |  | 44.5999 | 43.746 | 42.9466 | 42.1763 | 41.2318 | 37.473 | 33.6546 | 29.6768 | 22.7877 | 20.5028 | 12.2769 | -9.7996 | -24.5973 | -30.7735 | 42.8804 | 41.9733 | 41.135 | 40.3019 | 39.3823 | 35.6232 | 31.7666 | 27.7395 | 20.7462 | 18.2872 | 9.3929 | -14.5794 | -40.0376 | -72.5465 | 59.9384 | 59.0555 | 58.2561 | 57.48 | 56.5549 | 52.8166 | 49.0158 | 45.0423 | 38.1448 | 35.8444 | 27.6184 | 6.3973 | -7.492 | -12.9654
BRAMLEY (ANDO-THAT) | THATCHAM BSP | MINIMUM HEADROOM | SU5281066430 | YES | 55.7699 | 49.595 | 43.4872 | 27.1663 | 18.4532 | 8.7844 | -1.2242 | -11.6643 | -22.7022 | -33.1625 | -57.8609 | -86.7133 | -95.7034 | -99.9949 | 47.4193 | 44.0915 | 40.8251 | 27.3104 | 22.9081 | 17.9139 | 12.5977 | 6.7665 | -0.083832 | -6.4428 | -20.2085 | -35.8476 | -44.9229 | -66.3979 | 37.8466 | 32.3354 | 26.7691 | 10.9603 | 3.0547 | -5.6485 | -14.6644 | -24.2371 | -34.7381 | -44.501 | -67.0218 | -92.7844 | -100.5659 | -104.2395
|  | CT |  |  | 60.273 | 56.5248 | 52.6509 | 38.5681 | 33.0637 | 26.729 | 20.4243 | 13.4662 | 6.3998 | -3.6058 | -26.2685 | -60.085 | -79.0752 | -86.9775 | 48.7798 | 46.2144 | 43.5391 | 30.6074 | 27.3171 | 23.4807 | 19.5169 | 15.0062 | 10.2058 | 3.6464 | -10.4206 | -30.7576 | -44.4846 | -56.5859 | 41.2617 | 37.885 | 34.3558 | 20.5833 | 15.7754 | 10.0465 | 4.2415 | -2.218 | -8.84 | -18.2349 | -39.0625 | -69.5578 | -86.2927 | -92.9043
|  | LW |  |  | 55.7699 | 49.595 | 43.4872 | 27.1663 | 18.4532 | 8.7844 | -1.2242 | -11.6643 | -22.7022 | -33.1625 | -57.8609 | -86.7133 | -95.7034 | -99.9949 | 47.4193 | 44.0915 | 40.8251 | 27.3104 | 22.9081 | 17.9139 | 12.5977 | 6.7665 | -0.083832 | -6.4428 | -20.2085 | -35.8476 | -40.5861 | -42.9347 | 37.8466 | 32.3354 | 26.7691 | 10.9603 | 3.0547 | -5.6485 | -14.6644 | -24.2371 | -34.7381 | -44.501 | -67.0218 | -92.7844 | -100.5659 | -104.2395
|  | ST |  |  | 62.5341 | 60.1883 | 57.8795 | 55.5445 | 52.4073 | 48.6733 | 44.8928 | 40.8015 | 36.4103 | 31.2426 | 10.3287 | -23.4007 | -39.0975 | -47.5131 | 50.3836 | 48.7699 | 47.1717 | 45.5176 | 43.5216 | 41.0917 | 38.5648 | 35.7707 | 32.6756 | 29.0563 | 13.8076 | -10.9367 | -24.6237 | -37.0441 | 43.4415 | 41.3925 | 39.3516 | 37.2549 | 34.5124 | 31.2503 | 27.9077 | 24.1386 | 20.0561 | 15.2446 | -4.472 | -36.0111 | -50.2769 | -57.692
|  | SP |  |  | 63.1248 | 61.1106 | 59.2889 | 57.5622 | 53.536 | 47.589 | 41.6571 | 35.341 | 27.261 | 21.3364 | 1.1207 | -43.3161 | -68.3808 | -82.1627 | 50.5943 | 49.0831 | 47.6886 | 46.3291 | 44.1314 | 40.0966 | 36.0092 | 31.5836 | 25.3599 | 21.7121 | 8.5947 | -22.7869 | -44.9229 | -66.3979 | 43.9153 | 42.1245 | 40.5014 | 38.9474 | 35.5887 | 30.3756 | 24.9052 | 19.0476 | 11.4164 | 6.027 | -12.4746 | -53.8093 | -76.8094 | -88.8777
MINETY GSP | TOOTHILL BSP | MINIMUM HEADROOM | SU1321583986 | YES | 64.7046 | 58.9516 | 52.4424 | 45.5618 | 41.7543 | 37.5874 | 33.1704 | 28.3354 | 22.856 | 17.5108 | 2.1863 | -13.0543 | -22.4032 | -28.8199 | 51.9236 | 45.8232 | 39.2804 | 32.5348 | 30.4337 | 28.143 | 25.6635 | 22.9447 | 19.757 | 16.5967 | 7.7769 | -1.9966 | -9.6047 | -16.7931 | 67.3553 | 60.7604 | 53.5059 | 45.9348 | 42.6004 | 38.9583 | 35.0455 | 30.7611 | 25.8025 | 20.9034 | 7.1693 | -6.3026 | -13.6172 | -19.0313
|  | CT |  |  | 65.137 | 59.6809 | 53.5214 | 46.8594 | 43.7316 | 40.2628 | 36.679 | 32.7188 | 28.3399 | 23.1064 | 7.636 | -10.9242 | -22.4032 | -28.8199 | 51.9833 | 45.9369 | 39.485 | 32.7167 | 30.8162 | 28.7305 | 26.5374 | 24.1211 | 21.4188 | 18.2598 | 9.0506 | -1.9966 | -9.6047 | -16.7931 | 67.6792 | 61.3312 | 54.3887 | 46.9768 | 44.2163 | 41.1654 | 37.9814 | 34.4681 | 30.5414 | 25.777 | 11.9847 | -4.1403 | -13.6172 | -19.0313
|  | LW |  |  | 64.7046 | 58.9516 | 52.4424 | 45.5618 | 41.7543 | 37.5874 | 33.1704 | 28.3354 | 22.856 | 17.5108 | 2.1863 | -13.0543 | -19.453 | -23.3102 | 51.9236 | 45.8232 | 39.2804 | 32.5348 | 30.4337 | 28.143 | 25.6635 | 22.9447 | 19.757 | 16.5967 | 7.7769 | -0.62613 | -3.6812 | -5.6211 | 67.3553 | 60.7604 | 53.5059 | 45.9348 | 42.6004 | 38.9583 | 35.0455 | 30.7611 | 25.8025 | 20.9034 | 7.1693 | -6.3026 | -11.5831 | -14.7303
|  | ST |  |  | 65.9442 | 61.087 | 55.812 | 50.3426 | 48.5841 | 46.6305 | 44.5802 | 42.3038 | 39.7838 | 37.3466 | 28.1097 | 13.4007 | 5.87 | 1.1144 | 52.5171 | 46.8496 | 40.9178 | 34.8526 | 33.623 | 32.2765 | 30.8415 | 29.2552 | 27.4875 | 25.8195 | 19.4797 | 8.5836 | 1.8133 | -4.7972 | 68.4959 | 62.7362 | 56.6396 | 50.377 | 48.8349 | 47.1314 | 45.319 | 43.3064 | 41.0464 | 38.8934 | 30.6773 | 17.2602 | 10.6458 | 6.6602
|  | SP |  |  | 66.0465 | 61.2159 | 56.0386 | 50.7177 | 49.2651 | 47.6842 | 45.9587 | 44.037 | 42.0131 | 40.0283 | 33.0365 | 20.6217 | 12.5982 | 8.8293 | 52.554 | 46.8825 | 40.9797 | 34.9772 | 33.9545 | 32.8444 | 31.5925 | 30.1927 | 28.6959 | 27.1988 | 21.9306 | 11.4198 | 1.7156 | -8.9793 | 68.5883 | 62.841 | 56.832 | 50.7097 | 49.4922 | 48.1741 | 46.655 | 44.9461 | 43.1027 | 41.3082 | 35.0794 | 23.5762 | 16.4087 | 13.2912
IVER 132KV | UPTON BSP | MINIMUM HEADROOM | TQ0080079434 | NO | 38.5186 | 37.6324 | 36.6584 | 35.5588 | 33.8527 | 32.0221 | 29.9843 | 27.7342 | 24.9151 | 22.0951 | 14.7063 | 4.961 | -0.95953 | -5.9343 | 31.0654 | 30.7616 | 30.442 | 30.0756 | 29.5361 | 28.8978 | 27.6202 | 26.1864 | 24.3192 | 22.4608 | 17.7153 | 10.237 | 3.5767 | -4.5713 | 34.6616 | 33.8434 | 32.9282 | 31.8939 | 30.3142 | 28.6153 | 26.7113 | 24.6001 | 21.9264 | 19.2033 | 12.0463 | 2.7495 | -2.8283 | -6.9992
|  | CT |  |  | 38.7454 | 38.0423 | 37.2676 | 36.2847 | 35.0357 | 33.6801 | 32.2281 | 30.6289 | 28.6836 | 25.8565 | 18.5761 | 6.9226 | -0.95953 | -5.9343 | 31.0739 | 30.785 | 30.4707 | 30.092 | 29.6293 | 29.1236 | 28.1077 | 26.9134 | 25.4577 | 23.4815 | 18.3873 | 10.237 | 3.5767 | -3.4927 | 34.849 | 34.193 | 33.4565 | 32.5183 | 31.3477 | 30.0754 | 28.7041 | 27.1899 | 25.348 | 22.688 | 15.8388 | 4.6117 | -2.8283 | -6.9992
|  | LW |  |  | 38.5186 | 37.6324 | 36.6584 | 35.5588 | 33.8527 | 32.0221 | 29.9843 | 27.7342 | 24.9151 | 22.0951 | 14.7063 | 4.961 | 0.43046 | -2.4606 | 31.0654 | 30.7616 | 30.442 | 30.0756 | 29.5361 | 28.8978 | 27.6202 | 26.1864 | 24.3192 | 22.4608 | 17.7153 | 11.8211 | 9.4904 | 7.9533 | 34.6616 | 33.8434 | 32.9282 | 31.8939 | 30.3142 | 28.6153 | 26.7113 | 24.6001 | 21.9264 | 19.2033 | 12.0463 | 2.7495 | -1.3654 | -3.8956
|  | ST |  |  | 39.4022 | 39.0904 | 38.7526 | 38.3471 | 37.8073 | 37.1978 | 36.5183 | 35.7538 | 34.7706 | 33.711 | 29.1799 | 19.5908 | 13.9573 | 10.368 | 31.3024 | 31.1527 | 30.998 | 30.8155 | 30.5782 | 30.3089 | 30.0009 | 29.6539 | 29.1917 | 28.5334 | 24.709 | 16.4632 | 10.3247 | 3.716 | 35.4829 | 35.2031 | 34.8877 | 34.5089 | 34.0012 | 33.4268 | 32.784 | 32.058 | 31.1276 | 30.1323 | 25.7978 | 16.7684 | 11.7435 | 8.6866
|  | SP |  |  | 39.4728 | 39.1618 | 38.8591 | 38.5127 | 38.0906 | 37.6285 | 37.1302 | 36.5472 | 35.822 | 34.9742 | 31.8615 | 23.2519 | 17.19 | 14.2796 | 31.3155 | 31.1715 | 31.0241 | 30.8554 | 30.6494 | 30.4198 | 30.1653 | 29.8741 | 29.5064 | 29.046 | 25.9625 | 16.9931 | 7.4011 | -4.5713 | 35.5485 | 35.2664 | 34.9831 | 34.66 | 34.2682 | 33.8391 | 33.3743 | 32.8255 | 32.1469 | 31.3549 | 28.4059 | 20.2066 | 14.593 | 12.0579
IVER 66KV | UXBRIDGE | MINIMUM HEADROOM | TQ0496983466 | NO | 36.8833 | 36.455 | 35.7856 | 34.9825 | 33.6423 | 32.2402 | 30.7196 | 28.9996 | 26.1556 | 24.8917 | 19.527 | 12.2639 | 7.5932 | 4.5956 | 26.267 | 25.9272 | 25.573 | 25.1186 | 24.5455 | 23.2395 | 21.1756 | 19.1085 | 15.3566 | 14.4843 | 11.791 | 3.8615 | -5.265 | -18.4167 | 19.8956 | 19.5034 | 19.0758 | 18.4898 | 17.4856 | 16.3302 | 14.8507 | 12.9583 | 9.296 | 8.527 | 4.478 | -2.2591 | -6.5289 | -9.2708
|  | CT |  |  | 36.8833 | 36.455 | 36.0296 | 35.5094 | 34.6344 | 33.6275 | 32.514 | 31.2697 | 29.8583 | 27.8147 | 22.5417 | 13.6924 | 7.5932 | 4.5956 | 26.267 | 25.9272 | 25.573 | 25.1186 | 24.5455 | 23.8777 | 23.1511 | 22.4078 | 21.5944 | 20.2628 | 16.5146 | 9.6991 | 3.2287 | -3.8557 | 19.8956 | 19.5034 | 19.1079 | 18.6166 | 18.0374 | 17.28 | 16.4075 | 15.351 | 14.0512 | 12.1717 | 7.3021 | -0.89936 | -6.5289 | -9.2708
|  | LW |  |  | 36.9118 | 36.4636 | 35.7856 | 34.9825 | 33.6423 | 32.2402 | 30.7196 | 28.9996 | 26.9527 | 24.8917 | 19.527 | 12.2639 | 8.632 | 6.8971 | 26.2957 | 25.9629 | 25.6195 | 25.1918 | 24.6077 | 23.8984 | 23.1047 | 22.287 | 21.1999 | 19.9344 | 16.5662 | 11.4641 | 9.4592 | 8.3647 | 19.9218 | 19.5101 | 19.0758 | 18.4898 | 17.4856 | 16.3302 | 14.8507 | 13.2587 | 11.3813 | 9.4734 | 4.478 | -2.2591 | -5.6268 | -7.2121
|  | ST |  |  | 37.0757 | 36.7692 | 36.484 | 36.1424 | 35.6968 | 35.1824 | 34.6313 | 34.0755 | 33.4486 | 32.2025 | 27.6562 | 18.1998 | 13.6998 | 12.3852 | 26.4282 | 26.1929 | 25.9573 | 25.6529 | 25.2293 | 24.7105 | 24.1331 | 23.5461 | 22.8981 | 21.6402 | 17.694 | 10.1919 | 3.8938 | -3.0442 | 20.0868 | 19.8161 | 19.5598 | 19.2447 | 18.8214 | 18.32 | 17.7736 | 17.2196 | 16.5994 | 15.3607 | 11.3876 | 2.2194 | -2.1424 | -3.4113
|  | SP |  |  | 37.0816 | 36.78 | 36.502 | 36.1774 | 35.7739 | 33.8018 | 31.8051 | 29.8181 | 26.1556 | 25.3839 | 23.1003 | 16.3889 | 10.4588 | 8.809 | 26.4294 | 26.1945 | 25.9568 | 25.6569 | 25.25 | 23.2395 | 21.1756 | 19.1085 | 15.3566 | 14.4843 | 11.791 | 3.8615 | -5.265 | -18.4167 | 20.0933 | 19.8273 | 19.5782 | 19.2802 | 18.8986 | 16.9386 | 14.9454 | 12.9583 | 9.296 | 8.527 | 6.2665 | 0.26198 | -5.4764 | -7.0632
NURSLING GSP | VELMORE BSP | MINIMUM HEADROOM | SU4293519205 | NO | 27.2935 | 23.1203 | 18.5147 | 14.2054 | 8.2297 | 2.0258 | -4.4745 | -11.2194 | -19.3295 | -27.2733 | -46.1397 | -70.1974 | -86.1954 | -97.505 | 31.2148 | 28.3121 | 25.1765 | 22.2918 | 18.7614 | 15.0794 | 11.1361 | 6.9636 | 1.5849 | -3.6543 | -15.3657 | -33.4063 | -49.1836 | -68.0951 | 25.6959 | 21.8819 | 17.6577 | 13.6442 | 8.2161 | 2.5452 | -3.4209 | -9.6629 | -17.3201 | -24.8305 | -42.4456 | -64.352 | -77.569 | -86.7854
|  | CT |  |  | 28.0621 | 24.4695 | 20.4835 | 16.4806 | 11.8268 | 6.9898 | 2.1883 | -2.8041 | -8.3159 | -16.3186 | -35.6216 | -65.7343 | -86.1954 | -97.505 | 31.2148 | 28.3829 | 25.3454 | 22.3623 | 19.2174 | 15.9505 | 12.6025 | 9.0215 | 4.9117 | -0.63846 | -13.745 | -33.4063 | -49.1836 | -65.7579 | 26.2493 | 22.9214 | 19.2337 | 15.536 | 11.3195 | 6.9262 | 2.5155 | -2.1268 | -7.3347 | -14.8839 | -32.8767 | -60.0106 | -77.569 | -86.7854
|  | LW |  |  | 27.2935 | 23.1203 | 18.5147 | 14.2054 | 8.2297 | 2.0258 | -4.4745 | -11.2194 | -19.3295 | -27.2733 | -46.1397 | -70.1974 | -80.8587 | -86.9108 | 31.2181 | 28.3121 | 25.1765 | 22.2918 | 18.7614 | 15.0794 | 11.1361 | 6.9636 | 1.5849 | -3.6543 | -15.3657 | -29.0995 | -34.1378 | -37.1606 | 25.6959 | 21.8819 | 17.6577 | 13.6442 | 8.2161 | 2.5452 | -3.4209 | -9.6629 | -17.3201 | -24.8305 | -42.4456 | -64.352 | -73.4696 | -78.505
|  | ST |  |  | 29.7099 | 27.3402 | 24.8548 | 22.7764 | 20.3943 | 17.9393 | 15.3824 | 12.7876 | 9.9575 | 7.1407 | -5.0945 | -30.4578 | -44.3125 | -52.8437 | 32.4526 | 30.4351 | 28.4011 | 26.7077 | 24.8025 | 22.8079 | 20.7512 | 18.5997 | 16.1777 | 13.8348 | 3.4926 | -17.9719 | -32.6592 | -48.3403 | 27.9497 | 25.8565 | 23.6569 | 21.7671 | 19.5538 | 17.2737 | 14.9534 | 12.5583 | 9.8887 | 7.237 | -4.5235 | -28.4259 | -40.7289 | -47.9392
|  | SP |  |  | 29.8857 | 27.5782 | 25.273 | 23.4643 | 21.5414 | 19.6138 | 17.6921 | 15.6567 | 13.5423 | 11.2935 | 3.1322 | -20.1828 | -34.6363 | -41.0577 | 32.5066 | 30.4797 | 28.5043 | 26.928 | 25.3357 | 23.723 | 22.0259 | 20.2021 | 18.2222 | 16.03 | 7.7692 | -15.9736 | -39.1193 | -68.0951 | 28.1055 | 26.0509 | 24.0233 | 22.4021 | 20.6781 | 18.9342 | 17.172 | 15.3189 | 13.3483 | 11.243 | 3.4727 | -18.7878 | -32.1231 | -37.6517
NORTH HYDE GSP | VICARAGE FARM ROAD | MINIMUM HEADROOM | TQ1236576425 | NO | 24.8087 | 24.0437 | 23.1091 | 22.1692 | 20.7697 | 19.2669 | 17.6441 | 15.8973 | 13.9216 | 11.8419 | 5.5372 | -2.484 | -8.5835 | -12.5179 | 22.6645 | 22.4087 | 22.1215 | 21.8157 | 21.0815 | 20.2516 | 19.3337 | 18.34 | 17.1517 | 15.8513 | 11.7143 | 4.6873 | -1.9063 | -12.7927 | 25.1752 | 24.5195 | 23.6971 | 22.8576 | 21.6037 | 20.2386 | 18.7532 | 17.1515 | 15.3112 | 13.3568 | 7.4422 | 0.13575 | -4.9173 | -8.1156
|  | CT |  |  | 25.0054 | 24.3844 | 23.674 | 22.8211 | 21.7551 | 20.6061 | 19.3935 | 18.0708 | 16.6891 | 14.6836 | 8.3929 | -1.6768 | -8.5835 | -12.5179 | 22.6645 | 22.4087 | 22.1215 | 21.8157 | 21.0895 | 20.2987 | 19.4408 | 18.4849 | 17.4328 | 16.0769 | 11.7143 | 4.6873 | -1.9063 | -9.6458 | 25.3049 | 24.7817 | 24.16 | 23.3789 | 22.4337 | 21.413 | 20.3145 | 19.0983 | 17.8051 | 15.9351 | 10.0647 | 0.99251 | -4.9173 | -8.1156
|  | LW |  |  | 24.8087 | 24.0437 | 23.1091 | 22.1692 | 20.7697 | 19.2669 | 17.6441 | 15.8973 | 13.9216 | 11.8419 | 5.5372 | -2.484 | -6.1936 | -8.3396 | 22.7061 | 22.4609 | 22.1798 | 21.8481 | 21.0815 | 20.2516 | 19.3337 | 18.34 | 17.1517 | 15.8513 | 11.9514 | 7.4937 | 5.8407 | 4.8097 | 25.1752 | 24.5195 | 23.6971 | 22.8576 | 21.6037 | 20.2386 | 18.7532 | 17.1515 | 15.3112 | 13.3568 | 7.4422 | 0.13575 | -3.0245 | -4.8009
|  | ST |  |  | 25.4443 | 25.1185 | 24.7455 | 24.4006 | 23.9335 | 23.4201 | 22.8585 | 22.2298 | 21.5603 | 20.8845 | 18.1148 | 10.4425 | 5.7875 | 2.869 | 22.7883 | 22.6075 | 22.4093 | 22.2317 | 22.0201 | 21.786 | 21.4119 | 20.8484 | 20.2263 | 19.6078 | 17.0206 | 9.9824 | 4.1008 | -3.2806 | 25.6901 | 25.4225 | 25.1097 | 24.8141 | 24.3872 | 23.917 | 23.3977 | 22.8151 | 22.1845 | 21.5612 | 18.9487 | 11.8435 | 7.7625 | 5.3109
|  | SP |  |  | 25.4945 | 25.1585 | 24.792 | 24.4643 | 24.1171 | 23.7416 | 23.3316 | 22.8627 | 22.4074 | 21.9032 | 20.0537 | 14.5269 | 9.9272 | 7.8637 | 22.7944 | 22.6127 | 22.4111 | 22.2327 | 22.0416 | 21.8326 | 21.4836 | 20.9565 | 20.3947 | 19.7567 | 17.337 | 10.2835 | 0.78418 | -12.7927 | 25.7308 | 25.4452 | 25.1311 | 24.845 | 24.5342 | 24.1947 | 23.8183 | 23.3834 | 22.9541 | 22.4858 | 20.7356 | 15.5026 | 11.3195 | 9.5935
MANNINGTON GSP | WAREHAM | MINIMUM HEADROOM | SY9150188410 | YES | 9.8486 | 8.8908 | 7.6912 | 10.9838 | 8.9669 | 6.5772 | 4.046 | 1.3577 | -2.8694 | -4.7471 | -12.6584 | -22.1489 | -27.9579 | -32.1054 | 7.9183 | 7.6043 | 7.256 | 18.146 | 17.0508 | 15.4723 | 12.6163 | 9.7084 | 4.047 | 2.8166 | -1.2272 | -9.5299 | -15.7105 | -21.1159 | 6.3493 | 5.4723 | 4.3722 | 10.0303 | 8.2102 | 6.0326 | 3.7186 | 1.2582 | -3.59 | -5.0838 | -11.6153 | -20.33 | -25.5314 | -29.2896
|  | CT |  |  | 10.0984 | 9.6952 | 9.2385 | 12.8436 | 11.4429 | 9.7286 | 7.8484 | 5.826 | 3.698 | 0.78626 | -7.0293 | -19.0553 | -27.9579 | -32.1054 | 7.9183 | 7.6043 | 7.2667 | 18.2421 | 17.7925 | 16.7061 | 15.4449 | 14.0876 | 12.6387 | 10.82 | 6.0665 | -0.82451 | -6.4591 | -10.4794 | 6.9422 | 6.3914 | 5.745 | 11.6685 | 10.3929 | 8.8189 | 7.0922 | 5.2335 | 3.2666 | 0.5758 | -6.5885 | -17.4822 | -25.5314 | -29.2896
|  | LW |  |  | 9.8486 | 8.8908 | 7.6912 | 10.9838 | 8.9669 | 6.5772 | 4.046 | 1.3577 | -1.6925 | -4.7471 | -12.6584 | -22.1489 | -26.7863 | -29.3126 | 7.9355 | 7.6154 | 7.256 | 18.146 | 17.0508 | 15.6368 | 14.1113 | 12.4849 | 10.6169 | 8.7571 | 4.1906 | -1.3371 | -4.4469 | -6.1207 | 6.3493 | 5.4723 | 4.3722 | 10.0303 | 8.2102 | 6.0326 | 3.7186 | 1.2582 | -1.5517 | -4.3778 | -11.6153 | -20.33 | -24.6606 | -27.0117
|  | ST |  |  | 10.2978 | 10.0052 | 9.7002 | 13.9865 | 13.273 | 12.187 | 11.026 | 9.7953 | 8.5337 | 6.4898 | -0.39443 | -10.7882 | -16.4679 | -19.9654 | 8.0213 | 7.7641 | 7.5036 | 18.6019 | 18.2504 | 17.6814 | 17.0576 | 16.3734 | 15.4029 | 13.6896 | 7.9091 | -0.48504 | -5.2515 | -9.0145 | 7.2405 | 6.8621 | 6.4446 | 12.848 | 12.1271 | 11.1311 | 10.0646 | 8.934 | 7.77 | 5.823 | -0.77462 | -10.7129 | -16.0092 | -19.1954
|  | SP |  |  | 10.3162 | 10.0309 | 9.735 | 14.0364 | 13.4212 | 10.0551 | 6.6182 | 3.1089 | -2.8694 | -4.4796 | -9.6357 | -19.774 | -25.7977 | -28.528 | 8.0273 | 7.7672 | 7.506 | 18.6068 | 18.2812 | 15.4723 | 12.6163 | 9.7084 | 4.047 | 2.8166 | -1.2272 | -9.5299 | -15.7105 | -21.1159 | 7.3451 | 6.9688 | 6.575 | 13.0136 | 12.261 | 8.9992 | 5.6727 | 2.2775 | -3.59 | -5.0838 | -9.9007 | -19.5485 | -25.2454 | -27.7483
MELKSHAM GSP | WEST GRAFTON | MINIMUM HEADROOM | SU2432759109 | YES | 24.0495 | 22.6629 | 21.1691 | 19.6073 | 17.542 | 15.4263 | 13.1886 | 10.7956 | 7.9037 | 5.0062 | -1.9791 | -9.587 | -11.6451 | -12.6854 | 22.1418 | 21.4472 | 20.6773 | 19.8618 | 18.8352 | 17.7699 | 16.6116 | 15.3546 | 13.7581 | 12.1506 | 8.5334 | 4.8115 | 1.9574 | -1.1102 | 21.5292 | 20.2934 | 18.9438 | 17.527 | 15.6479 | 13.7138 | 11.6568 | 9.4498 | 6.7502 | 4.0438 | -2.3676 | -9.2578 | -11.0739 | -11.9053
|  | CT |  |  | 25.0755 | 24.2496 | 23.3616 | 22.2886 | 20.9698 | 19.6265 | 18.2177 | 16.6733 | 14.9132 | 12.2703 | 5.7895 | -3.9725 | -10.2691 | -12.6854 | 22.4955 | 21.9932 | 21.4425 | 20.76 | 20.0013 | 19.2174 | 18.3757 | 17.4394 | 16.3423 | 14.7823 | 11.0743 | 5.8027 | 1.9574 | -1.1102 | 22.4205 | 21.6791 | 20.8688 | 19.8745 | 18.6567 | 17.4097 | 16.0963 | 14.6516 | 12.9913 | 10.5096 | 4.5128 | -4.2441 | -9.7894 | -11.9053
|  | LW |  |  | 24.0495 | 22.6629 | 21.1691 | 19.6073 | 17.542 | 15.4263 | 13.1886 | 10.7956 | 7.9037 | 5.0062 | -1.9791 | -9.587 | -11.6451 | -12.5716 | 22.1418 | 21.4472 | 20.6773 | 19.8618 | 18.8352 | 17.7699 | 16.6116 | 15.3546 | 13.7581 | 12.1506 | 8.5334 | 4.8115 | 3.9315 | 3.5459 | 21.5292 | 20.2934 | 18.9438 | 17.527 | 15.6479 | 13.7138 | 11.6568 | 9.4498 | 6.7502 | 4.0438 | -2.3676 | -9.2578 | -11.0739 | -11.883
|  | ST |  |  | 25.6466 | 25.1861 | 24.7018 | 24.1724 | 23.4903 | 22.7987 | 22.0601 | 21.26 | 20.3561 | 19.3836 | 15.3464 | 8.1027 | 4.6185 | 2.3843 | 22.8436 | 22.557 | 22.2469 | 21.8998 | 21.4773 | 21.0416 | 20.5621 | 20.0343 | 19.4269 | 18.8101 | 16.1255 | 11.0739 | 8.2013 | 5.2097 | 22.9662 | 22.5715 | 22.1447 | 21.6719 | 21.0429 | 20.4001 | 19.7099 | 18.96 | 18.1081 | 17.1997 | 13.3603 | 6.5274 | 3.3981 | 1.4416
|  | SP |  |  | 25.7999 | 25.3937 | 24.9941 | 24.5767 | 23.8231 | 23.0578 | 22.2879 | 21.4476 | 20.5592 | 19.4238 | 15.493 | 6.0732 | 0.79979 | -1.927 | 22.8996 | 22.6222 | 22.3382 | 22.0335 | 21.6055 | 21.1618 | 20.7022 | 20.1835 | 19.6191 | 18.9359 | 16.4372 | 9.9735 | 5.2139 | 0.31609 | 23.1016 | 22.7516 | 22.4001 | 22.0296 | 21.3492 | 20.6536 | 19.9529 | 19.1823 | 18.3643 | 17.3245 | 13.6841 | 4.8437 | -0.0036921 | -2.43
NURSLING GSP | WINCHESTER | MINIMUM HEADROOM | SU4498126740 | NO | 41.465 | 28.5273 | 26.0999 | 23.3256 | 19.0341 | 14.5037 | 9.7002 | 4.6613 | -0.99932 | -6.618 | -22.0244 | -39.1058 | -43.9545 | -49.2694 | 39.5828 | 28.2804 | 27.5943 | 26.6259 | 25.5399 | 23.9944 | 21.1848 | 18.1779 | 14.4751 | 10.8485 | 1.8691 | -9.1636 | -18.8259 | -31.6469 | 32.251 | 19.576 | 17.3867 | 14.8721 | 11.209 | 7.3083 | 3.0671 | -1.4721 | -6.8746 | -12.1844 | -25.7165 | -40.0727 | -44.0699 | -48.1921
|  | CT |  |  | 42.9054 | 30.7731 | 29.137 | 27.1222 | 24.1975 | 21.0641 | 17.8342 | 14.4242 | 10.8011 | 5.4071 | -9.2913 | -31.2553 | -43.9545 | -49.2694 | 39.5828 | 28.2804 | 27.5943 | 26.6259 | 25.5399 | 24.3747 | 22.9198 | 20.4035 | 17.6265 | 13.8034 | 4.2305 | -9.1636 | -18.8259 | -29.0762 | 33.1351 | 21.0124 | 19.3642 | 17.3385 | 14.6948 | 11.8446 | 8.8436 | 5.598 | 2.0645 | -3.1389 | -16.1252 | -33.67 | -43.7081 | -48.1921
|  | LW |  |  | 41.465 | 28.5273 | 26.0999 | 23.3256 | 19.0341 | 14.5037 | 9.7002 | 4.6613 | -0.99932 | -6.618 | -22.0244 | -39.1058 | -43.9229 | -45.7217 | 39.6743 | 28.3547 | 27.6811 | 26.7141 | 25.5669 | 23.9944 | 21.1848 | 18.1779 | 14.4751 | 10.8485 | 1.8691 | -7.2251 | -9.1796 | -9.9143 | 32.251 | 19.576 | 17.3867 | 14.8721 | 11.209 | 7.3083 | 3.0671 | -1.4721 | -6.8746 | -12.1844 | -25.7165 | -40.0727 | -44.0699 | -45.6015
|  | ST |  |  | 44.0149 | 43.3089 | 42.4712 | 30.6216 | 29.0654 | 27.4038 | 25.6373 | 23.8293 | 21.8573 | 19.7378 | 11.2624 | -5.606 | -13.7369 | -18.2921 | 40.0149 | 39.7123 | 39.3437 | 27.9884 | 27.2227 | 26.3974 | 25.5027 | 24.6527 | 23.6426 | 22.5262 | 15.4894 | 1.3429 | -7.9308 | -18.0993 | 34.3482 | 33.697 | 32.8956 | 21.0927 | 19.6316 | 18.063 | 16.3701 | 14.5949 | 12.6149 | 10.5844 | 1.8229 | -13.762 | -20.7956 | -24.5338
|  | SP |  |  | 44.2284 | 43.6217 | 42.9307 | 42.019 | 40.4523 | 38.8391 | 26.3898 | 24.6819 | 22.9098 | 20.8111 | 13.6209 | -2.9934 | -13.1148 | -17.3384 | 40.0266 | 39.7439 | 39.3996 | 38.8247 | 38.138 | 37.4208 | 25.9143 | 25.2181 | 24.4595 | 23.6378 | 17.2553 | 1.0968 | -13.68 | -31.6469 | 34.5052 | 33.9078 | 33.2291 | 32.3514 | 30.9955 | 29.588 | 17.3292 | 15.7503 | 14.0882 | 12.1711 | 5.2674 | -10.9262 | -20.0143 | -23.5564
MANNINGTON GSP | WINFRITH HEATH | MINIMUM HEADROOM | SY8070586455 | YES | 32.3341 | 31.6798 | 30.8957 | 30.1226 | 29.262 | 28.4923 | 27.7063 | 26.6803 | 25.6076 | 24.6293 | 22.3391 | 20.2775 | 19.8062 | 19.492 | 21.2315 | 20.6431 | 19.917 | 19.2009 | 18.4653 | 17.8515 | 17.3325 | 16.8596 | 16.3604 | 15.9242 | 14.9732 | 14.4361 | 14.3644 | 14.2747 | 27.4225 | 26.7081 | 25.8328 | 24.9786 | 23.9915 | 23.07 | 22.1841 | 21.2858 | 20.3403 | 19.474 | 17.4418 | 15.6465 | 15.2343 | 14.9583
|  | CT |  |  | 32.4781 | 31.902 | 31.1966 | 30.5007 | 29.7413 | 29.0756 | 28.4606 | 27.8507 | 27.1576 | 26.2345 | 24.1014 | 21.5187 | 20.1365 | 19.9357 | 21.251 | 20.6745 | 19.9633 | 19.2556 | 18.5373 | 17.942 | 17.4446 | 16.9949 | 16.5344 | 16.1085 | 15.1848 | 14.5742 | 14.369 | 14.2747 | 27.6422 | 27.0417 | 26.2927 | 25.5451 | 24.7041 | 23.9318 | 23.1929 | 22.446 | 21.7005 | 20.8877 | 18.9997 | 16.748 | 15.5362 | 15.3597
|  | LW |  |  | 32.3341 | 31.6798 | 30.8957 | 30.1226 | 29.262 | 28.4923 | 27.7063 | 26.6803 | 25.6076 | 24.6293 | 22.3391 | 20.2775 | 19.8062 | 19.492 | 21.2315 | 20.6431 | 19.917 | 19.2009 | 18.4653 | 17.8515 | 17.3325 | 16.8596 | 16.3604 | 15.9242 | 14.9732 | 14.4361 | 14.3644 | 14.3213 | 27.4225 | 26.7081 | 25.8328 | 24.9786 | 23.9915 | 23.07 | 22.1841 | 21.2858 | 20.3403 | 19.474 | 17.4418 | 15.6465 | 15.2343 | 14.9583
|  | ST |  |  | 32.5294 | 31.9976 | 31.3541 | 30.7166 | 30.0488 | 29.4944 | 29.0138 | 28.5503 | 28.06 | 27.6087 | 26.3822 | 24.6673 | 23.8382 | 23.3175 | 21.2718 | 20.7127 | 20.0237 | 19.3437 | 18.6509 | 18.085 | 17.62 | 17.2081 | 16.7845 | 16.4221 | 15.542 | 14.8371 | 14.5777 | 14.444 | 27.6933 | 27.1477 | 26.4801 | 25.826 | 25.1148 | 24.4968 | 23.9375 | 23.4041 | 22.8618 | 22.3736 | 21.0281 | 19.5098 | 18.7505 | 18.2674
|  | SP |  |  | 32.547 | 32.0296 | 31.3867 | 30.7608 | 30.0769 | 29.5067 | 28.9938 | 28.5129 | 28.0168 | 27.5483 | 26.149 | 23.7666 | 22.5317 | 21.7851 | 21.2758 | 20.7186 | 20.0326 | 19.3569 | 18.6653 | 18.1028 | 17.6398 | 17.2301 | 16.8134 | 16.4548 | 15.6202 | 14.8871 | 14.4961 | 14.277 | 27.7246 | 27.1947 | 26.5488 | 25.9179 | 25.1619 | 24.5055 | 23.9087 | 23.3426 | 22.7786 | 22.2348 | 20.7834 | 18.7223 | 17.6235 | 16.9656
COWLEY GSP | WITNEY BSP | MINIMUM HEADROOM | SP3560808335 | YES | 24.1566 | 20.6657 | 16.784 | 12.6003 | 6.8946 | 0.73787 | -5.3188 | -11.7509 | -19.1279 | -26.5095 | -43.7493 | -62.9355 | -69.6347 | -73.5481 | 30.241 | 28.5213 | 26.5908 | 24.487 | 21.7603 | 18.6876 | 15.6059 | 12.2962 | 8.3257 | 4.3818 | -4.3595 | -16.1275 | -29.276 | -41.7798 | 25.1724 | 22.0741 | 18.6273 | 14.9105 | 9.8396 | 4.3411 | -1.1264 | -6.9492 | -13.7167 | -20.4921 | -36.1297 | -53.5359 | -59.6105 | -63.1221
|  | CT |  |  | 26.64 | 24.5337 | 22.1311 | 19.1772 | 15.3994 | 11.193 | 7.172 | 2.772 | -2.1535 | -8.9933 | -24.602 | -47.1035 | -60.6258 | -65.8233 | 30.6086 | 29.9376 | 28.5468 | 26.834 | 24.8017 | 22.4505 | 20.1601 | 17.6425 | 14.785 | 11.0031 | 2.3206 | -10.6593 | -19.8651 | -27.0324 | 27.472 | 25.5923 | 23.443 | 20.7737 | 17.3894 | 13.6007 | 9.932 | 5.9035 | 1.3478 | -4.9935 | -19.3158 | -39.4343 | -51.5011 | -56.1338
|  | LW |  |  | 24.1566 | 20.6657 | 16.784 | 12.6003 | 6.8946 | 0.73787 | -5.3188 | -11.7509 | -19.1279 | -26.5095 | -43.7493 | -62.9355 | -69.6347 | -73.5481 | 30.241 | 28.5213 | 26.5908 | 24.487 | 21.7603 | 18.6876 | 15.6059 | 12.2962 | 8.3257 | 4.3818 | -4.3595 | -14.3577 | -18.2787 | -20.5172 | 25.1724 | 22.0741 | 18.6273 | 14.9105 | 9.8396 | 4.3411 | -1.1264 | -6.9492 | -13.7167 | -20.4921 | -36.1297 | -53.5359 | -59.6105 | -63.1221
|  | ST |  |  | 27.8073 | 26.4525 | 24.9611 | 23.268 | 20.9893 | 18.3885 | 15.8902 | 13.2181 | 10.3231 | 6.6832 | -6.2527 | -27.1227 | -38.3067 | -45.039 | 30.9123 | 30.5444 | 30.1558 | 29.1453 | 27.8598 | 26.3084 | 24.7882 | 23.1509 | 21.3499 | 18.8709 | 10.0698 | -4.3728 | -13.4217 | -21.3236 | 28.5792 | 27.4142 | 26.1457 | 24.7074 | 22.703 | 20.3935 | 18.1354 | 15.7141 | 13.0678 | 9.6868 | -2.5937 | -22.2555 | -32.4306 | -38.411
|  | SP |  |  | 28.1427 | 26.9403 | 25.6836 | 24.307 | 21.5343 | 16.6289 | 11.8241 | 6.8116 | -0.34362 | -4.3981 | -17.0708 | -44.069 | -59.9569 | -68.6577 | 30.9217 | 30.5594 | 30.2069 | 29.5321 | 28.0874 | 24.5362 | 21.02 | 17.3734 | 11.6089 | 9.2249 | 1.495 | -16.1275 | -29.276 | -41.7798 | 28.8952 | 27.8714 | 26.8017 | 25.6304 | 23.2261 | 18.6514 | 14.1318 | 9.4535 | 2.6547 | -0.99618 | -12.5791 | -37.7199 | -52.1464 | -59.8932
BRAMLEY (FLEE) | WOKINGHAM BSP | MINIMUM HEADROOM | SU7959967739 | YES | 86.8629 | 54.105 | 51.797 | 48.271 | 45.5433 | 42.6246 | 39.5724 | 36.2392 | 32.2279 | 28.5194 | 19.5292 | 8.8824 | 3.3304 | -0.85917 | 68.7213 | 36.2358 | 34.2883 | 30.9847 | 29.4796 | 27.814 | 26.0246 | 24.0363 | 21.4667 | 19.122 | 13.8491 | 6.9731 | 0.88222 | -4.5566 | 80.3278 | 47.5253 | 45.2075 | 41.4596 | 39.1942 | 36.7405 | 34.1347 | 31.2575 | 27.6495 | 24.3385 | 16.1823 | 6.4742 | 1.7106 | -1.9603
|  | CT |  |  | 87.2517 | 54.7878 | 52.6377 | 49.3638 | 47.296 | 45.0762 | 42.8845 | 40.4875 | 37.6335 | 33.9003 | 24.8991 | 11.866 | 3.3304 | -0.85917 | 68.7394 | 36.3067 | 34.2965 | 30.9994 | 29.707 | 28.2787 | 26.8092 | 25.185 | 23.2136 | 20.7542 | 15.1165 | 6.9731 | 0.88222 | -4.5566 | 80.5466 | 47.9558 | 45.7072 | 42.1285 | 40.3692 | 38.46 | 36.5371 | 34.4182 | 31.8541 | 28.5163 | 20.9055 | 9.2769 | 1.7106 | -1.9603
|  | LW |  |  | 86.8629 | 54.105 | 51.797 | 48.271 | 45.5433 | 42.6246 | 39.5724 | 36.2392 | 32.2279 | 28.5194 | 19.5292 | 8.8824 | 4.4356 | 2.1139 | 68.7213 | 36.2358 | 34.2883 | 30.9847 | 29.4796 | 27.814 | 26.0246 | 24.0363 | 21.4667 | 19.122 | 13.8491 | 7.6436 | 5.1395 | 3.7937 | 80.3278 | 47.5253 | 45.2075 | 41.4596 | 39.1942 | 36.7405 | 34.1347 | 31.2575 | 27.6495 | 24.3385 | 16.1823 | 6.4742 | 2.5091 | 0.47373
|  | ST |  |  | 88.0669 | 86.7147 | 85.1952 | 51.9352 | 50.8004 | 49.5518 | 48.2758 | 46.8952 | 45.3216 | 43.46 | 36.0543 | 24.8124 | 18.9505 | 15.5143 | 69.3328 | 67.8687 | 66.2965 | 32.7903 | 31.984 | 31.0657 | 30.1044 | 29.0552 | 27.8464 | 26.3699 | 20.4153 | 11.1627 | 5.5447 | 0.39844 | 81.346 | 79.8511 | 78.2037 | 44.5815 | 43.5822 | 42.4678 | 41.3159 | 40.0633 | 38.6271 | 36.91 | 29.877 | 19.472 | 14.4564 | 11.6789
|  | SP |  |  | 88.1532 | 86.8497 | 85.4466 | 82.9778 | 81.9631 | 79.9337 | 77.888 | 75.719 | 72.4054 | 70.8791 | 65.5937 | 54.128 | 47.9173 | 45.2054 | 69.3619 | 67.9123 | 66.3974 | 63.6044 | 62.9138 | 61.1965 | 59.4335 | 57.5621 | 54.5634 | 53.3489 | 49.0056 | 38.793 | 31.1665 | 23.4467 | 81.4147 | 79.9574 | 78.4178 | 75.5785 | 74.7256 | 72.8531 | 70.9462 | 68.9152 | 65.747 | 64.3695 | 59.5052 | 48.5869 | 42.9775 | 40.6907
LOVEDEAN GSP | WYMERING BSP | MINIMUM HEADROOM | SU6497405375 | NO | 62.9247 | 60.6872 | 58.0504 | 54.7571 | 49.7169 | 44.0176 | 38.0633 | 31.7321 | 24.4034 | 16.6281 | -6.8484 | -37.7535 | -61.1997 | -75.8109 | 68.2145 | 67.332 | 66.3145 | 64.9702 | 63.5201 | 60.4034 | 57.082 | 53.4902 | 49.502 | 44.3606 | 27.9864 | -1.1888 | -38.8964 | -109.201 | 58.2543 | 56.2529 | 53.781 | 50.724 | 46.2006 | 41.0774 | 35.6402 | 29.8293 | 22.9707 | 15.632 | -6.1788 | -33.8246 | -52.2707 | -64.2438
|  | CT |  |  | 63.2889 | 61.8879 | 60.0026 | 57.0392 | 53.2329 | 48.8289 | 44.2505 | 39.3455 | 34.005 | 26.3612 | 2.7613 | -35.3892 | -61.1997 | -75.8109 | 68.2145 | 67.332 | 66.3145 | 64.9702 | 63.5201 | 60.4034 | 57.082 | 53.4902 | 49.502 | 44.3606 | 27.9864 | -1.1888 | -30.3826 | -67.091 | 58.8086 | 57.2135 | 55.4576 | 52.6274 | 49.1336 | 45.1019 | 40.8713 | 36.3174 | 31.2751 | 24.1511 | 2.3789 | -30.8594 | -52.2707 | -64.2438
|  | LW |  |  | 62.9247 | 60.6872 | 58.0504 | 54.7571 | 49.7169 | 44.0176 | 38.0633 | 31.7321 | 24.4034 | 16.6281 | -6.8484 | -37.7535 | -52.6786 | -62.0599 | 68.3224 | 67.4354 | 66.3949 | 65.0971 | 63.7148 | 60.7125 | 57.3458 | 53.7548 | 49.5175 | 44.9801 | 31.3385 | 14.2122 | 6.5645 | 1.6493 | 58.2543 | 56.2529 | 53.781 | 50.724 | 46.2006 | 41.0774 | 35.6402 | 29.8293 | 22.9707 | 15.632 | -6.1788 | -33.8246 | -46.289 | -54.028
|  | ST |  |  | 63.9112 | 63.1725 | 62.3817 | 61.3463 | 59.5899 | 57.3358 | 55.0025 | 52.4887 | 49.7043 | 46.3279 | 33.5696 | 5.8728 | -10.9014 | -21.7706 | 68.6575 | 68.0497 | 67.3537 | 66.475 | 65.5023 | 64.3317 | 62.9168 | 60.5354 | 57.8653 | 54.6789 | 42.7066 | 15.3193 | -11.745 | -46.9493 | 59.989 | 59.1678 | 58.2563 | 57.0254 | 55.3162 | 53.2555 | 51.0878 | 48.7367 | 46.0863 | 42.9132 | 30.6761 | 4.2856 | -10.3792 | -19.2655
|  | SP |  |  | 63.9499 | 63.2295 | 62.4603 | 61.4715 | 60.2375 | 57.4293 | 54.535 | 51.5089 | 47.2254 | 44.7096 | 35.7643 | 14.957 | -0.52068 | -8.1027 | 68.6779 | 68.0732 | 67.3774 | 66.5154 | 65.6254 | 63.514 | 60.656 | 57.1905 | 52.321 | 49.0672 | 37.0201 | 6.1688 | -38.8964 | -109.201 | 60.1522 | 59.2926 | 58.3689 | 57.1935 | 55.8925 | 53.2889 | 50.5636 | 47.6983 | 43.5502 | 41.2017 | 32.7308 | 12.4535 | -2.1538 | -8.6574
COWLEY GSP | YARNTON BSP | MINIMUM HEADROOM | SP3560808335 | YES | 33.2421 | 28.2441 | 22.8795 | 16.9913 | 8.8308 | 0.17323 | -8.4566 | -17.4816 | -27.4568 | -37.7507 | -61.5624 | -86.7946 | -95.0617 | -99.8182 | 38.8098 | 36.1843 | 33.3127 | 30.1769 | 26.0531 | 21.5997 | 17.0916 | 12.3426 | 6.9376 | 1.3869 | -10.9355 | -23.4865 | -31.2993 | -43.0722 | 31.7311 | 27.4649 | 22.7986 | 17.6802 | 10.6685 | 3.1863 | -4.3742 | -12.341 | -21.3668 | -30.6952 | -51.7328 | -73.637 | -80.9691 | -85.1608
|  | CT |  |  | 36.7581 | 33.4707 | 29.7301 | 25.2352 | 19.1757 | 12.6606 | 6.2967 | -0.3994 | -7.5399 | -17.036 | -39.2684 | -71.4916 | -90.7236 | -95.4673 | 40.0395 | 38.001 | 35.7076 | 32.9842 | 29.619 | 25.9532 | 22.3155 | 18.462 | 14.2804 | 8.9786 | -3.2398 | -19.9295 | -30.9244 | -37.5349 | 34.5282 | 31.6539 | 28.3548 | 24.3349 | 19.072 | 13.3845 | 7.7631 | 1.801 | -4.6611 | -13.3179 | -33.2962 | -60.7383 | -76.9557 | -81.1354
|  | LW |  |  | 33.2421 | 28.2441 | 22.8795 | 16.9913 | 8.8308 | 0.17323 | -8.4566 | -17.4816 | -27.4568 | -37.7507 | -61.5624 | -86.7946 | -95.0617 | -99.8182 | 38.8098 | 36.1843 | 33.3127 | 30.1769 | 26.0531 | 21.5997 | 17.0916 | 12.3426 | 6.9376 | 1.3869 | -10.9355 | -23.4865 | -27.6076 | -29.9401 | 31.7311 | 27.4649 | 22.7986 | 17.6802 | 10.6685 | 3.1863 | -4.3742 | -12.341 | -21.3668 | -30.6952 | -51.7328 | -73.637 | -80.9691 | -85.1608
|  | ST |  |  | 37.6634 | 35.1946 | 32.4435 | 29.435 | 25.2594 | 20.8068 | 16.6858 | 12.449 | 7.9705 | 3.0192 | -11.8403 | -35.8652 | -49.0483 | -57.3617 | 40.6639 | 39.1311 | 37.441 | 35.5922 | 33.1358 | 30.4623 | 27.8992 | 25.2351 | 22.3766 | 19.1565 | 9.2402 | -6.778 | -16.1408 | -24.1165 | 35.5233 | 33.4981 | 31.2136 | 28.6983 | 25.1269 | 21.2919 | 17.6839 | 13.9459 | 9.942 | 5.514 | -8.5476 | -31.2586 | -42.6409 | -49.4965
|  | SP |  |  | 38.0504 | 35.8264 | 33.4167 | 30.8381 | 25.5678 | 18.9334 | 12.2926 | 5.5292 | -2.5002 | -8.9264 | -27.1272 | -58.5145 | -76.3252 | -85.8381 | 40.8053 | 39.3473 | 37.7781 | 36.1017 | 33.3445 | 29.2807 | 25.1626 | 20.9348 | 15.4253 | 11.8238 | 1.5275 | -17.7764 | -31.2993 | -43.0722 | 35.8439 | 34.0027 | 32.0062 | 29.8726 | 25.5498 | 19.8773 | 14.116 | 8.2113 | 1.0194 | -4.4886 | -20.5092 | -49.5544 | -65.5217 | -73.5391
AXMINSTER | YEOVIL BSP | MINIMUM HEADROOM | ST5769016833 | YES | 43.6477 | 39.1733 | 34.0989 | 28.8583 | 21.5465 | 13.9735 | 6.4914 | -0.84415 | -9.2777 | -17.8519 | -39.8506 | -63.5683 | -71.9907 | -77.8929 | 50.0076 | 48.4131 | 46.364 | 43.5994 | 40.0377 | 36.2849 | 32.3667 | 28.3172 | 23.342 | 18.2387 | 6.509 | -4.943 | -12.5086 | -27.6119 | 38.9258 | 34.8885 | 30.3962 | 25.7639 | 19.2551 | 12.5275 | 5.889 | -0.60379 | -8.0253 | -15.7743 | -35.5362 | -56.6039 | -63.831 | -68.8336
|  | CT |  |  | 47.5075 | 45.0226 | 42.2748 | 38.8578 | 34.1294 | 29.1503 | 23.9878 | 18.7675 | 13.0181 | 5.0698 | -15.8351 | -46.0255 | -65.2156 | -74.561 | 50.321 | 49.2956 | 48.3748 | 46.7823 | 44.0745 | 41.1868 | 38.1179 | 34.8516 | 31.0726 | 26.0559 | 13.7368 | -1.697 | -12.5086 | -21.921 | 42.4807 | 40.2729 | 37.8917 | 34.9487 | 30.8099 | 26.4474 | 21.802 | 17.0709 | 11.8315 | 4.5608 | -14.301 | -41.0104 | -57.7149 | -65.7423
|  | LW |  |  | 43.6477 | 39.1733 | 34.0989 | 28.8583 | 21.5465 | 13.9735 | 6.4914 | -0.84415 | -9.2777 | -17.8519 | -39.8506 | -63.5683 | -71.9907 | -77.8929 | 50.0076 | 48.4131 | 46.364 | 43.5994 | 40.0377 | 36.2849 | 32.3667 | 28.3172 | 23.342 | 18.2387 | 6.509 | -4.943 | -8.5969 | -11.177 | 38.9258 | 34.8885 | 30.3962 | 25.7639 | 19.2551 | 12.5275 | 5.889 | -0.60379 | -8.0253 | -15.7743 | -35.5362 | -56.6039 | -63.831 | -68.8336
|  | ST |  |  | 48.4932 | 46.6412 | 44.7488 | 42.8141 | 39.9001 | 36.8367 | 33.6541 | 30.2343 | 26.4718 | 22.443 | 7.9267 | -16.1548 | -28.3422 | -36.4862 | 50.6496 | 49.8215 | 49.1874 | 48.4978 | 47.5344 | 46.1344 | 44.1601 | 41.9859 | 39.5352 | 37.0577 | 27.3782 | 10.6247 | 1.4644 | -7.5066 | 43.354 | 41.7106 | 40.0937 | 38.4508 | 35.9509 | 33.3322 | 30.5986 | 27.6508 | 24.4202 | 20.8339 | 7.6671 | -14.3918 | -25.1201 | -32.0923
|  | SP |  |  | 49.007 | 47.3487 | 45.7224 | 44.0969 | 40.3449 | 36.4921 | 32.5301 | 28.3689 | 24.023 | 18.8098 | 2.1934 | -31.454 | -52.1978 | -61.6007 | 50.653 | 49.8123 | 49.1691 | 48.588 | 47.6418 | 46.2017 | 44.1469 | 41.8847 | 39.4634 | 36.6265 | 26.9545 | 5.1901 | -11.3172 | -27.6119 | 43.8248 | 42.3696 | 41.002 | 39.646 | 36.3539 | 32.9887 | 29.5168 | 25.8688 | 22.0795 | 17.4892 | 2.9052 | -27.4087 | -45.9451 | -54.0881
IVER 66KV | YIEWSLEY | MINIMUM HEADROOM | TQ0565680987 | NO | 31.4109 | 30.6555 | 29.8182 | 28.8786 | 27.3991 | 25.8535 | 24.2581 | 22.5451 | 20.5331 | 18.4321 | 12.1579 | 4.4229 | -0.14428 | -3.7812 | 41.4821 | 41.207 | 40.8666 | 40.3168 | 39.5417 | 38.6924 | 37.7738 | 36.7439 | 35.4692 | 34.1234 | 30.1768 | 24.8808 | 19.9995 | 14.9491 | 34.2313 | 33.5859 | 32.8435 | 31.9913 | 30.6332 | 29.1882 | 27.6893 | 26.0869 | 24.1848 | 22.2001 | 16.291 | 9.2144 | 5.3752 | 2.3797
|  | CT |  |  | 31.7767 | 31.2419 | 30.7169 | 29.9334 | 28.8508 | 27.7188 | 26.6181 | 25.4202 | 24.0361 | 22.0274 | 15.9544 | 6.2949 | -0.14428 | -3.7812 | 41.494 | 41.2864 | 41.09 | 40.5264 | 39.8409 | 39.089 | 38.3221 | 37.4813 | 36.4766 | 35.1696 | 31.0734 | 24.8808 | 19.9995 | 14.9491 | 34.5104 | 34.0414 | 33.5707 | 32.8446 | 31.8699 | 30.824 | 29.7864 | 28.6483 | 27.3227 | 25.4335 | 19.7343 | 10.9916 | 5.3752 | 2.3797
|  | LW |  |  | 31.4109 | 30.6555 | 29.8182 | 28.8786 | 27.3991 | 25.8535 | 24.2581 | 22.5451 | 20.5331 | 18.4321 | 12.1579 | 4.4229 | 0.99878 | -0.94543 | 41.4821 | 41.207 | 40.8666 | 40.3168 | 39.5417 | 38.6924 | 37.7738 | 36.7439 | 35.4692 | 34.1234 | 30.1768 | 25.7305 | 24.0715 | 23.0786 | 34.2313 | 33.5859 | 32.8435 | 31.9913 | 30.6332 | 29.1882 | 27.6893 | 26.0869 | 24.1848 | 22.2001 | 16.291 | 9.2144 | 6.2666 | 4.6385
|  | ST |  |  | 32.2775 | 32.0127 | 31.776 | 31.4968 | 31.0228 | 30.5175 | 30.0054 | 29.438 | 28.7515 | 28.0134 | 25.1357 | 17.9275 | 13.6274 | 10.8099 | 41.6252 | 41.4919 | 41.3806 | 41.2532 | 41.0342 | 40.7008 | 40.2614 | 39.7768 | 39.1856 | 38.5824 | 36.1849 | 30.2358 | 25.8201 | 21.0281 | 34.9674 | 34.7402 | 34.5294 | 34.2809 | 33.8369 | 33.3417 | 32.8374 | 32.2914 | 31.6247 | 30.9312 | 28.1827 | 21.454 | 17.652 | 15.2522
|  | SP |  |  | 32.3528 | 32.081 | 31.8542 | 31.5879 | 31.2372 | 30.8568 | 30.4912 | 30.0826 | 29.5959 | 29.0052 | 26.9512 | 21.3151 | 16.8356 | 14.6766 | 41.6364 | 41.5014 | 41.3901 | 41.2637 | 41.0728 | 40.8147 | 40.4642 | 40.07 | 39.5967 | 39.0234 | 36.9365 | 31.0565 | 24.1071 | 15.3142 | 35.0328 | 34.7918 | 34.5843 | 34.3421 | 34.0134 | 33.6347 | 33.271 | 32.8751 | 32.3992 | 31.8465 | 29.8971 | 24.5935 | 20.5309 | 18.702

## Primary Headroom Gen
Grid Supply Point | Bulk Supply Point | Primary Substation | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Generation Headroom Winter MVA | [13 empty] | Generation Headroom Summer MVA | [13 empty] | Generation Headroom Spring/Autumn MVA
[6 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050
MANNINGTON GSP | BOURNEMOUTH | ALDERNEY | MINIMUM HEADROOM | SZ 04270 95141 | YES | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.0425 | 28.9143 | 28.8989 | 28.8687 | 28.8386 | 28.8077 | 28.7217 | 28.6357 | 28.5498 | 28.458 | 28.1735 | 27.5859 | 26.9051 | 29.0425 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.5904 | 29.5454 | 29.628
|  | ALDERNEY | CT |  |  | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.0425 | 28.9143 | 28.8989 | 28.8687 | 28.8386 | 28.8077 | 28.7767 | 28.6907 | 28.6048 | 28.5131 | 28.2285 | 27.6409 | 26.9601 | 29.0425 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.594 | 29.549 | 29.628
|  | ALDERNEY | LW |  |  | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.0425 | 28.9143 | 28.8989 | 28.8687 | 28.8386 | 28.8077 | 28.7217 | 28.6357 | 28.5498 | 28.458 | 28.1735 | 27.5859 | 26.9051 | 29.0425 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.5904 | 29.5454 | 29.628
|  | ALDERNEY | ST |  |  | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.0475 | 29.04 | 28.9145 | 28.9002 | 28.8827 | 28.8615 | 28.811 | 28.7607 | 28.7022 | 28.6396 | 28.4463 | 28.0459 | 27.6011 | 29.0425 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.6207 | 29.5914 | 29.628
|  | ALDERNEY | SP |  |  | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.8643 | 29.2159 | 29.052 | 28.9969 | 28.9947 | 28.9892 | 28.9828 | 28.9701 | 28.9574 | 28.9413 | 28.9171 | 28.8424 | 28.6834 | 28.495 | 29.0425 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628 | 29.628
BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT | MINIMUM HEADROOM | SU 85976 48834 | YES | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.2843 | 22.6228 | 22.619 | 22.6141 | 22.6048 | 22.5957 | 22.5865 | 22.5773 | 22.5695 | 22.5616 | 22.5533 | 22.5275 | 22.474 | 21.6616 | 20.4063 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 21.6349 | 20.3402
|  | ALDERSHOT | CT |  |  | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.2843 | 22.6228 | 22.619 | 22.6141 | 22.6048 | 22.5957 | 22.5865 | 22.5773 | 22.5695 | 22.5616 | 22.5533 | 22.5275 | 22.474 | 21.6616 | 20.4063 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 21.6349 | 20.3402
|  | ALDERSHOT | LW |  |  | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.379 | 22.6233 | 22.6198 | 22.6154 | 22.607 | 22.5988 | 22.5905 | 22.5827 | 22.5748 | 22.567 | 22.5587 | 22.5329 | 22.4793 | 21.7706 | 20.5149 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 21.7473 | 20.452
|  | ALDERSHOT | ST |  |  | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 22.6254 | 22.6235 | 22.6214 | 22.6183 | 22.6145 | 22.6098 | 22.604 | 22.5982 | 22.5928 | 22.5872 | 22.5696 | 22.533 | 22.4926 | 22.4531 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.4925
|  | ALDERSHOT | SP |  |  | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 23.5751 | 22.627 | 22.6264 | 22.6259 | 22.6255 | 22.6243 | 22.6228 | 22.6208 | 22.6188 | 22.6163 | 22.6141 | 22.6073 | 22.5927 | 22.5754 | 22.5578 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729 | 22.7729
MELKSHAM GSP | CHIPPENHAM | ALDERTON | MINIMUM HEADROOM | ST 84609 84059 | YES | 5.0163 | 5.0163 | 5.0163 | 7.4163 | 7.4163 | 7.4163 | 7.4152 | 7.4024 | 7.3638 | 7.3264 | 7.2147 | 7.0034 | 6.7737 | 6.5786 | 3.5407 | 3.5201 | 3.4931 | 6.7359 | 6.6805 | 6.6255 | 6.5711 | 6.5387 | 6.5034 | 6.4696 | 6.3685 | 6.1748 | 5.9631 | 5.7857 | 3.8712 | 3.8423 | 3.8044 | 6.1244 | 6.0468 | 5.9698 | 5.8936 | 5.8489 | 5.8014 | 5.7544 | 5.6145 | 5.3567 | 5.0791 | 4.8368
|  | ALDERTON | CT |  |  | 5.0163 | 5.0163 | 5.0163 | 7.4163 | 7.4163 | 7.4163 | 7.4163 | 7.4024 | 7.3638 | 7.3264 | 7.2147 | 7.0034 | 6.7737 | 6.5786 | 3.5407 | 3.5201 | 3.4931 | 6.7359 | 6.6805 | 6.6255 | 6.5711 | 6.5387 | 6.5034 | 6.4696 | 6.3685 | 6.1748 | 5.9631 | 5.7857 | 3.8712 | 3.8423 | 3.8044 | 6.1244 | 6.0468 | 5.9698 | 5.8936 | 5.8489 | 5.8014 | 5.7544 | 5.6145 | 5.3567 | 5.0791 | 4.8368
|  | ALDERTON | LW |  |  | 5.0163 | 5.0163 | 5.0163 | 7.4163 | 7.4163 | 7.4163 | 7.4152 | 7.4129 | 7.407 | 7.3724 | 7.258 | 7.0648 | 6.8474 | 6.6647 | 3.5432 | 3.5243 | 3.4996 | 6.7473 | 6.6967 | 6.6464 | 6.6143 | 6.5812 | 6.5448 | 6.5108 | 6.407 | 6.2313 | 6.032 | 5.867 | 3.8746 | 3.8482 | 3.8136 | 6.1404 | 6.0694 | 5.9991 | 5.9545 | 5.9091 | 5.8606 | 5.8133 | 5.6707 | 5.431 | 5.1657 | 4.9358
|  | ALDERTON | ST |  |  | 5.0163 | 5.0163 | 5.0163 | 7.4163 | 7.4163 | 7.4163 | 7.416 | 7.4154 | 7.4137 | 7.413 | 7.3966 | 7.2746 | 7.1418 | 7.0195 | 3.5466 | 3.5308 | 3.5122 | 6.7804 | 6.7413 | 6.6941 | 6.6707 | 6.6474 | 6.6248 | 6.6017 | 6.533 | 6.4227 | 6.3014 | 6.1907 | 3.8794 | 3.8573 | 3.8313 | 6.1867 | 6.1319 | 6.0659 | 6.0332 | 6.0008 | 5.9699 | 5.9377 | 5.8429 | 5.69 | 5.5262 | 5.3733
|  | ALDERTON | SP |  |  | 5.0163 | 5.0163 | 5.0163 | 7.4163 | 7.4163 | 7.4163 | 7.4163 | 7.4163 | 7.4162 | 7.416 | 7.4146 | 7.4136 | 7.4101 | 7.4071 | 3.565 | 3.563 | 3.5612 | 6.8593 | 6.8509 | 6.8409 | 6.8328 | 6.8248 | 6.8145 | 6.8056 | 6.7789 | 6.7377 | 6.6958 | 6.6565 | 3.9052 | 3.9024 | 3.8998 | 6.2972 | 6.2854 | 6.2714 | 6.2601 | 6.2489 | 6.2345 | 6.2221 | 6.1853 | 6.128 | 6.0707 | 6.017
BRAMLEY (FLEE) | ALTON | ALRESFORD | MINIMUM HEADROOM | SU 59684 32511 | YES | 17.4778 | 17.4778 | 17.4778 | 24.4778 | 24.4728 | 24.4626 | 24.4465 | 24.4242 | 24.3794 | 24.3716 | 23.9448 | 23.0472 | 22.1225 | 21.2998 | 12.7537 | 12.749 | 12.7426 | 22.7289 | 22.5425 | 22.2545 | 21.9655 | 21.7494 | 21.5193 | 21.3086 | 20.7143 | 19.6852 | 18.6265 | 17.6731 | 15.9452 | 15.9395 | 15.9317 | 22.915 | 22.8968 | 22.8772 | 22.8563 | 22.822 | 22.7645 | 22.7445 | 22.2114 | 21.1714 | 20.1016 | 19.1373
|  | ALRESFORD | CT |  |  | 17.4778 | 17.4778 | 17.4778 | 24.4778 | 24.4763 | 24.4735 | 24.4693 | 24.4631 | 24.4496 | 24.4472 | 23.9448 | 23.0472 | 22.1225 | 21.2998 | 12.7537 | 12.749 | 12.7426 | 22.7289 | 22.5425 | 22.2545 | 21.9655 | 21.7494 | 21.5193 | 21.3086 | 20.7143 | 19.6852 | 18.6265 | 17.6731 | 15.9452 | 15.9395 | 15.9317 | 22.915 | 22.8968 | 22.8772 | 22.8563 | 22.8378 | 22.8116 | 22.7827 | 22.2114 | 21.1714 | 20.1016 | 19.1373
|  | ALRESFORD | LW |  |  | 17.4778 | 17.4778 | 17.4778 | 24.4778 | 24.4728 | 24.4626 | 24.4465 | 24.4242 | 24.3794 | 24.3716 | 24.1805 | 23.2937 | 22.3009 | 21.5013 | 12.7555 | 12.7521 | 12.7473 | 22.7372 | 22.722 | 22.5579 | 22.3369 | 22.1044 | 21.8431 | 21.6272 | 21.0062 | 19.9879 | 18.8611 | 17.9307 | 15.9473 | 15.9432 | 15.9374 | 22.9251 | 22.9076 | 22.8848 | 22.8566 | 22.822 | 22.7645 | 22.7445 | 22.4919 | 21.4788 | 20.3408 | 19.3995
|  | ALRESFORD | ST |  |  | 17.4778 | 17.4778 | 17.4778 | 24.4778 | 24.4767 | 24.4747 | 24.4715 | 24.4668 | 24.4564 | 24.4514 | 24.4244 | 24.3891 | 23.7512 | 23.1943 | 12.757 | 12.7547 | 12.7518 | 22.7468 | 22.7395 | 22.7298 | 22.7199 | 22.6199 | 22.4622 | 22.3152 | 21.8952 | 21.2456 | 20.5167 | 19.8746 | 15.9491 | 15.9464 | 15.9429 | 22.9368 | 22.9281 | 22.9168 | 22.9055 | 22.8924 | 22.8733 | 22.86 | 22.81 | 22.72 | 22.0134 | 21.3643
|  | ALRESFORD | SP |  |  | 17.4778 | 17.4778 | 17.4778 | 24.4778 | 24.4778 | 24.4777 | 24.4776 | 24.4774 | 24.4769 | 24.4752 | 24.4655 | 24.4578 | 24.4208 | 24.3848 | 12.7594 | 12.7591 | 12.7586 | 22.758 | 22.756 | 22.7538 | 22.7512 | 22.7486 | 22.7451 | 22.7407 | 22.7237 | 22.7047 | 22.4666 | 22.226 | 15.9521 | 15.9517 | 15.9511 | 22.9504 | 22.948 | 22.9453 | 22.9422 | 22.9391 | 22.9349 | 22.9299 | 22.9113 | 22.8899 | 22.8401 | 22.792
BRAMLEY (FLEE) | ALTON | ALTON LOCAL | MINIMUM HEADROOM | SU 72434 39606 | YES | 58.704 | 58.6853 | 58.6666 | 57.5266 | 57.0534 | 56.7704 | 56.4497 | 56.09 | 55.5718 | 55.4727 | 55.1246 | 54.2747 | 51.9691 | 50.312 | 55.2628 | 55.2121 | 55.1734 | 53.9962 | 53.4888 | 53.174 | 52.8253 | 52.4376 | 51.8914 | 51.7626 | 51.3276 | 49.2951 | 46.7888 | 44.8218 | 55.7888 | 55.7458 | 55.712 | 54.5438 | 54.0447 | 53.7376 | 53.3956 | 53.0148 | 52.4754 | 52.3537 | 51.6653 | 49.334 | 46.6768 | 44.676
|  | ALTON LOCAL | CT |  |  | 58.7937 | 58.7825 | 58.7713 | 58.0873 | 57.8012 | 57.7303 | 57.6522 | 57.5625 | 57.4454 | 57.4139 | 57.3072 | 55.3849 | 53.3534 | 51.6594 | 55.3472 | 55.3002 | 55.264 | 54.5323 | 54.2017 | 54.0889 | 53.9689 | 53.8511 | 53.7061 | 53.6448 | 53.0338 | 50.3232 | 48.0596 | 46.0283 | 55.8745 | 55.8361 | 55.806 | 55.0858 | 54.766 | 54.6634 | 54.5536 | 54.4426 | 54.3044 | 54.2503 | 53.1602 | 50.3004 | 47.9174 | 45.8798
|  | ALTON LOCAL | LW |  |  | 58.704 | 58.6853 | 58.6666 | 57.5266 | 57.0534 | 56.7704 | 56.4497 | 56.09 | 55.5718 | 55.4727 | 55.1246 | 54.2747 | 51.9691 | 50.312 | 55.2628 | 55.2121 | 55.1734 | 53.9962 | 53.4888 | 53.174 | 52.8253 | 52.4376 | 51.8914 | 51.7626 | 51.3276 | 49.2951 | 46.7888 | 44.8218 | 55.7888 | 55.7458 | 55.712 | 54.5438 | 54.0447 | 53.7376 | 53.3956 | 53.0148 | 52.4754 | 52.3537 | 51.6653 | 49.334 | 46.6768 | 44.676
|  | ALTON LOCAL | ST |  |  | 58.8386 | 58.8311 | 58.8236 | 58.3676 | 58.3247 | 58.2764 | 58.2222 | 58.1597 | 58.0775 | 58.0447 | 57.9238 | 57.7636 | 57.4373 | 56.7799 | 55.4019 | 55.3836 | 55.3462 | 54.8702 | 54.8049 | 54.7314 | 54.6565 | 54.5734 | 54.472 | 54.419 | 54.2395 | 53.9844 | 52.9818 | 51.7667 | 55.9268 | 55.9111 | 55.8809 | 55.4098 | 55.35 | 55.2826 | 55.2127 | 55.1345 | 55.0378 | 54.9897 | 54.8244 | 54.5092 | 53.0913 | 51.7803
|  | ALTON LOCAL | SP |  |  | 58.8834 | 58.8797 | 58.8759 | 58.6479 | 58.629 | 58.6099 | 58.5904 | 58.5705 | 58.5492 | 58.5314 | 58.4499 | 58.3657 | 58.1205 | 57.8624 | 55.4566 | 55.4499 | 55.438 | 55.2071 | 55.1825 | 55.1575 | 55.131 | 55.104 | 55.0737 | 55.0481 | 54.944 | 54.8238 | 54.5451 | 54.2557 | 55.9791 | 55.9731 | 55.9632 | 55.733 | 55.7098 | 55.6862 | 55.6614 | 55.6362 | 55.608 | 55.5843 | 55.4856 | 55.3742 | 55.1036 | 54.8218
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER | MINIMUM HEADROOM | SU 35240 46643 | YES | 33.3211 | 33.3211 | 33.3211 | 33.3211 | 33.3204 | 33.319 | 33.3168 | 33.3138 | 33.3078 | 33.3067 | 33.3014 | 33.2884 | 33.2631 | 33.2396 | 32.4195 | 32.4173 | 32.4144 | 32.4083 | 32.4016 | 32.3943 | 32.3856 | 32.3761 | 32.3636 | 32.3556 | 32.3 | 32.0602 | 31.3614 | 30.6944 | 32.2782 | 32.2782 | 32.2782 | 32.2782 | 32.2775 | 32.2762 | 32.274 | 32.271 | 32.2649 | 32.2639 | 32.2585 | 32.2456 | 31.9403 | 31.2654
|  | ANDOVER | CT |  |  | 33.3211 | 33.3211 | 33.3211 | 33.3211 | 33.3209 | 33.3205 | 33.3199 | 33.3191 | 33.3173 | 33.3169 | 33.3152 | 33.3008 | 33.2846 | 33.2665 | 32.4201 | 32.4184 | 32.416 | 32.4111 | 32.4061 | 32.4009 | 32.3956 | 32.3883 | 32.38 | 32.3728 | 32.3503 | 32.1377 | 31.5045 | 30.8344 | 32.2782 | 32.2782 | 32.2782 | 32.2782 | 32.278 | 32.2776 | 32.2771 | 32.2762 | 32.2744 | 32.2741 | 32.2723 | 32.2579 | 32.0849 | 31.4069
|  | ANDOVER | LW |  |  | 33.3211 | 33.3211 | 33.3211 | 33.3211 | 33.3204 | 33.319 | 33.3168 | 33.3138 | 33.3078 | 33.3067 | 33.3014 | 33.2884 | 33.2631 | 33.2396 | 32.4195 | 32.4173 | 32.4144 | 32.4083 | 32.4016 | 32.3943 | 32.3856 | 32.3761 | 32.3636 | 32.3556 | 32.3 | 32.0602 | 31.3614 | 30.6944 | 32.2782 | 32.2782 | 32.2782 | 32.2782 | 32.2775 | 32.2762 | 32.274 | 32.271 | 32.2649 | 32.2639 | 32.2585 | 32.2456 | 31.9403 | 31.2654
|  | ANDOVER | ST |  |  | 33.3211 | 33.3211 | 33.3211 | 33.3211 | 33.3209 | 33.3206 | 33.3202 | 33.3196 | 33.3182 | 33.3175 | 33.3139 | 33.3091 | 33.2923 | 33.2862 | 32.4198 | 32.4179 | 32.4156 | 32.4117 | 32.4068 | 32.4008 | 32.3957 | 32.3904 | 32.3846 | 32.3792 | 32.3616 | 32.282 | 32.1272 | 31.7423 | 32.2782 | 32.2782 | 32.2782 | 32.2782 | 32.2781 | 32.2778 | 32.2774 | 32.2767 | 32.2753 | 32.2746 | 32.271 | 32.2662 | 32.2495 | 32.2434
|  | ANDOVER | SP |  |  | 33.3211 | 33.3211 | 33.3211 | 33.3211 | 33.3211 | 33.321 | 33.321 | 33.321 | 33.3209 | 33.3207 | 33.3194 | 33.3184 | 33.3134 | 33.3085 | 32.4221 | 32.4218 | 32.4216 | 32.4214 | 32.4204 | 32.4191 | 32.4176 | 32.416 | 32.414 | 32.4119 | 32.4052 | 32.3949 | 32.3805 | 32.3664 | 32.2782 | 32.2782 | 32.2782 | 32.2782 | 32.2782 | 32.2782 | 32.2782 | 32.2782 | 32.2781 | 32.2779 | 32.2766 | 32.2755 | 32.2705 | 32.2656
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST | MINIMUM HEADROOM | SU 37953 46433 | YES | 36.0108 | 35.9969 | 35.9829 | 35.1313 | 34.9144 | 34.6916 | 34.4606 | 34.2224 | 33.8943 | 33.8302 | 33.6194 | 33.2454 | 32.7233 | 32.2047 | 35.5042 | 35.4682 | 35.4486 | 34.5856 | 34.3571 | 34.1223 | 33.8799 | 33.6306 | 33.2919 | 33.2166 | 32.9726 | 32.5791 | 31.3934 | 30.24 | 35.8346 | 35.7986 | 35.7789 | 34.9159 | 34.6874 | 34.4525 | 34.2101 | 33.9608 | 33.622 | 33.5467 | 33.3026 | 32.909 | 32.0253 | 30.8716
|  | ANDOVER EAST | CT |  |  | 36.0778 | 36.0695 | 36.0611 | 35.5501 | 35.5079 | 35.4653 | 35.4224 | 35.3791 | 35.3339 | 35.3166 | 35.2632 | 34.5948 | 34.2814 | 33.8206 | 35.5715 | 35.5414 | 35.5276 | 35.0059 | 34.9527 | 34.8988 | 34.8446 | 34.7902 | 34.7344 | 34.7059 | 34.6193 | 33.9278 | 32.9999 | 31.8668 | 35.902 | 35.8718 | 35.858 | 35.3363 | 35.283 | 35.2291 | 35.1748 | 35.1204 | 35.0646 | 35.036 | 34.9494 | 34.2576 | 33.6318 | 32.4984
|  | ANDOVER EAST | LW |  |  | 36.0108 | 35.9969 | 35.9829 | 35.1313 | 34.9144 | 34.6916 | 34.4606 | 34.2224 | 33.8943 | 33.8302 | 33.6194 | 33.2454 | 32.7233 | 32.2047 | 35.5042 | 35.4682 | 35.4486 | 34.5856 | 34.3571 | 34.1223 | 33.8799 | 33.6306 | 33.2919 | 33.2166 | 32.9726 | 32.5791 | 31.3934 | 30.24 | 35.8346 | 35.7986 | 35.7789 | 34.9159 | 34.6874 | 34.4525 | 34.2101 | 33.9608 | 33.622 | 33.5467 | 33.3026 | 32.909 | 32.0253 | 30.8716
|  | ANDOVER EAST | ST |  |  | 36.1114 | 36.1058 | 36.1002 | 35.7595 | 35.7314 | 35.7029 | 35.6743 | 35.6452 | 35.6148 | 35.6024 | 35.5624 | 35.4981 | 35.4279 | 35.3115 | 35.6056 | 35.5948 | 35.5689 | 35.2209 | 35.1833 | 35.1434 | 35.11 | 35.0764 | 35.0388 | 35.0187 | 34.9563 | 34.8552 | 34.756 | 34.6482 | 35.936 | 35.9252 | 35.8993 | 35.5512 | 35.5137 | 35.4737 | 35.4402 | 35.4067 | 35.369 | 35.3489 | 35.2864 | 35.1853 | 35.0859 | 34.978
|  | ANDOVER EAST | SP |  |  | 36.1449 | 36.1421 | 36.1393 | 35.969 | 35.955 | 35.941 | 35.927 | 35.913 | 35.8989 | 35.8929 | 35.8739 | 35.8441 | 35.8184 | 35.779 | 35.6437 | 35.6393 | 35.6269 | 35.4561 | 35.4401 | 35.4236 | 35.408 | 35.3925 | 35.3767 | 35.3677 | 35.3399 | 35.2961 | 35.2573 | 35.2054 | 35.9741 | 35.9697 | 35.9574 | 35.7866 | 35.7705 | 35.754 | 35.7384 | 35.7229 | 35.7071 | 35.6981 | 35.6703 | 35.6265 | 35.5876 | 35.5357
BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER TOWN | MINIMUM HEADROOM | SU 36207 45078 | YES | 15.9377 | 15.9377 | 15.9377 | 15.9377 | 15.9371 | 15.9357 | 15.9336 | 15.9307 | 15.9249 | 15.9238 | 15.6303 | 14.9998 | 14.2951 | 13.6185 | 12.1583 | 12.1576 | 12.1567 | 12.1548 | 12.1528 | 12.1497 | 12.1407 | 12.1309 | 12.1182 | 12.1099 | 12.0825 | 12.0289 | 11.2872 | 10.4984 | 11.7407 | 11.7288 | 11.7132 | 11.6818 | 11.6505 | 11.6186 | 11.5062 | 11.3854 | 11.2623 | 11.1355 | 10.7502 | 10.0349 | 9.237 | 8.468
|  | ANDOVER TOWN | CT |  |  | 15.9377 | 15.9377 | 15.9377 | 15.9377 | 15.9375 | 15.9371 | 15.9366 | 15.9358 | 15.934 | 15.9337 | 15.7115 | 15.0798 | 14.384 | 13.7047 | 12.1583 | 12.1576 | 12.1567 | 12.1548 | 12.1528 | 12.1506 | 12.1482 | 12.1405 | 12.1319 | 12.1242 | 12.1003 | 12.0454 | 11.3875 | 10.596 | 11.7407 | 11.7288 | 11.7132 | 11.6818 | 11.6505 | 11.6186 | 11.5866 | 11.4679 | 11.349 | 11.2228 | 10.8409 | 10.1243 | 9.3353 | 8.5635
|  | ANDOVER TOWN | LW |  |  | 15.9377 | 15.9377 | 15.9377 | 15.9377 | 15.9371 | 15.9357 | 15.9336 | 15.9307 | 15.9249 | 15.9238 | 15.6303 | 14.9998 | 14.2951 | 13.6185 | 12.1583 | 12.1577 | 12.1568 | 12.1551 | 12.1528 | 12.1497 | 12.1407 | 12.1309 | 12.1182 | 12.1099 | 12.0825 | 12.0289 | 11.2872 | 10.4984 | 11.7418 | 11.7308 | 11.7162 | 11.687 | 11.6574 | 11.6268 | 11.5062 | 11.3854 | 11.2623 | 11.1355 | 10.7502 | 10.0349 | 9.237 | 8.468
|  | ANDOVER TOWN | ST |  |  | 15.9377 | 15.9377 | 15.9377 | 15.9377 | 15.9376 | 15.9373 | 15.9369 | 15.9363 | 15.9349 | 15.9343 | 15.8522 | 15.4574 | 14.9995 | 14.5587 | 12.1583 | 12.1577 | 12.157 | 12.1558 | 12.1541 | 12.1521 | 12.1464 | 12.1405 | 12.1345 | 12.1288 | 12.1102 | 12.078 | 12.0324 | 11.591 | 11.7417 | 11.7311 | 11.7185 | 11.6977 | 11.672 | 11.641 | 11.5499 | 11.4596 | 11.3782 | 11.2915 | 11.0308 | 10.5526 | 10.0342 | 9.5337
|  | ANDOVER TOWN | SP |  |  | 15.9377 | 15.9377 | 15.9377 | 15.9377 | 15.9377 | 15.9377 | 15.9377 | 15.9376 | 15.9376 | 15.9374 | 15.9361 | 15.9351 | 15.9166 | 15.7645 | 12.159 | 12.1589 | 12.1588 | 12.1587 | 12.1584 | 12.158 | 12.1563 | 12.1546 | 12.1524 | 12.1502 | 12.1432 | 12.1314 | 12.1149 | 12.0986 | 11.7534 | 11.7516 | 11.7498 | 11.7481 | 11.743 | 11.737 | 11.7079 | 11.6792 | 11.6423 | 11.6087 | 11.5078 | 11.3223 | 11.1177 | 10.9145
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD | MINIMUM HEADROOM | SU 75949 65766 | YES | 27.4437 | 27.4305 | 27.4172 | 26.6091 | 26.4666 | 26.3174 | 26.16 | 25.9949 | 25.7694 | 25.7196 | 25.5497 | 25.2518 | 24.8641 | 24.566 | 25.1622 | 25.1489 | 25.1357 | 24.3276 | 24.185 | 24.0358 | 23.8785 | 23.6454 | 23.3242 | 23.1715 | 22.6963 | 21.8883 | 20.9725 | 20.2862 | 26.2398 | 26.2265 | 26.2133 | 25.4052 | 25.2626 | 25.1134 | 24.9561 | 24.7909 | 24.5655 | 24.5157 | 24.3457 | 24.0479 | 23.6602 | 23.2206
|  | ARBORFIELD | CT |  |  | 27.5073 | 27.4994 | 27.4914 | 27.0066 | 26.9656 | 26.9235 | 26.8804 | 26.8356 | 26.7849 | 26.767 | 26.7088 | 26.0421 | 25.7404 | 25.3534 | 25.2258 | 25.2178 | 25.2099 | 24.725 | 24.684 | 24.642 | 24.5343 | 24.3927 | 24.2462 | 24.1253 | 23.7619 | 22.585 | 21.7554 | 21.0601 | 26.3034 | 26.2954 | 26.2875 | 25.8026 | 25.7617 | 25.7196 | 25.6764 | 25.6317 | 25.5809 | 25.5631 | 25.5048 | 24.8381 | 24.5365 | 23.9916
|  | ARBORFIELD | LW |  |  | 27.4437 | 27.4305 | 27.4172 | 26.6091 | 26.4666 | 26.3174 | 26.16 | 25.9949 | 25.7694 | 25.7196 | 25.5497 | 25.2518 | 24.8641 | 24.566 | 25.1622 | 25.1489 | 25.1357 | 24.3276 | 24.185 | 24.0358 | 23.8785 | 23.6454 | 23.3242 | 23.1715 | 22.6963 | 21.8883 | 20.9725 | 20.2862 | 26.2398 | 26.2265 | 26.2133 | 25.4052 | 25.2626 | 25.1134 | 24.9561 | 24.7909 | 24.5655 | 24.5157 | 24.3457 | 24.0479 | 23.6602 | 23.2206
|  | ARBORFIELD | ST |  |  | 27.5391 | 27.5338 | 27.5285 | 27.2053 | 27.1779 | 27.1497 | 27.1207 | 27.0904 | 27.0553 | 27.0407 | 26.9869 | 26.9051 | 26.7723 | 26.6773 | 25.2575 | 25.2522 | 25.247 | 24.9237 | 24.8964 | 24.8682 | 24.8391 | 24.8088 | 24.7738 | 24.7591 | 24.6302 | 24.2082 | 23.7349 | 23.3018 | 26.3352 | 26.3299 | 26.3246 | 26.0013 | 25.974 | 25.9458 | 25.9167 | 25.8864 | 25.8514 | 25.8367 | 25.783 | 25.7012 | 25.5683 | 25.4733
|  | ARBORFIELD | SP |  |  | 27.5709 | 27.5682 | 27.5656 | 27.404 | 27.3907 | 27.3774 | 27.364 | 27.3506 | 27.337 | 27.3303 | 27.3065 | 27.2737 | 27.2277 | 27.1691 | 25.2893 | 25.2867 | 25.284 | 25.1224 | 25.1092 | 25.0958 | 25.0825 | 25.0691 | 25.0555 | 25.0488 | 25.025 | 24.9922 | 24.9461 | 24.8876 | 26.367 | 26.3643 | 26.3617 | 26.2 | 26.1868 | 26.1735 | 26.1601 | 26.1467 | 26.1331 | 26.1264 | 26.1026 | 26.0698 | 26.0238 | 25.9652
LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD | MINIMUM HEADROOM | SZ 93193 99152 | NO | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 35.1247 | 33.9705 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 25.7444 | 24.3517 | 22.9515 | 22.9583 | 22.7635 | 22.737 | 22.6879 | 22.6375 | 22.5838 | 22.4416 | 22.2984 | 22.155 | 22.0029 | 21.5147 | 20.3688 | 18.9757 | 17.5751
|  | ARGYLE ROAD | CT |  |  | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 35.1951 | 34.0459 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 25.833 | 24.4405 | 23.0405 | 22.9584 | 22.7636 | 22.737 | 22.688 | 22.6376 | 22.584 | 22.5302 | 22.3873 | 22.2439 | 22.0918 | 21.6036 | 20.4575 | 19.0646 | 17.6641
|  | ARGYLE ROAD | LW |  |  | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 35.1247 | 33.9705 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 25.7444 | 24.3517 | 22.9515 | 22.9583 | 22.7635 | 22.737 | 22.6879 | 22.6375 | 22.5838 | 22.4416 | 22.2984 | 22.155 | 22.0029 | 21.5147 | 20.3688 | 18.9757 | 17.5751
|  | ARGYLE ROAD | ST |  |  | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 35.4552 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 25.661 | 24.7688 | 22.9672 | 22.9524 | 22.7639 | 22.7397 | 22.7099 | 22.6732 | 22.6007 | 22.5276 | 22.43 | 22.3262 | 21.9926 | 21.2023 | 20.2855 | 19.3929
|  | ARGYLE ROAD | SP |  |  | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 36.0004 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 26.4494 | 22.9783 | 22.9724 | 22.7948 | 22.7897 | 22.7795 | 22.7674 | 22.7465 | 22.7255 | 22.6996 | 22.6593 | 22.5298 | 22.2092 | 21.7989 | 21.3679
COWLEY GSP | HEADINGTON BSP | ARNCOTT | MINIMUM HEADROOM | SP 60730 18095 | NO | 18.2609 | 18.2609 | 18.2609 | 17.8398 | 17.7562 | 17.668 | 17.5725 | 17.4674 | 17.2105 | 17.0868 | 16.7753 | 16.2851 | 15.6399 | 15.3308 | 17.0258 | 17.0206 | 16.9791 | 16.5285 | 16.3095 | 15.9694 | 15.7397 | 15.5153 | 15.2182 | 15.0518 | 14.6657 | 14.0888 | 13.3634 | 12.9905 | 16.111 | 16.0548 | 15.6194 | 15.0021 | 14.71 | 14.406 | 14.1955 | 13.9886 | 13.7109 | 13.5649 | 13.2215 | 12.7044 | 12.0344 | 11.7117
|  | ARNCOTT | CT |  |  | 18.2609 | 18.2609 | 18.2609 | 17.8398 | 17.8392 | 17.8381 | 17.8364 | 17.8323 | 17.7543 | 17.6521 | 17.4233 | 17.0158 | 16.6151 | 16.3008 | 17.0267 | 17.022 | 16.9824 | 16.5348 | 16.4618 | 16.2289 | 16.0457 | 15.9196 | 15.7745 | 15.6297 | 15.3225 | 14.8283 | 14.3473 | 13.967 | 16.12 | 16.0703 | 15.6433 | 15.0441 | 14.8524 | 14.6527 | 14.4955 | 14.3869 | 14.2611 | 14.1368 | 13.8722 | 13.4379 | 13.0122 | 12.6821
|  | ARNCOTT | LW |  |  | 18.2609 | 18.2609 | 18.2609 | 17.8398 | 17.7562 | 17.668 | 17.5725 | 17.4674 | 17.2105 | 17.0868 | 16.7753 | 16.2851 | 15.6399 | 15.3308 | 17.0258 | 17.0206 | 16.9791 | 16.5285 | 16.3095 | 15.9694 | 15.7397 | 15.5153 | 15.2182 | 15.0518 | 14.6657 | 14.0888 | 13.3634 | 12.9905 | 16.111 | 16.0548 | 15.6194 | 15.0021 | 14.71 | 14.406 | 14.1955 | 13.9886 | 13.7109 | 13.5649 | 13.2215 | 12.7044 | 12.0344 | 11.7117
|  | ARNCOTT | ST |  |  | 18.2609 | 18.2609 | 18.2609 | 18.2609 | 18.2604 | 18.2596 | 18.2581 | 18.2556 | 18.2497 | 18.247 | 18.2331 | 18.2149 | 17.9975 | 17.812 | 17.0267 | 17.0224 | 17.0166 | 17.0049 | 16.9903 | 16.9684 | 16.9537 | 16.9391 | 16.9156 | 16.815 | 16.5964 | 16.2961 | 15.9816 | 15.7301 | 16.1207 | 16.0742 | 16.0114 | 15.8864 | 15.7333 | 15.5555 | 15.4666 | 15.3839 | 15.3 | 15.2134 | 15.0241 | 14.7642 | 14.4855 | 14.2668
|  | ARNCOTT | SP |  |  | 18.2609 | 18.2609 | 18.2609 | 18.2609 | 18.2608 | 18.2608 | 18.2608 | 18.2607 | 18.2604 | 18.2595 | 18.2542 | 18.2501 | 18.232 | 18.2145 | 17.05 | 17.0299 | 17.0283 | 17.0251 | 17.0203 | 17.0151 | 17.0119 | 17.0091 | 17.0055 | 17.0015 | 16.9899 | 16.9771 | 16.9506 | 16.923 | 16.3715 | 16.1546 | 16.1377 | 16.1034 | 16.0515 | 15.996 | 15.9627 | 15.9332 | 15.8968 | 15.8629 | 15.7891 | 15.6911 | 15.593 | 15.5082
BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT | MINIMUM HEADROOM | SU 91615 68855 | YES | 36.4924 | 36.4924 | 36.4924 | 36.4924 | 36.4918 | 36.4906 | 36.4888 | 36.4862 | 36.481 | 36.4802 | 36.4756 | 36.4646 | 35.8243 | 35.0537 | 35.5961 | 35.5961 | 35.5961 | 35.5961 | 35.5955 | 35.5943 | 35.5925 | 35.5899 | 35.5847 | 35.5838 | 35.3847 | 34.6111 | 33.716 | 32.823 | 35.5062 | 35.5062 | 35.5062 | 35.5062 | 35.5057 | 35.5045 | 35.5026 | 35.5001 | 35.4949 | 35.494 | 35.2066 | 34.3512 | 33.4211 | 32.5126
|  | ASCOT | CT |  |  | 36.4924 | 36.4924 | 36.4924 | 36.4924 | 36.4922 | 36.4919 | 36.4914 | 36.4907 | 36.4891 | 36.4889 | 36.4874 | 36.4751 | 35.8243 | 35.0537 | 35.5961 | 35.5961 | 35.5961 | 35.5961 | 35.5959 | 35.5956 | 35.5951 | 35.5944 | 35.5928 | 35.5925 | 35.3847 | 34.6111 | 33.716 | 32.823 | 35.5062 | 35.5062 | 35.5062 | 35.5062 | 35.5061 | 35.5057 | 35.5052 | 35.5045 | 35.503 | 35.5027 | 35.2066 | 34.3512 | 33.4211 | 32.5126
|  | ASCOT | LW |  |  | 36.4924 | 36.4924 | 36.4924 | 36.4924 | 36.4918 | 36.4906 | 36.4888 | 36.4862 | 36.481 | 36.4802 | 36.4756 | 36.4646 | 35.9308 | 35.1629 | 35.5961 | 35.5961 | 35.5961 | 35.5961 | 35.5955 | 35.5943 | 35.5925 | 35.5899 | 35.5847 | 35.5838 | 35.5061 | 34.7339 | 33.8424 | 32.9521 | 35.5062 | 35.5062 | 35.5062 | 35.5062 | 35.5057 | 35.5045 | 35.5026 | 35.5001 | 35.4949 | 35.494 | 35.3423 | 34.4883 | 33.5501 | 32.6442
|  | ASCOT | ST |  |  | 36.4924 | 36.4924 | 36.4924 | 36.4924 | 36.4923 | 36.492 | 36.4917 | 36.4911 | 36.4899 | 36.4893 | 36.4862 | 36.4822 | 36.4679 | 36.4627 | 35.5961 | 35.5961 | 35.5961 | 35.5961 | 35.596 | 35.5957 | 35.5953 | 35.5948 | 35.5936 | 35.593 | 35.5899 | 35.5859 | 35.2986 | 34.7678 | 35.5062 | 35.5062 | 35.5062 | 35.5062 | 35.5061 | 35.5059 | 35.5055 | 35.505 | 35.5038 | 35.5032 | 35.5001 | 35.496 | 35.1133 | 34.5261
|  | ASCOT | SP |  |  | 36.4924 | 36.4924 | 36.4924 | 36.4924 | 36.4924 | 36.4924 | 36.4924 | 36.4923 | 36.4923 | 36.4921 | 36.491 | 36.4901 | 36.4858 | 36.4817 | 35.5961 | 35.5961 | 35.5961 | 35.5961 | 35.5961 | 35.5961 | 35.596 | 35.596 | 35.596 | 35.5958 | 35.5947 | 35.5938 | 35.5895 | 35.5854 | 35.5062 | 35.5062 | 35.5062 | 35.5062 | 35.5062 | 35.5062 | 35.5062 | 35.5062 | 35.5061 | 35.5059 | 35.5048 | 35.5039 | 35.4997 | 35.4955
LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD | MINIMUM HEADROOM | SU 84085 06737 | YES | 32.4296 | 32.4167 | 32.4038 | 31.6175 | 43.5067 | 43.3943 | 43.2799 | 43.1636 | 43.0204 | 42.9837 | 42.869 | 42.2783 | 40.5124 | 38.9935 | 25.5775 | 25.5262 | 25.4895 | 24.685 | 42.5527 | 42.4187 | 42.2824 | 42.1433 | 41.9755 | 41.7288 | 39.59 | 36.772 | 34.667 | 32.9134 | 31.9673 | 31.9544 | 31.9415 | 31.1552 | 43.0443 | 42.932 | 42.8175 | 42.7013 | 42.5581 | 42.2669 | 40.0642 | 37.1759 | 35.0201 | 33.2331
|  | ASHLING ROAD | CT |  |  | 32.4915 | 32.4837 | 32.476 | 32.0042 | 43.8731 | 43.7405 | 43.6063 | 43.4679 | 43.2754 | 43.2404 | 43.1315 | 42.2783 | 40.5124 | 38.9935 | 25.6399 | 25.5942 | 25.5632 | 25.0743 | 42.9228 | 42.7695 | 42.6155 | 42.4543 | 42.2372 | 42.132 | 39.9993 | 36.772 | 34.667 | 32.9134 | 32.0291 | 32.0214 | 32.0137 | 31.5419 | 43.4108 | 43.2782 | 43.144 | 43.0055 | 42.8131 | 42.6748 | 40.4782 | 37.1759 | 35.0201 | 33.2331
|  | ASHLING ROAD | LW |  |  | 32.4296 | 32.4167 | 32.4038 | 31.6175 | 43.5067 | 43.3943 | 43.2799 | 43.1636 | 43.0204 | 42.9837 | 42.869 | 42.6662 | 41.0735 | 39.6175 | 25.5775 | 25.5262 | 25.4895 | 24.685 | 42.5527 | 42.4187 | 42.2824 | 42.1433 | 41.9755 | 41.7288 | 39.59 | 37.0313 | 35.207 | 33.5139 | 31.9673 | 31.9544 | 31.9415 | 31.1552 | 43.0443 | 42.932 | 42.8175 | 42.7013 | 42.5581 | 42.2669 | 40.0642 | 37.4306 | 35.5554 | 33.831
|  | ASHLING ROAD | ST |  |  | 32.5224 | 32.5172 | 32.5121 | 32.1976 | 44.1718 | 44.146 | 44.1202 | 44.0944 | 44.0687 | 44.0584 | 44.0274 | 43.9759 | 43.9449 | 43.8882 | 25.6736 | 25.6645 | 25.622 | 25.2992 | 43.2617 | 43.2227 | 43.1814 | 43.1395 | 43.0971 | 43.0685 | 42.9728 | 41.4493 | 40.3822 | 39.3319 | 32.0601 | 32.0549 | 32.0498 | 31.7352 | 43.7095 | 43.6837 | 43.6579 | 43.6321 | 43.6063 | 43.596 | 43.5651 | 41.9473 | 40.8475 | 39.7658
|  | ASHLING ROAD | SP |  |  | 32.5533 | 32.5508 | 32.5482 | 32.3909 | 44.378 | 44.3651 | 44.3523 | 44.3394 | 44.3265 | 44.3213 | 44.3058 | 44.2801 | 44.2646 | 44.2362 | 25.7071 | 25.7029 | 25.6788 | 25.5191 | 43.501 | 43.4827 | 43.464 | 43.4451 | 43.425 | 43.4127 | 43.3717 | 43.3164 | 43.2836 | 43.2398 | 32.091 | 32.0884 | 32.0859 | 31.9286 | 43.9157 | 43.9028 | 43.8899 | 43.877 | 43.8641 | 43.859 | 43.8435 | 43.8177 | 43.8023 | 43.7739
MELKSHAM GSP | NORRINGTON | ASHTON PARK | MINIMUM HEADROOM | ST 87141 57741 | NO | 37.8906 | 37.8906 | 37.8906 | 46.6906 | 46.6875 | 46.6812 | 46.666 | 46.6285 | 46.5771 | 46.5477 | 46.4523 | 46.2045 | 44.6895 | 43.3267 | 31.7074 | 31.5259 | 31.292 | 37.7122 | 37.4199 | 37.1503 | 36.8149 | 36.4734 | 36.1175 | 35.7714 | 34.7623 | 33.0657 | 31.2936 | 29.6819 | 33.7817 | 33.6082 | 33.3846 | 41.8214 | 41.5419 | 41.2838 | 40.9627 | 40.6356 | 40.2941 | 39.963 | 38.9972 | 37.3839 | 35.7378 | 34.248
|  | ASHTON PARK | CT |  |  | 37.8906 | 37.8906 | 37.8906 | 46.6906 | 46.6897 | 46.6879 | 46.6853 | 46.6735 | 46.6415 | 46.6154 | 46.5364 | 46.3531 | 45.0412 | 43.6644 | 31.728 | 31.5615 | 31.347 | 37.8084 | 37.5583 | 37.3329 | 37.1182 | 36.7867 | 36.4502 | 36.1073 | 35.1148 | 33.4214 | 31.6918 | 30.0663 | 33.8014 | 33.6421 | 33.4371 | 41.9134 | 41.6742 | 41.4586 | 41.2533 | 40.9362 | 40.6141 | 40.2862 | 39.337 | 37.7169 | 36.1132 | 34.6096
|  | ASHTON PARK | LW |  |  | 37.8906 | 37.8906 | 37.8906 | 46.6906 | 46.6875 | 46.6812 | 46.666 | 46.6285 | 46.5771 | 46.5477 | 46.4523 | 46.2045 | 44.6895 | 43.3267 | 31.7074 | 31.5259 | 31.292 | 37.7122 | 37.4199 | 37.1503 | 36.8149 | 36.4734 | 36.1175 | 35.7714 | 34.7623 | 33.0657 | 31.2936 | 29.6819 | 33.7817 | 33.6082 | 33.3846 | 41.8214 | 41.5419 | 41.2838 | 40.9627 | 40.6356 | 40.2941 | 39.963 | 38.9972 | 37.3839 | 35.7378 | 34.248
|  | ASHTON PARK | ST |  |  | 37.8906 | 37.8906 | 37.8906 | 46.6906 | 46.6899 | 46.6887 | 46.6867 | 46.6838 | 46.6768 | 46.6569 | 46.5921 | 46.4917 | 46.3405 | 45.882 | 31.7292 | 31.5834 | 31.4111 | 37.9662 | 37.7435 | 37.4997 | 37.3089 | 37.1161 | 36.886 | 36.6496 | 35.9655 | 34.8547 | 33.7456 | 32.6858 | 33.8025 | 33.6631 | 33.4984 | 42.0642 | 41.8513 | 41.6182 | 41.4357 | 41.2512 | 41.0309 | 40.8048 | 40.15 | 39.0871 | 38.0233 | 37.0322
|  | ASHTON PARK | SP |  |  | 37.8906 | 37.8906 | 37.8906 | 46.6906 | 46.6906 | 46.6905 | 46.6904 | 46.6903 | 46.69 | 46.689 | 46.683 | 46.6782 | 46.6553 | 46.6114 | 31.968 | 31.7584 | 31.6923 | 38.4241 | 38.3632 | 38.305 | 38.2443 | 38.1833 | 38.1072 | 38.0153 | 37.7503 | 37.3271 | 36.9243 | 36.55 | 34.0308 | 33.8304 | 33.7673 | 42.5021 | 42.4438 | 42.3882 | 42.3301 | 42.2718 | 42.1991 | 42.1111 | 41.8575 | 41.4527 | 41.0666 | 40.7078
BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT | MINIMUM HEADROOM | SU 91122 63523 | YES | 28.8388 | 28.8366 | 28.827 | 28.8068 | 28.6907 | 28.5682 | 28.4439 | 28.3201 | 28.1348 | 28.1 | 27.9897 | 27.5781 | 27.1351 | 26.5314 | 27.7363 | 27.728 | 27.7171 | 27.6941 | 27.5761 | 27.4512 | 27.3245 | 27.199 | 27.0121 | 26.9756 | 26.86 | 26.2914 | 24.9695 | 23.8313 | 23.8674 | 23.7713 | 23.6452 | 23.3798 | 23.1006 | 22.7637 | 22.4268 | 22.1584 | 21.8297 | 21.6405 | 21.0678 | 19.8326 | 18.5009 | 17.4465
|  | BAGSHOT | CT |  |  | 28.8388 | 28.8382 | 28.8295 | 28.8112 | 28.6907 | 28.5682 | 28.4439 | 28.3201 | 28.1348 | 28.1 | 27.9897 | 27.5781 | 27.1351 | 26.5314 | 27.7374 | 27.7299 | 27.7199 | 27.6991 | 27.5761 | 27.4512 | 27.3245 | 27.199 | 27.0121 | 26.9756 | 26.86 | 26.2914 | 24.9695 | 23.8313 | 23.8797 | 23.7924 | 23.6779 | 23.4371 | 23.1006 | 22.7637 | 22.4268 | 22.1584 | 21.8297 | 21.6405 | 21.0678 | 19.8326 | 18.5009 | 17.4465
|  | BAGSHOT | LW |  |  | 28.8388 | 28.8366 | 28.827 | 28.8068 | 28.7732 | 28.7381 | 28.7086 | 28.6773 | 28.6336 | 28.6161 | 28.5589 | 28.4544 | 28.3123 | 27.7789 | 27.7363 | 27.728 | 27.7171 | 27.6941 | 27.6578 | 27.62 | 27.5888 | 27.5559 | 27.5106 | 27.4914 | 27.4289 | 27.1387 | 26.1141 | 25.0736 | 23.8674 | 23.7713 | 23.6452 | 23.3798 | 23.1081 | 22.8367 | 22.6617 | 22.4858 | 22.2986 | 22.1268 | 21.6071 | 20.6793 | 19.6484 | 18.6916
|  | BAGSHOT | ST |  |  | 28.8388 | 28.8388 | 28.8388 | 28.8314 | 28.8213 | 28.8089 | 28.7984 | 28.7876 | 28.7772 | 28.7674 | 28.7358 | 28.6825 | 28.6078 | 28.5511 | 27.7413 | 27.7367 | 27.7313 | 27.7222 | 27.7107 | 27.6966 | 27.6847 | 27.6725 | 27.661 | 27.6501 | 27.6149 | 27.5553 | 27.4741 | 27.1665 | 23.9246 | 23.8718 | 23.8097 | 23.7036 | 23.5732 | 23.416 | 23.2854 | 23.1558 | 23.0474 | 22.9322 | 22.5879 | 21.9819 | 21.3313 | 20.7059
|  | BAGSHOT | SP |  |  | 28.8388 | 28.8388 | 28.8388 | 28.8388 | 28.8388 | 28.8388 | 28.8388 | 28.8359 | 28.8314 | 28.8277 | 28.8156 | 28.7963 | 28.7698 | 28.7439 | 27.7459 | 27.745 | 27.7441 | 27.7432 | 27.7395 | 27.735 | 27.7311 | 27.7272 | 27.7222 | 27.718 | 27.7045 | 27.6828 | 27.6538 | 27.6254 | 23.9777 | 23.9671 | 23.9569 | 23.947 | 23.9034 | 23.8519 | 23.8072 | 23.7627 | 23.7059 | 23.6613 | 23.5281 | 23.2952 | 23.0457 | 22.8013
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL | MINIMUM HEADROOM | SU 42417 63142 | YES | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 7.9521 | 7.8875 | 7.8027 | 7.6233 | 7.4494 | 7.2773 | 7.1865 | 7.1245 | 7.0631 | 6.9967 | 6.8008 | 6.4733 | 6.1326 | 5.7973 | 9.0191 | 9.0191 | 9.0191 | 9.0152 | 8.9761 | 8.9033 | 8.8342 | 8.7869 | 8.7401 | 8.6896 | 8.5192 | 8.1928 | 7.8531 | 7.5188
|  | BALL HILL | CT |  |  | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 7.9597 | 7.9005 | 7.8229 | 7.6588 | 7.4999 | 7.3424 | 7.1865 | 7.1245 | 7.0631 | 6.9967 | 6.8008 | 6.4733 | 6.1326 | 5.7973 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 8.9875 | 8.952 | 8.8342 | 8.7869 | 8.7401 | 8.6896 | 8.5192 | 8.1928 | 7.8531 | 7.5188
|  | BALL HILL | LW |  |  | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 7.9521 | 7.8875 | 7.8027 | 7.6233 | 7.4494 | 7.2773 | 7.2147 | 7.1528 | 7.0914 | 7.0251 | 6.829 | 6.5017 | 6.1607 | 5.825 | 9.0191 | 9.0191 | 9.0191 | 9.0152 | 8.9761 | 8.9033 | 8.8557 | 8.8085 | 8.7617 | 8.7112 | 8.5474 | 8.221 | 7.8811 | 7.5464
|  | BALL HILL | ST |  |  | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 7.9658 | 7.9129 | 7.8505 | 7.7438 | 7.6127 | 7.4548 | 7.4068 | 7.3593 | 7.3173 | 7.2722 | 7.14 | 6.9219 | 6.7019 | 6.4835 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0129 | 8.9773 | 8.9665 | 8.9558 | 8.9338 | 8.8994 | 8.7988 | 8.6326 | 8.4207 | 8.203
|  | BALL HILL | SP |  |  | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 11.1086 | 8.0271 | 8.0204 | 8.0138 | 8.0077 | 7.9788 | 7.9443 | 7.9272 | 7.9102 | 7.8881 | 7.8706 | 7.8196 | 7.7369 | 7.6563 | 7.5794 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0191 | 9.0054
BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY | MINIMUM HEADROOM | SU 42075 42720 | YES | 10.2565 | 10.252 | 10.246 | 10.2334 | 10.1698 | 10.1049 | 10.0387 | 9.9386 | 9.8065 | 9.749 | 9.574 | 9.1507 | 8.7058 | 8.4216 | 7.4508 | 7.4457 | 7.439 | 7.4248 | 7.3597 | 7.2933 | 7.2256 | 7.1202 | 6.9809 | 6.9156 | 6.7178 | 6.2536 | 5.7641 | 5.4361 | 7.1761 | 7.1761 | 7.1761 | 7.1761 | 7.1248 | 7.0721 | 7.0181 | 6.961 | 6.8715 | 6.8599 | 6.8207 | 6.6221 | 6.3222 | 6.0037
|  | BARTON STACEY | CT |  |  | 10.2565 | 10.252 | 10.246 | 10.2334 | 10.1698 | 10.1049 | 10.0387 | 9.9386 | 9.8065 | 9.749 | 9.574 | 9.1507 | 8.7058 | 8.4216 | 7.4508 | 7.4457 | 7.439 | 7.4248 | 7.3597 | 7.2933 | 7.2256 | 7.1202 | 6.9809 | 6.9156 | 6.7178 | 6.2536 | 5.7641 | 5.4361 | 7.1761 | 7.1761 | 7.1761 | 7.1761 | 7.1248 | 7.0721 | 7.0181 | 6.961 | 6.8715 | 6.8599 | 6.8207 | 6.6221 | 6.3222 | 6.0037
|  | BARTON STACEY | LW |  |  | 10.2567 | 10.2523 | 10.2465 | 10.2343 | 10.2205 | 10.2048 | 10.1555 | 10.1042 | 10.0449 | 9.996 | 9.8456 | 9.585 | 9.2822 | 9.0483 | 7.451 | 7.4461 | 7.4396 | 7.4259 | 7.4106 | 7.3935 | 7.3388 | 7.2808 | 7.2143 | 7.1577 | 6.9843 | 6.6823 | 6.3349 | 6.0571 | 7.1761 | 7.1761 | 7.1761 | 7.1761 | 7.1742 | 7.1704 | 7.1644 | 7.1561 | 7.1394 | 7.1365 | 7.1218 | 7.086 | 6.8951 | 6.6256
|  | BARTON STACEY | ST |  |  | 10.2587 | 10.2558 | 10.2524 | 10.2466 | 10.239 | 10.2296 | 10.1981 | 10.1664 | 10.1334 | 10.1002 | 9.9987 | 9.8358 | 9.6396 | 9.4738 | 7.4532 | 7.45 | 7.4462 | 7.4396 | 7.4312 | 7.4207 | 7.3856 | 7.3502 | 7.3129 | 7.2744 | 7.1575 | 6.9694 | 6.7452 | 6.5509 | 7.1761 | 7.1761 | 7.1761 | 7.1761 | 7.1757 | 7.1749 | 7.1737 | 7.172 | 7.1681 | 7.1662 | 7.1562 | 7.143 | 7.0968 | 7.08
|  | BARTON STACEY | SP |  |  | 10.2618 | 10.2613 | 10.2609 | 10.2605 | 10.2585 | 10.2563 | 10.2455 | 10.2347 | 10.2208 | 10.208 | 10.169 | 10.1095 | 10.0412 | 9.9758 | 7.4567 | 7.4562 | 7.4557 | 7.4552 | 7.4531 | 7.4505 | 7.4384 | 7.4264 | 7.4107 | 7.3965 | 7.3531 | 7.2849 | 7.2074 | 7.1332 | 7.1761 | 7.1761 | 7.1761 | 7.1761 | 7.1761 | 7.176 | 7.176 | 7.1759 | 7.1758 | 7.1751 | 7.1715 | 7.1686 | 7.1548 | 7.1414
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE | MINIMUM HEADROOM | SU 65155 52705 | YES | 31.7742 | 31.757 | 31.7381 | 30.9995 | 30.925 | 30.8498 | 30.7669 | 30.5825 | 30.3962 | 30.2416 | 29.7788 | 28.9691 | 28.0851 | 27.2666 | 24.2676 | 24.2557 | 24.2439 | 23.3689 | 23.1162 | 22.8627 | 22.6511 | 22.4395 | 22.2263 | 22.0426 | 21.4936 | 20.4773 | 19.4143 | 18.4276 | 24.0303 | 23.9504 | 23.8491 | 22.9364 | 22.6922 | 22.4472 | 22.2421 | 22.0371 | 21.8304 | 21.6537 | 21.1118 | 20.1183 | 19.0776 | 18.1131
|  | BASINGSTOKE | CT |  |  | 31.8301 | 31.8169 | 31.8018 | 31.3507 | 31.2984 | 31.246 | 31.0484 | 30.8902 | 30.7322 | 30.5878 | 30.1574 | 28.9691 | 28.0851 | 27.2666 | 24.3246 | 24.3174 | 24.3103 | 23.661 | 23.4061 | 23.1512 | 22.8993 | 22.7139 | 22.529 | 22.3555 | 21.8367 | 20.4773 | 19.4143 | 18.4276 | 24.0741 | 23.9895 | 23.8806 | 23.2313 | 22.986 | 22.7408 | 22.4984 | 22.3195 | 22.141 | 21.9746 | 21.4563 | 20.1183 | 19.0776 | 18.1131
|  | BASINGSTOKE | LW |  |  | 31.7742 | 31.757 | 31.7381 | 30.9995 | 30.925 | 30.8498 | 30.7669 | 30.5825 | 30.3962 | 30.2416 | 29.7788 | 28.9927 | 28.2105 | 27.4039 | 24.2676 | 24.2557 | 24.2439 | 23.3689 | 23.1162 | 22.8627 | 22.6511 | 22.4395 | 22.2263 | 22.0426 | 21.4936 | 20.5398 | 19.5787 | 18.5955 | 24.0303 | 23.9504 | 23.8491 | 22.9364 | 22.6922 | 22.4472 | 22.2421 | 22.0371 | 21.8304 | 21.6537 | 21.1118 | 20.1759 | 19.2372 | 18.276
|  | BASINGSTOKE | ST |  |  | 31.8625 | 31.8545 | 31.8459 | 31.5498 | 31.5178 | 31.4838 | 31.4514 | 31.4188 | 31.386 | 31.3676 | 31.1281 | 30.6394 | 30.1518 | 29.6557 | 24.353 | 24.3483 | 24.3435 | 24.054 | 23.9881 | 23.8324 | 23.6978 | 23.5642 | 23.4385 | 23.32 | 22.9696 | 22.3834 | 21.7889 | 21.1782 | 24.1523 | 24.1058 | 24.052 | 23.6784 | 23.5509 | 23.4009 | 23.2712 | 23.1424 | 23.021 | 22.9073 | 22.5709 | 22.0024 | 21.4138 | 20.8174
|  | BASINGSTOKE | SP |  |  | 31.8946 | 31.8916 | 31.8887 | 31.7435 | 31.7292 | 31.7145 | 31.6998 | 31.6851 | 31.6696 | 31.6615 | 31.6367 | 31.5966 | 31.562 | 31.5162 | 24.3815 | 24.3791 | 24.3768 | 24.232 | 24.2201 | 24.2083 | 24.1964 | 24.1845 | 24.1726 | 24.1676 | 24.0727 | 23.8452 | 23.6259 | 23.4028 | 24.2267 | 24.2172 | 24.208 | 24.0566 | 24.0143 | 23.9659 | 23.9185 | 23.8713 | 23.8142 | 23.7694 | 23.637 | 23.4185 | 23.208 | 22.9933
NURSLING GSP | VELMORE BSP | BASSETT | MINIMUM HEADROOM | SU 42193 15958 | YES | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3002 | 34.2419 | 34.1827 | 34.1209 | 34.0256 | 34.0135 | 33.9748 | 33.7879 | 33.0738 | 31.9488 | 25.4842 | 25.4816 | 25.4781 | 25.471 | 25.4067 | 25.3414 | 25.2753 | 25.207 | 25.1053 | 25.0863 | 25.026 | 24.792 | 23.3774 | 22.0647 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5322 | 26.474 | 26.4148 | 26.353 | 26.2577 | 26.2456 | 26.2068 | 25.3085 | 23.8722 | 22.5689
|  | BASSETT | CT |  |  | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3002 | 34.2419 | 34.1827 | 34.1209 | 34.0256 | 34.0135 | 33.9748 | 33.7879 | 33.0738 | 31.9488 | 25.4842 | 25.4816 | 25.4781 | 25.471 | 25.4067 | 25.3414 | 25.2753 | 25.207 | 25.1053 | 25.0863 | 25.026 | 24.792 | 23.3774 | 22.0647 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5322 | 26.474 | 26.4148 | 26.353 | 26.2577 | 26.2456 | 26.2068 | 25.3085 | 23.8722 | 22.5689
|  | BASSETT | LW |  |  | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3266 | 34.2949 | 34.2617 | 34.2272 | 34.175 | 34.1677 | 34.1429 | 34.1021 | 33.5367 | 32.4591 | 25.4843 | 25.4817 | 25.4783 | 25.4713 | 25.4337 | 25.395 | 25.3554 | 25.3145 | 25.2558 | 25.2417 | 25.1953 | 25.1073 | 23.8443 | 22.579 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5587 | 26.5269 | 26.4937 | 26.4593 | 26.407 | 26.3998 | 26.375 | 25.6487 | 24.3383 | 23.0832
|  | BASSETT | ST |  |  | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3468 | 25.4853 | 25.4835 | 25.4813 | 25.4777 | 25.4734 | 25.4681 | 25.4638 | 25.4595 | 25.4551 | 25.4504 | 25.4357 | 25.4033 | 25.3666 | 24.7351 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 25.9907 | 25.2116
|  | BASSETT | SP |  |  | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 34.3574 | 25.4872 | 25.4869 | 25.4866 | 25.4862 | 25.4852 | 25.484 | 25.4824 | 25.4808 | 25.4788 | 25.477 | 25.4713 | 25.4583 | 25.4423 | 25.4258 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895 | 26.5895
NORTH HYDE GSP | NORTH HYDE (D) | BATH ROAD EAST | MINIMUM HEADROOM | TQ 09097 76885 | YES | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.3628 | 15.3666 | 14.3594 | 15.0007 | 14.9943 | 14.993 | 14.9907 | 14.9884 | 14.9859 | 14.9807 | 14.9754 | 14.97 | 14.9644 | 14.8637 | 13.9642 | 12.8145 | 11.6519 | 14.8794 | 14.8538 | 14.8487 | 14.8395 | 14.83 | 14.82 | 14.7991 | 14.7569 | 14.7105 | 14.6617 | 14.4303 | 13.515 | 12.3451 | 11.1622
|  | BATH ROAD EAST | CT |  |  | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.403 | 15.4068 | 14.3996 | 15.0007 | 14.9943 | 14.993 | 14.9907 | 14.9884 | 14.9859 | 14.9833 | 14.9781 | 14.9727 | 14.9671 | 14.8892 | 14.0106 | 12.8609 | 11.6984 | 14.8794 | 14.8538 | 14.8487 | 14.8395 | 14.83 | 14.82 | 14.8098 | 14.7799 | 14.7335 | 14.6848 | 14.4706 | 13.5622 | 12.3923 | 11.2094
|  | BATH ROAD EAST | LW |  |  | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.3628 | 15.3666 | 14.3594 | 15.0007 | 14.9943 | 14.993 | 14.9907 | 14.9884 | 14.9859 | 14.9807 | 14.9754 | 14.97 | 14.9644 | 14.8637 | 13.9642 | 12.8145 | 11.6519 | 14.8794 | 14.8538 | 14.8487 | 14.8395 | 14.83 | 14.82 | 14.7991 | 14.7569 | 14.7105 | 14.6617 | 14.4303 | 13.515 | 12.3451 | 11.1622
|  | BATH ROAD EAST | ST |  |  | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.2424 | 15.6044 | 15.001 | 15.0004 | 14.9942 | 14.993 | 14.9916 | 14.9899 | 14.988 | 14.986 | 14.9824 | 14.9786 | 14.9655 | 14.586 | 13.8254 | 13.0889 | 14.8808 | 14.8782 | 14.8534 | 14.8488 | 14.8431 | 14.8363 | 14.8286 | 14.8206 | 14.806 | 14.7843 | 14.6714 | 14.1477 | 13.3737 | 12.6243
|  | BATH ROAD EAST | SP |  |  | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 16.5497 | 15.0015 | 15.0012 | 14.9955 | 14.9953 | 14.9948 | 14.9942 | 14.9935 | 14.9929 | 14.9921 | 14.9906 | 14.9855 | 14.9706 | 14.9046 | 14.5637 | 14.8826 | 14.8815 | 14.8588 | 14.8576 | 14.8556 | 14.8533 | 14.8507 | 14.848 | 14.8449 | 14.8389 | 14.8186 | 14.7156 | 14.4973 | 14.125
IVER 132KV | LONGFORD | BATH ROAD WEST | MINIMUM HEADROOM | TQ 05814 76820 | YES | 30.1346 | 30.1319 | 30.1283 | 30.1208 | 30.1134 | 30.1061 | 30.0933 | 30.0806 | 30.068 | 30.0544 | 30.0138 | 29.9432 | 29.868 | 29.7936 | 36.581 | 36.5801 | 36.5788 | 36.5762 | 36.5737 | 36.5712 | 36.5668 | 36.5624 | 36.558 | 36.5533 | 36.5393 | 36.515 | 36.4891 | 36.4634 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016
|  | BATH ROAD WEST | CT |  |  | 30.1346 | 30.1319 | 30.1283 | 30.1208 | 30.1134 | 30.1061 | 30.0988 | 30.0861 | 30.0734 | 30.0599 | 30.0192 | 29.9486 | 29.8734 | 29.7991 | 36.581 | 36.5801 | 36.5788 | 36.5762 | 36.5737 | 36.5712 | 36.5687 | 36.5643 | 36.5599 | 36.5552 | 36.5412 | 36.5169 | 36.4909 | 36.4653 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016
|  | BATH ROAD WEST | LW |  |  | 30.1346 | 30.1319 | 30.1283 | 30.1208 | 30.1134 | 30.1061 | 30.0933 | 30.0806 | 30.068 | 30.0544 | 30.0138 | 29.9432 | 29.868 | 29.7936 | 36.581 | 36.5801 | 36.5788 | 36.5762 | 36.5737 | 36.5712 | 36.5668 | 36.5624 | 36.558 | 36.5533 | 36.5393 | 36.515 | 36.4891 | 36.4634 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016
|  | BATH ROAD WEST | ST |  |  | 30.1359 | 30.1342 | 30.1322 | 30.1288 | 30.1246 | 30.1196 | 30.1137 | 30.1078 | 30.0992 | 30.09 | 30.0626 | 30.0155 | 29.9669 | 29.9188 | 36.5815 | 36.5809 | 36.5802 | 36.579 | 36.5776 | 36.5758 | 36.5738 | 36.5718 | 36.5688 | 36.5656 | 36.5562 | 36.5399 | 36.5232 | 36.5066 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016
|  | BATH ROAD WEST | SP |  |  | 30.1377 | 30.1374 | 30.1371 | 30.1368 | 30.1357 | 30.1343 | 30.1326 | 30.1308 | 30.1286 | 30.1251 | 30.1147 | 30.0967 | 30.0784 | 30.0606 | 36.5821 | 36.582 | 36.5819 | 36.5818 | 36.5814 | 36.5809 | 36.5803 | 36.5797 | 36.579 | 36.5777 | 36.5741 | 36.5679 | 36.5616 | 36.5555 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016 | 36.7016
IVER 132KV | UPTON BSP | BEACONSFIELD (END BB) | MINIMUM HEADROOM | SU 93668 91219 | YES | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9233 | 7.8987 | 7.8735 | 7.8474 | 7.8069 | 7.793 | 7.7484 | 7.7119 | 7.604 | 7.4309 | 4.9052 | 4.8359 | 4.7449 | 4.5522 | 4.365 | 4.1794 | 4.0306 | 3.9668 | 3.8954 | 3.8363 | 3.6498 | 3.3192 | 3.0117 | 2.7454 | 5.4264 | 5.4225 | 5.4174 | 5.4065 | 5.275 | 5.1028 | 4.9544 | 4.8908 | 4.8196 | 4.7606 | 4.5747 | 4.245 | 3.9382 | 3.6727
|  | BEACONSFIELD (END BB) | CT |  |  | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9366 | 7.9255 | 7.914 | 7.902 | 7.8833 | 7.8809 | 7.873 | 7.8341 | 7.6588 | 7.4309 | 4.912 | 4.8479 | 4.7635 | 4.5849 | 4.4006 | 4.2177 | 4.0306 | 3.9668 | 3.8954 | 3.8363 | 3.6498 | 3.3192 | 3.0117 | 2.7454 | 5.4268 | 5.4232 | 5.4184 | 5.4083 | 5.307 | 5.1372 | 4.9544 | 4.8908 | 4.8196 | 4.7606 | 4.5747 | 4.245 | 3.9382 | 3.6727
|  | BEACONSFIELD (END BB) | LW |  |  | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9473 | 7.9468 | 7.9461 | 7.9451 | 7.943 | 7.9426 | 7.9408 | 7.9363 | 7.8567 | 7.6399 | 4.9052 | 4.8359 | 4.7449 | 4.5522 | 4.365 | 4.1794 | 4.1276 | 4.0748 | 4.02 | 3.963 | 3.7825 | 3.4864 | 3.2195 | 2.9642 | 5.4264 | 5.4225 | 5.4174 | 5.4065 | 5.275 | 5.1028 | 5.0512 | 4.9986 | 4.9439 | 4.8871 | 4.7072 | 4.412 | 4.1458 | 3.8913
|  | BEACONSFIELD (END BB) | ST |  |  | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9233 | 7.8987 | 7.8735 | 7.8474 | 7.8069 | 7.793 | 7.7484 | 7.7119 | 7.604 | 7.5715 | 4.929 | 4.8791 | 4.82 | 4.7188 | 4.5701 | 4.3952 | 4.3205 | 4.2446 | 4.1682 | 4.1157 | 3.9488 | 3.7141 | 3.4392 | 3.2416 | 5.4278 | 5.4249 | 5.4216 | 5.4159 | 5.3847 | 5.2981 | 5.2282 | 5.1561 | 5.0824 | 5.0328 | 4.8723 | 4.6382 | 4.3639 | 4.1668
|  | BEACONSFIELD (END BB) | SP |  |  | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9476 | 7.9475 | 7.9475 | 7.9475 | 7.9475 | 7.9474 | 7.947 | 7.9466 | 7.9449 | 7.9432 | 4.9847 | 4.9775 | 4.9706 | 4.9641 | 4.9334 | 4.8969 | 4.8788 | 4.8607 | 4.8379 | 4.8228 | 4.7749 | 4.6978 | 4.6336 | 4.5716 | 5.431 | 5.4306 | 5.4302 | 5.4298 | 5.428 | 5.4259 | 5.4249 | 5.4239 | 5.4226 | 5.4217 | 5.4185 | 5.4138 | 5.4086 | 5.4035
IVER 132KV | DENHAM | BEACONSFIELD (MIDDLE BB) | MINIMUM HEADROOM | SU 93668 91219 | YES | 16.8402 | 16.8402 | 16.8402 | 18.9402 | 18.8918 | 18.8425 | 18.7921 | 18.7399 | 18.6588 | 18.6312 | 18.5419 | 18.4689 | 18.1742 | 17.7205 | 12.7523 | 12.7457 | 12.737 | 16.5187 | 16.4743 | 16.4107 | 16.3205 | 16.2004 | 16.0625 | 15.9446 | 15.5728 | 14.9136 | 14.3003 | 13.7694 | 15.9766 | 15.9656 | 15.9511 | 16.8204 | 16.7762 | 16.4895 | 16.2115 | 16.0926 | 15.9587 | 15.85 | 15.5069 | 14.8947 | 14.3074 | 13.7948
|  | BEACONSFIELD (MIDDLE BB) | CT |  |  | 16.8402 | 16.8402 | 16.8402 | 18.9402 | 18.9183 | 18.896 | 18.8732 | 18.8492 | 18.8118 | 18.807 | 18.791 | 18.709 | 18.1742 | 17.7205 | 12.753 | 12.7468 | 12.7388 | 16.5218 | 16.4835 | 16.4448 | 16.3205 | 16.2004 | 16.0625 | 15.9446 | 15.5728 | 14.9136 | 14.3003 | 13.7694 | 15.9777 | 15.9675 | 15.954 | 16.8256 | 16.7762 | 16.5563 | 16.2115 | 16.0926 | 15.9587 | 15.85 | 15.5069 | 14.8947 | 14.3074 | 13.7948
|  | BEACONSFIELD (MIDDLE BB) | LW |  |  | 16.8402 | 16.8402 | 16.8402 | 18.9402 | 18.9397 | 18.9388 | 18.9373 | 18.9352 | 18.931 | 18.9303 | 18.9266 | 18.9177 | 18.5695 | 18.138 | 12.7523 | 12.7457 | 12.737 | 16.5187 | 16.5004 | 16.4819 | 16.4755 | 16.407 | 16.3049 | 16.1975 | 15.8378 | 15.2476 | 14.7154 | 14.2066 | 15.9766 | 15.9656 | 15.9511 | 16.8204 | 16.7902 | 16.4895 | 16.3946 | 16.2976 | 16.1969 | 16.0923 | 15.7614 | 15.2182 | 14.7178 | 14.2274
|  | BEACONSFIELD (MIDDLE BB) | ST |  |  | 16.8402 | 16.8402 | 16.8402 | 18.9402 | 18.8918 | 18.8425 | 18.7921 | 18.7399 | 18.6588 | 18.6312 | 18.5419 | 18.4689 | 18.2531 | 18.188 | 12.7546 | 12.7498 | 12.7442 | 16.5345 | 16.4743 | 16.4107 | 16.3556 | 16.2986 | 16.2142 | 16.1828 | 16.082 | 15.6998 | 15.1513 | 14.7571 | 15.9805 | 15.9725 | 15.963 | 16.8469 | 16.7787 | 16.7055 | 16.6472 | 16.5871 | 16.4456 | 16.347 | 16.0337 | 15.5976 | 15.076 | 14.7084
|  | BEACONSFIELD (MIDDLE BB) | SP |  |  | 16.8402 | 16.8402 | 16.8402 | 18.9402 | 18.9402 | 18.9402 | 18.9402 | 18.9402 | 18.9401 | 18.94 | 18.9391 | 18.9383 | 18.9349 | 18.9315 | 12.76 | 12.7593 | 12.7586 | 16.558 | 16.555 | 16.5515 | 16.5498 | 16.548 | 16.5458 | 16.5442 | 16.5388 | 16.5307 | 16.5214 | 16.5123 | 15.9895 | 15.9883 | 15.9872 | 16.8861 | 16.8812 | 16.8753 | 16.8724 | 16.8695 | 16.8658 | 16.8633 | 16.8548 | 16.8418 | 16.8284 | 16.8155
BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM | MINIMUM HEADROOM | SU 58204 69025 | YES | 15.2036 | 15.1948 | 15.1832 | 15.1586 | 15.1345 | 15.1096 | 15.0859 | 15.0704 | 15.0485 | 15.0316 | 14.9207 | 14.715 | 14.4908 | 14.3024 | 10.9242 | 10.8892 | 10.8432 | 10.7461 | 10.6515 | 10.5574 | 10.4639 | 10.4065 | 10.348 | 10.2876 | 10.1077 | 9.7899 | 9.4584 | 9.15 | 11.4772 | 11.4772 | 11.4772 | 11.4772 | 11.4761 | 11.4738 | 11.4702 | 11.4652 | 11.4552 | 11.4534 | 11.4446 | 11.4231 | 11.3811 | 11.2712
|  | BEENHAM | CT |  |  | 15.2036 | 15.1948 | 15.1832 | 15.1586 | 15.1345 | 15.1102 | 15.0859 | 15.0704 | 15.0533 | 15.033 | 14.9207 | 14.715 | 14.5 | 14.3062 | 10.9242 | 10.8892 | 10.8432 | 10.7461 | 10.6515 | 10.5574 | 10.4639 | 10.4065 | 10.348 | 10.2876 | 10.1077 | 9.7899 | 9.4584 | 9.15 | 11.4772 | 11.4772 | 11.4772 | 11.4772 | 11.4769 | 11.4763 | 11.4753 | 11.474 | 11.4709 | 11.4704 | 11.4675 | 11.4435 | 11.4168 | 11.2712
|  | BEENHAM | LW |  |  | 15.2039 | 15.1952 | 15.1838 | 15.1596 | 15.1351 | 15.1096 | 15.0917 | 15.0726 | 15.0485 | 15.0316 | 14.9244 | 14.7213 | 14.4908 | 14.3024 | 10.9251 | 10.8907 | 10.8455 | 10.75 | 10.6562 | 10.5621 | 10.5021 | 10.441 | 10.3755 | 10.3139 | 10.1279 | 9.8126 | 9.4657 | 9.1627 | 11.4772 | 11.4772 | 11.4772 | 11.4772 | 11.4761 | 11.4738 | 11.4702 | 11.4652 | 11.4552 | 11.4534 | 11.4446 | 11.4231 | 11.3811 | 11.2841
|  | BEENHAM | ST |  |  | 15.2056 | 15.1984 | 15.19 | 15.1755 | 15.1576 | 15.1357 | 15.123 | 15.1101 | 15.0982 | 15.0868 | 15.0507 | 14.9434 | 14.7942 | 14.6634 | 10.932 | 10.9036 | 10.8703 | 10.813 | 10.7425 | 10.6573 | 10.6092 | 10.5615 | 10.5213 | 10.4793 | 10.3541 | 10.1508 | 9.9265 | 9.7211 | 11.4772 | 11.4772 | 11.4772 | 11.4772 | 11.477 | 11.4765 | 11.4758 | 11.4748 | 11.4724 | 11.4713 | 11.4653 | 11.4574 | 11.4296 | 11.4195
|  | BEENHAM | SP |  |  | 15.2139 | 15.213 | 15.2122 | 15.2113 | 15.2075 | 15.2028 | 15.1986 | 15.1944 | 15.189 | 15.1847 | 15.1709 | 15.1505 | 15.1242 | 15.0989 | 10.9649 | 10.9613 | 10.9579 | 10.9546 | 10.9393 | 10.9211 | 10.9045 | 10.8881 | 10.867 | 10.8509 | 10.8027 | 10.7273 | 10.6476 | 10.5715 | 11.4772 | 11.4772 | 11.4772 | 11.4772 | 11.4772 | 11.4772 | 11.4772 | 11.4771 | 11.477 | 11.4767 | 11.4745 | 11.4728 | 11.4645 | 11.4564
MANNINGTON GSP | SALISBURY | BEMERTON | MINIMUM HEADROOM | SU 11583 31233 | YES | 35.0955 | 35.0955 | 35.0955 | 35.0955 | 35.0146 | 34.9319 | 34.847 | 34.7585 | 34.6201 | 34.5723 | 34.4144 | 34.2805 | 33.8489 | 33.7057 | 33.9372 | 33.9349 | 33.9317 | 33.9269 | 33.8509 | 33.767 | 33.6783 | 33.5861 | 33.442 | 33.3884 | 33.1891 | 32.8995 | 32.3163 | 31.9296 | 33.6708 | 33.6708 | 33.6708 | 33.6708 | 33.5899 | 33.5073 | 33.4223 | 33.3339 | 33.1954 | 33.1477 | 32.9897 | 32.8558 | 32.4242 | 32.1978
|  | BEMERTON | CT |  |  | 35.0955 | 35.0955 | 35.0955 | 35.0955 | 35.0856 | 35.0749 | 35.0634 | 35.0504 | 35.0284 | 35.0252 | 35.0125 | 34.9296 | 34.7805 | 34.129 | 33.9372 | 33.9349 | 33.9317 | 33.9269 | 33.9137 | 33.9 | 33.8854 | 33.8642 | 33.8339 | 33.7885 | 33.6352 | 33.3193 | 32.6923 | 31.9296 | 33.6708 | 33.6708 | 33.6708 | 33.6708 | 33.6609 | 33.6502 | 33.6387 | 33.6257 | 33.6037 | 33.6005 | 33.5878 | 33.4963 | 32.9582 | 32.1978
|  | BEMERTON | LW |  |  | 35.0955 | 35.0955 | 35.0955 | 35.0955 | 35.093 | 35.0877 | 35.0795 | 35.0682 | 35.0453 | 35.0414 | 35.0213 | 34.9723 | 34.8182 | 34.1871 | 33.9378 | 33.9359 | 33.9333 | 33.9297 | 33.9249 | 33.9179 | 33.9015 | 33.8819 | 33.8508 | 33.8046 | 33.6439 | 33.3619 | 32.7299 | 31.9876 | 33.6708 | 33.6708 | 33.6708 | 33.6708 | 33.6683 | 33.6631 | 33.6549 | 33.6435 | 33.6206 | 33.6167 | 33.5966 | 33.539 | 32.9958 | 32.2557
|  | BEMERTON | ST |  |  | 35.0955 | 35.0955 | 35.0955 | 35.0955 | 35.0146 | 34.9319 | 34.847 | 34.7585 | 34.6201 | 34.5723 | 34.4144 | 34.2805 | 33.8489 | 33.7057 | 33.951 | 33.9369 | 33.9352 | 33.9331 | 33.8509 | 33.767 | 33.6783 | 33.5861 | 33.442 | 33.3884 | 33.1891 | 32.8995 | 32.3163 | 32.0238 | 33.6708 | 33.6708 | 33.6708 | 33.6708 | 33.5899 | 33.5073 | 33.4223 | 33.3339 | 33.1954 | 33.1477 | 32.9897 | 32.8558 | 32.4242 | 32.2586
|  | BEMERTON | SP |  |  | 35.0955 | 35.0955 | 35.0955 | 35.0955 | 35.0955 | 35.0955 | 35.0954 | 35.0953 | 35.0951 | 35.0942 | 35.0892 | 35.0853 | 35.0665 | 35.0481 | 33.9515 | 33.9507 | 33.9371 | 33.9363 | 33.9358 | 33.9353 | 33.9341 | 33.9329 | 33.9312 | 33.928 | 33.9165 | 33.9018 | 33.873 | 33.8132 | 33.6708 | 33.6708 | 33.6708 | 33.6708 | 33.6708 | 33.6708 | 33.6707 | 33.6706 | 33.6704 | 33.6695 | 33.6646 | 33.6606 | 33.6418 | 33.6234
COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD | MINIMUM HEADROOM | SU 58382 95467 | NO | 24.8546 | 24.7868 | 24.7327 | 23.954 | 23.6924 | 23.3153 | 22.8313 | 22.2778 | 21.6522 | 21.0223 | 18.6448 | 15.2815 | 14.2618 | 13.5368 | 23.8062 | 23.7293 | 23.6683 | 22.8705 | 22.5763 | 22.1486 | 21.5973 | 20.966 | 20.2525 | 19.5266 | 16.5412 | 12.2707 | 11.0575 | 10.2113 | 23.8018 | 23.7206 | 23.6563 | 22.8491 | 22.5389 | 22.0865 | 21.5024 | 20.833 | 20.0767 | 19.3038 | 16.3834 | 12.2622 | 11.0902 | 10.2698
|  | BERINSFIELD | CT |  |  | 24.8948 | 24.8229 | 24.7621 | 24.2234 | 23.9624 | 23.5876 | 23.1656 | 22.6406 | 22.0498 | 21.4307 | 19.0906 | 15.3538 | 14.2618 | 13.5368 | 23.8445 | 23.7622 | 23.6928 | 23.1313 | 22.834 | 22.4051 | 21.9214 | 21.3186 | 20.64 | 19.9248 | 16.9689 | 12.3289 | 11.0575 | 10.2113 | 23.8392 | 23.7519 | 23.6783 | 23.1056 | 22.7907 | 22.3353 | 21.8215 | 21.1807 | 20.4592 | 19.6971 | 16.8141 | 12.3234 | 11.0902 | 10.2698
|  | BERINSFIELD | LW |  |  | 24.8546 | 24.7868 | 24.7327 | 23.954 | 23.6924 | 23.3153 | 22.8313 | 22.2778 | 21.6522 | 21.0223 | 18.6448 | 15.2815 | 14.2623 | 13.5473 | 23.8062 | 23.7293 | 23.6683 | 22.8705 | 22.5763 | 22.1486 | 21.5973 | 20.966 | 20.2525 | 19.5266 | 16.5412 | 12.2707 | 11.0719 | 10.2358 | 23.8018 | 23.7206 | 23.6563 | 22.8491 | 22.5389 | 22.0865 | 21.5024 | 20.833 | 20.0767 | 19.3038 | 16.3834 | 12.2622 | 11.1016 | 10.2913
|  | BERINSFIELD | ST |  |  | 24.9494 | 24.9078 | 24.8803 | 24.554 | 24.4074 | 24.1803 | 23.8817 | 23.5379 | 23.1417 | 22.7156 | 21.0342 | 18.6636 | 18.0444 | 17.6171 | 23.9037 | 23.8562 | 23.825 | 23.4886 | 23.3223 | 23.0627 | 22.7203 | 22.3257 | 21.8706 | 21.3785 | 19.3975 | 16.3728 | 15.6006 | 15.0712 | 23.9007 | 23.8503 | 23.8173 | 23.4761 | 23.3001 | 23.0246 | 22.6608 | 22.2413 | 21.7575 | 21.2332 | 19.1631 | 16.2458 | 15.4987 | 14.9861
|  | BERINSFIELD | SP |  |  | 24.9859 | 24.9607 | 24.9479 | 24.7868 | 24.7126 | 24.605 | 24.4786 | 24.339 | 24.1824 | 24.0121 | 23.3404 | 22.344 | 22.0956 | 21.9322 | 23.9419 | 23.913 | 23.8985 | 23.7327 | 23.6484 | 23.5255 | 23.3807 | 23.2207 | 23.041 | 22.8444 | 22.0688 | 20.918 | 20.6347 | 20.4515 | 23.9397 | 23.909 | 23.8937 | 23.7256 | 23.6365 | 23.506 | 23.3522 | 23.1822 | 22.9912 | 22.7818 | 21.9554 | 20.7293 | 20.4289 | 20.236
NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY | MINIMUM HEADROOM | SU 42648 13187 | YES | 35.444 | 35.4276 | 35.4112 | 34.41 | 34.3279 | 34.2458 | 34.1637 | 34.0817 | 33.9996 | 33.9668 | 33.8683 | 32.8363 | 31.7119 | 30.5114 | 25.6372 | 25.6137 | 25.5879 | 24.5681 | 24.4369 | 24.3096 | 24.1722 | 24.0309 | 23.8848 | 23.7857 | 23.5122 | 22.2679 | 20.9697 | 19.5963 | 26.4038 | 26.3874 | 26.371 | 25.3697 | 25.2877 | 25.2056 | 25.1235 | 25.0415 | 24.9594 | 24.9266 | 24.8281 | 23.5932 | 22.2899 | 20.9114
|  | BEVOIS VALLEY | CT |  |  | 35.5228 | 35.513 | 35.5031 | 34.9024 | 34.8531 | 34.8039 | 34.7546 | 34.7054 | 34.6562 | 34.6365 | 34.5774 | 33.0555 | 31.7762 | 30.5759 | 25.7169 | 25.7006 | 25.6822 | 25.0648 | 24.9712 | 24.8793 | 24.7867 | 24.6783 | 24.565 | 24.4791 | 24.245 | 22.498 | 21.0448 | 19.6718 | 26.4826 | 26.4728 | 26.4629 | 25.8622 | 25.8129 | 25.7637 | 25.7144 | 25.6652 | 25.616 | 25.5963 | 25.5372 | 23.8237 | 22.3654 | 20.9872
|  | BEVOIS VALLEY | LW |  |  | 35.444 | 35.4276 | 35.4112 | 34.41 | 34.3279 | 34.2458 | 34.1637 | 34.0817 | 33.9996 | 33.9668 | 33.8683 | 32.8363 | 31.7119 | 30.5114 | 25.6372 | 25.6137 | 25.5879 | 24.5681 | 24.4369 | 24.3096 | 24.1722 | 24.0309 | 23.8848 | 23.7857 | 23.5122 | 22.2679 | 20.9697 | 19.5963 | 26.4038 | 26.3874 | 26.371 | 25.3697 | 25.2877 | 25.2056 | 25.1235 | 25.0415 | 24.9594 | 24.9266 | 24.8281 | 23.5932 | 22.2899 | 20.9114
|  | BEVOIS VALLEY | ST |  |  | 35.5622 | 35.5556 | 35.5491 | 35.1486 | 35.1158 | 35.0829 | 35.0501 | 35.0173 | 34.9844 | 34.9713 | 34.9319 | 34.7868 | 34.072 | 33.3502 | 25.7582 | 25.7464 | 25.7337 | 25.3233 | 25.2669 | 25.2009 | 25.1301 | 25.0568 | 24.9808 | 24.9224 | 24.7617 | 24.3519 | 23.5227 | 22.6909 | 26.522 | 26.5154 | 26.5089 | 26.1084 | 26.0755 | 26.0427 | 26.0099 | 25.9771 | 25.9442 | 25.9311 | 25.8917 | 25.6812 | 24.8486 | 24.0135
|  | BEVOIS VALLEY | SP |  |  | 35.6016 | 35.5983 | 35.595 | 35.3948 | 35.3784 | 35.362 | 35.3455 | 35.3291 | 35.3127 | 35.3062 | 35.2865 | 35.2536 | 35.2339 | 35.1978 | 25.803 | 25.7985 | 25.794 | 25.5925 | 25.5666 | 25.5425 | 25.5161 | 25.4892 | 25.4585 | 25.4342 | 25.3671 | 25.2376 | 25.1064 | 24.9545 | 26.5614 | 26.5581 | 26.5548 | 26.3546 | 26.3382 | 26.3218 | 26.3053 | 26.2889 | 26.2725 | 26.2659 | 26.2463 | 26.2134 | 26.1937 | 26.1576
EAST CLAYDON GSP | BICESTER NORTH | BICESTER | MINIMUM HEADROOM | SP 58381 21988 | NO | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704
|  | BICESTER | CT |  |  | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704
|  | BICESTER | LW |  |  | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704
|  | BICESTER | ST |  |  | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704
|  | BICESTER | SP |  |  | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 66.5844 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 64.6334 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704 | 65.2704
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST | MINIMUM HEADROOM | TQ 08305 26315 | YES | 26.5946 | 26.5946 | 26.5946 | 26.5946 | 26.5929 | 26.5894 | 26.5839 | 26.5764 | 26.5611 | 26.5585 | 26.5451 | 26.5124 | 26.4418 | 26.2021 | 23.9247 | 23.872 | 23.8099 | 23.6749 | 23.5393 | 23.4043 | 23.2701 | 23.1848 | 23.0975 | 23.0077 | 22.7377 | 22.2357 | 21.6974 | 21.1926 | 23.9191 | 23.8625 | 23.7959 | 23.6509 | 23.5053 | 23.3604 | 23.2164 | 23.125 | 23.0316 | 22.9353 | 22.6457 | 22.1093 | 21.5342 | 20.9931
|  | BILLINGSHURST | CT |  |  | 26.5946 | 26.5946 | 26.5946 | 26.5946 | 26.5941 | 26.5931 | 26.5917 | 26.5896 | 26.585 | 26.5842 | 26.5798 | 26.5435 | 26.4891 | 26.2021 | 23.9304 | 23.88 | 23.814 | 23.6749 | 23.5393 | 23.4043 | 23.2701 | 23.1848 | 23.0975 | 23.0077 | 22.7377 | 22.2357 | 21.6974 | 21.1926 | 23.9252 | 23.8712 | 23.8003 | 23.6509 | 23.5053 | 23.3604 | 23.2164 | 23.125 | 23.0316 | 22.9353 | 22.6457 | 22.1093 | 21.5342 | 20.9931
|  | BILLINGSHURST | LW |  |  | 26.5946 | 26.5946 | 26.5946 | 26.5946 | 26.5929 | 26.5894 | 26.5839 | 26.5764 | 26.5611 | 26.5585 | 26.5451 | 26.5124 | 26.4418 | 26.238 | 23.9355 | 23.8888 | 23.8276 | 23.6985 | 23.5715 | 23.4437 | 23.3543 | 23.2634 | 23.1655 | 23.0739 | 22.7948 | 22.2968 | 21.735 | 21.2386 | 23.9308 | 23.8806 | 23.8148 | 23.6762 | 23.54 | 23.403 | 23.3074 | 23.2104 | 23.1064 | 23.0082 | 22.7095 | 22.1771 | 21.5787 | 21.0459
|  | BILLINGSHURST | ST |  |  | 26.5946 | 26.5946 | 26.5946 | 26.5946 | 26.5942 | 26.5935 | 26.5925 | 26.5909 | 26.5873 | 26.5856 | 26.5765 | 26.5644 | 26.5223 | 26.507 | 23.9247 | 23.872 | 23.8099 | 23.7039 | 23.5734 | 23.4158 | 23.3399 | 23.2642 | 23.2041 | 23.1418 | 22.953 | 22.6292 | 22.2649 | 21.9311 | 23.9191 | 23.8625 | 23.7959 | 23.682 | 23.5419 | 23.3728 | 23.2913 | 23.2101 | 23.1459 | 23.0791 | 22.8771 | 22.5302 | 22.1422 | 21.7849
|  | BILLINGSHURST | SP |  |  | 26.5946 | 26.5946 | 26.5946 | 26.5946 | 26.5946 | 26.5946 | 26.5945 | 26.5945 | 26.5943 | 26.5937 | 26.5904 | 26.5878 | 26.5752 | 26.563 | 23.9893 | 23.9842 | 23.9793 | 23.9746 | 23.9535 | 23.9283 | 23.9037 | 23.8792 | 23.8478 | 23.8237 | 23.751 | 23.6284 | 23.4923 | 23.3603 | 23.9885 | 23.9831 | 23.9778 | 23.9727 | 23.95 | 23.923 | 23.8966 | 23.8703 | 23.8366 | 23.8108 | 23.7329 | 23.6015 | 23.4563 | 23.3154
LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM | MINIMUM HEADROOM | SU 97366 01594 | NO | 24.8068 | 24.5492 | 24.3493 | 22.9859 | 22.555 | 22.0722 | 21.5329 | 20.9612 | 20.3713 | 19.8556 | 18.188 | 16.6525 | 15.3796 | 14.2373 | 20.8959 | 20.6 | 20.3709 | 18.9605 | 18.4748 | 17.9288 | 17.3173 | 16.6683 | 15.9982 | 15.4057 | 13.4884 | 11.7356 | 10.3174 | 9.0123 | 19.5132 | 19.2125 | 18.9797 | 17.5633 | 17.0706 | 16.5166 | 15.8959 | 15.2371 | 14.5567 | 13.9544 | 12.0053 | 10.2249 | 8.7963 | 7.4866
|  | BILSHAM | CT |  |  | 24.9001 | 24.6564 | 24.4723 | 23.5552 | 23.1557 | 22.7036 | 22.2444 | 21.6844 | 21.0935 | 20.5872 | 18.9471 | 16.748 | 15.3796 | 14.2373 | 20.9907 | 20.7097 | 20.4978 | 19.5367 | 19.0852 | 18.5729 | 18.0523 | 17.4149 | 16.7438 | 16.1607 | 14.2709 | 11.8545 | 10.3174 | 9.0123 | 19.6083 | 19.3225 | 19.1071 | 18.1404 | 17.6823 | 17.1623 | 16.6338 | 15.9866 | 15.3053 | 14.7124 | 12.7908 | 10.3468 | 8.7963 | 7.4866
|  | BILSHAM | LW |  |  | 24.8068 | 24.5492 | 24.3493 | 22.9859 | 22.555 | 22.0722 | 21.5329 | 20.9612 | 20.3713 | 19.8556 | 18.188 | 16.6525 | 15.5367 | 14.4139 | 20.8959 | 20.6 | 20.3709 | 18.9605 | 18.4748 | 17.9288 | 17.3173 | 16.6683 | 15.9982 | 15.4057 | 13.4884 | 11.7356 | 10.4488 | 9.1631 | 19.5132 | 19.2125 | 18.9797 | 17.5633 | 17.0706 | 16.5166 | 15.8959 | 15.2371 | 14.5567 | 13.9544 | 12.0053 | 10.2249 | 8.927 | 7.6367
|  | BILSHAM | ST |  |  | 24.9604 | 24.8331 | 24.6176 | 24.0077 | 23.6931 | 23.3233 | 22.9459 | 22.5455 | 22.0983 | 21.7295 | 20.5051 | 19.4332 | 18.512 | 17.7635 | 21.0539 | 20.9074 | 20.6585 | 20.0196 | 19.6674 | 19.2515 | 18.8267 | 18.3757 | 17.8745 | 17.4531 | 16.0526 | 14.8313 | 13.8058 | 12.9608 | 19.6718 | 19.5228 | 19.2697 | 18.6271 | 18.2702 | 17.8484 | 17.4176 | 16.9602 | 16.4521 | 16.024 | 14.6011 | 13.3607 | 12.322 | 11.4647
|  | BILSHAM | SP |  |  | 25.0573 | 24.9883 | 24.8443 | 24.5621 | 24.4487 | 24.321 | 24.1899 | 24.0545 | 23.9089 | 23.7719 | 23.3157 | 22.9119 | 22.6484 | 22.4021 | 21.1595 | 21.0801 | 20.9136 | 20.6205 | 20.4918 | 20.3465 | 20.1972 | 20.043 | 19.877 | 19.7192 | 19.1935 | 18.7307 | 18.4284 | 18.149 | 19.7786 | 19.6978 | 19.5285 | 19.234 | 19.1033 | 18.9558 | 18.8042 | 18.6475 | 18.4789 | 18.3185 | 17.7839 | 17.3137 | 17.0065 | 16.7228
FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD | MINIMUM HEADROOM | SZ 56409 91399 | NO | 16.8434 | 16.8434 | 16.8434 | 16.8434 | 16.8423 | 16.8401 | 16.8367 | 16.8319 | 16.8222 | 16.8205 | 16.812 | 16.7913 | 16.5185 | 16.0557 | 16.306 | 16.2891 | 16.2668 | 16.22 | 16.1733 | 16.1259 | 16.0144 | 15.9024 | 15.7867 | 15.6707 | 15.3235 | 14.7353 | 14.0998 | 13.5068 | 16.339 | 16.338 | 16.3368 | 16.3341 | 16.3304 | 16.3256 | 16.316 | 16.305 | 16.2893 | 16.2764 | 16.0061 | 15.5466 | 14.9847 | 14.4395
|  | BINSTEAD | CT |  |  | 16.8434 | 16.8434 | 16.8434 | 16.8434 | 16.8431 | 16.8425 | 16.8416 | 16.8403 | 16.8373 | 16.8368 | 16.834 | 16.811 | 16.6241 | 16.1562 | 16.3086 | 16.2934 | 16.2736 | 16.232 | 16.1913 | 16.1505 | 16.1096 | 16.0013 | 15.8922 | 15.7773 | 15.436 | 14.8451 | 14.2255 | 13.6276 | 16.3391 | 16.3383 | 16.3371 | 16.3348 | 16.3321 | 16.3292 | 16.326 | 16.3186 | 16.3096 | 16.3026 | 16.098 | 15.636 | 15.1031 | 14.5528
|  | BINSTEAD | LW |  |  | 16.8434 | 16.8434 | 16.8434 | 16.8434 | 16.8423 | 16.8401 | 16.8367 | 16.8319 | 16.8222 | 16.8205 | 16.812 | 16.7913 | 16.5185 | 16.0557 | 16.306 | 16.2891 | 16.2668 | 16.22 | 16.1733 | 16.1259 | 16.0144 | 15.9024 | 15.7867 | 15.6707 | 15.3235 | 14.7353 | 14.0998 | 13.5068 | 16.339 | 16.338 | 16.3368 | 16.3341 | 16.3304 | 16.3256 | 16.316 | 16.305 | 16.2893 | 16.2764 | 16.0061 | 15.5466 | 14.9847 | 14.4395
|  | BINSTEAD | ST |  |  | 16.8434 | 16.8434 | 16.8434 | 16.8434 | 16.8432 | 16.8427 | 16.8421 | 16.841 | 16.8388 | 16.8377 | 16.8319 | 16.8243 | 16.7976 | 16.7879 | 16.3233 | 16.3191 | 16.314 | 16.3056 | 16.2949 | 16.2819 | 16.2213 | 16.1613 | 16.0865 | 16.0073 | 15.7729 | 15.3867 | 14.9777 | 14.5889 | 16.34 | 16.3397 | 16.3395 | 16.339 | 16.3381 | 16.337 | 16.3329 | 16.3285 | 16.3221 | 16.3166 | 16.2977 | 16.0577 | 15.7354 | 15.4327
|  | BINSTEAD | SP |  |  | 16.8434 | 16.8434 | 16.8434 | 16.8434 | 16.8434 | 16.8434 | 16.8434 | 16.8433 | 16.8432 | 16.8429 | 16.8408 | 16.8391 | 16.8311 | 16.8234 | 16.3254 | 16.3235 | 16.3217 | 16.3199 | 16.3123 | 16.3033 | 16.2905 | 16.2778 | 16.2611 | 16.2304 | 16.1398 | 15.9939 | 15.8449 | 15.7029 | 16.3401 | 16.34 | 16.3399 | 16.3398 | 16.3393 | 16.3388 | 16.3381 | 16.3373 | 16.3363 | 16.3342 | 16.327 | 16.3171 | 16.3011 | 16.2856
LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM | MINIMUM HEADROOM | SZ 81965 99422 | NO | 18.3136 | 18.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 24.7416 | 23.9373 | 23.1467 | 12.8021 | 12.7996 | 22.7963 | 22.7894 | 22.7827 | 22.7761 | 22.7682 | 22.7604 | 22.7513 | 22.7413 | 22.709 | 21.7887 | 20.9228 | 19.9993 | 16.2058 | 16.2058 | 16.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.1678 | 22.4659 | 21.4214 | 20.5071 | 19.608
|  | BIRDHAM | CT |  |  | 18.3136 | 18.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 24.8742 | 24.0701 | 23.2798 | 12.8026 | 12.8005 | 22.7978 | 22.792 | 22.7863 | 22.7807 | 22.7751 | 22.7674 | 22.7583 | 22.7482 | 22.716 | 21.9252 | 21.0747 | 20.1568 | 16.2058 | 16.2058 | 16.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 22.617 | 21.5722 | 20.658 | 19.7594
|  | BIRDHAM | LW |  |  | 18.3136 | 18.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 24.7416 | 23.9373 | 23.1467 | 12.8021 | 12.7996 | 22.7963 | 22.7894 | 22.7827 | 22.7761 | 22.7682 | 22.7604 | 22.7513 | 22.7413 | 22.709 | 21.7887 | 20.9228 | 19.9993 | 16.2058 | 16.2058 | 16.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.1678 | 22.4659 | 21.4214 | 20.5071 | 19.608
|  | BIRDHAM | ST |  |  | 18.3136 | 18.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.0533 | 24.5391 | 12.8025 | 12.8004 | 22.7979 | 22.7937 | 22.7885 | 22.7822 | 22.7771 | 22.772 | 22.7658 | 22.759 | 22.7369 | 22.6427 | 22.1096 | 21.5803 | 16.2058 | 16.2058 | 16.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.0716 | 22.3647 | 21.7759 | 21.1912
|  | BIRDHAM | SP |  |  | 18.3136 | 18.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 25.3136 | 12.805 | 12.8047 | 22.8044 | 22.8042 | 22.8031 | 22.8018 | 22.8002 | 22.7987 | 22.7964 | 22.7938 | 22.7852 | 22.7727 | 22.7629 | 22.7536 | 16.2058 | 16.2058 | 16.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058 | 23.2058
BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM | MINIMUM HEADROOM | SU 56691 16683 | YES | 25.0661 | 24.8613 | 24.6518 | 23.2521 | 22.7316 | 22.0939 | 21.6099 | 21.1269 | 20.5313 | 20.2558 | 19.4166 | 18.0015 | 16.4041 | 15.2005 | 21.8605 | 21.6498 | 21.4343 | 20.0229 | 19.4578 | 18.7228 | 18.1856 | 17.6523 | 17.0074 | 16.6794 | 15.6862 | 14.0647 | 12.2742 | 10.8816 | 20.4577 | 20.2343 | 19.9978 | 18.5274 | 17.9377 | 17.2313 | 16.7098 | 16.1912 | 15.5608 | 15.2483 | 14.3004 | 12.7528 | 11.0371 | 9.7178
|  | BISHOPS WALTHAM | CT |  |  | 25.1276 | 24.9156 | 24.6945 | 23.6666 | 23.213 | 22.7611 | 22.3102 | 22.0696 | 21.8283 | 21.6111 | 20.9624 | 19.1749 | 17.8464 | 16.6564 | 21.9214 | 21.7031 | 21.4753 | 20.4346 | 19.9051 | 19.3459 | 18.7881 | 18.4974 | 18.2066 | 17.937 | 17.1424 | 15.1638 | 13.6423 | 12.2634 | 20.5173 | 20.2853 | 20.0308 | 18.9249 | 18.3949 | 17.8673 | 17.341 | 17.065 | 16.7888 | 16.5346 | 15.7853 | 13.8807 | 12.434 | 11.1283
|  | BISHOPS WALTHAM | LW |  |  | 25.0661 | 24.8613 | 24.6518 | 23.2521 | 22.7316 | 22.0939 | 21.6099 | 21.1269 | 20.5313 | 20.2558 | 19.4166 | 18.0015 | 16.4041 | 15.2005 | 21.8605 | 21.6498 | 21.4343 | 20.0229 | 19.4578 | 18.7228 | 18.1856 | 17.6523 | 17.0074 | 16.6794 | 15.6862 | 14.0647 | 12.2742 | 10.8816 | 20.4577 | 20.2343 | 19.9978 | 18.5274 | 17.9377 | 17.2313 | 16.7098 | 16.1912 | 15.5608 | 15.2483 | 14.3004 | 12.7528 | 11.0371 | 9.7178
|  | BISHOPS WALTHAM | ST |  |  | 25.2522 | 25.1477 | 24.9911 | 24.4057 | 24.1573 | 23.8659 | 23.6761 | 23.4937 | 23.3291 | 23.1796 | 22.7387 | 22.0293 | 21.3163 | 20.5802 | 22.0487 | 21.941 | 21.7797 | 21.1889 | 20.9338 | 20.6343 | 20.439 | 20.2173 | 20.019 | 19.8337 | 19.2889 | 18.4121 | 17.5353 | 16.6729 | 20.6504 | 20.5361 | 20.3646 | 19.7561 | 19.4672 | 19.1271 | 18.9081 | 18.6979 | 18.5095 | 18.3348 | 17.8205 | 16.993 | 16.1643 | 15.3496
|  | BISHOPS WALTHAM | SP |  |  | 25.3847 | 25.3567 | 25.2932 | 25.0707 | 24.9918 | 24.9025 | 24.8318 | 24.7646 | 24.6838 | 24.6246 | 24.4498 | 24.1762 | 23.9172 | 23.6559 | 22.1841 | 22.1553 | 22.0898 | 21.8668 | 21.786 | 21.6944 | 21.622 | 21.5532 | 21.4705 | 21.4096 | 21.2302 | 20.9491 | 20.6833 | 20.3845 | 20.792 | 20.7615 | 20.692 | 20.4678 | 20.3828 | 20.2863 | 20.2102 | 20.138 | 20.051 | 19.9861 | 19.783 | 19.4646 | 19.164 | 18.8637
NURSLING GSP | VELMORE BSP | BISHOPSTOKE | MINIMUM HEADROOM | SU 46463 18472 | YES | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9138 | 14.8804 | 14.8454 | 14.8092 | 14.7542 | 14.7465 | 14.7204 | 14.6731 | 14.535 | 14.4667 | 11.2335 | 11.2329 | 11.2321 | 11.2305 | 11.1965 | 11.1615 | 11.1236 | 11.0845 | 11.0266 | 11.0159 | 10.9798 | 10.9166 | 10.8109 | 10.7752 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3654 | 11.332 | 11.297 | 11.2608 | 11.2058 | 11.1982 | 11.172 | 11.133 | 11.0571 | 11.0187
|  | BISHOPSTOKE | CT |  |  | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9406 | 14.8784 | 14.8157 | 11.2335 | 11.2329 | 11.2321 | 11.2305 | 11.2289 | 11.2273 | 11.2257 | 11.2228 | 11.2199 | 11.2168 | 11.2068 | 11.1827 | 11.1529 | 11.1229 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3683
|  | BISHOPSTOKE | LW |  |  | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9138 | 14.8804 | 14.8454 | 14.8092 | 14.7542 | 14.7465 | 14.7204 | 14.6731 | 14.535 | 14.4667 | 11.2335 | 11.2329 | 11.2321 | 11.2305 | 11.1965 | 11.1615 | 11.1236 | 11.0845 | 11.0266 | 11.0159 | 10.9798 | 10.9166 | 10.8109 | 10.7752 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3654 | 11.332 | 11.297 | 11.2608 | 11.2058 | 11.1982 | 11.172 | 11.133 | 11.0571 | 11.0187
|  | BISHOPSTOKE | ST |  |  | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9327 | 14.8929 | 11.2337 | 11.2333 | 11.2329 | 11.2321 | 11.2312 | 11.2301 | 11.2281 | 11.2261 | 11.2242 | 11.2221 | 11.2153 | 11.1985 | 11.1789 | 11.1599 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979
|  | BISHOPSTOKE | SP |  |  | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 14.9462 | 11.2341 | 11.2339 | 11.2338 | 11.2337 | 11.2334 | 11.2331 | 11.2324 | 11.2318 | 11.231 | 11.2302 | 11.2275 | 11.2207 | 11.2119 | 11.2026 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979 | 11.3979
BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE | MINIMUM HEADROOM | SU 45116 13082 | YES | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.4947 | 16.3486 | 16.196 | 16.0379 | 15.7976 | 15.7644 | 15.6503 | 15.4779 | 14.0142 | 12.2966 | 12.4661 | 12.4648 | 12.4633 | 12.4609 | 12.3419 | 12.1936 | 12.0332 | 11.867 | 11.6186 | 11.5769 | 11.4336 | 10.323 | 8.0857 | 6.0663 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.3856 | 12.2395 | 12.0869 | 11.9287 | 11.6885 | 11.6551 | 11.5117 | 11.1563 | 8.8714 | 6.858
|  | BITTERNE | CT |  |  | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 15.5529 | 13.8577 | 12.4669 | 12.466 | 12.4648 | 12.463 | 12.461 | 12.4588 | 12.4565 | 12.4485 | 12.4404 | 12.4319 | 12.4027 | 11.554 | 9.6392 | 7.6422 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.4808 | 12.3903 | 10.4246 | 8.4337
|  | BITTERNE | LW |  |  | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.4947 | 16.3486 | 16.196 | 16.0379 | 15.7976 | 15.7644 | 15.6503 | 15.4779 | 14.0142 | 12.2966 | 12.4669 | 12.466 | 12.4648 | 12.463 | 12.3419 | 12.1936 | 12.0332 | 11.867 | 11.6186 | 11.5769 | 11.4336 | 10.323 | 8.0857 | 6.0663 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.3856 | 12.2395 | 12.0869 | 11.9287 | 11.6885 | 11.6551 | 11.5117 | 11.1563 | 8.8714 | 6.858
|  | BITTERNE | ST |  |  | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.5883 | 16.5623 | 16.5358 | 16.5085 | 16.4661 | 16.4517 | 16.4059 | 16.369 | 16.2369 | 15.173 | 12.4661 | 12.4648 | 12.4633 | 12.4609 | 12.4325 | 12.4031 | 12.3717 | 12.3394 | 12.2915 | 12.2713 | 12.2053 | 11.9288 | 10.5329 | 9.2656 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.4792 | 12.4532 | 12.4267 | 12.3993 | 12.357 | 12.3426 | 12.2834 | 12.1868 | 11.3489 | 10.0509
|  | BITTERNE | SP |  |  | 16.6138 | 16.6138 | 16.6138 | 16.6138 | 16.6041 | 16.5946 | 16.5851 | 16.5755 | 16.5603 | 16.5183 | 16.385 | 16.3215 | 16.1216 | 15.9544 | 12.4673 | 12.4669 | 12.4665 | 12.4661 | 12.4558 | 12.4457 | 12.4346 | 12.4233 | 12.4063 | 12.362 | 12.2207 | 12.1323 | 11.8973 | 11.4815 | 12.5047 | 12.5047 | 12.5047 | 12.5047 | 12.495 | 12.4855 | 12.476 | 12.4663 | 12.4512 | 12.4092 | 12.2759 | 12.2105 | 11.9754 | 11.7703
MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON | MINIMUM HEADROOM | SP 28349 03818 | NO | 15.0696 | 15.0696 | 15.0696 | 15.0696 | 15.067 | 15.0615 | 15.053 | 15.0411 | 15.0173 | 15.0131 | 14.839 | 14.5269 | 14.1662 | 13.9031 | 11.1391 | 11.1391 | 11.1391 | 11.1391 | 11.1365 | 11.1133 | 11.0331 | 10.9495 | 10.8566 | 10.7788 | 10.5404 | 10.1288 | 9.6685 | 9.3077 | 11.4439 | 11.4439 | 11.4439 | 11.4439 | 11.4413 | 11.4358 | 11.4273 | 11.4154 | 11.3915 | 11.3874 | 11.2575 | 10.8702 | 10.4257 | 10.0804
|  | BLACK BOURTON | CT |  |  | 15.0696 | 15.0696 | 15.0696 | 15.0696 | 15.0688 | 15.0673 | 15.0651 | 15.0618 | 15.0546 | 15.0534 | 14.93 | 14.612 | 14.2877 | 14.0118 | 11.1391 | 11.1391 | 11.1391 | 11.1391 | 11.1383 | 11.1368 | 11.0957 | 11.0208 | 10.9446 | 10.8695 | 10.6454 | 10.2278 | 9.804 | 9.4303 | 11.4439 | 11.4439 | 11.4439 | 11.4439 | 11.4431 | 11.4416 | 11.4394 | 11.4361 | 11.4289 | 11.4277 | 11.3517 | 10.9669 | 10.5589 | 10.2008
|  | BLACK BOURTON | LW |  |  | 15.0696 | 15.0696 | 15.0696 | 15.0696 | 15.067 | 15.0615 | 15.053 | 15.0411 | 15.0173 | 15.0131 | 14.839 | 14.5269 | 14.1662 | 13.9031 | 11.1391 | 11.1391 | 11.1391 | 11.1391 | 11.1365 | 11.1133 | 11.0331 | 10.9495 | 10.8566 | 10.7788 | 10.5404 | 10.1288 | 9.6685 | 9.3077 | 11.4439 | 11.4439 | 11.4439 | 11.4439 | 11.4413 | 11.4358 | 11.4273 | 11.4154 | 11.3915 | 11.3874 | 11.2575 | 10.8702 | 10.4257 | 10.0804
|  | BLACK BOURTON | ST |  |  | 15.0696 | 15.0696 | 15.0696 | 15.0696 | 15.0691 | 15.068 | 15.0663 | 15.0638 | 15.0583 | 15.0556 | 15.0413 | 14.8743 | 14.6402 | 14.4498 | 11.1391 | 11.1391 | 11.1391 | 11.1391 | 11.1385 | 11.1374 | 11.1358 | 11.104 | 11.0514 | 10.9984 | 10.8373 | 10.5776 | 10.2795 | 10.0256 | 11.4439 | 11.4439 | 11.4439 | 11.4439 | 11.4434 | 11.4423 | 11.4406 | 11.4381 | 11.4325 | 11.4299 | 11.4155 | 11.2932 | 11.0148 | 10.7711
|  | BLACK BOURTON | SP |  |  | 15.0696 | 15.0696 | 15.0696 | 15.0696 | 15.0696 | 15.0696 | 15.0695 | 15.0694 | 15.0692 | 15.0683 | 15.0631 | 15.059 | 15.0393 | 15.0201 | 11.1391 | 11.1391 | 11.1391 | 11.1391 | 11.1391 | 11.1391 | 11.139 | 11.1389 | 11.1386 | 11.1377 | 11.1326 | 11.126 | 11.0217 | 10.9227 | 11.4439 | 11.4439 | 11.4439 | 11.4439 | 11.4439 | 11.4439 | 11.4438 | 11.4437 | 11.4435 | 11.4426 | 11.4374 | 11.4333 | 11.4136 | 11.3944
MANNINGTON GSP | LYTCHETT | BLANDFORD | MINIMUM HEADROOM | ST 88810 05536 | YES | 40.0416 | 40.0215 | 39.9989 | 39.2551 | 39.1685 | 39.0799 | 38.9742 | 38.862 | 38.7274 | 38.6582 | 38.4522 | 38.0884 | 37.7046 | 37.4205 | 44.0302 | 44.0137 | 43.9959 | 43.2621 | 43.1857 | 43.1062 | 43.0148 | 42.7967 | 42.4546 | 42.1611 | 41.3743 | 40.0788 | 38.8412 | 37.729 | 44.8421 | 44.8269 | 44.8107 | 44.0804 | 44.0075 | 43.931 | 43.8445 | 43.7521 | 43.6387 | 43.5925 | 43.4459 | 43.1774 | 41.9882 | 40.859
|  | BLANDFORD | CT |  |  | 40.0995 | 40.0848 | 40.068 | 39.6148 | 39.557 | 39.5008 | 39.4422 | 39.368 | 39.2848 | 39.2298 | 39.0756 | 38.3033 | 37.8681 | 37.5629 | 44.0875 | 44.0762 | 44.0637 | 43.6196 | 43.5711 | 43.5229 | 43.4729 | 43.4135 | 43.1419 | 42.8625 | 42.1275 | 40.4235 | 39.1346 | 38.0017 | 44.8993 | 44.8891 | 44.878 | 44.4371 | 44.3917 | 44.3463 | 44.2993 | 44.2448 | 44.1828 | 44.1507 | 44.056 | 43.3789 | 42.2842 | 41.1344
|  | BLANDFORD | LW |  |  | 40.0416 | 40.0215 | 39.9989 | 39.2551 | 39.1685 | 39.0799 | 38.9742 | 38.862 | 38.7274 | 38.6582 | 38.4522 | 38.0884 | 37.7046 | 37.4205 | 44.0302 | 44.0137 | 43.9959 | 43.2621 | 43.1857 | 43.1062 | 43.0148 | 42.7967 | 42.4546 | 42.1611 | 41.3743 | 40.0788 | 38.8412 | 37.729 | 44.8421 | 44.8269 | 44.8107 | 44.0804 | 44.0075 | 43.931 | 43.8445 | 43.7521 | 43.6387 | 43.5925 | 43.4459 | 43.1774 | 41.9882 | 40.859
|  | BLANDFORD | ST |  |  | 40.1286 | 40.1173 | 40.1049 | 39.8029 | 39.7546 | 39.7046 | 39.6498 | 39.5929 | 39.5238 | 39.4795 | 39.3463 | 39.1493 | 38.8848 | 38.6894 | 44.1163 | 44.1079 | 44.0989 | 43.8029 | 43.762 | 43.7196 | 43.674 | 43.6266 | 43.5683 | 43.4033 | 42.8746 | 42.0508 | 41.2363 | 40.5026 | 44.9279 | 44.9206 | 44.9127 | 44.6187 | 44.5803 | 44.5405 | 44.4982 | 44.454 | 44.3994 | 44.3707 | 44.2779 | 44.1451 | 43.9368 | 43.6634
|  | BLANDFORD | SP |  |  | 40.1725 | 40.1587 | 40.1545 | 40.0074 | 39.9798 | 39.9528 | 39.9231 | 39.893 | 39.8543 | 39.7912 | 39.5942 | 39.4515 | 39.1484 | 38.8731 | 44.1533 | 44.1446 | 44.1412 | 43.9954 | 43.97 | 43.9451 | 43.9185 | 43.8917 | 43.8573 | 43.7987 | 43.6134 | 43.4892 | 43.1134 | 42.6521 | 44.9626 | 44.9556 | 44.9525 | 44.8071 | 44.7825 | 44.7582 | 44.7328 | 44.707 | 44.6741 | 44.6171 | 44.4358 | 44.3179 | 44.0354 | 43.7791
COWLEY GSP | WITNEY BSP | BLEDDINGTON | MINIMUM HEADROOM | SP 25641 22580 | NO | 14.9614 | 14.9335 | 14.8969 | 14.8195 | 14.5259 | 14.2262 | 13.942 | 13.6497 | 13.2312 | 13.1282 | 12.7997 | 12.2843 | 11.4959 | 11.2048 | 14.9959 | 14.993 | 14.9892 | 14.981 | 14.7547 | 14.5215 | 14.2809 | 14.0318 | 13.6562 | 13.5994 | 13.4074 | 13.0921 | 12.4853 | 12.3729 | 16.4159 | 16.384 | 16.3421 | 16.2535 | 15.9492 | 15.6388 | 15.3476 | 15.0483 | 14.623 | 14.5126 | 14.1622 | 13.6105 | 12.7846 | 12.4566
|  | BLEDDINGTON | CT |  |  | 14.9669 | 14.943 | 14.9117 | 14.8454 | 14.7625 | 14.68 | 14.5977 | 14.5294 | 14.4507 | 14.3952 | 14.2302 | 13.9189 | 13.5935 | 13.3202 | 14.9965 | 14.994 | 14.9907 | 14.9837 | 14.9584 | 14.9329 | 14.9071 | 14.882 | 14.8461 | 14.8368 | 14.8082 | 14.7038 | 14.5599 | 14.4653 | 16.4222 | 16.3948 | 16.359 | 16.2831 | 16.1911 | 16.0994 | 16.008 | 15.9328 | 15.8472 | 15.7843 | 15.5974 | 15.2499 | 14.8869 | 14.5767
|  | BLEDDINGTON | LW |  |  | 14.9614 | 14.9335 | 14.8969 | 14.8195 | 14.5259 | 14.2262 | 13.942 | 13.6497 | 13.2312 | 13.1282 | 12.7997 | 12.2843 | 11.4959 | 11.2048 | 14.9959 | 14.993 | 14.9892 | 14.981 | 14.7547 | 14.5215 | 14.2809 | 14.0318 | 13.6562 | 13.5994 | 13.4074 | 13.0921 | 12.4853 | 12.3729 | 16.4159 | 16.384 | 16.3421 | 16.2535 | 15.9492 | 15.6388 | 15.3476 | 15.0483 | 14.623 | 14.5126 | 14.1622 | 13.6105 | 12.7846 | 12.4566
|  | BLEDDINGTON | ST |  |  | 14.9665 | 14.9431 | 14.9155 | 14.8683 | 14.8104 | 14.7405 | 14.7115 | 14.6829 | 14.6502 | 14.615 | 14.5121 | 14.3444 | 14.1764 | 14.0093 | 14.9965 | 14.994 | 14.9911 | 14.9861 | 14.98 | 14.9727 | 14.9696 | 14.9666 | 14.9632 | 14.9595 | 14.9487 | 14.931 | 14.9093 | 14.8583 | 16.4217 | 16.3949 | 16.3634 | 16.3094 | 16.2431 | 16.1632 | 16.13 | 16.0973 | 16.0599 | 16.0197 | 15.9021 | 15.7103 | 15.5181 | 15.327
|  | BLEDDINGTON | SP |  |  | 14.9937 | 14.9908 | 14.988 | 14.9853 | 14.9675 | 14.9475 | 14.9329 | 14.9183 | 14.8982 | 14.8615 | 14.7487 | 14.65 | 14.4789 | 14.3292 | 14.9993 | 14.999 | 14.9987 | 14.9985 | 14.9918 | 14.9851 | 14.9788 | 14.9725 | 14.963 | 14.9385 | 14.8611 | 14.8195 | 14.7033 | 14.6053 | 16.4528 | 16.4495 | 16.4463 | 16.4432 | 16.4236 | 16.4015 | 16.3855 | 16.3696 | 16.3477 | 16.3091 | 16.1906 | 16.0828 | 15.9029 | 15.7448
BRAMLEY (FLEE) | ALTON | BORDON | MINIMUM HEADROOM | SU 82256 35269 | YES | 31.1777 | 31.1777 | 31.1777 | 31.1777 | 31.1751 | 31.1697 | 31.1612 | 31.1494 | 31.1258 | 31.1217 | 30.5745 | 29.2794 | 28.0198 | 26.8911 | 25.0286 | 25.0211 | 25.0118 | 24.9965 | 24.9798 | 24.9586 | 24.932 | 24.9006 | 24.7593 | 24.3085 | 23.0197 | 21.4165 | 19.8696 | 18.4631 | 24.2921 | 24.283 | 24.2716 | 24.2531 | 24.2332 | 24.2086 | 24.1503 | 23.7264 | 23.2705 | 22.8143 | 21.5105 | 19.8889 | 18.3249 | 16.9018
|  | BORDON | CT |  |  | 31.1777 | 31.1777 | 31.1777 | 31.1777 | 31.1769 | 31.1754 | 31.1732 | 31.17 | 31.1628 | 31.1616 | 30.6412 | 29.3401 | 28.1167 | 26.9759 | 25.0286 | 25.0211 | 25.0118 | 24.9965 | 24.981 | 24.9636 | 24.9448 | 24.9219 | 24.8123 | 24.3641 | 23.0895 | 21.4803 | 19.9697 | 18.5513 | 24.2921 | 24.283 | 24.2716 | 24.2531 | 24.2343 | 24.2134 | 24.1782 | 23.763 | 23.3236 | 22.8701 | 21.5805 | 19.9529 | 18.4251 | 16.9902
|  | BORDON | LW |  |  | 31.1777 | 31.1777 | 31.1777 | 31.1777 | 31.1751 | 31.1697 | 31.1612 | 31.1494 | 31.1258 | 31.1217 | 30.5745 | 29.2794 | 28.0198 | 26.8911 | 25.0287 | 25.0213 | 25.012 | 24.997 | 24.9798 | 24.9586 | 24.932 | 24.9006 | 24.7593 | 24.3085 | 23.0197 | 21.4165 | 19.8696 | 18.4631 | 24.2922 | 24.2832 | 24.2719 | 24.2536 | 24.2332 | 24.2086 | 24.1503 | 23.7264 | 23.2705 | 22.8143 | 21.5105 | 19.8889 | 18.3249 | 16.9018
|  | BORDON | ST |  |  | 31.1777 | 31.1777 | 31.1777 | 31.1777 | 31.1772 | 31.1761 | 31.1744 | 31.1719 | 31.1664 | 31.1638 | 31.1496 | 30.9298 | 30.1155 | 29.3621 | 25.031 | 25.0259 | 25.02 | 25.0122 | 25.0027 | 24.9905 | 24.9764 | 24.9607 | 24.9412 | 24.9238 | 24.5199 | 23.4554 | 22.4557 | 21.5218 | 24.295 | 24.2888 | 24.2817 | 24.2722 | 24.2607 | 24.246 | 24.2293 | 24.2106 | 24.1882 | 23.9273 | 23.028 | 21.951 | 20.9403 | 19.9956
|  | BORDON | SP |  |  | 31.1777 | 31.1777 | 31.1777 | 31.1777 | 31.1777 | 31.1776 | 31.1776 | 31.1775 | 31.1772 | 31.1764 | 31.1712 | 31.1672 | 31.1477 | 31.1287 | 25.0343 | 25.0321 | 25.0299 | 25.0281 | 25.0251 | 25.0213 | 25.0169 | 25.0122 | 25.0064 | 24.9997 | 24.978 | 24.9545 | 24.9184 | 24.8841 | 24.299 | 24.2964 | 24.2937 | 24.2915 | 24.2878 | 24.2833 | 24.2779 | 24.2722 | 24.2651 | 24.2572 | 24.2319 | 24.2042 | 24.1366 | 23.7966
MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN | MINIMUM HEADROOM | SU 17186 41044 | YES | 31.632 | 31.6135 | 31.5898 | 31.552 | 31.524 | 31.4976 | 31.429 | 31.358 | 31.2802 | 31.2106 | 31.0017 | 30.6442 | 30.2542 | 29.9263 | 28.2109 | 28.1908 | 28.165 | 28.1238 | 28.0935 | 28.065 | 27.9909 | 27.9142 | 27.8308 | 27.7552 | 27.5289 | 27.1424 | 26.723 | 26.3664 | 26.7913 | 26.7695 | 26.7418 | 26.6974 | 26.6648 | 26.6343 | 26.5548 | 26.4726 | 26.3838 | 26.3024 | 26.0594 | 25.645 | 25.1974 | 24.8132
|  | BOSCOMBE DOWN | CT |  |  | 31.6333 | 31.6158 | 31.5934 | 31.5582 | 31.5339 | 31.5124 | 31.4896 | 31.4237 | 31.3558 | 31.2879 | 31.0873 | 30.7265 | 30.3578 | 30.0227 | 28.2124 | 28.1933 | 28.1689 | 28.1306 | 28.1042 | 28.0808 | 28.0562 | 27.9846 | 27.9111 | 27.8372 | 27.6192 | 27.2294 | 26.8313 | 26.4676 | 26.7929 | 26.7723 | 26.746 | 26.7047 | 26.6762 | 26.6511 | 26.6247 | 26.5476 | 26.4687 | 26.389 | 26.1542 | 25.7365 | 25.3103 | 24.9189
|  | BOSCOMBE DOWN | LW |  |  | 31.632 | 31.6135 | 31.5898 | 31.552 | 31.524 | 31.4976 | 31.429 | 31.358 | 31.2802 | 31.2106 | 31.0017 | 30.6442 | 30.2542 | 29.9263 | 28.2109 | 28.1908 | 28.165 | 28.1238 | 28.0935 | 28.065 | 27.9909 | 27.9142 | 27.8308 | 27.7552 | 27.5289 | 27.1424 | 26.723 | 26.3664 | 26.7913 | 26.7695 | 26.7418 | 26.6974 | 26.6648 | 26.6343 | 26.5548 | 26.4726 | 26.3838 | 26.3024 | 26.0594 | 25.645 | 25.1974 | 24.8132
|  | BOSCOMBE DOWN | ST |  |  | 31.635 | 31.6206 | 31.6038 | 31.5802 | 31.5435 | 31.5051 | 31.4507 | 31.3949 | 31.32 | 31.263 | 31.0912 | 30.8359 | 30.4957 | 30.2456 | 28.2142 | 28.1986 | 28.1802 | 28.1545 | 28.1162 | 28.0759 | 28.0183 | 27.9593 | 27.8806 | 27.8195 | 27.636 | 27.3613 | 27.0021 | 26.7334 | 26.7949 | 26.778 | 26.7582 | 26.7305 | 26.6905 | 26.6485 | 26.5878 | 26.5257 | 26.4433 | 26.3783 | 26.1834 | 25.8901 | 25.5127 | 25.226
|  | BOSCOMBE DOWN | SP |  |  | 31.6435 | 31.6368 | 31.6299 | 31.6227 | 31.6114 | 31.6006 | 31.5834 | 31.566 | 31.5422 | 31.4977 | 31.3606 | 31.2351 | 31.021 | 30.832 | 28.2234 | 28.2161 | 28.2086 | 28.2008 | 28.189 | 28.1779 | 28.1596 | 28.1413 | 28.1161 | 28.0701 | 27.9284 | 27.7955 | 27.5745 | 27.3789 | 26.8048 | 26.7969 | 26.7888 | 26.7804 | 26.7681 | 26.7566 | 26.7374 | 26.718 | 26.6917 | 26.6441 | 26.498 | 26.358 | 26.1303 | 25.9284
MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST | MINIMUM HEADROOM | SZ 11636 92447 | YES | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 33.8302 | 32.5194 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4321 | 32.3334 | 30.811 | 29.2722 | 34.0188 | 34.006 | 34.0033 | 33.9983 | 33.9932 | 33.988 | 33.9827 | 33.9745 | 33.9662 | 33.9574 | 33.9288 | 33.2433 | 31.7358 | 30.2175
|  | BOSCOMBE EAST | CT |  |  | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 33.8302 | 32.5194 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4321 | 32.3334 | 30.811 | 29.2722 | 34.0188 | 34.006 | 34.0033 | 33.9983 | 33.9932 | 33.988 | 33.9827 | 33.9745 | 33.9662 | 33.9574 | 33.9288 | 33.2433 | 31.7358 | 30.2175
|  | BOSCOMBE EAST | LW |  |  | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 33.8548 | 32.5438 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4335 | 32.3615 | 30.8399 | 29.3008 | 34.0193 | 34.0069 | 34.0048 | 34.0008 | 33.9967 | 33.9926 | 33.9844 | 33.9761 | 33.9678 | 33.959 | 33.9304 | 33.2719 | 31.7643 | 30.2458
|  | BOSCOMBE EAST | ST |  |  | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 34.9468 | 34.1132 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.0994 | 32.122 | 31.1434 | 34.0199 | 34.0189 | 34.0068 | 34.0049 | 34.0025 | 33.9997 | 33.9914 | 33.9831 | 33.9775 | 33.9715 | 33.9519 | 33.9036 | 33.0292 | 32.0637
|  | BOSCOMBE EAST | SP |  |  | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 35.0321 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.4484 | 33.444 | 33.3069 | 34.0312 | 34.0205 | 34.0093 | 34.0089 | 34.0081 | 34.0072 | 34.0045 | 34.0017 | 33.9983 | 33.9959 | 33.9884 | 33.9687 | 33.9429 | 33.9156
MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY | MINIMUM HEADROOM | SZ 06207 92415 | YES | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0445 | 38.0098 | 37.9745 | 37.9376 | 37.8808 | 37.8736 | 37.8505 | 37.6553 | 36.419 | 34.3904 | 35.7039 | 35.6922 | 35.6869 | 35.6766 | 35.6322 | 35.587 | 35.5412 | 35.4924 | 35.4235 | 35.4036 | 35.3387 | 34.2731 | 31.8189 | 29.4314 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.933 | 35.8983 | 35.863 | 35.8262 | 35.7693 | 35.7621 | 35.739 | 34.8375 | 32.444 | 30.1175
|  | BOURNE VALLEY | CT |  |  | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0445 | 38.0098 | 37.9745 | 37.9376 | 37.8808 | 37.8736 | 37.8505 | 37.6553 | 36.419 | 34.3904 | 35.7039 | 35.6922 | 35.6869 | 35.6766 | 35.6322 | 35.587 | 35.5412 | 35.4924 | 35.4235 | 35.4036 | 35.3387 | 34.2731 | 31.8189 | 29.4314 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.933 | 35.8983 | 35.863 | 35.8262 | 35.7693 | 35.7621 | 35.739 | 34.8375 | 32.444 | 30.1175
|  | BOURNE VALLEY | LW |  |  | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0083 | 37.0901 | 35.0927 | 35.7057 | 35.6954 | 35.6919 | 35.6853 | 35.6787 | 35.6718 | 35.6599 | 35.648 | 35.6359 | 35.6232 | 35.5814 | 34.8622 | 32.5295 | 30.1731 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.4247 | 33.1478 | 30.8525
|  | BOURNE VALLEY | ST |  |  | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0769 | 37.969 | 37.326 | 35.7056 | 35.7031 | 35.6924 | 35.6876 | 35.6817 | 35.6745 | 35.6622 | 35.65 | 35.6418 | 35.633 | 35.6044 | 35.5312 | 34.3051 | 32.8078 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 34.8773 | 33.4189
|  | BOURNE VALLEY | SP |  |  | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 38.0786 | 35.7081 | 35.7074 | 35.6991 | 35.6984 | 35.6968 | 35.6949 | 35.6911 | 35.6872 | 35.6823 | 35.6789 | 35.6677 | 35.6376 | 35.5977 | 35.5554 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672 | 35.9672
MANNINGTON GSP | SHAFTESBURY BSP | BOURTON | MINIMUM HEADROOM | ST 77363 30262 | YES | 15.8284 | 15.7601 | 15.7569 | 15.7501 | 15.66 | 15.5684 | 15.4755 | 15.3091 | 15.0677 | 14.9399 | 14.5575 | 13.7504 | 12.8993 | 12.2692 | 9.4638 | 9.265 | 9.2555 | 9.2359 | 9.1333 | 9.0291 | 8.9236 | 8.7091 | 8.4468 | 8.2963 | 7.8471 | 6.9285 | 5.9614 | 5.2173 | 11.0715 | 10.9195 | 10.9123 | 10.8973 | 10.7992 | 10.6995 | 10.5985 | 10.4133 | 10.18 | 10.0342 | 9.5951 | 8.6936 | 7.7442 | 7.0174
|  | BOURTON | CT |  |  | 15.8284 | 15.7601 | 15.7569 | 15.7502 | 15.66 | 15.5684 | 15.4755 | 15.3091 | 15.0677 | 14.9399 | 14.5575 | 13.7504 | 12.8993 | 12.2692 | 9.4638 | 9.265 | 9.2556 | 9.236 | 9.1333 | 9.0291 | 8.9236 | 8.7091 | 8.4468 | 8.2963 | 7.8471 | 6.9285 | 5.9614 | 5.2173 | 11.0715 | 10.9195 | 10.9124 | 10.8974 | 10.7992 | 10.6995 | 10.5985 | 10.4133 | 10.18 | 10.0342 | 9.5951 | 8.6936 | 7.7442 | 7.0174
|  | BOURTON | LW |  |  | 15.8284 | 15.7601 | 15.7569 | 15.7501 | 15.6982 | 15.6447 | 15.5278 | 15.3739 | 15.1947 | 15.0739 | 14.7114 | 14.1134 | 13.4562 | 12.8944 | 9.4638 | 9.265 | 9.2555 | 9.2359 | 9.1713 | 9.1052 | 8.9308 | 8.7558 | 8.5556 | 8.4121 | 7.9828 | 7.2734 | 6.5002 | 5.8242 | 11.0715 | 10.9195 | 10.9123 | 10.8973 | 10.8372 | 10.7757 | 10.6309 | 10.4851 | 10.2928 | 10.1528 | 9.7337 | 9.0412 | 8.2857 | 7.6271
|  | BOURTON | ST |  |  | 15.8295 | 15.828 | 15.7604 | 15.7573 | 15.7535 | 15.7489 | 15.7263 | 15.6935 | 15.6236 | 15.5485 | 15.3286 | 14.9668 | 14.6023 | 14.2405 | 9.4672 | 9.4627 | 9.2657 | 9.2567 | 9.2457 | 9.2323 | 9.1664 | 9.1015 | 9.0173 | 8.9268 | 8.6618 | 8.2258 | 7.7865 | 7.3505 | 11.0741 | 11.0706 | 10.9201 | 10.9132 | 10.9048 | 10.8946 | 10.8442 | 10.7946 | 10.7302 | 10.661 | 10.4032 | 9.9785 | 9.5507 | 9.126
|  | BOURTON | SP |  |  | 15.8312 | 15.8309 | 15.7648 | 15.7645 | 15.7601 | 15.7555 | 15.7457 | 15.7361 | 15.7226 | 15.6957 | 15.589 | 15.4286 | 15.2242 | 15.0379 | 9.4719 | 9.4711 | 9.2786 | 9.2778 | 9.2713 | 9.2643 | 9.2424 | 9.2208 | 9.1916 | 9.1416 | 8.9921 | 8.8034 | 8.5716 | 8.3591 | 11.0777 | 11.077 | 10.9299 | 10.9293 | 10.9235 | 10.9174 | 10.8999 | 10.8825 | 10.859 | 10.8173 | 10.692 | 10.5385 | 10.3108 | 10.1023
MANNINGTON GSP | WAREHAM | BOVINGTON | MINIMUM HEADROOM | SY 83933 87831 | YES | 9.2188 | 9.2161 | 9.199 | 9.164 | 9.1048 | 9.0194 | 8.8968 | 8.7541 | 8.5949 | 8.4735 | 8.11 | 7.7595 | 7.4411 | 7.2401 | 5.3138 | 5.3106 | 5.2906 | 5.2495 | 5.1812 | 5.0826 | 4.9409 | 4.7762 | 4.5945 | 4.4529 | 4.0301 | 3.6279 | 3.2727 | 3.0379 | 3.4568 | 3.4537 | 3.4339 | 3.3933 | 3.3259 | 3.2285 | 3.0885 | 2.9258 | 2.7461 | 2.6063 | 2.1889 | 1.7913 | 1.4395 | 1.2077
|  | BOVINGTON | CT |  |  | 9.2188 | 9.2161 | 9.199 | 9.164 | 9.1111 | 9.0342 | 8.951 | 8.8215 | 8.6856 | 8.5679 | 8.2213 | 7.8715 | 7.6009 | 7.3889 | 5.3138 | 5.3106 | 5.2906 | 5.2495 | 5.1875 | 5.0974 | 5.0001 | 4.8486 | 4.6902 | 4.5523 | 4.1464 | 3.7449 | 3.4374 | 3.1917 | 3.4568 | 3.4537 | 3.4339 | 3.3933 | 3.3322 | 3.2432 | 3.1472 | 2.9977 | 2.8413 | 2.7053 | 2.3047 | 1.9079 | 1.6037 | 1.361
|  | BOVINGTON | LW |  |  | 9.2188 | 9.2161 | 9.199 | 9.164 | 9.1048 | 9.0194 | 8.8968 | 8.7541 | 8.5949 | 8.4735 | 8.11 | 7.7595 | 7.4411 | 7.2401 | 5.3138 | 5.3106 | 5.2906 | 5.2495 | 5.1812 | 5.0826 | 4.9409 | 4.7762 | 4.5945 | 4.4529 | 4.0301 | 3.6279 | 3.2727 | 3.0379 | 3.4568 | 3.4537 | 3.4339 | 3.3933 | 3.3259 | 3.2285 | 3.0885 | 2.9258 | 2.7461 | 2.6063 | 2.1889 | 1.7913 | 1.4395 | 1.2077
|  | BOVINGTON | ST |  |  | 9.2201 | 9.2184 | 9.2069 | 9.1852 | 9.1506 | 9.099 | 9.0258 | 8.9409 | 8.849 | 8.7666 | 8.5135 | 8.2905 | 8.0922 | 7.944 | 5.3153 | 5.3133 | 5.2999 | 5.2743 | 5.2338 | 5.1734 | 5.0878 | 4.9884 | 4.8814 | 4.7852 | 4.4904 | 4.2316 | 4.0094 | 3.8393 | 3.4582 | 3.4563 | 3.443 | 3.4178 | 3.3778 | 3.3183 | 3.2338 | 3.1357 | 3.0301 | 2.935 | 2.644 | 2.3885 | 2.1684 | 2.0003
|  | BOVINGTON | SP |  |  | 9.2218 | 9.2215 | 9.215 | 9.2036 | 9.1855 | 9.161 | 9.1312 | 9.0979 | 9.0625 | 9.0259 | 8.9131 | 8.8216 | 8.7316 | 8.6525 | 5.3173 | 5.317 | 5.3093 | 5.2959 | 5.2748 | 5.2463 | 5.2114 | 5.1725 | 5.1313 | 5.0892 | 4.9599 | 4.8542 | 4.7551 | 4.6682 | 3.4603 | 3.4599 | 3.4523 | 3.4392 | 3.4183 | 3.3901 | 3.3557 | 3.3173 | 3.2767 | 3.235 | 3.1072 | 3.0028 | 2.9045 | 2.8184
AMERSHAM | LOUDWATER BSP | BOWERDEAN | MINIMUM HEADROOM | SU 87718 93880 | YES | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.573 | 32.5491 | 32.5261 | 32.5019 | 32.4308 | 32.3089 | 31.157 | 29.7222 | 24.7346 | 24.7256 | 24.714 | 24.695 | 24.6769 | 24.6584 | 24.6399 | 24.6254 | 24.6114 | 24.5966 | 24.5533 | 23.1097 | 21.4012 | 19.7279 | 24.9884 | 24.977 | 24.9622 | 24.938 | 24.9149 | 24.8913 | 24.8677 | 24.8492 | 24.8313 | 24.8125 | 23.9022 | 22.2702 | 20.5716 | 18.8784
|  | BOWERDEAN | CT |  |  | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.573 | 32.5491 | 32.5261 | 32.5019 | 32.4308 | 32.3089 | 31.157 | 29.7222 | 24.7346 | 24.7256 | 24.714 | 24.695 | 24.6769 | 24.6584 | 24.6399 | 24.6254 | 24.6114 | 24.5966 | 24.5533 | 23.1097 | 21.4012 | 19.7279 | 24.9884 | 24.977 | 24.9622 | 24.938 | 24.9149 | 24.8913 | 24.8677 | 24.8492 | 24.8313 | 24.8125 | 23.9022 | 22.2702 | 20.5716 | 18.8784
|  | BOWERDEAN | LW |  |  | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5913 | 32.5674 | 32.5444 | 32.5202 | 32.4491 | 32.3272 | 31.3707 | 29.9351 | 24.7355 | 24.7272 | 24.7165 | 24.6993 | 24.683 | 24.6663 | 24.6511 | 24.6365 | 24.6225 | 24.6078 | 24.5645 | 23.3591 | 21.6504 | 19.9761 | 24.9896 | 24.979 | 24.9654 | 24.9435 | 24.9227 | 24.9014 | 24.882 | 24.8634 | 24.8455 | 24.8268 | 24.1475 | 22.516 | 20.8238 | 19.1296
|  | BOWERDEAN | ST |  |  | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5842 | 32.536 | 32.4542 | 32.3729 | 32.293 | 24.7373 | 24.7309 | 24.7235 | 24.7137 | 24.7022 | 24.6881 | 24.677 | 24.6664 | 24.6568 | 24.6467 | 24.6174 | 24.5676 | 23.9789 | 22.894 | 24.9919 | 24.9838 | 24.9743 | 24.9618 | 24.9471 | 24.9292 | 24.915 | 24.9014 | 24.8892 | 24.8764 | 24.839 | 24.2152 | 23.1266 | 22.0577
|  | BOWERDEAN | SP |  |  | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5915 | 32.5846 | 24.7424 | 24.7403 | 24.7382 | 24.7369 | 24.7339 | 24.7303 | 24.7264 | 24.7228 | 24.7183 | 24.7144 | 24.703 | 24.6838 | 24.665 | 24.647 | 24.9984 | 24.9957 | 24.993 | 24.9914 | 24.9876 | 24.983 | 24.978 | 24.9734 | 24.9677 | 24.9627 | 24.9482 | 24.9237 | 24.8997 | 24.8768
BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL | MINIMUM HEADROOM | SU 86075 69397 | YES | 95.4815 | 95.4554 | 95.4364 | 95.397 | 95.214 | 95.0195 | 94.8276 | 94.6382 | 94.3532 | 94.2878 | 94.0755 | 93.0278 | 91.3466 | 90.1181 | 92.3539 | 92.3361 | 92.3231 | 92.2963 | 92.1227 | 91.9405 | 91.7592 | 91.5774 | 91.3019 | 91.247 | 91.0692 | 89.1789 | 87.2227 | 85.7305 | 92.2472 | 92.2175 | 92.1958 | 92.1508 | 91.9636 | 91.7637 | 91.5671 | 91.3744 | 91.0852 | 91.0151 | 90.7875 | 90.1467 | 89.2967 | 87.8312
|  | BRACKNELL | CT |  |  | 95.4839 | 95.4596 | 95.4428 | 95.4083 | 95.214 | 95.0195 | 94.8276 | 94.6382 | 94.3532 | 94.2878 | 94.0755 | 93.0278 | 91.3466 | 90.1181 | 92.3555 | 92.3389 | 92.3275 | 92.304 | 92.1227 | 91.9405 | 91.7592 | 91.5774 | 91.3019 | 91.247 | 91.0692 | 89.1789 | 87.2227 | 85.7305 | 92.25 | 92.2222 | 92.2031 | 92.1637 | 91.9636 | 91.7637 | 91.5671 | 91.3744 | 91.0852 | 91.0151 | 90.7875 | 90.1467 | 89.2967 | 87.8312
|  | BRACKNELL | LW |  |  | 95.4815 | 95.4554 | 95.4364 | 95.397 | 95.3351 | 95.2752 | 95.2356 | 95.1936 | 95.1364 | 95.0994 | 94.9779 | 94.2943 | 93.1016 | 92.0021 | 92.3539 | 92.3361 | 92.3231 | 92.2963 | 92.2489 | 92.2027 | 92.1702 | 92.1358 | 92.088 | 92.0616 | 91.9745 | 90.42 | 88.9523 | 87.589 | 92.2472 | 92.2175 | 92.1958 | 92.1508 | 92.0825 | 92.0165 | 91.9738 | 91.9285 | 91.867 | 91.8254 | 91.6886 | 91.5079 | 91.0288 | 89.6922
|  | BRACKNELL | ST |  |  | 95.4909 | 95.4757 | 95.4553 | 95.4354 | 95.3926 | 95.3473 | 95.317 | 95.2851 | 95.2409 | 95.2101 | 95.1077 | 94.9879 | 94.8562 | 94.7367 | 92.3603 | 92.3499 | 92.336 | 92.3225 | 92.2887 | 92.2531 | 92.2276 | 92.2009 | 92.1631 | 92.1395 | 92.0613 | 91.9729 | 91.732 | 91.0244 | 92.258 | 92.2406 | 92.2174 | 92.1947 | 92.1479 | 92.0983 | 92.0659 | 92.0316 | 91.9846 | 91.9506 | 91.8374 | 91.7037 | 91.5628 | 91.4708
|  | BRACKNELL | SP |  |  | 95.4998 | 95.4956 | 95.4805 | 95.4766 | 95.4668 | 95.4573 | 95.4515 | 95.4454 | 95.4369 | 95.4279 | 95.3979 | 95.3585 | 95.3323 | 95.3074 | 92.3664 | 92.3635 | 92.3532 | 92.3505 | 92.3438 | 92.3374 | 92.3334 | 92.3293 | 92.3235 | 92.3174 | 92.2968 | 92.27 | 92.2521 | 92.2351 | 92.2681 | 92.2634 | 92.2461 | 92.2417 | 92.2305 | 92.2196 | 92.2131 | 92.2061 | 92.1964 | 92.1862 | 92.1518 | 92.107 | 92.077 | 92.0486
MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON | MINIMUM HEADROOM | ST 81260 60564 | NO | 35.942 | 35.9034 | 35.4776 | 35.4675 | 35.4568 | 35.4454 | 35.4275 | 35.4015 | 35.3627 | 35.3441 | 35.0231 | 34.1367 | 33.1989 | 32.3378 | 34.2324 | 34.1903 | 33.764 | 33.7496 | 33.7313 | 33.6871 | 33.5515 | 33.3647 | 33.1752 | 32.9778 | 32.3902 | 31.3568 | 30.2737 | 29.2535 | 34.113 | 33.7084 | 33.2369 | 33.1306 | 33.0266 | 32.9226 | 32.8187 | 32.6756 | 32.5294 | 32.3787 | 31.9294 | 31.0158 | 30.0091 | 29.0657
|  | BRADFORD-ON-AVON | CT |  |  | 35.942 | 35.9034 | 35.4776 | 35.4675 | 35.4568 | 35.4454 | 35.4334 | 35.4166 | 35.3957 | 35.3801 | 35.0231 | 34.1367 | 33.207 | 32.3378 | 34.2324 | 34.1903 | 33.764 | 33.7496 | 33.7313 | 33.6871 | 33.5515 | 33.3647 | 33.1752 | 32.9778 | 32.3902 | 31.3568 | 30.2737 | 29.2535 | 34.113 | 33.7084 | 33.2369 | 33.1306 | 33.0266 | 32.9226 | 32.8187 | 32.6756 | 32.5294 | 32.3787 | 31.9294 | 31.0158 | 30.0099 | 29.0657
|  | BRADFORD-ON-AVON | LW |  |  | 35.9432 | 35.9056 | 35.481 | 35.4734 | 35.4632 | 35.4501 | 35.4275 | 35.4015 | 35.3627 | 35.3441 | 35.0478 | 34.1676 | 33.1989 | 32.3429 | 34.2338 | 34.1927 | 33.7677 | 33.7594 | 33.7443 | 33.7254 | 33.6362 | 33.4401 | 33.2328 | 33.0324 | 32.4297 | 31.4024 | 30.2804 | 29.2732 | 34.1262 | 33.7312 | 33.2724 | 33.1929 | 33.1128 | 33.0302 | 32.8801 | 32.7277 | 32.5637 | 32.4101 | 31.9456 | 31.054 | 30.0091 | 29.078
|  | BRADFORD-ON-AVON | ST |  |  | 35.9565 | 35.9417 | 35.9042 | 35.8998 | 35.4728 | 35.4651 | 35.4531 | 35.4403 | 35.4254 | 35.4128 | 35.3691 | 34.962 | 34.3355 | 33.7582 | 34.2483 | 34.2321 | 34.1912 | 34.1863 | 33.7588 | 33.7467 | 33.7268 | 33.6652 | 33.5349 | 33.3983 | 32.9916 | 32.3228 | 31.5973 | 30.9218 | 34.2652 | 34.11 | 33.7166 | 33.6703 | 33.1919 | 33.1223 | 33.0133 | 32.9049 | 32.8043 | 32.6996 | 32.3862 | 31.8719 | 31.2353 | 30.6093
|  | BRADFORD-ON-AVON | SP |  |  | 35.9677 | 35.9461 | 35.9109 | 35.9106 | 35.9072 | 35.9035 | 35.8978 | 35.4711 | 35.463 | 35.4485 | 35.4008 | 35.3636 | 35.2783 | 35.2019 | 34.2606 | 34.2369 | 34.1985 | 34.1982 | 34.1946 | 34.1907 | 34.1848 | 33.7577 | 33.7493 | 33.7344 | 33.6782 | 33.5478 | 33.2389 | 32.9493 | 34.3831 | 34.1562 | 33.7869 | 33.784 | 33.7691 | 33.7517 | 33.7143 | 33.2562 | 33.2077 | 33.1574 | 33.0055 | 32.798 | 32.5466 | 32.3118
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN | MINIMUM HEADROOM | SU 67431 58511 | YES | 16.5849 | 16.5431 | 16.4881 | 16.3719 | 16.2563 | 16.1384 | 16.033 | 15.9728 | 15.9062 | 15.8451 | 15.6594 | 15.2725 | 14.8506 | 14.5144 | 15.9817 | 15.9212 | 15.8419 | 15.6743 | 15.5087 | 15.3414 | 15.261 | 15.221 | 15.1744 | 15.1348 | 14.9945 | 14.7341 | 14.3972 | 14.0269 | 16.1941 | 16.1851 | 16.1734 | 16.1485 | 16.1213 | 16.0235 | 15.8704 | 15.8003 | 15.7238 | 15.6521 | 15.4348 | 14.9947 | 14.5204 | 14.1258
|  | BRAMLEY GREEN | CT |  |  | 16.5899 | 16.5517 | 16.5014 | 16.3951 | 16.2912 | 16.1875 | 16.033 | 15.9728 | 15.9062 | 15.8451 | 15.6594 | 15.2725 | 14.854 | 14.5144 | 15.9889 | 15.9337 | 15.8611 | 15.7078 | 15.5582 | 15.4093 | 15.261 | 15.221 | 15.1744 | 15.1348 | 15.0129 | 14.7341 | 14.4226 | 14.0269 | 16.1952 | 16.187 | 16.1762 | 16.1535 | 16.1305 | 16.1069 | 15.8704 | 15.8003 | 15.7238 | 15.6521 | 15.4348 | 14.9947 | 14.5204 | 14.1258
|  | BRAMLEY GREEN | LW |  |  | 16.5849 | 16.5431 | 16.4881 | 16.3719 | 16.2563 | 16.1384 | 16.0957 | 16.0249 | 15.9381 | 15.8735 | 15.6693 | 15.3024 | 14.8506 | 14.535 | 15.9817 | 15.9212 | 15.8419 | 15.6743 | 15.5087 | 15.3414 | 15.2953 | 15.2447 | 15.1779 | 15.1348 | 14.9945 | 14.7356 | 14.3972 | 14.0617 | 16.1941 | 16.1851 | 16.1734 | 16.1485 | 16.1213 | 16.0235 | 15.947 | 15.8664 | 15.7697 | 15.6945 | 15.4588 | 15.0386 | 14.531 | 14.1603
|  | BRAMLEY GREEN | ST |  |  | 16.5936 | 16.5591 | 16.5185 | 16.449 | 16.3632 | 16.2591 | 16.2346 | 16.2091 | 16.1849 | 16.1636 | 16.0926 | 15.8719 | 15.5836 | 15.3534 | 15.9941 | 15.9443 | 15.8858 | 15.7855 | 15.6619 | 15.5124 | 15.4779 | 15.4426 | 15.4111 | 15.3819 | 15.288 | 15.1377 | 14.9226 | 14.7649 | 16.1959 | 16.1886 | 16.1799 | 16.165 | 16.1461 | 16.1228 | 16.1159 | 16.1078 | 16.0965 | 16.089 | 15.9487 | 15.6906 | 15.3662 | 15.1003
|  | BRAMLEY GREEN | SP |  |  | 16.634 | 16.6297 | 16.6257 | 16.6219 | 16.6038 | 16.5823 | 16.5746 | 16.5669 | 16.5568 | 16.5487 | 16.5216 | 16.4829 | 16.4246 | 16.3686 | 16.0524 | 16.0463 | 16.0405 | 16.035 | 16.0089 | 15.978 | 15.9668 | 15.9557 | 15.9414 | 15.9302 | 15.8942 | 15.8408 | 15.768 | 15.6981 | 16.2046 | 16.2037 | 16.2028 | 16.202 | 16.1981 | 16.1935 | 16.1918 | 16.19 | 16.1876 | 16.1849 | 16.1735 | 16.1609 | 16.1283 | 16.097
LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD | MINIMUM HEADROOM | SZ 64712 98665 | YES | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.5972 | 36.5678 | 36.5378 | 36.5068 | 36.4589 | 36.4426 | 36.3907 | 36.349 | 35.5821 | 34.3653 | 34.3506 | 34.3425 | 34.3318 | 34.3113 | 34.2916 | 34.2519 | 34.2027 | 34.1525 | 34.0935 | 34.0655 | 33.9785 | 32.8775 | 31.5317 | 30.1947 | 34.5998 | 34.594 | 34.5864 | 34.5718 | 34.5515 | 34.5128 | 34.4692 | 34.4245 | 34.3687 | 34.3442 | 34.2673 | 34.1764 | 33.1653 | 31.7494
|  | BRANDON ROAD | CT |  |  | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 35.7219 | 34.5158 | 34.3522 | 34.3453 | 34.3362 | 34.3189 | 34.3023 | 34.2855 | 34.2686 | 34.2511 | 34.2349 | 34.2178 | 34.166 | 33.0418 | 31.696 | 30.3593 | 34.6009 | 34.596 | 34.5895 | 34.5773 | 34.5655 | 34.5536 | 34.5415 | 34.5292 | 34.5176 | 34.5055 | 34.4688 | 34.3964 | 33.3394 | 31.9237
|  | BRANDON ROAD | LW |  |  | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 35.5821 | 34.3653 | 34.3506 | 34.3425 | 34.3318 | 34.3113 | 34.2916 | 34.2716 | 34.2545 | 34.2371 | 34.2209 | 34.2038 | 34.0705 | 32.8775 | 31.5317 | 30.1947 | 34.5998 | 34.594 | 34.5864 | 34.5718 | 34.5579 | 34.5437 | 34.5316 | 34.5192 | 34.5077 | 34.4955 | 34.4588 | 34.3865 | 33.1653 | 31.7494
|  | BRANDON ROAD | ST |  |  | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.5972 | 36.5678 | 36.5378 | 36.5068 | 36.4589 | 36.4426 | 36.3907 | 36.349 | 36.2105 | 35.7315 | 34.3543 | 34.3494 | 34.3434 | 34.3342 | 34.2944 | 34.2519 | 34.2027 | 34.1525 | 34.0935 | 34.0655 | 33.9785 | 33.7062 | 32.6895 | 31.7879 | 34.6024 | 34.5989 | 34.5947 | 34.5881 | 34.5515 | 34.5128 | 34.4692 | 34.4245 | 34.3687 | 34.3442 | 34.2673 | 34.1764 | 33.9847 | 33.4638
|  | BRANDON ROAD | SP |  |  | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 36.6261 | 34.3776 | 34.3571 | 34.3555 | 34.3541 | 34.3505 | 34.3462 | 34.3391 | 34.332 | 34.3234 | 34.3189 | 34.3053 | 34.2779 | 34.2467 | 34.2152 | 34.6189 | 34.6044 | 34.6033 | 34.6022 | 34.5997 | 34.5967 | 34.5916 | 34.5866 | 34.5805 | 34.5773 | 34.5676 | 34.5482 | 34.526 | 34.5037
BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD | MINIMUM HEADROOM | SU 88887 80726 | YES | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0091 | 37.9819 | 37.9541 | 37.9254 | 37.881 | 37.8659 | 37.8179 | 37.31 | 36.4116 | 35.5936 | 37.0289 | 37.0208 | 37.0084 | 36.9844 | 36.9415 | 36.8975 | 36.8638 | 36.8278 | 36.7794 | 36.7554 | 35.8934 | 34.515 | 33.4616 | 32.5017 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5557 | 36.5285 | 36.5007 | 36.472 | 36.4277 | 36.4126 | 36.3434 | 35.0779 | 34.0378 | 33.0907
|  | BRAYWICK ROAD | CT |  |  | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 37.3963 | 36.5476 | 35.733 | 37.0296 | 37.022 | 37.0103 | 36.9877 | 36.9647 | 36.9411 | 36.9173 | 36.9019 | 36.8849 | 36.8653 | 35.9387 | 34.5871 | 33.5852 | 32.6288 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5677 | 36.5445 | 36.4674 | 35.151 | 34.1625 | 33.2189
|  | BRAYWICK ROAD | LW |  |  | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0174 | 37.9983 | 37.9784 | 37.9577 | 37.9264 | 37.922 | 37.9071 | 37.31 | 36.4116 | 35.5936 | 37.0289 | 37.0208 | 37.0084 | 36.9844 | 36.9415 | 36.8975 | 36.8638 | 36.8278 | 36.7794 | 36.7554 | 35.8934 | 34.515 | 33.4616 | 32.5017 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.564 | 36.5449 | 36.525 | 36.5044 | 36.463 | 36.4354 | 36.3434 | 35.0779 | 34.0378 | 33.0907
|  | BRAYWICK ROAD | ST |  |  | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0091 | 37.9819 | 37.9541 | 37.9254 | 37.881 | 37.8659 | 37.8179 | 37.7793 | 37.652 | 37.612 | 37.0371 | 37.029 | 37.0224 | 37.0119 | 36.9723 | 36.9299 | 36.8901 | 36.8483 | 36.7925 | 36.764 | 36.67 | 36.5761 | 35.8019 | 35.1446 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5557 | 36.5285 | 36.5007 | 36.472 | 36.4277 | 36.4126 | 36.3534 | 36.2616 | 36.0976 | 35.6954
|  | BRAYWICK ROAD | SP |  |  | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 38.0358 | 37.0409 | 37.0359 | 37.0337 | 37.0312 | 37.0261 | 37.0204 | 37.0157 | 37.0106 | 37.0045 | 36.9992 | 36.9811 | 36.9632 | 36.9508 | 36.9391 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825 | 36.5825
EALING GSP | EALING (D) | BRENTFORD | MINIMUM HEADROOM | TQ 17659 78277 | YES | 47.808 | 47.808 | 47.808 | 47.808 | 47.7425 | 47.6758 | 47.6078 | 47.5305 | 47.4096 | 47.3785 | 47.27 | 47.0617 | 45.8769 | 43.7622 | 36.8518 | 36.8409 | 36.8264 | 36.8004 | 36.7144 | 36.6255 | 36.5405 | 36.4524 | 36.3292 | 36.2958 | 36.1844 | 35.6195 | 33.0455 | 30.5338 | 37.2047 | 37.1937 | 37.1792 | 37.1532 | 37.0671 | 36.9781 | 36.8984 | 36.8158 | 36.6981 | 36.6701 | 36.5528 | 36.3798 | 34.1847 | 31.6777
|  | BRENTFORD | CT |  |  | 47.808 | 47.808 | 47.808 | 47.808 | 47.7762 | 47.7438 | 47.6943 | 47.6429 | 47.5735 | 47.5501 | 47.4742 | 47.2359 | 45.8902 | 43.7622 | 36.8518 | 36.8409 | 36.8264 | 36.8004 | 36.7435 | 36.6853 | 36.6162 | 36.5625 | 36.4908 | 36.4651 | 36.3817 | 35.6195 | 33.0455 | 30.5338 | 37.2047 | 37.1937 | 37.1792 | 37.1532 | 37.0961 | 37.0381 | 36.9795 | 36.9314 | 36.8651 | 36.8449 | 36.7795 | 36.5677 | 34.1847 | 31.6777
|  | BRENTFORD | LW |  |  | 47.808 | 47.808 | 47.808 | 47.808 | 47.7464 | 47.6829 | 47.6164 | 47.5305 | 47.4096 | 47.3785 | 47.2746 | 47.0617 | 45.8769 | 43.7651 | 36.8519 | 36.841 | 36.8267 | 36.8009 | 36.7144 | 36.6255 | 36.5405 | 36.4524 | 36.3292 | 36.2958 | 36.1844 | 35.6645 | 33.0686 | 30.573 | 37.2048 | 37.1939 | 37.1795 | 37.1536 | 37.0671 | 36.9781 | 36.8984 | 36.8158 | 36.6981 | 36.6701 | 36.5767 | 36.3904 | 34.2035 | 31.7164
|  | BRENTFORD | ST |  |  | 47.808 | 47.808 | 47.808 | 47.808 | 47.7425 | 47.6758 | 47.6078 | 47.5376 | 47.4289 | 47.392 | 47.27 | 47.0784 | 46.6649 | 46.4608 | 36.8579 | 36.8519 | 36.8447 | 36.8347 | 36.7573 | 36.6763 | 36.5953 | 36.5117 | 36.3941 | 36.348 | 36.1936 | 35.9887 | 35.5594 | 33.9738 | 37.2108 | 37.2048 | 37.1976 | 37.1876 | 37.1102 | 37.0291 | 36.948 | 36.8644 | 36.7468 | 36.7007 | 36.5528 | 36.3798 | 35.9881 | 35.0589
|  | BRENTFORD | SP |  |  | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.808 | 47.7563 | 36.8623 | 36.8601 | 36.8578 | 36.8562 | 36.8517 | 36.8465 | 36.8416 | 36.8366 | 36.8307 | 36.8271 | 36.8154 | 36.7834 | 36.737 | 36.6733 | 37.2153 | 37.2131 | 37.2108 | 37.2091 | 37.2047 | 37.1994 | 37.1945 | 37.1895 | 37.1835 | 37.1799 | 37.1682 | 37.1361 | 37.0935 | 37.0482
LOVEDEAN GSP | HAVANT | BROCKHAMPTON | MINIMUM HEADROOM | SU 70868 05828 | YES | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3489 | 35.3456 | 35.3422 | 35.3376 | 35.3288 | 35.3276 | 35.3226 | 35.2883 | 35.2354 | 35.1926 | 27.7465 | 27.57 | 27.5528 | 27.5168 | 27.4785 | 27.4402 | 27.402 | 27.3489 | 27.2921 | 27.2391 | 27.078 | 26.7569 | 26.3969 | 26.0714 | 26.9828 | 26.9686 | 26.9672 | 26.9643 | 26.9582 | 26.9521 | 26.9459 | 26.9373 | 26.9247 | 26.9193 | 26.9017 | 26.8443 | 26.7292 | 26.3941
|  | BROCKHAMPTON | CT |  |  | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3489 | 35.3456 | 35.3422 | 35.3376 | 35.3288 | 35.3276 | 35.3226 | 35.2883 | 35.2354 | 35.1926 | 27.7465 | 27.57 | 27.5528 | 27.5168 | 27.4785 | 27.4402 | 27.402 | 27.3489 | 27.2921 | 27.2391 | 27.078 | 26.7569 | 26.3969 | 26.0714 | 26.9828 | 26.9686 | 26.9672 | 26.9643 | 26.9582 | 26.9521 | 26.9459 | 26.9373 | 26.9247 | 26.9193 | 26.9017 | 26.8443 | 26.7292 | 26.3941
|  | BROCKHAMPTON | LW |  |  | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3514 | 35.3497 | 35.3456 | 35.3448 | 35.3402 | 35.3291 | 35.2978 | 35.2666 | 27.7482 | 27.5728 | 27.5571 | 27.5244 | 27.4925 | 27.4606 | 27.4111 | 27.361 | 27.3088 | 27.2563 | 27.0955 | 26.7977 | 26.4593 | 26.1453 | 26.9829 | 26.9688 | 26.9675 | 26.9649 | 26.9623 | 26.9597 | 26.955 | 26.9495 | 26.9415 | 26.9366 | 26.9193 | 26.8851 | 26.7915 | 26.4679
|  | BROCKHAMPTON | ST |  |  | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3519 | 35.3515 | 35.3503 | 35.3498 | 35.3475 | 35.3447 | 35.3342 | 35.3305 | 27.76 | 27.7567 | 27.5895 | 27.5831 | 27.5753 | 27.5659 | 27.5345 | 27.5033 | 27.4692 | 27.4334 | 27.3256 | 27.1295 | 26.9148 | 26.7097 | 26.9839 | 26.9836 | 26.9701 | 26.9696 | 26.969 | 26.9682 | 26.9655 | 26.9626 | 26.9587 | 26.9554 | 26.9446 | 26.9262 | 26.8993 | 26.8793
|  | BROCKHAMPTON | SP |  |  | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3521 | 35.3519 | 35.3509 | 35.3502 | 35.3478 | 35.3456 | 27.7616 | 27.7601 | 27.7587 | 27.7573 | 27.7519 | 27.7455 | 27.7352 | 27.7251 | 27.7121 | 27.6983 | 27.6565 | 27.5808 | 27.4976 | 27.4155 | 26.984 | 26.9839 | 26.9838 | 26.9837 | 26.9832 | 26.9827 | 26.9819 | 26.9811 | 26.98 | 26.9787 | 26.9744 | 26.9677 | 26.9587 | 26.9501
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST | MINIMUM HEADROOM | SU 59381 02061 | YES | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 33.4261 | 31.9762 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2244 | 35.2029 | 35.1834 | 35.1651 | 35.1445 | 34.3866 | 32.5228 | 30.8213 | 29.1385 | 36.5355 | 36.5255 | 36.523 | 36.5187 | 36.5136 | 36.5078 | 36.4925 | 36.4787 | 36.4657 | 36.4511 | 36.4008 | 35.1107 | 33.4343 | 31.7762
|  | BROCKHURST | CT |  |  | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 33.5639 | 32.1143 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2244 | 35.2158 | 35.1963 | 35.1781 | 35.1574 | 34.547 | 32.6827 | 30.9813 | 29.2988 | 36.5355 | 36.5255 | 36.523 | 36.5187 | 36.5136 | 36.5078 | 36.5017 | 36.4879 | 36.4749 | 36.4602 | 36.41 | 35.2683 | 33.5919 | 31.9342
|  | BROCKHURST | LW |  |  | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 33.4261 | 31.9762 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2244 | 35.2029 | 35.1834 | 35.1651 | 35.1445 | 34.3866 | 32.5228 | 30.8213 | 29.1385 | 36.5355 | 36.5255 | 36.523 | 36.5187 | 36.5136 | 36.5078 | 36.4925 | 36.4787 | 36.4657 | 36.4511 | 36.4008 | 35.1107 | 33.4343 | 31.7762
|  | BROCKHURST | ST |  |  | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.1376 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2214 | 35.2091 | 35.1967 | 35.1825 | 35.1317 | 33.8383 | 32.7244 | 31.6471 | 36.536 | 36.5347 | 36.5249 | 36.5225 | 36.5193 | 36.5153 | 36.5056 | 36.4969 | 36.4881 | 36.4781 | 36.4434 | 36.3695 | 35.3094 | 34.2479
|  | BROCKHURST | SP |  |  | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 34.6476 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2303 | 35.2283 | 35.2092 | 35.1668 | 35.0653 | 34.5797 | 36.5365 | 36.5358 | 36.5269 | 36.5259 | 36.5244 | 36.5228 | 36.5198 | 36.5173 | 36.5145 | 36.5106 | 36.497 | 36.4669 | 36.4396 | 36.4118
MELKSHAM GSP | NORRINGTON | BROMHAM | MINIMUM HEADROOM | ST 98670 65994 | NO | 5.9257 | 5.9242 | 5.9222 | 5.918 | 5.7964 | 5.6695 | 5.5413 | 5.4085 | 5.2037 | 5.1322 | 4.901 | 4.7055 | 4.0943 | 3.8786 | 4.9749 | 4.9567 | 4.9328 | 4.8824 | 4.7497 | 4.579 | 4.4201 | 4.2566 | 4.0263 | 3.9275 | 3.6163 | 3.2897 | 2.5471 | 2.2234 | 4.9712 | 4.9503 | 4.923 | 4.8652 | 4.7307 | 4.553 | 4.3939 | 4.2305 | 4.0003 | 3.9016 | 3.5907 | 3.2645 | 2.5223 | 2.199
|  | BROMHAM | CT |  |  | 5.9261 | 5.9249 | 5.9233 | 5.9199 | 5.9048 | 5.889 | 5.8726 | 5.8553 | 5.8289 | 5.8226 | 5.8013 | 5.7145 | 5.5276 | 5.3326 | 4.9798 | 4.9651 | 4.9459 | 4.9053 | 4.854 | 4.8025 | 4.7459 | 4.6911 | 4.6275 | 4.5809 | 4.441 | 4.1575 | 3.8519 | 3.6128 | 4.9768 | 4.96 | 4.938 | 4.8914 | 4.8344 | 4.7771 | 4.7197 | 4.665 | 4.6015 | 4.5551 | 4.4156 | 4.1327 | 3.8278 | 3.5894
|  | BROMHAM | LW |  |  | 5.9257 | 5.9242 | 5.9222 | 5.918 | 5.9123 | 5.9048 | 5.8964 | 5.886 | 5.8681 | 5.8623 | 5.8398 | 5.7922 | 5.5968 | 5.4172 | 4.9749 | 4.9567 | 4.9328 | 4.8824 | 4.8318 | 4.7746 | 4.7283 | 4.6802 | 4.6251 | 4.5792 | 4.438 | 4.1938 | 3.9111 | 3.6904 | 4.9712 | 4.9503 | 4.923 | 4.8652 | 4.8074 | 4.7484 | 4.7022 | 4.6543 | 4.5992 | 4.5535 | 4.4128 | 4.1692 | 3.8871 | 3.6671
|  | BROMHAM | ST |  |  | 5.9259 | 5.9246 | 5.923 | 5.9203 | 5.7964 | 5.6695 | 5.5413 | 5.4085 | 5.2037 | 5.1322 | 4.901 | 4.7055 | 4.0943 | 3.8786 | 4.9772 | 4.9611 | 4.9423 | 4.91 | 4.7497 | 4.579 | 4.4201 | 4.2566 | 4.0263 | 3.9275 | 3.6163 | 3.2897 | 2.5471 | 2.2234 | 4.9739 | 4.9554 | 4.9338 | 4.8968 | 4.7307 | 4.553 | 4.3939 | 4.2305 | 4.0003 | 3.9016 | 3.5907 | 3.2645 | 2.5223 | 2.199
|  | BROMHAM | SP |  |  | 5.9275 | 5.9273 | 5.9272 | 5.927 | 5.9244 | 5.9216 | 5.9189 | 5.916 | 5.9118 | 5.902 | 5.8696 | 5.8504 | 5.7942 | 5.745 | 4.9959 | 4.9939 | 4.992 | 4.9902 | 4.98 | 4.9683 | 4.9567 | 4.945 | 4.9295 | 4.9105 | 4.8514 | 4.7896 | 4.6906 | 4.5957 | 4.9953 | 4.993 | 4.9909 | 4.9888 | 4.9773 | 4.9642 | 4.9512 | 4.9381 | 4.9207 | 4.9003 | 4.837 | 4.7684 | 4.6644 | 4.5696
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET | MINIMUM HEADROOM | SU 63480 52228 | YES | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6229 | 34.6156 | 34.6054 | 34.594 | 34.5812 | 34.5501 | 34.37 | 33.6239 | 32.6282 | 28.3925 | 28.3893 | 28.3852 | 28.3771 | 28.3691 | 28.3608 | 28.3526 | 28.341 | 28.3279 | 28.3134 | 28.1491 | 27.5106 | 26.7083 | 25.6994 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5328 | 31.301 | 30.1498 | 28.8958
|  | BROOK STREET | CT |  |  | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6229 | 34.6156 | 34.6054 | 34.594 | 34.5812 | 34.5501 | 34.37 | 33.6239 | 32.6282 | 28.3925 | 28.3893 | 28.3852 | 28.3771 | 28.3691 | 28.3608 | 28.3526 | 28.341 | 28.3279 | 28.3134 | 28.1491 | 27.5106 | 26.7083 | 25.6994 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5328 | 31.301 | 30.1498 | 28.8958
|  | BROOK STREET | LW |  |  | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6235 | 34.6173 | 34.6071 | 34.5957 | 34.5829 | 34.5518 | 34.376 | 33.643 | 32.6473 | 28.3926 | 28.3895 | 28.3854 | 28.3775 | 28.3696 | 28.3615 | 28.3545 | 28.3429 | 28.3299 | 28.3153 | 28.1647 | 27.5261 | 26.7239 | 25.7228 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5341 | 31.3233 | 30.1722 | 28.9199
|  | BROOK STREET | ST |  |  | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6268 | 34.6191 | 34.6103 | 34.5887 | 34.5402 | 34.3759 | 33.9969 | 28.3943 | 28.3925 | 28.3905 | 28.3872 | 28.3832 | 28.3784 | 28.3733 | 28.3652 | 28.3565 | 28.3465 | 28.3219 | 28.0574 | 27.5258 | 27.0125 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5248 | 31.3229 | 30.5863
|  | BROOK STREET | SP |  |  | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.6269 | 34.609 | 34.5816 | 34.5521 | 28.3956 | 28.3951 | 28.3945 | 28.3939 | 28.3924 | 28.3906 | 28.3887 | 28.3855 | 28.3816 | 28.3777 | 28.368 | 28.345 | 28.3138 | 28.1669 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5436 | 31.5343
MELKSHAM GSP | FROME BSP | BRUTON | MINIMUM HEADROOM | ST 69094 35148 | YES | 9.5873 | 9.573 | 9.5542 | 9.5145 | 9.4748 | 9.434 | 9.3927 | 9.3502 | 9.3024 | 9.261 | 9.1343 | 8.916 | 8.6674 | 8.4652 | 5.0841 | 5.0675 | 5.0457 | 4.9996 | 4.9537 | 4.9068 | 4.8595 | 4.811 | 4.7574 | 4.7096 | 4.5641 | 4.3145 | 4.0334 | 3.7993 | 5.0732 | 5.0604 | 5.0436 | 5.0079 | 4.9721 | 4.9353 | 4.8921 | 4.8437 | 4.7901 | 4.7424 | 4.5972 | 4.3481 | 4.0675 | 3.8338
|  | BRUTON | CT |  |  | 9.59 | 9.5776 | 9.5614 | 9.527 | 9.4932 | 9.4595 | 9.4256 | 9.3872 | 9.3472 | 9.3071 | 9.187 | 8.9658 | 8.7342 | 8.5262 | 5.0872 | 5.0728 | 5.054 | 5.0141 | 4.9749 | 4.9359 | 4.8968 | 4.8524 | 4.8065 | 4.7601 | 4.6212 | 4.3688 | 4.1046 | 3.8647 | 5.0757 | 5.0645 | 5.05 | 5.0191 | 4.9888 | 4.9584 | 4.928 | 4.885 | 4.8392 | 4.7928 | 4.6542 | 4.4022 | 4.1386 | 3.8991
|  | BRUTON | LW |  |  | 9.5873 | 9.573 | 9.5542 | 9.5145 | 9.4748 | 9.434 | 9.3927 | 9.3502 | 9.3024 | 9.261 | 9.1343 | 8.916 | 8.6674 | 8.4652 | 5.0841 | 5.0675 | 5.0457 | 4.9996 | 4.9537 | 4.9068 | 4.8595 | 4.811 | 4.7574 | 4.7096 | 4.5641 | 4.3145 | 4.0334 | 3.7993 | 5.0732 | 5.0604 | 5.0436 | 5.0079 | 4.9721 | 4.9353 | 4.8921 | 4.8437 | 4.7901 | 4.7424 | 4.5972 | 4.3481 | 4.0675 | 3.8338
|  | BRUTON | ST |  |  | 9.6018 | 9.5981 | 9.5938 | 9.5864 | 9.577 | 9.5654 | 9.5415 | 9.5174 | 9.4898 | 9.4616 | 9.3761 | 9.238 | 9.077 | 8.9365 | 5.101 | 5.0967 | 5.0917 | 5.083 | 5.0722 | 5.0589 | 5.0312 | 5.0034 | 4.9718 | 4.9392 | 4.8411 | 4.6823 | 4.5003 | 4.3389 | 5.0863 | 5.083 | 5.0791 | 5.0724 | 5.064 | 5.0536 | 5.032 | 5.0102 | 4.9852 | 4.9598 | 4.8737 | 4.7152 | 4.5335 | 4.3724
|  | BRUTON | SP |  |  | 9.6038 | 9.6023 | 9.6008 | 9.5993 | 9.5928 | 9.5853 | 9.5779 | 9.5704 | 9.5609 | 9.5501 | 9.5172 | 9.4662 | 9.4093 | 9.3551 | 5.1033 | 5.1015 | 5.0997 | 5.098 | 5.0905 | 5.0818 | 5.0731 | 5.0645 | 5.0535 | 5.041 | 5.0032 | 4.9443 | 4.8797 | 4.8183 | 5.0881 | 5.0867 | 5.0853 | 5.084 | 5.0782 | 5.0714 | 5.0648 | 5.0581 | 5.0496 | 5.0398 | 5.0101 | 4.964 | 4.912 | 4.8509
COWLEY GSP | WITNEY BSP | BURFORD | MINIMUM HEADROOM | SP 25671 12529 | NO | 7.6889 | 7.6806 | 7.6712 | 7.6659 | 7.6605 | 7.6542 | 7.6362 | 7.6182 | 7.601 | 7.5794 | 7.5129 | 7.4012 | 7.2899 | 7.1807 | 7.0091 | 7.0084 | 7.0075 | 7.0071 | 7.0066 | 7.006 | 7.0044 | 7.0028 | 7.0013 | 6.9997 | 6.9949 | 6.9868 | 6.9575 | 6.78 | 7.316 | 7.3058 | 7.2941 | 7.2876 | 7.2809 | 7.2731 | 7.2508 | 7.2284 | 7.2071 | 7.1845 | 7.1178 | 7.0058 | 6.8943 | 6.7848
|  | BURFORD | CT |  |  | 7.6889 | 7.6806 | 7.6712 | 7.6659 | 7.6605 | 7.6543 | 7.6475 | 7.6295 | 7.6123 | 7.5934 | 7.5269 | 7.4152 | 7.304 | 7.1948 | 7.0091 | 7.0084 | 7.0075 | 7.0071 | 7.0066 | 7.006 | 7.0054 | 7.0038 | 7.0023 | 7.0007 | 6.9959 | 6.9878 | 6.9798 | 6.803 | 7.316 | 7.3058 | 7.2941 | 7.2876 | 7.2809 | 7.2732 | 7.2648 | 7.2425 | 7.2212 | 7.1985 | 7.1318 | 7.0198 | 6.9084 | 6.799
|  | BURFORD | LW |  |  | 7.6889 | 7.6806 | 7.6712 | 7.6659 | 7.6605 | 7.6542 | 7.6362 | 7.6182 | 7.601 | 7.5794 | 7.5129 | 7.4012 | 7.2899 | 7.1807 | 7.0091 | 7.0084 | 7.0075 | 7.0071 | 7.0066 | 7.006 | 7.0044 | 7.0028 | 7.0013 | 6.9997 | 6.9949 | 6.9868 | 6.9575 | 6.78 | 7.316 | 7.3058 | 7.2941 | 7.2876 | 7.2809 | 7.2731 | 7.2508 | 7.2284 | 7.2071 | 7.1845 | 7.1178 | 7.0058 | 6.8943 | 6.7848
|  | BURFORD | ST |  |  | 7.6906 | 7.6846 | 7.6783 | 7.676 | 7.6728 | 7.6685 | 7.6617 | 7.6549 | 7.6431 | 7.6307 | 7.5938 | 7.519 | 7.4472 | 7.3762 | 7.0093 | 7.0087 | 7.0082 | 7.008 | 7.0077 | 7.0073 | 7.0067 | 7.0061 | 7.005 | 7.0039 | 7.0007 | 6.9953 | 6.9901 | 6.985 | 7.3181 | 7.3108 | 7.303 | 7.3 | 7.2961 | 7.2908 | 7.2824 | 7.2739 | 7.2594 | 7.2439 | 7.1989 | 7.1239 | 7.052 | 6.9808
|  | BURFORD | SP |  |  | 7.6925 | 7.6888 | 7.6854 | 7.6852 | 7.6843 | 7.6829 | 7.6806 | 7.6782 | 7.6755 | 7.6707 | 7.6567 | 7.6336 | 7.6123 | 7.591 | 7.0094 | 7.0091 | 7.0088 | 7.0088 | 7.0087 | 7.0086 | 7.0084 | 7.0082 | 7.0079 | 7.0075 | 7.0062 | 7.0042 | 7.0023 | 7.0005 | 7.3205 | 7.3159 | 7.3117 | 7.3115 | 7.3103 | 7.3087 | 7.3057 | 7.3028 | 7.2995 | 7.2935 | 7.2761 | 7.2476 | 7.2211 | 7.196
MANNINGTON GSP | WAREHAM | BUSHEY | MINIMUM HEADROOM | SY 97671 83532 | YES | 5.0016 | 4.9975 | 4.9921 | 4.9806 | 4.9694 | 4.9582 | 4.9386 | 4.9191 | 4.8998 | 4.8789 | 4.8172 | 4.7159 | 4.6114 | 4.5085 | 4.8467 | 4.8419 | 4.8355 | 4.822 | 4.8088 | 4.7957 | 4.7727 | 4.7498 | 4.7271 | 4.7026 | 4.6302 | 4.5112 | 4.3885 | 4.2678 | 4.8466 | 4.8418 | 4.8354 | 4.8219 | 4.8088 | 4.7957 | 4.7726 | 4.7497 | 4.727 | 4.7025 | 4.6301 | 4.5111 | 4.3883 | 4.2675
|  | BUSHEY | CT |  |  | 5.0016 | 4.9975 | 4.9921 | 4.9806 | 4.9694 | 4.9582 | 4.9471 | 4.9277 | 4.9083 | 4.8875 | 4.8258 | 4.7244 | 4.6199 | 4.517 | 4.8467 | 4.8419 | 4.8355 | 4.822 | 4.8088 | 4.7957 | 4.7827 | 4.7599 | 4.7372 | 4.7127 | 4.6403 | 4.5212 | 4.3985 | 4.2777 | 4.8466 | 4.8418 | 4.8354 | 4.8219 | 4.8088 | 4.7957 | 4.7827 | 4.7598 | 4.7371 | 4.7126 | 4.6402 | 4.5211 | 4.3983 | 4.2774
|  | BUSHEY | LW |  |  | 5.0016 | 4.9975 | 4.9921 | 4.9806 | 4.9694 | 4.9582 | 4.9386 | 4.9191 | 4.8998 | 4.8789 | 4.8172 | 4.7159 | 4.6114 | 4.5085 | 4.8467 | 4.8419 | 4.8355 | 4.822 | 4.8088 | 4.7957 | 4.7727 | 4.7498 | 4.7271 | 4.7026 | 4.6302 | 4.5112 | 4.3885 | 4.2678 | 4.8466 | 4.8418 | 4.8354 | 4.8219 | 4.8088 | 4.7957 | 4.7726 | 4.7497 | 4.727 | 4.7025 | 4.6301 | 4.5111 | 4.3883 | 4.2675
|  | BUSHEY | ST |  |  | 5.0037 | 5.0011 | 4.9981 | 4.9929 | 4.9866 | 4.9789 | 4.9687 | 4.9586 | 4.9454 | 4.9312 | 4.8898 | 4.8225 | 4.7554 | 4.6885 | 4.8491 | 4.8461 | 4.8426 | 4.8365 | 4.829 | 4.82 | 4.808 | 4.7962 | 4.7807 | 4.764 | 4.7154 | 4.6364 | 4.5576 | 4.479 | 4.849 | 4.8461 | 4.8425 | 4.8364 | 4.829 | 4.82 | 4.808 | 4.7961 | 4.7807 | 4.7639 | 4.7153 | 4.6363 | 4.5574 | 4.4789
|  | BUSHEY | SP |  |  | 5.1313 | 5.006 | 5.0056 | 5.0053 | 5.0035 | 5.0015 | 4.9983 | 4.9951 | 4.9909 | 4.9855 | 4.9696 | 4.9444 | 4.9203 | 4.8978 | 4.999 | 4.8519 | 4.8514 | 4.851 | 4.8489 | 4.8465 | 4.8428 | 4.8391 | 4.8341 | 4.8277 | 4.8092 | 4.7795 | 4.7513 | 4.7247 | 4.999 | 4.8518 | 4.8514 | 4.8509 | 4.8489 | 4.8465 | 4.8427 | 4.839 | 4.8341 | 4.8277 | 4.8091 | 4.7794 | 4.7512 | 4.7247
FAWLEY GSP | LANGLEY BSP | BUTTS ASH | MINIMUM HEADROOM | SU 41923 05772 | NO | 34.0969 | 34.0969 | 34.0969 | 34.0969 | 34.0963 | 34.0951 | 34.0932 | 34.0907 | 34.0855 | 34.0846 | 34.08 | 34.0688 | 34.0471 | 33.3319 | 32.4407 | 32.4407 | 32.4407 | 32.4407 | 32.4402 | 32.439 | 32.4371 | 32.4345 | 32.4293 | 32.4284 | 32.4238 | 31.4156 | 30.1897 | 29.0023 | 33.5008 | 33.5008 | 33.5008 | 33.5008 | 33.5002 | 33.499 | 33.4971 | 33.4945 | 33.4893 | 33.4884 | 33.4839 | 33.4727 | 32.4769 | 31.2688
|  | BUTTS ASH | CT |  |  | 34.0969 | 34.0969 | 34.0969 | 34.0969 | 34.0967 | 34.0964 | 34.0959 | 34.0952 | 34.0936 | 34.0933 | 34.0918 | 34.0794 | 34.0656 | 33.6273 | 32.4407 | 32.4407 | 32.4407 | 32.4407 | 32.4406 | 32.4402 | 32.4398 | 32.439 | 32.4375 | 32.4372 | 32.4357 | 31.7438 | 30.5261 | 29.3365 | 33.5008 | 33.5008 | 33.5008 | 33.5008 | 33.5006 | 33.5003 | 33.4998 | 33.4991 | 33.4975 | 33.4972 | 33.4957 | 33.4833 | 32.8138 | 31.6086
|  | BUTTS ASH | LW |  |  | 34.0969 | 34.0969 | 34.0969 | 34.0969 | 34.0963 | 34.0951 | 34.0932 | 34.0907 | 34.0855 | 34.0846 | 34.08 | 34.0688 | 34.0471 | 33.3319 | 32.4407 | 32.4407 | 32.4407 | 32.4407 | 32.4402 | 32.439 | 32.4371 | 32.4345 | 32.4293 | 32.4284 | 32.4238 | 31.4156 | 30.1897 | 29.0023 | 33.5008 | 33.5008 | 33.5008 | 33.5008 | 33.5002 | 33.499 | 33.4971 | 33.4945 | 33.4893 | 33.4884 | 33.4839 | 33.4727 | 32.4769 | 31.2688
|  | BUTTS ASH | ST |  |  | 34.0969 | 34.0969 | 34.0969 | 34.0969 | 34.0968 | 34.0965 | 34.0961 | 34.0956 | 34.0944 | 34.0938 | 34.0907 | 34.0866 | 34.0722 | 34.067 | 32.4407 | 32.4407 | 32.4407 | 32.4407 | 32.4406 | 32.4404 | 32.44 | 32.4395 | 32.4383 | 32.4377 | 32.4346 | 32.4087 | 31.6201 | 30.8445 | 33.5008 | 33.5008 | 33.5008 | 33.5008 | 33.5006 | 33.5004 | 33.5 | 33.4995 | 33.4983 | 33.4977 | 33.4946 | 33.4905 | 33.4761 | 33.1183
|  | BUTTS ASH | SP |  |  | 34.0969 | 34.0969 | 34.0969 | 34.0969 | 34.0969 | 34.0969 | 34.0968 | 34.0968 | 34.0968 | 34.0966 | 34.0954 | 34.0946 | 34.0903 | 34.0861 | 32.4407 | 32.4407 | 32.4407 | 32.4407 | 32.4407 | 32.4407 | 32.4407 | 32.4407 | 32.4406 | 32.4404 | 32.4393 | 32.4384 | 32.4341 | 32.4299 | 33.5008 | 33.5008 | 33.5008 | 33.5008 | 33.5008 | 33.5008 | 33.5007 | 33.5007 | 33.5007 | 33.5005 | 33.4993 | 33.4984 | 33.4942 | 33.49
MELKSHAM GSP | CHIPPENHAM | CALNE | MINIMUM HEADROOM | SU 00521 72497 | YES | 26.0546 | 26.0113 | 25.9632 | 25.8653 | 25.7696 | 25.6729 | 25.5196 | 25.368 | 25.2184 | 25.0574 | 24.5822 | 23.8002 | 22.9984 | 22.2103 | 20.9368 | 20.9339 | 20.9307 | 20.9241 | 20.9178 | 20.9113 | 20.9011 | 20.891 | 20.881 | 20.8703 | 20.6362 | 19.5619 | 18.4607 | 17.3781 | 19.0917 | 19.0883 | 19.0845 | 19.0768 | 19.0692 | 19.0616 | 19.0495 | 19.0375 | 19.0257 | 19.013 | 18.9755 | 17.9757 | 16.946 | 15.9147
|  | CALNE | CT |  |  | 26.0622 | 26.0244 | 25.9835 | 25.9007 | 25.8197 | 25.7376 | 25.6564 | 25.505 | 25.3554 | 25.1944 | 24.7193 | 23.937 | 23.1355 | 22.3477 | 20.9373 | 20.9347 | 20.932 | 20.9265 | 20.9211 | 20.9156 | 20.9102 | 20.9001 | 20.8902 | 20.8794 | 20.8244 | 19.7498 | 18.649 | 17.5668 | 19.0923 | 19.0893 | 19.0861 | 19.0796 | 19.0732 | 19.0667 | 19.0603 | 19.0483 | 19.0365 | 19.0238 | 18.9863 | 18.1514 | 17.122 | 16.1041
|  | CALNE | LW |  |  | 26.0546 | 26.0113 | 25.9632 | 25.8653 | 25.7696 | 25.6729 | 25.5196 | 25.368 | 25.2184 | 25.0574 | 24.5822 | 23.8002 | 22.9984 | 22.2103 | 20.9368 | 20.9339 | 20.9307 | 20.9241 | 20.9178 | 20.9113 | 20.9011 | 20.891 | 20.881 | 20.8703 | 20.6362 | 19.5619 | 18.4607 | 17.3781 | 19.0917 | 19.0883 | 19.0845 | 19.0768 | 19.0692 | 19.0616 | 19.0495 | 19.0375 | 19.0257 | 19.013 | 18.9755 | 17.9757 | 16.946 | 15.9147
|  | CALNE | ST |  |  | 26.0634 | 26.0281 | 25.9923 | 25.9332 | 25.8601 | 25.7711 | 25.6711 | 25.5727 | 25.4704 | 25.3605 | 25.04 | 24.5193 | 24.0029 | 23.4901 | 20.9373 | 20.935 | 20.9326 | 20.9287 | 20.9238 | 20.9179 | 20.9112 | 20.9047 | 20.8978 | 20.8905 | 20.8692 | 20.5498 | 19.8404 | 19.1361 | 19.0924 | 19.0896 | 19.0868 | 19.0821 | 19.0764 | 19.0693 | 19.0614 | 19.0537 | 19.0456 | 19.0369 | 19.0116 | 18.8993 | 18.2361 | 17.5775
|  | CALNE | SP |  |  | 26.0989 | 26.0908 | 26.0863 | 26.0829 | 26.0631 | 26.0397 | 26.0046 | 25.9698 | 25.9243 | 25.8649 | 25.6875 | 25.4646 | 25.1975 | 24.9539 | 20.9397 | 20.9392 | 20.9389 | 20.9386 | 20.9337 | 20.9286 | 20.9227 | 20.9168 | 20.9082 | 20.8885 | 20.8271 | 20.7886 | 20.6963 | 20.6178 | 19.0952 | 19.0946 | 19.0942 | 19.0939 | 19.0888 | 19.0835 | 19.0772 | 19.0709 | 19.0618 | 19.0416 | 18.9786 | 18.9377 | 18.8431 | 18.7625
BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY | MINIMUM HEADROOM | SU 86584 59452 | YES | 91.2198 | 91.205 | 91.1902 | 90.2869 | 90.2129 | 90.1388 | 90.0648 | 89.9907 | 89.9167 | 89.8871 | 89.7982 | 89.2334 | 88.8157 | 88.6094 | 88.4454 | 88.4157 | 88.3867 | 87.4302 | 87.2426 | 87.0497 | 86.8866 | 86.7235 | 86.5605 | 86.4359 | 86.0411 | 84.3256 | 82.2593 | 80.4063 | 88.6656 | 88.6508 | 88.636 | 87.7304 | 87.6353 | 87.5403 | 87.4541 | 87.3679 | 87.2817 | 87.2392 | 87.1102 | 86.4685 | 84.9613 | 83.1617
|  | CAMBERLEY | CT |  |  | 91.2909 | 91.282 | 91.2731 | 90.7311 | 90.6305 | 90.5289 | 90.4264 | 90.3212 | 90.1833 | 90.1536 | 90.0622 | 89.2334 | 88.8157 | 88.6094 | 88.5184 | 88.4961 | 88.4748 | 87.9071 | 87.7107 | 87.5104 | 87.2927 | 87.0986 | 86.8717 | 86.7471 | 86.3612 | 84.3256 | 82.2593 | 80.4063 | 88.7367 | 88.7278 | 88.7189 | 88.177 | 88.0623 | 87.9424 | 87.8218 | 87.7045 | 87.5544 | 87.5118 | 87.3803 | 86.4685 | 84.9613 | 83.1617
|  | CAMBERLEY | LW |  |  | 91.2198 | 91.205 | 91.1902 | 90.2869 | 90.2129 | 90.1388 | 90.0648 | 89.9907 | 89.9167 | 89.8871 | 89.7982 | 89.6501 | 89.5613 | 89.3984 | 88.4454 | 88.4157 | 88.3867 | 87.4302 | 87.2426 | 87.0497 | 86.8866 | 86.7235 | 86.5605 | 86.4359 | 86.0411 | 84.6381 | 82.9006 | 81.0906 | 88.6656 | 88.6508 | 88.636 | 87.7304 | 87.6353 | 87.5403 | 87.4541 | 87.3679 | 87.2817 | 87.2392 | 87.1102 | 86.8792 | 85.606 | 83.8494
|  | CAMBERLEY | ST |  |  | 91.3264 | 91.3205 | 91.3146 | 90.9533 | 90.9236 | 90.894 | 90.8644 | 90.8348 | 90.8052 | 90.7933 | 90.7578 | 90.6986 | 90.663 | 90.5979 | 88.5594 | 88.5482 | 88.5321 | 88.1604 | 88.118 | 88.073 | 87.9995 | 87.9144 | 87.8402 | 87.7806 | 87.5649 | 87.091 | 86.2999 | 85.1983 | 88.7723 | 88.7663 | 88.7604 | 88.3991 | 88.3695 | 88.3399 | 88.3064 | 88.2665 | 88.2286 | 88.2079 | 88.1451 | 88.0293 | 87.931 | 87.8043
|  | CAMBERLEY | SP |  |  | 91.362 | 91.359 | 91.356 | 91.1754 | 91.157 | 91.1387 | 91.1204 | 91.102 | 91.0816 | 91.0601 | 90.9931 | 90.94 | 90.8484 | 90.754 | 88.5997 | 88.5954 | 88.5912 | 88.4093 | 88.3859 | 88.3618 | 88.3386 | 88.3155 | 88.289 | 88.2629 | 88.1813 | 88.046 | 87.8108 | 87.5275 | 88.8078 | 88.8048 | 88.8019 | 88.6212 | 88.6028 | 88.5845 | 88.5662 | 88.5478 | 88.5274 | 88.506 | 88.4389 | 88.3766 | 88.2584 | 88.1368
WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 73.4682 | 73.4314 | 73.4268 | 73.4173 | 73.3955 | 73.3647 | 73.3382 | 73.3109 | 73.2709 | 73.2554 | 73.2053 | 73.1457 | 72.9976 | 72.8448 | 74.2646 | 74.1685 | 74.1563 | 74.1314 | 74.1071 | 74.0673 | 74.0357 | 74.0031 | 73.9588 | 73.9387 | 73.873 | 73.7576 | 73.5354 | 73.3834 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5522 | 74.5293 | 74.506 | 74.4819 | 74.4446 | 74.432 | 74.3884 | 74.3367 | 74.1739 | 74.0377
|  | CANAL BANK 11kV | CT |  |  | 73.4691 | 73.4329 | 73.429 | 73.4212 | 73.4135 | 73.4058 | 73.3981 | 73.3942 | 73.3902 | 73.386 | 73.3719 | 73.3329 | 73.2829 | 73.2323 | 74.2668 | 74.1723 | 74.1622 | 74.1418 | 74.1217 | 74.1015 | 74.0813 | 74.0711 | 74.0607 | 74.0498 | 74.0129 | 73.8626 | 73.6675 | 73.4701 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747
|  | CANAL BANK 11kV | LW |  |  | 73.4682 | 73.4314 | 73.4268 | 73.4173 | 73.4079 | 73.3986 | 73.3947 | 73.3908 | 73.3868 | 73.3827 | 73.3685 | 73.3296 | 73.2795 | 73.2289 | 74.2646 | 74.1685 | 74.1563 | 74.1314 | 74.1071 | 74.0826 | 74.0725 | 74.0623 | 74.0519 | 74.041 | 74.0016 | 73.8495 | 73.6544 | 73.457 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5747
|  | CANAL BANK 11kV | ST |  |  | 73.4692 | 73.4665 | 73.43 | 73.4246 | 73.3955 | 73.3647 | 73.3382 | 73.3109 | 73.2709 | 73.2554 | 73.2053 | 73.1457 | 73.0195 | 72.9605 | 74.2671 | 74.26 | 74.1647 | 74.1506 | 74.1109 | 74.0673 | 74.0357 | 74.0031 | 73.9588 | 73.9387 | 73.873 | 73.7576 | 73.5354 | 73.3834 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5522 | 74.5293 | 74.506 | 74.4819 | 74.4446 | 74.432 | 74.3916 | 74.3591 | 74.2661 | 74.2391
|  | CANAL BANK 11kV | SP |  |  | 73.4721 | 73.4716 | 73.4378 | 73.4374 | 73.4278 | 73.4181 | 73.4092 | 73.4002 | 73.3865 | 73.3512 | 73.2389 | 73.1759 | 72.9976 | 72.8448 | 74.2747 | 74.2734 | 74.1852 | 74.1839 | 74.1717 | 74.1589 | 74.1481 | 74.1372 | 74.1212 | 74.0842 | 73.9658 | 73.8847 | 73.6813 | 73.5016 | 74.5747 | 74.5747 | 74.5747 | 74.5747 | 74.5668 | 74.5591 | 74.5513 | 74.5434 | 74.5311 | 74.4969 | 74.3884 | 74.3367 | 74.1739 | 74.0377
WILLESDEN GSP | ACTON LANE | CANAL BANK 6.6kV | MINIMUM HEADROOM | TQ 20927 83082 | YES | 30.7107 | 30.7107 | 39.7107 | 39.7107 | 39.7082 | 39.7056 | 39.7031 | 39.7004 | 39.6962 | 39.6948 | 39.69 | 39.6842 | 39.6662 | 39.651 | 24.7991 | 24.7991 | 37.5991 | 37.5991 | 37.5966 | 37.594 | 37.5914 | 37.5887 | 37.5846 | 37.5832 | 37.5784 | 37.5695 | 37.5396 | 37.5128 | 30.4855 | 30.4823 | 39.4819 | 39.481 | 39.4786 | 39.4753 | 39.4725 | 39.4695 | 39.4651 | 39.4635 | 39.4581 | 39.4521 | 39.4348 | 39.3861
|  | CANAL BANK 6.6kV | CT |  |  | 30.7107 | 30.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 24.7991 | 24.7991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5767 | 37.5473 | 37.517 | 30.4856 | 30.4824 | 39.4821 | 39.4814 | 39.4807 | 39.48 | 39.4793 | 39.479 | 39.4786 | 39.4782 | 39.477 | 39.4735 | 39.4496 | 39.3907
|  | CANAL BANK 6.6kV | LW |  |  | 30.7107 | 30.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 39.7107 | 24.7991 | 24.7991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5991 | 37.5977 | 37.5748 | 37.5453 | 37.5128 | 30.4855 | 30.4823 | 39.4819 | 39.481 | 39.4802 | 39.4794 | 39.479 | 39.4787 | 39.4783 | 39.4779 | 39.4767 | 39.4732 | 39.4462 | 39.3861
|  | CANAL BANK 6.6kV | ST |  |  | 30.7107 | 30.7107 | 39.7107 | 39.7107 | 39.7082 | 39.7056 | 39.7031 | 39.7004 | 39.6962 | 39.6948 | 39.6903 | 39.6867 | 39.6764 | 39.6734 | 24.7991 | 24.7991 | 37.5991 | 37.5991 | 37.5966 | 37.594 | 37.5914 | 37.5887 | 37.5846 | 37.5832 | 37.5787 | 37.5695 | 37.5396 | 37.5178 | 30.4856 | 30.4854 | 39.4821 | 39.4817 | 39.4786 | 39.4753 | 39.4725 | 39.4695 | 39.4651 | 39.4635 | 39.4581 | 39.4521 | 39.4388 | 39.4259
|  | CANAL BANK 6.6kV | SP |  |  | 30.7107 | 30.7107 | 39.7107 | 39.7107 | 39.7098 | 39.709 | 39.7081 | 39.7072 | 39.7058 | 39.702 | 39.69 | 39.6842 | 39.6662 | 39.651 | 24.7991 | 24.7991 | 37.5991 | 37.5991 | 37.5982 | 37.5973 | 37.5965 | 37.5956 | 37.5942 | 37.5904 | 37.5784 | 37.5726 | 37.5545 | 37.5394 | 30.4859 | 30.4858 | 39.4828 | 39.4828 | 39.4818 | 39.4807 | 39.4798 | 39.4788 | 39.4773 | 39.4734 | 39.461 | 39.4543 | 39.4348 | 39.4182
COWLEY GSP | WITNEY BSP | CARTERTON | MINIMUM HEADROOM | SP 28261 07823 | NO | 36.463 | 36.4602 | 36.4568 | 36.4523 | 36.3821 | 36.3082 | 36.2341 | 36.1578 | 36.0438 | 36.0243 | 35.9595 | 35.8539 | 35.6259 | 35.5845 | 35.2283 | 35.2262 | 35.2236 | 35.2202 | 35.1514 | 35.0792 | 35.0062 | 34.9309 | 34.8178 | 34.7994 | 34.7377 | 34.639 | 34.4188 | 34.2005 | 35.1355 | 35.1042 | 35.0648 | 35.0133 | 34.8881 | 34.7412 | 34.6232 | 34.5071 | 34.3513 | 34.2879 | 34.0914 | 33.7001 | 33.1485 | 32.7643
|  | CARTERTON | CT |  |  | 36.463 | 36.4602 | 36.4568 | 36.4523 | 36.447 | 36.44 | 36.4374 | 36.4336 | 36.4296 | 36.4254 | 36.4127 | 36.3853 | 36.3542 | 36.3243 | 35.2283 | 35.2262 | 35.2236 | 35.2202 | 35.2163 | 35.211 | 35.2091 | 35.2062 | 35.2032 | 35.2001 | 35.1906 | 35.17 | 35.1467 | 34.9603 | 35.1355 | 35.1043 | 35.0649 | 35.0134 | 34.953 | 34.873 | 34.844 | 34.8003 | 34.7546 | 34.7065 | 34.5622 | 34.249 | 33.8943 | 33.5242
|  | CARTERTON | LW |  |  | 36.463 | 36.4602 | 36.4568 | 36.4523 | 36.3821 | 36.3082 | 36.2341 | 36.1578 | 36.0438 | 36.0243 | 35.9595 | 35.8539 | 35.6259 | 35.5845 | 35.2283 | 35.2262 | 35.2236 | 35.2202 | 35.1514 | 35.0792 | 35.0062 | 34.9309 | 34.8178 | 34.7994 | 34.7377 | 34.639 | 34.4188 | 34.2005 | 35.1355 | 35.1042 | 35.0648 | 35.0133 | 34.8881 | 34.7412 | 34.6232 | 34.5071 | 34.3513 | 34.2879 | 34.0914 | 33.7001 | 33.1485 | 32.7643
|  | CARTERTON | ST |  |  | 36.4633 | 36.4613 | 36.4589 | 36.4561 | 36.4527 | 36.448 | 36.4457 | 36.4437 | 36.441 | 36.4381 | 36.4293 | 36.4103 | 36.3897 | 36.3707 | 35.2285 | 35.227 | 35.2252 | 35.2231 | 35.2205 | 35.217 | 35.2153 | 35.2138 | 35.2118 | 35.2096 | 35.203 | 35.1887 | 35.1733 | 35.159 | 35.1396 | 35.1166 | 35.0896 | 35.0574 | 35.018 | 34.9644 | 34.9384 | 34.9152 | 34.8844 | 34.8514 | 34.7516 | 34.5338 | 34.2996 | 34.0822
|  | CARTERTON | SP |  |  | 36.4637 | 36.4623 | 36.4609 | 36.4594 | 36.4577 | 36.4555 | 36.4548 | 36.4542 | 36.4534 | 36.4523 | 36.4489 | 36.441 | 36.4317 | 36.4223 | 35.2288 | 35.2278 | 35.2267 | 35.2256 | 35.2243 | 35.2227 | 35.2221 | 35.2217 | 35.2211 | 35.2203 | 35.2177 | 35.2118 | 35.2048 | 35.1977 | 35.1438 | 35.1281 | 35.1118 | 35.0947 | 35.0751 | 35.0505 | 35.042 | 35.035 | 35.0268 | 35.014 | 34.9749 | 34.8852 | 34.7784 | 34.6711
AXMINSTER | YEOVIL BSP | CASTLE CARY | MINIMUM HEADROOM | ST 64534 31039 | YES | 14.86 | 14.8545 | 14.8491 | 14.8409 | 14.8318 | 14.8211 | 14.7894 | 14.7592 | 14.7285 | 14.699 | 14.611 | 14.4633 | 14.3045 | 14.1666 | 13.6362 | 13.6251 | 13.6142 | 13.5978 | 13.5795 | 13.5579 | 13.495 | 13.4355 | 13.3771 | 13.3187 | 13.1455 | 12.8577 | 12.5579 | 12.2824 | 13.7718 | 13.7598 | 13.7481 | 13.7305 | 13.7109 | 13.6877 | 13.6201 | 13.5564 | 13.494 | 13.4312 | 13.2455 | 12.9372 | 12.6167 | 12.321
|  | CASTLE CARY | CT |  |  | 14.86 | 14.8545 | 14.8491 | 14.8409 | 14.8318 | 14.8211 | 14.8104 | 14.7806 | 14.7505 | 14.7212 | 14.6347 | 14.4769 | 14.3113 | 14.1666 | 13.6362 | 13.6251 | 13.6142 | 13.5978 | 13.5795 | 13.5579 | 13.5365 | 13.4775 | 13.4197 | 13.3614 | 13.1898 | 12.8918 | 12.5854 | 12.303 | 13.7718 | 13.7598 | 13.7481 | 13.7305 | 13.7109 | 13.6877 | 13.6646 | 13.6014 | 13.5396 | 13.477 | 13.2929 | 12.9743 | 12.6472 | 12.3446
|  | CASTLE CARY | LW |  |  | 14.86 | 14.8545 | 14.8491 | 14.8409 | 14.8318 | 14.8211 | 14.7894 | 14.7592 | 14.7285 | 14.699 | 14.611 | 14.4633 | 14.3045 | 14.1667 | 13.6362 | 13.6251 | 13.6142 | 13.5978 | 13.5795 | 13.5579 | 13.495 | 13.4355 | 13.3771 | 13.3187 | 13.1455 | 12.8577 | 12.5579 | 12.2824 | 13.7718 | 13.7598 | 13.7481 | 13.7305 | 13.7109 | 13.6877 | 13.6201 | 13.5564 | 13.494 | 13.4312 | 13.2455 | 12.9372 | 12.6167 | 12.321
|  | CASTLE CARY | ST |  |  | 14.9257 | 14.8585 | 14.8551 | 14.8508 | 14.8428 | 14.8329 | 14.8134 | 14.7951 | 14.7712 | 14.7497 | 14.6863 | 14.5875 | 14.4759 | 14.3803 | 13.7683 | 13.6332 | 13.6263 | 13.6177 | 13.6041 | 13.5868 | 13.5505 | 13.5168 | 13.4741 | 13.4328 | 13.3118 | 13.1194 | 12.9168 | 12.7316 | 13.9136 | 13.7685 | 13.7611 | 13.7519 | 13.7375 | 13.7191 | 13.6804 | 13.6444 | 13.5989 | 13.5547 | 13.4252 | 13.219 | 13.0032 | 12.8048
|  | CASTLE CARY | SP |  |  | 14.9281 | 14.926 | 14.8612 | 14.8599 | 14.8578 | 14.855 | 14.8493 | 14.8443 | 14.8384 | 14.8307 | 14.8078 | 14.7719 | 14.7369 | 14.7042 | 13.7732 | 13.7688 | 13.6386 | 13.636 | 13.6317 | 13.6261 | 13.6147 | 13.6047 | 13.5929 | 13.5774 | 13.5322 | 13.4606 | 13.3924 | 13.3283 | 13.9188 | 13.9142 | 13.7743 | 13.7716 | 13.7669 | 13.7609 | 13.7486 | 13.7379 | 13.7252 | 13.7086 | 13.6602 | 13.5833 | 13.5102 | 13.4416
LALEHAM | STAINES | CAUSEWAY | MINIMUM HEADROOM | TQ 02763 71680 | NO | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.8923 | 60.8796 | 60.8668 | 60.8539 | 60.8336 | 60.7774 | 60.5989 | 60.5139 | 59.8553 | 58.409 | 58.8369 | 58.7789 | 58.6709 | 58.5276 | 58.3859 | 58.1861 | 57.9039 | 57.5978 | 57.3802 | 57.1647 | 56.5118 | 55.0679 | 53.3453 | 51.6222 | 59.0051 | 58.9575 | 58.8689 | 58.7514 | 58.6195 | 58.4264 | 58.1618 | 57.8748 | 57.6707 | 57.4686 | 56.8563 | 55.4736 | 53.7408 | 51.9973
|  | CAUSEWAY | CT |  |  | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 59.9746 | 58.5286 | 58.847 | 58.7964 | 58.6982 | 58.5754 | 58.4537 | 58.279 | 58.0459 | 57.7398 | 57.5223 | 57.3066 | 56.6539 | 55.2098 | 53.4875 | 51.7646 | 59.0134 | 58.9718 | 58.8913 | 58.7905 | 58.6869 | 58.5135 | 58.295 | 58.0079 | 57.804 | 57.6017 | 56.9896 | 55.6152 | 53.8847 | 52.1414
|  | CAUSEWAY | LW |  |  | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 59.8553 | 58.409 | 58.8369 | 58.7789 | 58.6709 | 58.5276 | 58.3859 | 58.1861 | 57.9039 | 57.5978 | 57.3802 | 57.1647 | 56.5118 | 55.0679 | 53.3453 | 51.6222 | 59.0051 | 58.9575 | 58.8689 | 58.7514 | 58.6195 | 58.4264 | 58.1618 | 57.8748 | 57.6707 | 57.4686 | 56.8563 | 55.4736 | 53.7408 | 51.9973
|  | CAUSEWAY | ST |  |  | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.8963 | 60.8873 | 60.878 | 60.8684 | 60.8536 | 60.8486 | 60.8326 | 60.8197 | 60.7736 | 60.285 | 58.8523 | 58.8081 | 58.7336 | 58.6531 | 58.5453 | 58.3834 | 58.1838 | 57.9616 | 57.7991 | 57.6468 | 57.1841 | 56.1757 | 54.9967 | 53.885 | 59.0177 | 58.9814 | 58.9203 | 58.8543 | 58.7643 | 58.6169 | 58.4226 | 58.2136 | 58.0603 | 57.9172 | 57.4823 | 56.5359 | 55.4023 | 54.2887
|  | CAUSEWAY | SP |  |  | 60.9052 | 60.9052 | 60.9052 | 60.9052 | 60.8923 | 60.8796 | 60.8668 | 60.8539 | 60.8336 | 60.7774 | 60.5989 | 60.5139 | 60.2463 | 60.0225 | 58.8948 | 58.8841 | 58.8585 | 58.8498 | 58.811 | 58.7517 | 58.6688 | 58.5813 | 58.5 | 58.3897 | 58.0477 | 57.5638 | 56.7929 | 56.0448 | 59.0526 | 59.0438 | 59.0229 | 59.0156 | 58.9815 | 58.9306 | 58.8603 | 58.7862 | 58.7158 | 58.6153 | 58.2814 | 57.8185 | 57.0789 | 56.3634
BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM | MINIMUM HEADROOM | SU 71512 75747 | YES | 34.0234 | 34.0234 | 34.0234 | 34.0077 | 33.9669 | 33.9264 | 33.8897 | 33.8754 | 33.7876 | 33.6019 | 33.0295 | 31.8708 | 30.541 | 29.2145 | 32.8733 | 32.861 | 32.8449 | 32.8111 | 32.7782 | 32.4239 | 31.901 | 31.6962 | 31.4921 | 31.2738 | 30.6013 | 29.2397 | 27.677 | 26.1183 | 33.0017 | 32.9894 | 32.9732 | 32.9393 | 32.9063 | 32.3717 | 31.8843 | 31.6815 | 31.4793 | 31.2631 | 30.5969 | 29.2483 | 27.7004 | 26.1564
|  | CAVERSHAM | CT |  |  | 34.0234 | 34.0234 | 34.0234 | 34.0092 | 33.9691 | 33.9292 | 33.8897 | 33.8754 | 33.7876 | 33.6019 | 33.0295 | 31.8708 | 30.541 | 29.2145 | 32.8736 | 32.8615 | 32.8456 | 32.8123 | 32.78 | 32.464 | 31.901 | 31.6962 | 31.4921 | 31.2738 | 30.6013 | 29.2397 | 27.677 | 26.1183 | 33.002 | 32.9898 | 32.9739 | 32.9405 | 32.9081 | 32.409 | 31.8843 | 31.6815 | 31.4793 | 31.2631 | 30.5969 | 29.2483 | 27.7004 | 26.1564
|  | CAVERSHAM | LW |  |  | 34.0234 | 34.0234 | 34.0234 | 34.0077 | 33.9669 | 33.9264 | 33.912 | 33.8977 | 33.8833 | 33.868 | 33.2998 | 32.1416 | 30.8115 | 29.4847 | 32.8733 | 32.861 | 32.8449 | 32.8111 | 32.7782 | 32.4239 | 32.2187 | 32.0141 | 31.8099 | 31.5916 | 30.9189 | 29.5579 | 27.9949 | 26.4358 | 33.0017 | 32.9894 | 32.9732 | 32.9393 | 32.9063 | 32.3717 | 32.1807 | 31.9903 | 31.7941 | 31.5779 | 30.9115 | 29.5634 | 28.0152 | 26.4709
|  | CAVERSHAM | ST |  |  | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0044 | 33.9917 | 33.9791 | 33.9693 | 33.9589 | 33.9267 | 33.796 | 32.927 | 32.0753 | 32.8797 | 32.8722 | 32.8635 | 32.8486 | 32.8304 | 32.8085 | 32.7982 | 32.7881 | 32.7802 | 32.7717 | 32.4284 | 31.502 | 30.4808 | 29.48 | 33.0081 | 33.0006 | 32.9919 | 32.977 | 32.9587 | 32.9367 | 32.9264 | 32.9162 | 32.9083 | 32.8017 | 32.3759 | 31.4891 | 30.4776 | 29.4862
|  | CAVERSHAM | SP |  |  | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 34.0234 | 33.9955 | 33.9649 | 32.8874 | 32.886 | 32.8847 | 32.8834 | 32.878 | 32.8715 | 32.8679 | 32.8643 | 32.8598 | 32.8565 | 32.8464 | 32.8256 | 32.8013 | 32.7766 | 33.0159 | 33.0145 | 33.0132 | 33.0119 | 33.0064 | 32.9999 | 32.9963 | 32.9927 | 32.9881 | 32.9848 | 32.9747 | 32.9538 | 32.9295 | 32.8812
MANNINGTON GSP | BOURNEMOUTH | CENTRAL | MINIMUM HEADROOM | SZ 10293 91931 | YES | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.3929 | 38.6018 | 37.341 | 36.3484 | 36.344 | 36.3383 | 36.3265 | 36.3143 | 36.3021 | 36.2927 | 36.2827 | 36.2725 | 36.2615 | 36.2282 | 36.1559 | 34.9823 | 33.5399 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.798 | 36.0834 | 34.5954
|  | CENTRAL | CT |  |  | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.4061 | 38.7618 | 37.501 | 36.3497 | 36.3463 | 36.3417 | 36.3325 | 36.3229 | 36.3131 | 36.3033 | 36.2933 | 36.2831 | 36.2721 | 36.2389 | 36.1665 | 35.1653 | 33.723 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8087 | 36.2722 | 34.7842
|  | CENTRAL | LW |  |  | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.3929 | 38.6018 | 37.341 | 36.3484 | 36.344 | 36.3383 | 36.3265 | 36.3143 | 36.3021 | 36.2927 | 36.2827 | 36.2725 | 36.2615 | 36.2282 | 36.1559 | 34.9823 | 33.5399 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.798 | 36.0834 | 34.5954
|  | CENTRAL | ST |  |  | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.4095 | 39.2563 | 36.3523 | 36.3508 | 36.349 | 36.3462 | 36.3423 | 36.3377 | 36.3245 | 36.3111 | 36.3042 | 36.2967 | 36.274 | 36.2241 | 36.1692 | 35.731 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8114 | 36.7579
|  | CENTRAL | SP |  |  | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 39.449 | 36.353 | 36.3524 | 36.3517 | 36.351 | 36.3485 | 36.3456 | 36.3411 | 36.3364 | 36.3306 | 36.3277 | 36.3189 | 36.2988 | 36.2746 | 36.2493 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411 | 36.8411
NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE | MINIMUM HEADROOM | SU 42591 11255 | YES | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.5773 | 46.531 | 46.4827 | 46.4327 | 46.3566 | 46.3461 | 46.31 | 45.6014 | 44.4702 | 43.44 | 44.3648 | 44.3478 | 44.3263 | 44.2097 | 44.0162 | 43.7582 | 43.5976 | 43.4259 | 43.2328 | 43.1073 | 42.7097 | 41.7174 | 40.5241 | 39.3406 | 45.1083 | 45.0038 | 44.8719 | 44.7356 | 44.5788 | 44.418 | 44.2984 | 44.1186 | 43.9176 | 43.7844 | 43.3627 | 42.3075 | 41.0412 | 39.8765
|  | CENTRAL BRIDGE | CT |  |  | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.0533 | 45.0261 | 44.0038 | 44.3663 | 44.3504 | 44.3303 | 44.2475 | 44.1657 | 43.9958 | 43.8281 | 43.7064 | 43.5893 | 43.4743 | 43.1129 | 42.1745 | 41.0851 | 39.9197 | 45.1175 | 45.0198 | 44.8967 | 44.7789 | 44.6851 | 44.5883 | 44.4976 | 44.4051 | 44.2802 | 44.1575 | 43.7719 | 42.7706 | 41.6084 | 40.4516
|  | CENTRAL BRIDGE | LW |  |  | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.5773 | 46.531 | 46.4827 | 46.4327 | 46.3566 | 46.3461 | 46.31 | 45.6014 | 44.4702 | 43.44 | 44.3648 | 44.3478 | 44.3263 | 44.2097 | 44.0162 | 43.7582 | 43.5976 | 43.4259 | 43.2328 | 43.1073 | 42.7097 | 41.7174 | 40.5241 | 39.3406 | 45.1083 | 45.0038 | 44.8719 | 44.7356 | 44.5788 | 44.418 | 44.2984 | 44.1186 | 43.9176 | 43.7844 | 43.3627 | 42.3075 | 41.0412 | 39.8765
|  | CENTRAL BRIDGE | ST |  |  | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.2317 | 45.5847 | 44.3691 | 44.3575 | 44.344 | 44.3333 | 44.3146 | 44.2541 | 44.2058 | 44.1515 | 44.0727 | 43.9942 | 43.7437 | 43.0853 | 42.3637 | 41.6776 | 45.135 | 45.0638 | 44.9809 | 44.9149 | 44.856 | 44.7865 | 44.731 | 44.6725 | 44.6299 | 44.5875 | 44.445 | 43.7425 | 42.9725 | 42.2405
|  | CENTRAL BRIDGE | SP |  |  | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 46.6221 | 44.3727 | 44.3656 | 44.3583 | 44.3546 | 44.3507 | 44.3464 | 44.3429 | 44.3393 | 44.3352 | 44.3325 | 44.3161 | 44.1869 | 43.879 | 43.5195 | 45.1569 | 45.1133 | 45.0684 | 45.0457 | 45.0219 | 44.9954 | 44.974 | 44.9518 | 44.9266 | 44.9102 | 44.8576 | 44.7093 | 44.5251 | 44.2058
CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS | MINIMUM HEADROOM | ST 66140 01039 | YES | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.2076 | 2.2068 | 2.2058 | 2.2037 | 2.2016 | 2.1996 | 2.1868 | 2.1742 | 2.1617 | 2.1482 | 2.1083 | 2.041 | 1.9706 | 1.9012 | 2.3105 | 2.3098 | 2.3089 | 2.3069 | 2.305 | 2.3031 | 2.2913 | 2.2797 | 2.2681 | 2.2557 | 2.2188 | 2.1566 | 2.0916 | 2.0275
|  | CERNE ABBAS | CT |  |  | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.2076 | 2.2068 | 2.2058 | 2.2037 | 2.2016 | 2.1996 | 2.1975 | 2.1849 | 2.1724 | 2.1589 | 2.119 | 2.0517 | 1.9813 | 1.9119 | 2.3105 | 2.3098 | 2.3089 | 2.3069 | 2.305 | 2.3031 | 2.3012 | 2.2895 | 2.278 | 2.2655 | 2.2287 | 2.1665 | 2.1014 | 2.0373
|  | CERNE ABBAS | LW |  |  | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.2076 | 2.2068 | 2.2058 | 2.2037 | 2.2016 | 2.1996 | 2.1868 | 2.1742 | 2.1617 | 2.1482 | 2.1083 | 2.041 | 1.9706 | 1.9012 | 2.3105 | 2.3098 | 2.3089 | 2.3069 | 2.305 | 2.3031 | 2.2913 | 2.2797 | 2.2681 | 2.2557 | 2.2188 | 2.1566 | 2.0916 | 2.0275
|  | CERNE ABBAS | ST |  |  | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.2079 | 2.2075 | 2.2069 | 2.2059 | 2.2048 | 2.2033 | 2.1966 | 2.19 | 2.1814 | 2.1722 | 2.1453 | 2.1004 | 2.055 | 2.01 | 2.3108 | 2.3104 | 2.3099 | 2.309 | 2.3079 | 2.3066 | 2.3004 | 2.2942 | 2.2863 | 2.2779 | 2.2529 | 2.2115 | 2.1695 | 2.128
|  | CERNE ABBAS | SP |  |  | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.6147 | 2.2084 | 2.2083 | 2.2083 | 2.2082 | 2.2078 | 2.2074 | 2.2052 | 2.2031 | 2.2003 | 2.1968 | 2.1864 | 2.1692 | 2.1523 | 2.1363 | 2.3113 | 2.3112 | 2.3111 | 2.311 | 2.3107 | 2.3104 | 2.3083 | 2.3064 | 2.3038 | 2.3005 | 2.2909 | 2.275 | 2.2595 | 2.2447
IVER 132KV | CHALVEY BSP | CHALVEY | MINIMUM HEADROOM | SU 96669 79364 | YES | 93.4965 | 93.4853 | 93.4741 | 92.7912 | 92.7267 | 92.6621 | 92.597 | 92.5316 | 92.4301 | 92.3609 | 92.1728 | 91.8566 | 91.1141 | 88.6614 | 90.5884 | 90.5285 | 90.4544 | 89.673 | 89.5046 | 89.3308 | 89.1461 | 88.953 | 88.7475 | 88.4727 | 87.5643 | 85.1921 | 82.4198 | 79.5397 | 91.2652 | 91.2238 | 91.1736 | 90.4295 | 90.3005 | 90.1681 | 90.0287 | 89.8841 | 89.6548 | 89.0855 | 87.6243 | 85.0227 | 82.1119 | 79.2335
|  | CHALVEY | CT |  |  | 93.5502 | 93.5435 | 93.5368 | 93.127 | 93.0934 | 93.0598 | 93.0263 | 92.9927 | 92.9403 | 92.882 | 92.7276 | 92.0436 | 91.3283 | 88.9019 | 90.6434 | 90.589 | 90.5206 | 90.015 | 89.88 | 89.7399 | 89.6126 | 89.4514 | 89.2826 | 89.0572 | 88.2023 | 85.5273 | 82.6761 | 79.8073 | 91.3198 | 91.2834 | 91.2384 | 90.7692 | 90.6726 | 90.5729 | 90.4811 | 90.3683 | 90.2508 | 89.7454 | 88.3178 | 85.3686 | 82.3703 | 79.4941
|  | CHALVEY | LW |  |  | 93.4965 | 93.4853 | 93.4741 | 92.7912 | 92.7267 | 92.6621 | 92.597 | 92.5316 | 92.4301 | 92.3609 | 92.1728 | 91.8566 | 91.1141 | 88.6614 | 90.5884 | 90.5285 | 90.4544 | 89.673 | 89.5046 | 89.3308 | 89.1461 | 88.953 | 88.7475 | 88.4727 | 87.5643 | 85.1921 | 82.4198 | 79.5397 | 91.2652 | 91.2238 | 91.1736 | 90.4295 | 90.3005 | 90.1681 | 90.0287 | 89.8841 | 89.6548 | 89.0855 | 87.6243 | 85.0227 | 82.1119 | 79.2335
|  | CHALVEY | ST |  |  | 93.5771 | 93.5726 | 93.5681 | 93.2949 | 93.2285 | 93.1613 | 93.0931 | 93.0235 | 92.928 | 92.8943 | 92.7647 | 92.5231 | 92.1722 | 91.9395 | 90.6891 | 90.6553 | 90.6159 | 90.2987 | 90.1792 | 90.0507 | 89.9044 | 89.7514 | 89.5645 | 89.4386 | 89.0976 | 88.1441 | 86.6358 | 84.8726 | 91.3583 | 91.3356 | 91.3095 | 91.009 | 90.9096 | 90.8043 | 90.6876 | 90.5663 | 90.414 | 90.323 | 90.0602 | 88.357 | 86.5116 | 84.6739
|  | CHALVEY | SP |  |  | 93.6039 | 93.6017 | 93.5995 | 93.4629 | 93.4517 | 93.4405 | 93.4293 | 93.4181 | 93.4069 | 93.4024 | 93.389 | 93.3666 | 93.3532 | 93.3045 | 90.727 | 90.7078 | 90.6877 | 90.5338 | 90.4975 | 90.4591 | 90.4187 | 90.3769 | 90.3284 | 90.2878 | 90.1828 | 90.0027 | 89.8236 | 89.6365 | 91.392 | 91.3793 | 91.3659 | 91.2186 | 91.1918 | 91.1638 | 91.1344 | 91.1042 | 91.0698 | 91.043 | 90.9726 | 90.8523 | 90.7361 | 90.5982
NURSLING GSP | VELMORE BSP | CHANDLERSFORD | MINIMUM HEADROOM | SU 43494 21552 | YES | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2001 | 34.1955 | 34.17 | 34.1551 | 34.1402 | 34.1246 | 34.0755 | 33.5247 | 32.0029 | 30.4836 | 13.146 | 13.1403 | 13.1327 | 13.1167 | 13.1008 | 13.0844 | 13.0682 | 13.0588 | 13.0494 | 12.8643 | 12.1629 | 10.6497 | 8.8629 | 7.0792 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8793 | 13.876 | 13.8727 | 13.7253 | 13.5281 | 13.3204 | 12.6702 | 11.2673 | 9.6109 | 7.9572
|  | CHANDLERSFORD | CT |  |  | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.1955 | 34.17 | 34.1551 | 34.1402 | 34.1246 | 34.0755 | 33.5247 | 32.0029 | 30.4836 | 13.146 | 13.1403 | 13.1327 | 13.1167 | 13.1008 | 13.0844 | 13.0682 | 13.0588 | 13.0494 | 12.8643 | 12.1629 | 10.6497 | 8.8629 | 7.0792 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.7253 | 13.5281 | 13.3204 | 12.6702 | 11.2673 | 9.6109 | 7.9572
|  | CHANDLERSFORD | LW |  |  | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.194 | 34.1791 | 34.1635 | 34.1144 | 33.9987 | 32.4768 | 30.9567 | 13.1482 | 13.144 | 13.1386 | 13.1269 | 13.1153 | 13.1031 | 13.0929 | 13.0835 | 13.074 | 13.0641 | 12.7193 | 11.2062 | 9.4193 | 7.6347 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8363 | 13.186 | 11.7832 | 10.1267 | 8.4722
|  | CHANDLERSFORD | ST |  |  | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.1729 | 34.1004 | 34.0185 | 33.147 | 13.1566 | 13.1471 | 13.1437 | 13.1379 | 13.1306 | 13.1216 | 13.1128 | 13.1045 | 13.0981 | 13.0913 | 13.0701 | 12.5193 | 11.3475 | 10.2062 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.0006 | 11.9143 | 10.8562
|  | CHANDLERSFORD | SP |  |  | 34.2035 | 34.2035 | 34.2035 | 34.2035 | 34.2001 | 34.1969 | 34.1936 | 34.1902 | 34.185 | 34.1705 | 34.1246 | 34.1027 | 34.0267 | 33.9323 | 13.1595 | 13.1523 | 13.1517 | 13.1511 | 13.1456 | 13.1398 | 13.1334 | 13.1273 | 13.1185 | 13.1014 | 13.0472 | 13.0068 | 12.9153 | 12.8343 | 13.8826 | 13.8826 | 13.8826 | 13.8826 | 13.8793 | 13.876 | 13.8727 | 13.8694 | 13.8642 | 13.8497 | 13.8037 | 13.7818 | 13.7129 | 13.5589
NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL | MINIMUM HEADROOM | SU 42849 11983 | YES | 19.411 | 19.411 | 19.411 | 19.411 | 19.3654 | 19.3191 | 19.2721 | 19.223 | 19.1472 | 19.1376 | 19.1068 | 18.9644 | 18.781 | 17.8911 | 14.1004 | 14.0985 | 14.096 | 14.092 | 14.0437 | 13.9952 | 13.9458 | 13.8932 | 13.8138 | 13.8006 | 13.6946 | 12.8703 | 11.7027 | 10.6654 | 14.176 | 14.176 | 14.176 | 14.176 | 14.1305 | 14.0842 | 14.0371 | 13.988 | 13.9122 | 13.9026 | 13.8718 | 13.5154 | 12.2979 | 11.2134
|  | CHAPEL | CT |  |  | 19.411 | 19.411 | 19.411 | 19.411 | 19.3654 | 19.3191 | 19.2721 | 19.223 | 19.1472 | 19.1376 | 19.1068 | 18.9644 | 18.781 | 17.8911 | 14.1004 | 14.0985 | 14.096 | 14.092 | 14.0437 | 13.9952 | 13.9458 | 13.8932 | 13.8138 | 13.8006 | 13.6946 | 12.8703 | 11.7027 | 10.6654 | 14.176 | 14.176 | 14.176 | 14.176 | 14.1305 | 14.0842 | 14.0371 | 13.988 | 13.9122 | 13.9026 | 13.8718 | 13.5154 | 12.2979 | 11.2134
|  | CHAPEL | LW |  |  | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 18.5454 | 14.1004 | 14.0985 | 14.096 | 14.092 | 14.0892 | 14.087 | 14.0838 | 14.0803 | 14.0766 | 14.073 | 13.9813 | 13.2967 | 12.3126 | 11.3166 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 13.9408 | 12.9069 | 11.8645
|  | CHAPEL | ST |  |  | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 14.1008 | 14.0994 | 14.0978 | 14.0954 | 14.0937 | 14.0922 | 14.0906 | 14.0888 | 14.0863 | 14.0839 | 14.0754 | 13.7823 | 13.1859 | 12.5593 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 13.8243 | 13.166
|  | CHAPEL | SP |  |  | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 19.411 | 14.1013 | 14.1005 | 14.0996 | 14.0985 | 14.0978 | 14.0973 | 14.0967 | 14.096 | 14.0952 | 14.0943 | 14.091 | 14.0804 | 14.0657 | 13.779 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176 | 14.176
COWLEY GSP | YARNTON BSP | CHARLBURY | MINIMUM HEADROOM | SP 36034 18376 | NO | 14.5201 | 14.4922 | 14.4556 | 14.3783 | 14.3033 | 14.2291 | 14.1555 | 14.0816 | 14.0083 | 13.9293 | 13.6962 | 13.3117 | 12.9149 | 12.5248 | 7.7502 | 7.7176 | 7.6748 | 7.5844 | 7.4968 | 7.4099 | 7.3235 | 7.2365 | 7.1503 | 7.0573 | 6.783 | 6.3305 | 5.8637 | 5.4046 | 9.2736 | 9.2486 | 9.2157 | 9.1437 | 9.0622 | 8.9814 | 8.9013 | 8.8208 | 8.7411 | 8.6551 | 8.4014 | 7.9802 | 7.5264 | 7.0803
|  | CHARLBURY | CT |  |  | 14.5201 | 14.4922 | 14.4556 | 14.3783 | 14.3033 | 14.2291 | 14.1555 | 14.0816 | 14.0083 | 13.9293 | 13.6962 | 13.3117 | 12.9149 | 12.5248 | 7.7502 | 7.7176 | 7.6748 | 7.5844 | 7.4968 | 7.4099 | 7.3235 | 7.2365 | 7.1503 | 7.0573 | 6.783 | 6.3305 | 5.8637 | 5.4046 | 9.2736 | 9.2486 | 9.2157 | 9.1437 | 9.0622 | 8.9814 | 8.9013 | 8.8208 | 8.7411 | 8.6551 | 8.4014 | 7.9802 | 7.5264 | 7.0803
|  | CHARLBURY | LW |  |  | 14.5297 | 14.5089 | 14.4816 | 14.4239 | 14.3679 | 14.3123 | 14.2376 | 14.1636 | 14.0903 | 14.0113 | 13.7781 | 13.3939 | 12.9969 | 12.6066 | 7.7615 | 7.7372 | 7.7053 | 7.6377 | 7.5722 | 7.5073 | 7.42 | 7.333 | 7.2468 | 7.1538 | 6.8793 | 6.4273 | 5.9602 | 5.5009 | 9.2823 | 9.2636 | 9.2391 | 9.1873 | 9.1324 | 9.072 | 8.9907 | 8.9101 | 8.8304 | 8.7444 | 8.4905 | 8.0723 | 7.6202 | 7.1739
|  | CHARLBURY | ST |  |  | 14.5546 | 14.5519 | 14.5486 | 14.5431 | 14.5363 | 14.5281 | 14.4799 | 14.4321 | 14.382 | 14.3281 | 14.1708 | 13.9153 | 13.6597 | 13.4055 | 7.7906 | 7.7874 | 7.7836 | 7.7772 | 7.7692 | 7.7596 | 7.7032 | 7.6474 | 7.5888 | 7.5258 | 7.3414 | 7.0407 | 6.74 | 6.4409 | 9.3046 | 9.3021 | 9.2992 | 9.2943 | 9.2882 | 9.2808 | 9.2375 | 9.1947 | 9.1479 | 9.0892 | 8.9179 | 8.6398 | 8.3616 | 8.085
|  | CHARLBURY | SP |  |  | 14.5557 | 14.5543 | 14.5531 | 14.5518 | 14.5459 | 14.5389 | 14.5219 | 14.505 | 14.4833 | 14.4609 | 14.3953 | 14.2962 | 14.1962 | 14.1027 | 7.7919 | 7.7903 | 7.7888 | 7.7874 | 7.7805 | 7.7724 | 7.7525 | 7.7329 | 7.7075 | 7.6816 | 7.6057 | 7.4902 | 7.3744 | 7.2653 | 9.3055 | 9.3043 | 9.3032 | 9.3021 | 9.2967 | 9.2904 | 9.2751 | 9.26 | 9.2404 | 9.2201 | 9.1609 | 9.0554 | 8.9471 | 8.8458
CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER | MINIMUM HEADROOM | SY 67309 93186 | YES | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.6244 | 16.3663 | 13.7325 | 13.2344 | 12.8125 | 16.0054 | 15.9768 | 15.9405 | 15.9021 | 15.8743 | 15.8278 | 15.7099 | 15.5884 | 15.2488 | 14.8508 | 13.2292 | 10.1115 | 9.5219 | 9.0226 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.5436 | 17.1613 | 15.6037 | 12.6091 | 12.0427 | 11.5631
|  | CHARMINSTER | CT |  |  | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.6766 | 16.4283 | 13.7941 | 13.2963 | 12.8745 | 16.0055 | 15.9771 | 15.9409 | 15.9028 | 15.8754 | 15.8292 | 15.7828 | 15.6616 | 15.322 | 14.924 | 13.3026 | 10.1845 | 9.5952 | 9.0959 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.2316 | 15.6742 | 12.6791 | 12.1132 | 11.6336
|  | CHARMINSTER | LW |  |  | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.6244 | 16.3663 | 13.7325 | 13.2344 | 12.8125 | 16.0054 | 15.9768 | 15.9405 | 15.9021 | 15.8743 | 15.8278 | 15.7099 | 15.5884 | 15.2488 | 14.8508 | 13.2292 | 10.1115 | 9.5219 | 9.0226 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.5436 | 17.1613 | 15.6037 | 12.6091 | 12.0427 | 11.5631
|  | CHARMINSTER | ST |  |  | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.0969 | 15.2234 | 14.8997 | 14.625 | 16.0162 | 15.9958 | 15.972 | 15.9517 | 15.9352 | 15.9031 | 15.8379 | 15.7705 | 15.5425 | 15.2694 | 14.1113 | 11.8763 | 11.4932 | 11.168 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 16.451 | 14.3042 | 13.9362 | 13.6239
|  | CHARMINSTER | SP |  |  | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.8398 | 17.2515 | 17.1473 | 17.0681 | 16.0279 | 16.0164 | 16.0045 | 15.9987 | 15.9939 | 15.9823 | 15.959 | 15.9352 | 15.8482 | 15.7399 | 15.2796 | 14.328 | 14.182 | 14.071 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 17.551 | 16.6591 | 16.5189 | 16.4122
LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER | MINIMUM HEADROOM | SU 92198 07420 | NO | 18.8106 | 18.4919 | 18.3619 | 18.1466 | 17.9043 | 17.6253 | 17.2289 | 16.7839 | 16.3913 | 16.0292 | 15.0357 | 13.891 | 12.8762 | 11.9548 | 13.9506 | 13.5614 | 13.4026 | 13.1395 | 12.8582 | 12.5318 | 12.0627 | 11.5361 | 11.0722 | 10.6435 | 9.4676 | 8.1141 | 6.9171 | 5.8259 | 15.3583 | 15.0109 | 14.8691 | 14.6344 | 14.3832 | 14.0975 | 13.6916 | 13.177 | 12.7221 | 12.3017 | 11.1488 | 9.7971 | 8.5959 | 7.5007
|  | CHICHESTER | CT |  |  | 18.8152 | 18.4998 | 18.3741 | 18.1679 | 17.9371 | 17.6685 | 17.3813 | 16.9388 | 16.5509 | 16.1895 | 15.2004 | 14.0537 | 13.0498 | 12.1254 | 13.9563 | 13.5711 | 13.4175 | 13.1657 | 12.8958 | 12.5828 | 12.2426 | 11.7185 | 11.2594 | 10.8312 | 9.6598 | 8.3043 | 7.1183 | 6.0242 | 15.3633 | 15.0195 | 14.8825 | 14.6577 | 14.4168 | 14.1418 | 13.8476 | 13.3559 | 12.9058 | 12.486 | 11.3376 | 9.9879 | 8.7977 | 7.6997
|  | CHICHESTER | LW |  |  | 18.8106 | 18.4919 | 18.3619 | 18.1466 | 17.9043 | 17.6253 | 17.2289 | 16.7839 | 16.3913 | 16.0292 | 15.0357 | 13.891 | 12.8762 | 11.9548 | 13.9506 | 13.5614 | 13.4026 | 13.1395 | 12.8582 | 12.5318 | 12.0627 | 11.5361 | 11.0722 | 10.6435 | 9.4676 | 8.1141 | 6.9171 | 5.8259 | 15.3583 | 15.0109 | 14.8691 | 14.6344 | 14.3832 | 14.0975 | 13.6916 | 13.177 | 12.7221 | 12.3017 | 11.1488 | 9.7971 | 8.5959 | 7.5007
|  | CHICHESTER | ST |  |  | 18.8236 | 18.7457 | 18.4303 | 18.2874 | 18.1221 | 17.9118 | 17.6541 | 17.3645 | 17.1028 | 16.8549 | 16.1657 | 15.3935 | 14.7371 | 14.1326 | 13.9665 | 13.8714 | 13.4861 | 13.3116 | 13.1097 | 12.8668 | 12.5657 | 12.2228 | 11.913 | 11.6194 | 10.8037 | 9.8898 | 9.1157 | 8.4008 | 15.3724 | 15.2875 | 14.9437 | 14.7879 | 14.6077 | 14.3909 | 14.1269 | 13.8304 | 13.5466 | 13.2588 | 12.459 | 11.5629 | 10.8023 | 10.0848
|  | CHICHESTER | SP |  |  | 18.8621 | 18.8206 | 18.6256 | 18.5673 | 18.5007 | 18.427 | 18.3317 | 18.2276 | 18.1307 | 18.0303 | 17.7434 | 17.4352 | 17.1681 | 16.9346 | 14.0136 | 13.9629 | 13.7246 | 13.6535 | 13.5724 | 13.4826 | 13.3665 | 13.2396 | 13.1216 | 13.0044 | 12.677 | 12.3134 | 12.0026 | 11.7308 | 15.4144 | 15.3692 | 15.1566 | 15.0931 | 15.0206 | 14.9403 | 14.8366 | 14.7232 | 14.6177 | 14.5125 | 14.2192 | 13.9037 | 13.6309 | 13.3662
CHICKERELL GSP | CHICKERELL BSP | CHICKERELL | MINIMUM HEADROOM | SY 65479 80511 | YES | 14.8579 | 14.809 | 3.5462 | 2.766 | 2.6551 | 2.5351 | 2.3458 | 2.1449 | 1.9483 | 1.7899 | 1.2868 | 0.37338 | -0.36195 | -1.1034 | 14.7399 | 14.6832 | 3.4098 | 2.615 | 2.4934 | 2.361 | 2.1451 | 1.9156 | 1.692 | 1.5059 | 0.91437 | -0.16059 | -1.0263 | -1.8947 | 14.7384 | 14.6855 | 3.4172 | 2.6294 | 2.513 | 2.3866 | 2.1835 | 1.9677 | 1.7572 | 1.5843 | 1.0354 | 0.038252 | -0.76468 | -1.5719
|  | CHICKERELL | CT |  |  | 14.9138 | 14.8695 | 3.6114 | 3.1152 | 3.0283 | 2.9331 | 2.8315 | 2.6573 | 2.4903 | 2.3422 | 1.8725 | 0.5638 | -0.26739 | -1.0135 | 14.7958 | 14.7437 | 3.475 | 2.9642 | 2.8666 | 2.759 | 2.6437 | 2.4408 | 2.2469 | 2.071 | 1.513 | 0.042708 | -0.91884 | -1.7919 | 14.7943 | 14.746 | 3.4824 | 2.9787 | 2.8862 | 2.7846 | 2.6759 | 2.4868 | 2.3058 | 2.1433 | 1.6278 | 0.23535 | -0.66343 | -1.4754
|  | CHICKERELL | LW |  |  | 14.8579 | 14.809 | 3.5462 | 2.766 | 2.6551 | 2.5351 | 2.3458 | 2.1449 | 1.9483 | 1.7899 | 1.2868 | 0.37338 | -0.36195 | -1.1034 | 14.7399 | 14.6832 | 3.4098 | 2.615 | 2.4934 | 2.361 | 2.1451 | 1.9156 | 1.692 | 1.5059 | 0.91437 | -0.16059 | -1.0263 | -1.8947 | 14.7384 | 14.6855 | 3.4172 | 2.6294 | 2.513 | 2.3866 | 2.1835 | 1.9677 | 1.7572 | 1.5843 | 1.0354 | 0.038252 | -0.76468 | -1.5719
|  | CHICKERELL | ST |  |  | 14.9472 | 14.9156 | 14.8765 | 14.55 | 3.294 | 3.2301 | 3.1328 | 3.0283 | 2.9153 | 2.8136 | 2.4853 | 1.8918 | 1.4291 | 0.97615 | 14.8303 | 14.7931 | 14.7468 | 14.4116 | 3.1488 | 3.0765 | 2.9639 | 2.8428 | 2.7116 | 2.5909 | 2.2013 | 1.4957 | 0.94785 | 0.41329 | 14.8284 | 14.7938 | 14.751 | 14.42 | 3.1605 | 3.0922 | 2.987 | 2.8739 | 2.7514 | 2.6398 | 2.2798 | 1.6282 | 1.1213 | 0.62604
|  | CHICKERELL | SP |  |  | 14.9815 | 14.9619 | 14.9398 | 14.7771 | 14.7509 | 14.7226 | 14.6864 | 3.4481 | 3.4094 | 3.3685 | 3.237 | 2.9939 | 2.803 | 2.6036 | 14.8659 | 14.8428 | 14.8165 | 14.6495 | 14.6204 | 14.5886 | 14.5473 | 3.3034 | 3.2591 | 3.2108 | 3.0553 | 2.7667 | 2.5406 | 2.3067 | 14.8633 | 14.8419 | 14.8176 | 14.6526 | 14.625 | 14.5949 | 14.556 | 3.3148 | 3.2731 | 3.2284 | 3.0845 | 2.8178 | 2.6087 | 2.3914
AXMINSTER | YEOVIL BSP | CHILTON CANTELLO | MINIMUM HEADROOM | ST 57910 21616 | YES | 11.462 | 11.3019 | 11.2714 | 11.2272 | 11.1415 | 11.0429 | 10.9374 | 10.7848 | 10.6068 | 10.4846 | 10.2235 | 9.7646 | 9.3174 | 8.989 | 5.3992 | 5.2041 | 5.169 | 5.1195 | 5.0295 | 4.9275 | 4.8169 | 4.6597 | 4.4753 | 4.3472 | 4.074 | 3.5979 | 3.1348 | 2.7914 | 5.781 | 5.5603 | 5.5207 | 5.4648 | 5.3671 | 5.256 | 5.1293 | 4.9623 | 4.7611 | 4.6172 | 4.3115 | 3.7897 | 3.2841 | 2.901
|  | CHILTON CANTELLO | CT |  |  | 11.462 | 11.3019 | 11.2714 | 11.2272 | 11.1415 | 11.0429 | 10.9374 | 10.7848 | 10.6068 | 10.4846 | 10.2235 | 9.7646 | 9.3174 | 8.989 | 5.3992 | 5.2041 | 5.169 | 5.1195 | 5.0295 | 4.9275 | 4.8182 | 4.6597 | 4.4753 | 4.3472 | 4.074 | 3.5979 | 3.1348 | 2.7914 | 5.781 | 5.5603 | 5.5207 | 5.4648 | 5.3671 | 5.256 | 5.1369 | 4.9623 | 4.7611 | 4.6172 | 4.3115 | 3.7897 | 3.2841 | 2.901
|  | CHILTON CANTELLO | LW |  |  | 11.462 | 11.3019 | 11.2714 | 11.2272 | 11.1581 | 11.0751 | 10.9384 | 10.8 | 10.6424 | 10.5223 | 10.2643 | 9.8898 | 9.5035 | 9.2079 | 5.3992 | 5.2041 | 5.169 | 5.1195 | 5.0461 | 4.9597 | 4.8169 | 4.6725 | 4.5086 | 4.3825 | 4.1123 | 3.7207 | 3.3185 | 3.008 | 5.781 | 5.5603 | 5.5207 | 5.4648 | 5.3837 | 5.2883 | 5.1293 | 4.9688 | 4.7881 | 4.6463 | 4.3436 | 3.9063 | 3.4616 | 3.1113
|  | CHILTON CANTELLO | ST |  |  | 11.4655 | 11.4487 | 11.2918 | 11.2641 | 11.23 | 11.187 | 11.1199 | 11.0527 | 10.9676 | 10.8876 | 10.7181 | 10.4842 | 10.252 | 10.0517 | 5.4035 | 5.383 | 5.1918 | 5.1609 | 5.1227 | 5.0757 | 5.0052 | 4.9346 | 4.8453 | 4.7612 | 4.5833 | 4.3378 | 4.0953 | 3.8853 | 5.7858 | 5.7627 | 5.5465 | 5.5115 | 5.4684 | 5.4154 | 5.3357 | 5.2561 | 5.1554 | 5.0605 | 4.8603 | 4.5839 | 4.3139 | 4.078
|  | CHILTON CANTELLO | SP |  |  | 11.469 | 11.4577 | 11.3086 | 11.2952 | 11.2785 | 11.2596 | 11.2345 | 11.2108 | 11.1831 | 11.1516 | 11.0855 | 10.9962 | 10.9119 | 10.8362 | 5.4078 | 5.394 | 5.2123 | 5.1959 | 5.177 | 5.1558 | 5.1278 | 5.1012 | 5.0716 | 5.0385 | 4.9691 | 4.8753 | 4.7872 | 4.7081 | 5.7907 | 5.7751 | 5.5696 | 5.5511 | 5.5297 | 5.5057 | 5.4741 | 5.4441 | 5.4106 | 5.3732 | 5.2951 | 5.1893 | 5.0909 | 5.0027
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM | MINIMUM HEADROOM | SU 65105 55805 | YES | 34.1067 | 34.1067 | 34.1067 | 34.1067 | 34.0229 | 33.9354 | 33.8431 | 33.7464 | 33.5974 | 33.5765 | 33.5025 | 33.3462 | 33.0863 | 33.0222 | 32.8566 | 32.8266 | 32.7793 | 32.6858 | 32.5186 | 32.3465 | 32.2053 | 32.0608 | 31.8641 | 31.7957 | 31.5844 | 31.236 | 30.5495 | 29.8162 | 33.1336 | 33.1336 | 33.1336 | 33.1336 | 33.0498 | 32.9623 | 32.8176 | 32.5739 | 32.278 | 32.1111 | 31.615 | 30.7876 | 29.8568 | 29.1468
|  | CHINEHAM | CT |  |  | 34.1067 | 34.1067 | 34.1067 | 34.1067 | 34.1064 | 34.1059 | 34.1052 | 34.104 | 34.1015 | 34.1011 | 34.0987 | 34.0396 | 33.9652 | 33.908 | 32.8608 | 32.8337 | 32.7903 | 32.7049 | 32.6293 | 32.5521 | 32.4636 | 32.4147 | 32.3645 | 32.3165 | 32.1769 | 31.9265 | 31.4174 | 30.6913 | 33.1336 | 33.1336 | 33.1336 | 33.1336 | 33.1333 | 33.1328 | 33.0683 | 32.9202 | 32.7709 | 32.6243 | 32.1999 | 31.4704 | 30.7251 | 30.0222
|  | CHINEHAM | LW |  |  | 34.1067 | 34.1067 | 34.1067 | 34.1067 | 34.0229 | 33.9354 | 33.8431 | 33.7464 | 33.5974 | 33.5765 | 33.5025 | 33.3462 | 33.0863 | 33.0222 | 32.8566 | 32.8266 | 32.7793 | 32.6858 | 32.5186 | 32.3465 | 32.2053 | 32.0608 | 31.8641 | 31.7957 | 31.5844 | 31.236 | 30.5495 | 29.8162 | 33.1336 | 33.1336 | 33.1336 | 33.1336 | 33.0498 | 32.9623 | 32.8176 | 32.5739 | 32.278 | 32.1111 | 31.615 | 30.7876 | 29.8568 | 29.1468
|  | CHINEHAM | ST |  |  | 34.1067 | 34.1067 | 34.1067 | 34.1067 | 34.1065 | 34.1061 | 34.1056 | 34.1047 | 34.1028 | 34.1019 | 34.0969 | 34.0904 | 34.0677 | 34.0469 | 32.9767 | 32.8533 | 32.8261 | 32.7816 | 32.7346 | 32.6779 | 32.6476 | 32.6224 | 32.5987 | 32.576 | 32.5087 | 32.358 | 32.1831 | 32.0282 | 33.1336 | 33.1336 | 33.1336 | 33.1336 | 33.1334 | 33.133 | 33.1324 | 33.1316 | 33.1297 | 33.1287 | 33.1238 | 32.7739 | 32.2834 | 31.824
|  | CHINEHAM | SP |  |  | 34.1067 | 34.1067 | 34.1067 | 34.1067 | 34.1067 | 34.1067 | 34.1067 | 34.1066 | 34.1066 | 34.1063 | 34.1045 | 34.103 | 34.0963 | 34.0896 | 32.994 | 32.9897 | 32.8766 | 32.8668 | 32.851 | 32.8325 | 32.8212 | 32.8122 | 32.8012 | 32.7925 | 32.7665 | 32.7249 | 32.6793 | 32.6366 | 33.1336 | 33.1336 | 33.1336 | 33.1336 | 33.1336 | 33.1336 | 33.1336 | 33.1335 | 33.1334 | 33.1331 | 33.1313 | 33.1299 | 33.1231 | 33.1165
COWLEY GSP | YARNTON BSP | CHIPPING NORTON | MINIMUM HEADROOM | SP 31382 26792 | NO | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.6566 | 19.5746 | 19.4889 | 19.4001 | 19.2652 | 19.2465 | 19.1824 | 18.8173 | 18.1664 | 17.7326 | 18.6568 | 18.6553 | 18.6526 | 18.6488 | 18.565 | 18.4781 | 18.3767 | 18.1099 | 17.7966 | 17.6106 | 17.1585 | 16.4913 | 15.741 | 15.2134 | 18.8747 | 18.8727 | 18.8693 | 18.8644 | 18.7795 | 18.6913 | 18.5956 | 18.3632 | 18.0491 | 17.8624 | 17.4085 | 16.7388 | 15.9799 | 15.436
|  | CHIPPING NORTON | CT |  |  | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7302 | 19.7242 | 19.7181 | 19.7117 | 19.7018 | 19.7006 | 19.6966 | 19.4745 | 19.0109 | 18.5859 | 18.6568 | 18.6553 | 18.6526 | 18.6488 | 18.6387 | 18.6278 | 18.6172 | 18.4974 | 18.3091 | 18.1405 | 17.7485 | 17.1623 | 16.5995 | 16.0806 | 18.8747 | 18.8727 | 18.8693 | 18.8645 | 18.8532 | 18.841 | 18.8292 | 18.7511 | 18.562 | 18.3926 | 17.9989 | 17.4101 | 16.8407 | 16.3056
|  | CHIPPING NORTON | LW |  |  | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.6566 | 19.5746 | 19.4889 | 19.4001 | 19.2652 | 19.2465 | 19.1824 | 18.8173 | 18.1664 | 17.7326 | 18.6568 | 18.6553 | 18.6526 | 18.6488 | 18.565 | 18.4781 | 18.3767 | 18.1099 | 17.7966 | 17.6106 | 17.1585 | 16.4913 | 15.741 | 15.2134 | 18.8747 | 18.8727 | 18.8693 | 18.8644 | 18.7795 | 18.6913 | 18.5956 | 18.3632 | 18.0491 | 17.8624 | 17.4085 | 16.7388 | 15.9799 | 15.436
|  | CHIPPING NORTON | ST |  |  | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.4672 | 18.6571 | 18.6559 | 18.6541 | 18.6518 | 18.6491 | 18.6458 | 18.6408 | 18.6356 | 18.5864 | 18.4719 | 18.2069 | 17.8253 | 17.4746 | 17.1404 | 18.875 | 18.8736 | 18.8712 | 18.8684 | 18.8648 | 18.8606 | 18.8542 | 18.8476 | 18.8404 | 18.7254 | 18.4591 | 18.0758 | 17.7235 | 17.3879
|  | CHIPPING NORTON | SP |  |  | 19.7361 | 19.7361 | 19.7361 | 19.7361 | 19.7348 | 19.7334 | 19.7321 | 19.7307 | 19.7286 | 19.7227 | 19.704 | 19.6951 | 19.667 | 19.6435 | 18.6574 | 18.6567 | 18.6557 | 18.6547 | 18.652 | 18.6493 | 18.646 | 18.6427 | 18.6384 | 18.6304 | 18.607 | 18.5914 | 18.4401 | 18.3021 | 18.8755 | 18.8746 | 18.8733 | 18.872 | 18.869 | 18.8658 | 18.862 | 18.8582 | 18.8533 | 18.8447 | 18.82 | 18.8026 | 18.6937 | 18.5552
COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE | MINIMUM HEADROOM | SU 80226 89155 | YES | 11.7902 | 11.7848 | 11.7777 | 11.7627 | 11.6908 | 11.6089 | 11.5269 | 11.4423 | 11.318 | 11.2932 | 11.2125 | 11.0838 | 10.8797 | 10.775 | 7.937 | 7.937 | 7.937 | 7.937 | 7.8685 | 7.7978 | 7.7239 | 7.6474 | 7.5311 | 7.515 | 7.4598 | 7.3735 | 7.2131 | 7.2024 | 8.7504 | 8.7491 | 8.7474 | 8.7438 | 8.6745 | 8.6011 | 8.5253 | 8.4468 | 8.3287 | 8.3105 | 8.2492 | 8.1527 | 7.8677 | 7.6982
|  | CHISBRIDGE | CT |  |  | 11.7902 | 11.7848 | 11.7777 | 11.7627 | 11.7482 | 11.7338 | 11.7195 | 11.7114 | 11.7034 | 11.6948 | 11.6692 | 11.6269 | 11.581 | 11.4455 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 8.7504 | 8.7491 | 8.7474 | 8.7438 | 8.7404 | 8.7369 | 8.7335 | 8.7315 | 8.7296 | 8.7275 | 8.7214 | 8.6777 | 8.5163 | 8.3577
|  | CHISBRIDGE | LW |  |  | 11.7919 | 11.7877 | 11.7822 | 11.7706 | 11.6908 | 11.6089 | 11.5269 | 11.4423 | 11.318 | 11.2932 | 11.2125 | 11.0838 | 10.8797 | 10.775 | 7.937 | 7.937 | 7.937 | 7.937 | 7.8685 | 7.7978 | 7.7239 | 7.6474 | 7.5311 | 7.515 | 7.4598 | 7.3735 | 7.2131 | 7.2024 | 8.7508 | 8.7498 | 8.7485 | 8.7457 | 8.6745 | 8.6011 | 8.5253 | 8.4468 | 8.3287 | 8.3105 | 8.2492 | 8.1527 | 7.8677 | 7.6982
|  | CHISBRIDGE | ST |  |  | 11.7938 | 11.7911 | 11.788 | 11.7826 | 11.7759 | 11.7679 | 11.7618 | 11.7558 | 11.7503 | 11.7444 | 11.7272 | 11.699 | 11.6709 | 11.6428 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 8.7513 | 8.7506 | 8.7499 | 8.7486 | 8.747 | 8.7451 | 8.7436 | 8.7422 | 8.7408 | 8.7394 | 8.7353 | 8.7286 | 8.7218 | 8.7151
|  | CHISBRIDGE | SP |  |  | 11.7968 | 11.7964 | 11.7961 | 11.7957 | 11.7941 | 11.7922 | 11.79 | 11.7879 | 11.7851 | 11.7828 | 11.7762 | 11.7655 | 11.7553 | 11.7456 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 7.937 | 8.752 | 8.7519 | 8.7518 | 8.7517 | 8.7514 | 8.7509 | 8.7504 | 8.7499 | 8.7492 | 8.7487 | 8.7471 | 8.7445 | 8.7421 | 8.7397
MINETY GSP | TOOTHILL BSP | CHISLEDON | MINIMUM HEADROOM | SU 18894 79934 | YES | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5286 | 16.4923 | 16.1874 | 15.7811 | 15.3034 | 14.7825 | 12.8368 | 11.6157 | 11.2932 | 11.0414 | 16.0299 | 16.0139 | 16.0004 | 15.9797 | 15.9443 | 15.8875 | 15.6598 | 15.1843 | 14.6196 | 14.006 | 11.7167 | 10.2798 | 9.9003 | 9.6041 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2518 | 15.9031 | 15.5104 | 15.0375 | 14.4815 | 13.8775 | 11.6238 | 10.2093 | 9.8357 | 9.5441
|  | CHISLEDON | CT |  |  | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.2165 | 15.8102 | 15.3326 | 14.8117 | 12.8662 | 11.645 | 11.3226 | 11.0708 | 16.0303 | 16.0147 | 16.0016 | 15.9818 | 15.9583 | 15.9287 | 15.6938 | 15.2188 | 14.6541 | 14.0405 | 11.7512 | 10.3143 | 9.9349 | 9.6387 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 15.9501 | 15.5443 | 15.0714 | 14.5154 | 13.9114 | 11.6578 | 10.2432 | 9.8698 | 9.5781
|  | CHISLEDON | LW |  |  | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5248 | 16.1874 | 15.7811 | 15.3034 | 14.7825 | 12.8368 | 11.6157 | 11.2932 | 11.0414 | 16.0299 | 16.0139 | 16.0004 | 15.9797 | 15.9554 | 15.9249 | 15.6598 | 15.1843 | 14.6196 | 14.006 | 11.7167 | 10.2798 | 9.9003 | 9.6041 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2804 | 15.9031 | 15.5104 | 15.0375 | 14.4815 | 13.8775 | 11.6238 | 10.2093 | 9.8357 | 9.5441
|  | CHISLEDON | ST |  |  | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5286 | 16.4923 | 16.4553 | 16.2457 | 15.8673 | 15.4907 | 14.0305 | 13.0945 | 12.6994 | 12.4822 | 16.0313 | 16.0273 | 16.008 | 15.9956 | 15.9443 | 15.8875 | 15.8291 | 15.7523 | 15.3209 | 14.8823 | 13.1726 | 12.0803 | 11.648 | 11.4019 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2518 | 16.2155 | 15.9583 | 15.6024 | 15.1716 | 14.7366 | 13.0525 | 11.9764 | 11.548 | 11.3049
|  | CHISLEDON | SP |  |  | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.5643 | 16.2148 | 15.8548 | 15.772 | 15.7152 | 16.033 | 16.031 | 16.0157 | 16.0098 | 16.0024 | 15.9933 | 15.9841 | 15.9735 | 15.9613 | 15.948 | 15.6919 | 15.2715 | 15.1735 | 15.1064 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.2875 | 16.1886 | 15.5423 | 15.1232 | 15.0268 | 14.9608
BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM | MINIMUM HEADROOM | SU 97173 63223 | YES | 16.5265 | 16.5084 | 16.4857 | 16.438 | 16.3895 | 16.3389 | 16.3027 | 16.2642 | 16.2167 | 16.1823 | 16.0727 | 15.8691 | 15.6165 | 15.4382 | 12.7419 | 12.7254 | 12.7048 | 12.6301 | 12.498 | 12.3641 | 12.2588 | 12.1743 | 12.0838 | 11.9933 | 11.7158 | 11.2172 | 10.5973 | 9.9696 | 13.6298 | 13.6253 | 13.6198 | 13.6081 | 13.5947 | 13.5791 | 13.5652 | 13.5488 | 13.5232 | 13.5123 | 13.4732 | 13.3933 | 12.7956 | 12.0676
|  | CHOBHAM | CT |  |  | 16.5271 | 16.5095 | 16.4875 | 16.4412 | 16.3955 | 16.3493 | 16.3031 | 16.2713 | 16.2367 | 16.2045 | 16.1059 | 15.8977 | 15.6735 | 15.4852 | 12.7424 | 12.7265 | 12.7064 | 12.6391 | 12.5123 | 12.3852 | 12.2588 | 12.1743 | 12.0875 | 11.9992 | 11.7327 | 11.2295 | 10.6307 | 9.9932 | 13.6299 | 13.6256 | 13.6202 | 13.6089 | 13.5972 | 13.585 | 13.5724 | 13.5627 | 13.55 | 13.5414 | 13.5132 | 13.4289 | 12.8238 | 12.0859
|  | CHOBHAM | LW |  |  | 16.5265 | 16.5084 | 16.4857 | 16.438 | 16.3895 | 16.3389 | 16.3027 | 16.2642 | 16.2167 | 16.1823 | 16.0727 | 15.8691 | 15.6165 | 15.4382 | 12.7419 | 12.7254 | 12.7048 | 12.6301 | 12.498 | 12.3641 | 12.2748 | 12.1836 | 12.0838 | 11.9933 | 11.7158 | 11.2172 | 10.5973 | 9.9696 | 13.6298 | 13.6253 | 13.6198 | 13.6081 | 13.5947 | 13.5791 | 13.5652 | 13.5488 | 13.5232 | 13.5123 | 13.4732 | 13.3933 | 12.7956 | 12.0676
|  | CHOBHAM | ST |  |  | 16.5724 | 16.5335 | 16.5255 | 16.5119 | 16.4947 | 16.4736 | 16.4484 | 16.4228 | 16.3987 | 16.3754 | 16.3012 | 16.1767 | 16.0121 | 15.8814 | 12.7836 | 12.7482 | 12.741 | 12.7286 | 12.713 | 12.6936 | 12.6639 | 12.5959 | 12.5361 | 12.4745 | 12.287 | 11.9646 | 11.596 | 11.2638 | 13.641 | 13.6315 | 13.6295 | 13.6262 | 13.6217 | 13.6158 | 13.6087 | 13.601 | 13.5918 | 13.5845 | 13.558 | 13.5164 | 13.4374 | 13.3914
|  | CHOBHAM | SP |  |  | 16.5796 | 16.5779 | 16.5451 | 16.5439 | 16.5388 | 16.5325 | 16.5242 | 16.516 | 16.5053 | 16.4964 | 16.468 | 16.4226 | 16.3639 | 16.3067 | 12.7902 | 12.7886 | 12.7588 | 12.7578 | 12.753 | 12.7474 | 12.7398 | 12.7323 | 12.7226 | 12.7144 | 12.6883 | 12.6021 | 12.4653 | 12.332 | 13.6428 | 13.6424 | 13.6343 | 13.6341 | 13.6328 | 13.6312 | 13.6291 | 13.6271 | 13.6243 | 13.6216 | 13.6116 | 13.5981 | 13.5722 | 13.5469
COWLEY GSP | DRAYTON BSP | CHOLSEY | MINIMUM HEADROOM | SU 58223 84685 | NO | 17.355 | 17.3392 | 17.3359 | 17.3297 | 17.3203 | 17.2968 | 17.2699 | 17.2424 | 17.2017 | 17.1852 | 17.1335 | 16.9222 | 16.5661 | 16.2157 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.3976 | 16.3749 | 16.3518 | 16.3278 | 16.2909 | 16.2783 | 16.2382 | 15.881 | 15.4916 | 15.1084 | 14.9695 | 14.8014 | 14.7665 | 14.7009 | 14.6367 | 14.5718 | 14.5071 | 14.4486 | 14.3911 | 14.3295 | 14.1476 | 13.8442 | 13.5344 | 13.2296
|  | CHOLSEY | CT |  |  | 17.355 | 17.3392 | 17.3359 | 17.3297 | 17.3236 | 17.3175 | 17.3114 | 17.3059 | 17.3005 | 17.2946 | 17.2708 | 16.9222 | 16.5661 | 16.2157 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.2624 | 15.881 | 15.4916 | 15.1084 | 14.9695 | 14.8014 | 14.7665 | 14.7009 | 14.6367 | 14.5718 | 14.5071 | 14.4486 | 14.3911 | 14.3295 | 14.1476 | 13.8442 | 13.5344 | 13.2296
|  | CHOLSEY | LW |  |  | 17.3558 | 17.3405 | 17.338 | 17.3333 | 17.3288 | 17.3242 | 17.3186 | 17.3131 | 17.3076 | 17.3018 | 17.2847 | 17.0098 | 16.6534 | 16.3029 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.358 | 15.9769 | 15.5871 | 15.2038 | 14.9779 | 14.8158 | 14.7887 | 14.7397 | 14.6916 | 14.6426 | 14.5833 | 14.5247 | 14.4673 | 14.4057 | 14.2237 | 13.9204 | 13.6104 | 13.3055
|  | CHOLSEY | ST |  |  | 17.3579 | 17.357 | 17.3437 | 17.3432 | 17.3203 | 17.2968 | 17.2699 | 17.2424 | 17.2017 | 17.1852 | 17.1335 | 17.0822 | 16.9476 | 16.6862 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.3976 | 16.3749 | 16.3518 | 16.3278 | 16.2909 | 16.2783 | 16.2382 | 16.2061 | 15.9388 | 15.6561 | 14.9999 | 14.9903 | 14.8497 | 14.8446 | 14.8157 | 14.7843 | 14.7218 | 14.6592 | 14.5829 | 14.5283 | 14.3653 | 14.1307 | 13.8247 | 13.593
|  | CHOLSEY | SP |  |  | 17.3579 | 17.3573 | 17.3569 | 17.3568 | 17.356 | 17.3551 | 17.3537 | 17.3523 | 17.3506 | 17.349 | 17.3446 | 17.3373 | 17.3304 | 17.3238 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 16.4199 | 15.0004 | 14.9933 | 14.9898 | 14.988 | 14.9799 | 14.97 | 14.9552 | 14.9408 | 14.9225 | 14.9061 | 14.8585 | 14.7816 | 14.7083 | 14.6388
MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH | MINIMUM HEADROOM | SZ 15698 93141 | YES | 38.0619 | 38.0484 | 38.0348 | 37.2077 | 37.1392 | 37.07 | 37 | 36.9291 | 36.7527 | 36.7123 | 36.5852 | 35.6201 | 35.0055 | 34.7541 | 35.9 | 35.8841 | 35.8677 | 35.0352 | 34.9619 | 34.8883 | 34.8066 | 34.7241 | 34.5432 | 34.4903 | 34.3259 | 33.2935 | 32.606 | 30.8606 | 36.1578 | 36.1443 | 36.1307 | 35.3036 | 35.2351 | 35.1659 | 35.0959 | 35.025 | 34.8486 | 34.8082 | 34.6811 | 33.716 | 33.0642 | 31.7057
|  | CHRISTCHURCH | CT |  |  | 38.127 | 38.1189 | 38.1107 | 37.6145 | 37.4606 | 37.3047 | 37.1467 | 36.9832 | 36.7527 | 36.7123 | 36.5852 | 35.6201 | 35.0055 | 34.7541 | 35.965 | 35.9546 | 35.9436 | 35.4419 | 35.2833 | 35.123 | 34.9605 | 34.7853 | 34.5432 | 34.4903 | 34.3259 | 33.2935 | 32.606 | 30.8606 | 36.2229 | 36.2148 | 36.2066 | 35.7104 | 35.5565 | 35.4006 | 35.2426 | 35.0791 | 34.8486 | 34.8082 | 34.6811 | 33.716 | 33.0642 | 31.7057
|  | CHRISTCHURCH | LW |  |  | 38.0619 | 38.0484 | 38.0348 | 37.2077 | 37.1392 | 37.07 | 37 | 36.9291 | 36.8552 | 36.827 | 36.7402 | 36.5914 | 36.4843 | 36.3334 | 35.9 | 35.8841 | 35.8677 | 35.0352 | 34.9619 | 34.8883 | 34.8066 | 34.7241 | 34.6385 | 34.5979 | 34.4738 | 34.2577 | 33.9413 | 32.2899 | 36.1578 | 36.1443 | 36.1307 | 35.3036 | 35.2351 | 35.1659 | 35.0959 | 35.025 | 34.9511 | 34.9229 | 34.8361 | 34.6873 | 34.5346 | 33.1404
|  | CHRISTCHURCH | ST |  |  | 38.1596 | 38.1541 | 38.1487 | 37.8179 | 37.7836 | 37.7491 | 37.7143 | 37.679 | 37.6389 | 37.6234 | 37.5746 | 37.5054 | 37.4248 | 37.3484 | 35.9981 | 35.991 | 35.9836 | 35.6498 | 35.6123 | 35.5742 | 35.5306 | 35.4865 | 35.4384 | 35.4144 | 35.3404 | 35.2259 | 35.098 | 34.9752 | 36.2555 | 36.25 | 36.2446 | 35.9138 | 35.8795 | 35.845 | 35.8102 | 35.7749 | 35.7348 | 35.7193 | 35.6705 | 35.6013 | 35.5207 | 35.4382
|  | CHRISTCHURCH | SP |  |  | 38.1921 | 38.1894 | 38.1867 | 38.0212 | 38.0077 | 37.9941 | 37.9805 | 37.967 | 37.9533 | 37.9477 | 37.9301 | 37.9019 | 37.8805 | 37.8457 | 36.0319 | 36.0287 | 36.0254 | 35.8594 | 35.8449 | 35.8305 | 35.8142 | 35.7979 | 35.7808 | 35.7719 | 35.7446 | 35.6988 | 35.6589 | 35.606 | 36.288 | 36.2853 | 36.2826 | 36.1172 | 36.1036 | 36.09 | 36.0764 | 36.0629 | 36.0492 | 36.0436 | 36.026 | 35.9978 | 35.9764 | 35.9417
LALEHAM | EAST BEDFONT A | CHURCH ROAD | MINIMUM HEADROOM | TQ 06820 71722 | YES | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8836 | 17.8725 | 17.8613 | 17.8496 | 17.8315 | 17.8292 | 17.8219 | 17.7879 | 17.2485 | 15.8424 | 12.5969 | 12.5946 | 12.5916 | 12.5812 | 12.5588 | 12.5419 | 12.5247 | 12.4891 | 12.4465 | 12.4181 | 11.9386 | 10.5745 | 8.9431 | 7.3139 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8754 | 12.8644 | 12.8532 | 12.8415 | 12.8234 | 12.8211 | 12.8137 | 12.0108 | 10.4761 | 8.9522
|  | CHURCH ROAD | CT |  |  | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8836 | 17.8725 | 17.8613 | 17.8496 | 17.8315 | 17.8292 | 17.8219 | 17.7879 | 17.2485 | 15.8424 | 12.5969 | 12.5946 | 12.5916 | 12.5812 | 12.5588 | 12.5419 | 12.5247 | 12.4891 | 12.4465 | 12.4181 | 12 | 10.6015 | 8.9431 | 7.3139 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8754 | 12.8644 | 12.8532 | 12.8415 | 12.8234 | 12.8211 | 12.8137 | 12.0291 | 10.4761 | 8.9522
|  | CHURCH ROAD | LW |  |  | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.2768 | 15.8808 | 12.5969 | 12.5946 | 12.5916 | 12.5812 | 12.5697 | 12.5638 | 12.5402 | 12.5164 | 12.4918 | 12.4657 | 11.9386 | 10.5745 | 8.953 | 7.334 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.0108 | 10.4947 | 8.9809
|  | CHURCH ROAD | ST |  |  | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.6618 | 12.5977 | 12.5962 | 12.5943 | 12.5883 | 12.5811 | 12.577 | 12.5584 | 12.5397 | 12.523 | 12.5051 | 12.4344 | 11.4974 | 10.433 | 9.3994 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8737 | 11.8785 | 10.9121
|  | CHURCH ROAD | SP |  |  | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 17.8944 | 12.5988 | 12.5982 | 12.5975 | 12.5949 | 12.5916 | 12.5903 | 12.5844 | 12.5785 | 12.5708 | 12.5639 | 12.5424 | 12.4928 | 12.293 | 11.809 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863 | 12.8863
MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN | MINIMUM HEADROOM | SP 02761 00827 | NO | 33.8933 | 33.8908 | 33.8549 | 33.8478 | 33.7952 | 33.7393 | 33.6822 | 33.6179 | 33.5228 | 33.5011 | 33.4323 | 33.1839 | 32.9162 | 32.8066 | 25.0061 | 25.0044 | 24.9799 | 24.975 | 24.9237 | 24.8697 | 24.8144 | 24.7533 | 24.6612 | 24.6429 | 24.584 | 23.7376 | 22.7709 | 21.9733 | 25.184 | 25.1818 | 25.1489 | 25.1424 | 25.0901 | 25.0347 | 24.9781 | 24.9147 | 24.8203 | 24.7996 | 24.6426 | 23.7253 | 22.7631 | 21.97
|  | CIRENCESTER TOWN | CT |  |  | 33.8937 | 33.8915 | 33.8561 | 33.8497 | 33.7952 | 33.7393 | 33.6822 | 33.6179 | 33.5228 | 33.5011 | 33.4323 | 33.1839 | 32.9162 | 32.8066 | 25.0063 | 25.0049 | 24.9807 | 24.9764 | 24.9237 | 24.8697 | 24.8144 | 24.7533 | 24.6612 | 24.6429 | 24.584 | 23.7376 | 22.7709 | 21.9733 | 25.1844 | 25.1824 | 25.1499 | 25.1442 | 25.0901 | 25.0347 | 24.9781 | 24.9147 | 24.8203 | 24.7996 | 24.6426 | 23.7253 | 22.7631 | 21.97
|  | CIRENCESTER TOWN | LW |  |  | 33.8933 | 33.8908 | 33.8549 | 33.8478 | 33.8392 | 33.8285 | 33.8122 | 33.7935 | 33.7661 | 33.7525 | 33.7059 | 33.6159 | 33.488 | 33.4296 | 25.0061 | 25.0044 | 24.9799 | 24.975 | 24.9685 | 24.96 | 24.9469 | 24.9313 | 24.907 | 24.8968 | 24.8335 | 24.0704 | 23.2432 | 22.4967 | 25.184 | 25.1818 | 25.1489 | 25.1424 | 25.1343 | 25.1242 | 25.1088 | 25.0909 | 25.0643 | 25.0516 | 24.8173 | 24.0587 | 23.2361 | 22.4941
|  | CIRENCESTER TOWN | ST |  |  | 33.894 | 33.892 | 33.8892 | 33.885 | 33.8798 | 33.8731 | 33.8663 | 33.859 | 33.8482 | 33.839 | 33.8074 | 33.7587 | 33.6749 | 33.6226 | 25.0065 | 25.0052 | 25.0032 | 25.0004 | 24.9967 | 24.9919 | 24.9869 | 24.9813 | 24.9726 | 24.9658 | 24.9408 | 24.9032 | 24.7431 | 24.2441 | 25.1847 | 25.1829 | 25.1803 | 25.1765 | 25.1716 | 25.1654 | 25.1591 | 25.1523 | 25.142 | 25.1335 | 25.1036 | 25.0578 | 24.7273 | 24.2313
|  | CIRENCESTER TOWN | SP |  |  | 33.8962 | 33.896 | 33.8953 | 33.895 | 33.8938 | 33.8925 | 33.8906 | 33.8886 | 33.886 | 33.8825 | 33.8706 | 33.8543 | 33.8269 | 33.8004 | 25.0081 | 25.0079 | 25.0075 | 25.0072 | 25.0064 | 25.0055 | 25.0042 | 25.0028 | 25.001 | 24.9984 | 24.9891 | 24.977 | 24.9537 | 24.9311 | 25.1867 | 25.1865 | 25.1859 | 25.1856 | 25.1846 | 25.1833 | 25.1815 | 25.1797 | 25.1774 | 25.1741 | 25.1629 | 25.1477 | 25.1213 | 25.0959
IVER 132KV | CIPPENHAM | CLARENCE ROAD | MINIMUM HEADROOM | SU 95654 76652 | YES | 54.1734 | 54.1626 | 79.9517 | 79.2878 | 79.1644 | 79.0379 | 78.9072 | 78.7728 | 78.5948 | 78.5557 | 78.4285 | 78.2205 | 77.9625 | 77.8285 | 50.7066 | 50.6695 | 75.0238 | 74.2864 | 74.0917 | 73.8927 | 73.5053 | 72.9941 | 72.4285 | 71.9721 | 70.6727 | 68.6854 | 66.5937 | 64.6572 | 51.684 | 51.6732 | 77.4623 | 76.7644 | 76.5904 | 76.4124 | 76.2609 | 75.9232 | 75.3716 | 74.9303 | 73.6734 | 71.7506 | 69.7253 | 67.854
|  | CLARENCE ROAD | CT |  |  | 54.2257 | 54.2192 | 80.0126 | 79.6143 | 79.5814 | 79.5482 | 79.5148 | 79.4811 | 79.446 | 79.4325 | 79.3911 | 78.8958 | 78.7065 | 78.2554 | 50.7595 | 50.7272 | 75.0864 | 74.6159 | 74.5129 | 74.4084 | 73.6481 | 73.2375 | 72.8148 | 72.3839 | 71.1705 | 68.8953 | 66.8726 | 64.9445 | 51.7363 | 51.7298 | 77.5232 | 77.093 | 77.0103 | 76.9266 | 76.5804 | 76.1834 | 75.7748 | 75.359 | 74.188 | 71.9773 | 70.021 | 68.1582
|  | CLARENCE ROAD | LW |  |  | 54.1734 | 54.1626 | 79.9517 | 79.2878 | 79.1644 | 79.0379 | 78.9072 | 78.7728 | 78.5948 | 78.5557 | 78.4285 | 78.2205 | 77.9625 | 77.8285 | 50.7066 | 50.6695 | 75.0238 | 74.2864 | 74.0917 | 73.8927 | 73.5053 | 72.9941 | 72.4285 | 71.9721 | 70.6727 | 68.6854 | 66.5937 | 64.6572 | 51.684 | 51.6732 | 77.4623 | 76.7644 | 76.5904 | 76.4124 | 76.2609 | 75.9232 | 75.3716 | 74.9303 | 73.6734 | 71.7506 | 69.7253 | 67.854
|  | CLARENCE ROAD | ST |  |  | 54.2518 | 54.2475 | 80.0431 | 79.7776 | 79.7556 | 79.7335 | 79.7111 | 79.6885 | 79.6649 | 79.6553 | 79.6244 | 79.5746 | 79.5263 | 79.4704 | 50.8038 | 50.7873 | 75.1682 | 74.8776 | 74.825 | 74.7647 | 74.7164 | 74.6675 | 74.6229 | 74.5906 | 74.4962 | 73.5627 | 72.3298 | 71.1059 | 51.7624 | 51.7581 | 77.5537 | 77.2882 | 77.2662 | 77.2332 | 77.1924 | 77.1512 | 77.1126 | 77.0869 | 77.011 | 76.5002 | 75.3102 | 74.1287
|  | CLARENCE ROAD | SP |  |  | 54.2779 | 54.2758 | 80.0736 | 79.9408 | 79.9251 | 79.9096 | 79.894 | 79.8783 | 79.8599 | 79.8345 | 79.7541 | 79.6996 | 79.5815 | 79.4688 | 50.8417 | 50.8369 | 75.2319 | 75.0964 | 75.0691 | 75.0393 | 75.0143 | 74.989 | 74.9585 | 74.9243 | 74.8192 | 74.7283 | 74.5748 | 74.4281 | 51.7885 | 51.7864 | 77.5842 | 77.4514 | 77.4357 | 77.4202 | 77.4046 | 77.3889 | 77.3705 | 77.3451 | 77.2647 | 77.1976 | 77.0543 | 76.9174
MELKSHAM GSP | CHIPPENHAM | COCKLEBURY | MINIMUM HEADROOM | ST 92447 73890 | YES | 54.2778 | 54.2543 | 54.2265 | 53.5325 | 53.452 | 53.3714 | 53.2962 | 53.2184 | 53.1322 | 53.0918 | 52.9662 | 52.7459 | 52.4394 | 51.4549 | 24.7021 | 24.6689 | 24.628 | 23.9108 | 23.8114 | 23.7135 | 23.6203 | 23.5138 | 23.2884 | 23.1009 | 22.5506 | 21.623 | 20.6514 | 19.5138 | 25.5321 | 25.4365 | 25.3121 | 24.4461 | 24.2265 | 23.9739 | 23.717 | 23.4488 | 23.1675 | 22.925 | 22.2156 | 21.023 | 19.8492 | 18.7146
|  | COCKLEBURY | CT |  |  | 54.3306 | 54.3118 | 54.289 | 53.8617 | 53.8053 | 53.7504 | 53.6946 | 53.6445 | 53.5915 | 53.5617 | 53.472 | 52.8804 | 52.4771 | 51.4838 | 24.7554 | 24.7272 | 24.6917 | 24.2421 | 24.1677 | 24.0964 | 24.0153 | 23.9259 | 23.7311 | 23.5543 | 23.0399 | 21.7409 | 20.6854 | 19.539 | 25.5881 | 25.4997 | 25.3834 | 24.7909 | 24.6019 | 24.4138 | 24.0933 | 23.852 | 23.6041 | 23.3722 | 22.6987 | 21.1347 | 19.8832 | 18.7399
|  | COCKLEBURY | LW |  |  | 54.2778 | 54.2543 | 54.2265 | 53.5325 | 53.452 | 53.3714 | 53.2962 | 53.2184 | 53.1322 | 53.0918 | 52.9662 | 52.7459 | 52.4394 | 51.4549 | 24.7021 | 24.6689 | 24.628 | 23.9108 | 23.8114 | 23.7135 | 23.6203 | 23.5138 | 23.2884 | 23.1009 | 22.5506 | 21.623 | 20.6514 | 19.5138 | 25.5321 | 25.4365 | 25.3121 | 24.4461 | 24.2265 | 23.9739 | 23.717 | 23.4488 | 23.1675 | 22.925 | 22.2156 | 21.023 | 19.8492 | 18.7146
|  | COCKLEBURY | ST |  |  | 54.4706 | 54.4573 | 54.442 | 54.1603 | 54.1228 | 54.0832 | 54.0491 | 54.0142 | 53.9782 | 53.9569 | 53.8899 | 53.7823 | 53.662 | 53.5499 | 24.8977 | 24.8776 | 24.8539 | 24.5596 | 24.5102 | 24.4575 | 24.4147 | 24.3711 | 24.327 | 24.2972 | 24.1584 | 23.5773 | 23.0047 | 22.4501 | 25.7456 | 25.6814 | 25.6039 | 25.2295 | 25.1042 | 24.9672 | 24.8693 | 24.7693 | 24.6737 | 24.5316 | 24.0797 | 23.3211 | 22.5791 | 21.8588
|  | COCKLEBURY | SP |  |  | 54.5032 | 54.4978 | 54.492 | 54.3555 | 54.3403 | 54.3251 | 54.3103 | 54.2955 | 54.2795 | 54.2704 | 54.2418 | 54.1976 | 54.153 | 54.0991 | 24.9354 | 24.9275 | 24.9189 | 24.7795 | 24.761 | 24.7425 | 24.7248 | 24.7069 | 24.6872 | 24.6747 | 24.6369 | 24.5776 | 24.5191 | 24.4522 | 25.8155 | 25.7916 | 25.7651 | 25.6074 | 25.5677 | 25.5278 | 25.4912 | 25.4541 | 25.4101 | 25.377 | 25.28 | 25.1239 | 24.9766 | 24.827
MELKSHAM GSP | FROME BSP | CODFORD | MINIMUM HEADROOM | ST 97372 39559 | YES | 6.2114 | 6.2035 | 6.1942 | 6.1783 | 5.999 | 5.7778 | 5.5347 | 5.2834 | 4.9102 | 4.8438 | 4.6242 | 4.2883 | 3.7277 | 3.6169 | 4.1927 | 4.1798 | 4.1647 | 4.1388 | 3.9793 | 3.7557 | 3.5026 | 3.2414 | 2.8583 | 2.7813 | 2.5303 | 2.1428 | 1.5289 | 1.3656 | 4.1931 | 4.1852 | 4.1759 | 4.1599 | 3.9807 | 3.7595 | 3.5163 | 3.2651 | 2.8918 | 2.8254 | 2.6057 | 2.2696 | 1.7088 | 1.5978
|  | CODFORD | CT |  |  | 6.2207 | 6.2193 | 6.2175 | 6.2136 | 6.2098 | 6.206 | 6.2022 | 6.1865 | 6.1708 | 6.1539 | 6.1042 | 6.0222 | 5.9375 | 5.8542 | 4.2079 | 4.2056 | 4.2026 | 4.1963 | 4.1901 | 4.1839 | 4.1778 | 4.1521 | 4.1266 | 4.0991 | 4.018 | 3.8843 | 3.7465 | 3.6107 | 4.2025 | 4.2011 | 4.1992 | 4.1953 | 4.1915 | 4.1877 | 4.1839 | 4.1681 | 4.1525 | 4.1355 | 4.0857 | 4.0035 | 3.9187 | 3.8352
|  | CODFORD | LW |  |  | 6.2207 | 6.2193 | 6.2175 | 6.2136 | 5.999 | 5.7778 | 5.5347 | 5.2834 | 4.9102 | 4.8438 | 4.6242 | 4.2883 | 3.7277 | 3.6169 | 4.2079 | 4.2056 | 4.2026 | 4.1963 | 3.9793 | 3.7557 | 3.5026 | 3.2414 | 2.8583 | 2.7813 | 2.5303 | 2.1428 | 1.5289 | 1.3656 | 4.2025 | 4.2011 | 4.1992 | 4.1953 | 3.9807 | 3.7595 | 3.5163 | 3.2651 | 2.8918 | 2.8254 | 2.6057 | 2.2696 | 1.7088 | 1.5978
|  | CODFORD | ST |  |  | 6.2114 | 6.2035 | 6.1942 | 6.1783 | 6.1587 | 6.1352 | 6.1275 | 6.12 | 6.1093 | 6.0978 | 6.0642 | 6.0097 | 5.9552 | 5.901 | 4.1927 | 4.1798 | 4.1647 | 4.1388 | 4.1069 | 4.0686 | 4.0561 | 4.0438 | 4.0263 | 4.0076 | 3.9529 | 3.8641 | 3.7752 | 3.6869 | 4.1931 | 4.1852 | 4.1759 | 4.1599 | 4.1403 | 4.1168 | 4.1091 | 4.1015 | 4.0908 | 4.0793 | 4.0456 | 3.991 | 3.9363 | 3.882
|  | CODFORD | SP |  |  | 6.2223 | 6.2222 | 6.2221 | 6.2219 | 6.2213 | 6.2206 | 6.218 | 6.2154 | 6.2121 | 6.2076 | 6.1947 | 6.174 | 6.1543 | 6.1356 | 4.2106 | 4.2103 | 4.2101 | 4.2099 | 4.2089 | 4.2078 | 4.2035 | 4.1993 | 4.1939 | 4.1866 | 4.1655 | 4.1319 | 4.0997 | 4.0693 | 4.2041 | 4.2039 | 4.2038 | 4.2037 | 4.2031 | 4.2024 | 4.1998 | 4.1972 | 4.1938 | 4.1894 | 4.1764 | 4.1557 | 4.1359 | 4.1172
IVER 132KV | DENHAM | COKES LANE | MINIMUM HEADROOM | SU 99240 97483 | YES | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.7546 | 17.3651 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7608 | 10.2608 | 9.8196 | 9.3762 | 11.1007 | 11.0445 | 10.9707 | 10.8171 | 10.6674 | 10.5184 | 10.4256 | 10.3607 | 10.2918 | 10.2186 | 9.9584 | 9.4497 | 9.0008 | 8.5496
|  | COKES LANE | CT |  |  | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.7546 | 17.3651 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7608 | 10.2608 | 9.8196 | 9.3762 | 11.1076 | 11.0564 | 10.9892 | 10.8495 | 10.7133 | 10.5776 | 10.4256 | 10.3607 | 10.2918 | 10.2186 | 9.9584 | 9.4497 | 9.0008 | 8.5496
|  | COKES LANE | LW |  |  | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.7821 | 17.3924 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.2922 | 9.8509 | 9.4072 | 11.1007 | 11.0445 | 10.9707 | 10.8171 | 10.6674 | 10.5184 | 10.4574 | 10.3926 | 10.3238 | 10.2507 | 9.9904 | 9.4817 | 9.0327 | 8.5812
|  | COKES LANE | ST |  |  | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7843 | 10.4934 | 10.2109 | 11.119 | 11.0777 | 11.0289 | 10.9465 | 10.8453 | 10.7234 | 10.6728 | 10.6198 | 10.5732 | 10.5232 | 10.3408 | 9.9823 | 9.6863 | 9.3989
|  | COKES LANE | SP |  |  | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 17.9656 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 10.7902 | 11.1605 | 11.1563 | 11.1508 | 11.1443 | 11.1187 | 11.0885 | 11.0692 | 11.0492 | 11.025 | 11.0053 | 10.9335 | 10.7859 | 10.652 | 10.5109
LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK | MINIMUM HEADROOM | SU 65893 02686 | NO | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 15.6104 | 14.394 | 12.2051 | 12.194 | 12.1931 | 12.1915 | 12.1898 | 12.1881 | 12.1801 | 12.172 | 12.1639 | 12.1553 | 12.1284 | 11.3726 | 9.9824 | 8.5782 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.0473 | 10.651 | 9.2181
|  | COLLEGE PARK | CT |  |  | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 15.7224 | 14.5062 | 12.2051 | 12.194 | 12.1931 | 12.1915 | 12.1898 | 12.1881 | 12.1864 | 12.1783 | 12.1702 | 12.1616 | 12.1347 | 11.5007 | 10.1106 | 8.7105 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.1761 | 10.7797 | 9.3505
|  | COLLEGE PARK | LW |  |  | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 15.6104 | 14.394 | 12.2051 | 12.194 | 12.1931 | 12.1915 | 12.1898 | 12.1881 | 12.1801 | 12.172 | 12.1639 | 12.1553 | 12.1284 | 11.3726 | 9.9824 | 8.5782 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.0473 | 10.651 | 9.2181
|  | COLLEGE PARK | ST |  |  | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 15.9736 | 12.2054 | 12.2049 | 12.1939 | 12.1931 | 12.1921 | 12.1909 | 12.1857 | 12.1805 | 12.1749 | 12.1691 | 12.1507 | 12.111 | 11.2874 | 10.398 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 11.9618 | 11.0684
|  | COLLEGE PARK | SP |  |  | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 16.2689 | 12.2057 | 12.2055 | 12.1948 | 12.1946 | 12.1943 | 12.1939 | 12.1925 | 12.1911 | 12.1893 | 12.187 | 12.1799 | 12.164 | 12.1446 | 12.1246 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665 | 12.3665
BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS | MINIMUM HEADROOM | SU 88285 81857 | YES | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.0356 | 37.818 | 37.5907 | 37.355 | 36.9972 | 36.9476 | 36.7777 | 36.5211 | 35.9641 | 34.838 | 36.887 | 36.8753 | 36.8656 | 36.8466 | 36.6188 | 36.3833 | 36.1478 | 35.9038 | 35.537 | 35.2858 | 34.5045 | 33.1149 | 31.385 | 30.0614 | 37.0635 | 37.0635 | 37.0635 | 37.0635 | 36.8526 | 36.616 | 36.3783 | 36.132 | 35.7628 | 35.701 | 35.1195 | 33.8265 | 32.1664 | 30.8749
|  | CORDWALLIS | CT |  |  | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 37.93 | 36.8315 | 36.887 | 36.8753 | 36.8656 | 36.8466 | 36.8284 | 36.8101 | 36.7926 | 36.7477 | 36.5525 | 36.3423 | 35.731 | 34.5978 | 33.3129 | 32.0168 | 37.0635 | 37.0635 | 37.0635 | 37.0635 | 37.0635 | 37.0424 | 37.0201 | 37.0093 | 36.998 | 36.9116 | 36.376 | 35.3221 | 34.1033 | 32.8336
|  | CORDWALLIS | LW |  |  | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.0356 | 37.818 | 37.5907 | 37.355 | 36.9972 | 36.9476 | 36.7777 | 36.5211 | 35.9641 | 34.838 | 36.8872 | 36.8756 | 36.8662 | 36.8476 | 36.6188 | 36.3833 | 36.1478 | 35.9038 | 35.537 | 35.2858 | 34.5045 | 33.1149 | 31.385 | 30.0614 | 37.0635 | 37.0635 | 37.0635 | 37.0635 | 36.8526 | 36.616 | 36.3783 | 36.132 | 35.7628 | 35.701 | 35.1195 | 33.8265 | 32.1664 | 30.8749
|  | CORDWALLIS | ST |  |  | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2388 | 38.231 | 38.2231 | 38.2148 | 38.2021 | 38.1978 | 38.184 | 38.1729 | 38.1412 | 38.1297 | 36.8912 | 36.8871 | 36.878 | 36.8704 | 36.8539 | 36.8355 | 36.8208 | 36.8056 | 36.7868 | 36.776 | 36.743 | 36.3653 | 35.5027 | 34.6863 | 37.0635 | 37.0635 | 37.0635 | 37.0635 | 37.0559 | 37.0481 | 37.0401 | 37.0319 | 37.0192 | 37.0123 | 36.9741 | 36.9178 | 36.1629 | 35.3998
|  | CORDWALLIS | SP |  |  | 38.2465 | 38.2465 | 38.2465 | 38.2465 | 38.2462 | 38.2459 | 38.2456 | 38.2453 | 38.2448 | 38.2434 | 38.2391 | 38.237 | 38.2305 | 38.2251 | 36.8966 | 36.8932 | 36.8876 | 36.8862 | 36.8829 | 36.879 | 36.8763 | 36.8735 | 36.8699 | 36.866 | 36.8542 | 36.8379 | 36.8152 | 36.7933 | 37.0635 | 37.0635 | 37.0635 | 37.0635 | 37.0632 | 37.0629 | 37.0626 | 37.0623 | 37.0618 | 37.0604 | 37.0561 | 37.054 | 37.0475 | 37.0269
MANNINGTON GSP | LYTCHETT | CORFE MULLEN | MINIMUM HEADROOM | SY 98583 96071 | YES | 29.9949 | 29.9914 | 29.9862 | 29.9792 | 29.826 | 29.6633 | 29.4774 | 29.2821 | 28.9936 | 28.9268 | 28.6953 | 28.3205 | 27.7905 | 27.6117 | 29.9639 | 29.9394 | 29.9033 | 29.8535 | 29.6444 | 29.4108 | 29.0691 | 28.7121 | 28.2562 | 28.0089 | 27.1778 | 25.836 | 24.3544 | 23.2317 | 32.0916 | 32.0901 | 32.088 | 32.0852 | 31.9374 | 31.7818 | 31.6112 | 31.4318 | 31.1597 | 31.1107 | 30.5416 | 29.2186 | 27.7555 | 26.6512
|  | CORFE MULLEN | CT |  |  | 29.9949 | 29.9914 | 29.9862 | 29.9792 | 29.9691 | 29.956 | 29.9419 | 29.9123 | 29.8784 | 29.8474 | 29.7422 | 29.5332 | 29.3211 | 29.148 | 29.9639 | 29.9394 | 29.9033 | 29.8535 | 29.7868 | 29.7025 | 29.6148 | 29.4234 | 29.2223 | 29.0107 | 28.306 | 27.1297 | 25.9663 | 24.8495 | 32.0916 | 32.0901 | 32.088 | 32.0852 | 32.0807 | 32.0746 | 32.0677 | 32.054 | 32.0365 | 32.0233 | 31.6682 | 30.5108 | 29.3658 | 28.2674
|  | CORFE MULLEN | LW |  |  | 29.9949 | 29.9914 | 29.9863 | 29.9793 | 29.826 | 29.6633 | 29.4774 | 29.2821 | 28.9936 | 28.9268 | 28.6953 | 28.3205 | 27.7905 | 27.6117 | 29.9641 | 29.9396 | 29.9036 | 29.8541 | 29.6444 | 29.4108 | 29.0691 | 28.7121 | 28.2562 | 28.0089 | 27.1778 | 25.836 | 24.3544 | 23.2317 | 32.0916 | 32.0902 | 32.0881 | 32.0852 | 31.9374 | 31.7818 | 31.6112 | 31.4318 | 31.1597 | 31.1107 | 30.5416 | 29.2186 | 27.7555 | 26.6512
|  | CORFE MULLEN | ST |  |  | 29.9958 | 29.9932 | 29.9897 | 29.9858 | 29.8895 | 29.7887 | 29.6737 | 29.5544 | 29.3826 | 29.3095 | 29.0679 | 28.8116 | 28.2433 | 27.9979 | 29.9705 | 29.9521 | 29.9274 | 29.8998 | 29.765 | 29.6106 | 29.37 | 29.1217 | 28.8363 | 28.6397 | 27.9825 | 27.0594 | 25.8693 | 25.018 | 32.0919 | 32.0909 | 32.0894 | 32.0879 | 31.9953 | 31.8999 | 31.7972 | 31.6906 | 31.5299 | 31.469 | 31.2682 | 30.4277 | 29.2497 | 28.4102
|  | CORFE MULLEN | SP |  |  | 29.9979 | 29.997 | 29.9958 | 29.9953 | 29.9925 | 29.9889 | 29.981 | 29.9729 | 29.9625 | 29.951 | 29.9111 | 29.8595 | 29.7866 | 29.7159 | 29.9853 | 29.979 | 29.9705 | 29.9671 | 29.9514 | 29.9296 | 29.8778 | 29.8251 | 29.7596 | 29.6996 | 29.4967 | 29.1795 | 28.8462 | 28.5124 | 32.0928 | 32.0924 | 32.0919 | 32.0917 | 32.0902 | 32.0884 | 32.0847 | 32.081 | 32.0761 | 32.0694 | 32.0454 | 32.0199 | 31.9727 | 31.8701
MELKSHAM GSP | NORRINGTON | CORSHAM | MINIMUM HEADROOM | ST 86766 69583 | NO | 17.4066 | 17.4066 | 17.4066 | 17.4066 | 17.4052 | 17.4024 | 17.3931 | 17.3776 | 17.3559 | 17.3438 | 17.3032 | 17.2263 | 16.7287 | 16.0911 | 12.7626 | 12.7581 | 12.7521 | 12.7397 | 12.7262 | 12.7113 | 12.6961 | 12.6793 | 12.6564 | 12.6429 | 12.2507 | 11.5519 | 10.7823 | 10.0282 | 13.1287 | 13.1287 | 13.1287 | 13.1287 | 13.1273 | 13.1245 | 13.12 | 13.1139 | 13.1015 | 13.0969 | 12.9999 | 12.3038 | 11.5132 | 10.781
|  | CORSHAM | CT |  |  | 17.4066 | 17.4066 | 17.4066 | 17.4066 | 17.4061 | 17.4054 | 17.4005 | 17.3894 | 17.3764 | 17.3657 | 17.3324 | 17.2525 | 16.7859 | 16.1415 | 12.7628 | 12.7584 | 12.7527 | 12.7407 | 12.7286 | 12.7163 | 12.7036 | 12.6913 | 12.677 | 12.6649 | 12.2935 | 11.5913 | 10.8419 | 10.081 | 13.1287 | 13.1287 | 13.1287 | 13.1287 | 13.1282 | 13.1275 | 13.1263 | 13.1246 | 13.1209 | 13.1186 | 13.0426 | 12.3437 | 11.5723 | 10.8334
|  | CORSHAM | LW |  |  | 17.4066 | 17.4066 | 17.4066 | 17.4066 | 17.4052 | 17.4024 | 17.3931 | 17.3776 | 17.3559 | 17.3438 | 17.3032 | 17.2263 | 16.7287 | 16.0911 | 12.7626 | 12.7581 | 12.7521 | 12.7397 | 12.7262 | 12.7113 | 12.6961 | 12.6793 | 12.6564 | 12.6429 | 12.2507 | 11.5519 | 10.7823 | 10.0282 | 13.1287 | 13.1287 | 13.1287 | 13.1287 | 13.1273 | 13.1245 | 13.12 | 13.1139 | 13.1015 | 13.0969 | 12.9999 | 12.3038 | 11.5132 | 10.781
|  | CORSHAM | ST |  |  | 17.4066 | 17.4066 | 17.4066 | 17.4066 | 17.4063 | 17.4057 | 17.4048 | 17.4035 | 17.3972 | 17.389 | 17.3615 | 17.3181 | 17.2498 | 17.1961 | 12.7635 | 12.7598 | 12.7554 | 12.7479 | 12.7384 | 12.7268 | 12.7188 | 12.7106 | 12.7005 | 12.6913 | 12.661 | 12.2565 | 11.7665 | 11.3025 | 13.1287 | 13.1287 | 13.1287 | 13.1287 | 13.1284 | 13.1278 | 13.1269 | 13.1256 | 13.1228 | 13.1214 | 13.114 | 13.0057 | 12.5179 | 12.0432
|  | CORSHAM | SP |  |  | 17.4066 | 17.4066 | 17.4066 | 17.4066 | 17.4065 | 17.4065 | 17.4065 | 17.4064 | 17.4063 | 17.4059 | 17.4032 | 17.401 | 17.3909 | 17.3714 | 12.7678 | 12.7673 | 12.7668 | 12.7664 | 12.7644 | 12.7619 | 12.7596 | 12.7572 | 12.7542 | 12.7507 | 12.7392 | 12.7224 | 12.6977 | 12.6738 | 13.1287 | 13.1287 | 13.1287 | 13.1287 | 13.1286 | 13.1286 | 13.1286 | 13.1285 | 13.1284 | 13.1279 | 13.1253 | 13.1231 | 13.113 | 13.103
EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD | MINIMUM HEADROOM | SP 59021 31128 | NO | 4.7942 | 4.7942 | 4.7942 | 4.7942 | 4.7456 | 4.6957 | 4.6442 | 4.5877 | 4.4964 | 4.4843 | 4.3868 | 4.0398 | 3.6598 | 3.4693 | 3.9978 | 3.9963 | 3.9943 | 3.9899 | 3.9392 | 3.8856 | 3.8307 | 3.7718 | 3.6782 | 3.6637 | 3.6135 | 3.3687 | 3.0941 | 3.0074 | 3.976 | 3.9586 | 3.9358 | 3.8876 | 3.8145 | 3.7246 | 3.6335 | 3.5512 | 3.4344 | 3.3947 | 3.2704 | 2.9028 | 2.5015 | 2.2901
|  | COTTISFORD | CT |  |  | 4.7942 | 4.7942 | 4.7942 | 4.7942 | 4.7456 | 4.6957 | 4.6442 | 4.5877 | 4.4964 | 4.4843 | 4.3868 | 4.0398 | 3.6598 | 3.4693 | 3.9982 | 3.9968 | 3.995 | 3.9913 | 3.9392 | 3.8856 | 3.8307 | 3.7718 | 3.6782 | 3.6637 | 3.6135 | 3.3687 | 3.0941 | 3.0074 | 3.9794 | 3.9644 | 3.9447 | 3.9033 | 3.8145 | 3.7246 | 3.6335 | 3.5512 | 3.4344 | 3.3947 | 3.2704 | 2.9028 | 2.5015 | 2.2901
|  | COTTISFORD | LW |  |  | 4.7942 | 4.7942 | 4.7942 | 4.7942 | 4.7918 | 4.7868 | 4.7775 | 4.7633 | 4.7338 | 4.7286 | 4.6338 | 4.4539 | 4.2048 | 4.0794 | 3.9978 | 3.9963 | 3.9943 | 3.9899 | 3.9833 | 3.9743 | 3.9626 | 3.9461 | 3.9143 | 3.9066 | 3.872 | 3.7941 | 3.6505 | 3.629 | 3.976 | 3.9586 | 3.9358 | 3.8876 | 3.8384 | 3.7872 | 3.7518 | 3.7118 | 3.6568 | 3.624 | 3.5151 | 3.3147 | 3.0443 | 2.898
|  | COTTISFORD | ST |  |  | 4.7942 | 4.7942 | 4.7942 | 4.7942 | 4.7559 | 4.7166 | 4.6755 | 4.6319 | 4.5621 | 4.5375 | 4.4527 | 4.3183 | 3.992 | 3.8357 | 3.9982 | 3.9969 | 3.9954 | 3.9927 | 3.9513 | 3.9081 | 3.8653 | 3.8199 | 3.7485 | 3.7222 | 3.6325 | 3.5474 | 3.2891 | 3.2005 | 3.9794 | 3.965 | 3.9481 | 3.9191 | 3.8452 | 3.7629 | 3.7018 | 3.6384 | 3.5511 | 3.5077 | 3.368 | 3.2014 | 2.8614 | 2.6915
|  | COTTISFORD | SP |  |  | 4.7942 | 4.7942 | 4.7942 | 4.7942 | 4.7942 | 4.7941 | 4.794 | 4.7939 | 4.7936 | 4.7924 | 4.7857 | 4.7805 | 4.7577 | 4.7359 | 3.9997 | 3.9995 | 3.9993 | 3.9992 | 3.9985 | 3.9976 | 3.9969 | 3.9962 | 3.9951 | 3.9933 | 3.9846 | 3.9765 | 3.9507 | 3.9261 | 3.9961 | 3.9944 | 3.9926 | 3.991 | 3.9833 | 3.974 | 3.9671 | 3.9603 | 3.9513 | 3.9428 | 3.9149 | 3.876 | 3.8207 | 3.768
BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES | MINIMUM HEADROOM | SU 70990 69570 | YES | 44.3821 | 44.3821 | 44.3821 | 44.3821 | 44.3565 | 44.33 | 44.3024 | 44.2738 | 44.2199 | 44.2124 | 44.1868 | 44.1485 | 44.0781 | 44.0732 | 33.0887 | 33.0865 | 33.0839 | 33.0789 | 33.0481 | 33.0163 | 32.9814 | 32.9455 | 32.8843 | 32.8691 | 32.8193 | 32.7288 | 32.5973 | 32.5313 | 32.7106 | 32.7106 | 32.7106 | 32.7106 | 32.685 | 32.6586 | 32.631 | 32.6024 | 32.5485 | 32.541 | 32.5154 | 32.3474 | 32.0892 | 31.8963
|  | COURAGES | CT |  |  | 44.3821 | 44.3821 | 44.3821 | 44.3821 | 44.3778 | 44.3734 | 44.3689 | 44.3642 | 44.3498 | 44.348 | 44.3421 | 44.3151 | 44.2872 | 44.2808 | 33.0888 | 33.0867 | 33.0843 | 33.0796 | 33.0704 | 33.0609 | 33.0514 | 33.0394 | 33.0178 | 33.0083 | 32.9782 | 32.8989 | 32.81 | 32.7424 | 32.7106 | 32.7106 | 32.7106 | 32.7106 | 32.7063 | 32.7019 | 32.6975 | 32.6928 | 32.6784 | 32.6766 | 32.6707 | 32.5249 | 32.3094 | 32.115
|  | COURAGES | LW |  |  | 44.3821 | 44.3821 | 44.3821 | 44.3821 | 44.3565 | 44.33 | 44.3024 | 44.2738 | 44.2199 | 44.2124 | 44.1868 | 44.1485 | 44.0781 | 44.0732 | 33.0887 | 33.0865 | 33.0839 | 33.0789 | 33.0481 | 33.0163 | 32.9814 | 32.9455 | 32.8843 | 32.8691 | 32.8193 | 32.7288 | 32.5973 | 32.5313 | 32.7106 | 32.7106 | 32.7106 | 32.7106 | 32.685 | 32.6586 | 32.631 | 32.6024 | 32.5485 | 32.541 | 32.5154 | 32.3474 | 32.0892 | 31.8963
|  | COURAGES | ST |  |  | 44.3821 | 44.3821 | 44.3821 | 44.3821 | 44.3787 | 44.3752 | 44.3717 | 44.3681 | 44.3597 | 44.3568 | 44.3477 | 44.3403 | 44.3193 | 44.3132 | 33.1467 | 33.0881 | 33.0864 | 33.0838 | 33.077 | 33.0694 | 33.0607 | 33.0519 | 33.0385 | 33.0304 | 33.0048 | 32.9617 | 32.9006 | 32.8555 | 32.7106 | 32.7106 | 32.7106 | 32.7106 | 32.7073 | 32.7038 | 32.7003 | 32.6967 | 32.6882 | 32.6854 | 32.6762 | 32.6657 | 32.5217 | 32.3953
|  | COURAGES | SP |  |  | 44.3821 | 44.3821 | 44.3821 | 44.3821 | 44.3816 | 44.3812 | 44.3807 | 44.3803 | 44.3796 | 44.3776 | 44.3714 | 44.3684 | 44.359 | 44.3512 | 33.1484 | 33.1479 | 33.0905 | 33.0902 | 33.0889 | 33.0873 | 33.085 | 33.0827 | 33.0797 | 33.0757 | 33.0631 | 33.0458 | 33.0192 | 32.9934 | 32.7106 | 32.7106 | 32.7106 | 32.7106 | 32.7102 | 32.7097 | 32.7093 | 32.7088 | 32.7081 | 32.7062 | 32.6999 | 32.697 | 32.6876 | 32.6798
BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE | MINIMUM HEADROOM | SU 85415 55937 | YES | 27.6368 | 27.6335 | 27.6292 | 27.6235 | 27.618 | 27.6123 | 27.6019 | 27.5915 | 27.5809 | 27.5696 | 27.535 | 27.4678 | 27.3695 | 26.5 | 27.1099 | 27.1061 | 27.1012 | 27.0948 | 27.0885 | 27.0821 | 27.0702 | 27.0584 | 27.0468 | 27.0344 | 26.9966 | 26.553 | 25.5527 | 24.5581 | 26.5023 | 26.4761 | 26.4424 | 26.3983 | 26.3548 | 26.3104 | 26.229 | 26.1475 | 26.0673 | 25.9818 | 25.7214 | 25.2152 | 24.6497 | 24.0874
|  | COVE | CT |  |  | 27.6372 | 27.6341 | 27.6301 | 27.6252 | 27.6204 | 27.6154 | 27.6103 | 27.5999 | 27.5897 | 27.5783 | 27.5437 | 27.4766 | 27.4015 | 26.6021 | 27.1103 | 27.1068 | 27.1023 | 27.0968 | 27.0913 | 27.0856 | 27.0798 | 27.0679 | 27.0563 | 27.0439 | 27.0061 | 26.6691 | 25.6689 | 24.6749 | 26.5051 | 26.4811 | 26.4501 | 26.4116 | 26.3737 | 26.3347 | 26.2946 | 26.2131 | 26.1329 | 26.0474 | 25.7871 | 25.2808 | 24.7154 | 24.1535
|  | COVE | LW |  |  | 27.6368 | 27.6335 | 27.6292 | 27.6235 | 27.618 | 27.6123 | 27.6019 | 27.5915 | 27.5809 | 27.5696 | 27.535 | 27.4678 | 27.3695 | 26.5 | 27.1099 | 27.1061 | 27.1012 | 27.0948 | 27.0885 | 27.0821 | 27.0702 | 27.0584 | 27.0468 | 27.0344 | 26.9966 | 26.553 | 25.5527 | 24.5581 | 26.5023 | 26.4761 | 26.4424 | 26.3983 | 26.3548 | 26.3104 | 26.229 | 26.1475 | 26.0673 | 25.9818 | 25.7214 | 25.2152 | 24.6497 | 24.0874
|  | COVE | ST |  |  | 27.639 | 27.6376 | 27.6359 | 27.635 | 27.6338 | 27.6324 | 27.6269 | 27.6213 | 27.6143 | 27.6069 | 27.5841 | 27.5385 | 27.4896 | 27.4416 | 27.1124 | 27.1108 | 27.1089 | 27.1079 | 27.1066 | 27.1049 | 27.0986 | 27.0923 | 27.0843 | 27.0759 | 27.0502 | 27.0003 | 26.8423 | 26.2027 | 26.5196 | 26.5084 | 26.4954 | 26.4881 | 26.4792 | 26.4678 | 26.4243 | 26.3808 | 26.326 | 26.2677 | 26.0909 | 25.7473 | 25.3788 | 25.0172
|  | COVE | SP |  |  | 27.6391 | 27.6382 | 27.6372 | 27.6369 | 27.6359 | 27.6347 | 27.6328 | 27.6309 | 27.6286 | 27.6257 | 27.617 | 27.5997 | 27.58 | 27.5597 | 27.1126 | 27.1115 | 27.1103 | 27.11 | 27.1089 | 27.1075 | 27.1054 | 27.1033 | 27.1006 | 27.0973 | 27.0874 | 27.0677 | 27.0457 | 27.0236 | 26.5207 | 26.5131 | 26.5052 | 26.5029 | 26.4952 | 26.4859 | 26.4711 | 26.4564 | 26.4381 | 26.4154 | 26.3468 | 26.2113 | 26.0599 | 25.9074
COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL | MINIMUM HEADROOM | SP 56113 03074 | NO | 39.0159 | 38.9985 | 38.981 | 37.9172 | 37.8103 | 37.6993 | 37.5834 | 37.4626 | 37.3167 | 37.2726 | 37.1274 | 36.8648 | 35.7416 | 33.7123 | 36.8952 | 36.8757 | 36.8547 | 35.7837 | 35.6703 | 35.5516 | 35.4182 | 35.2807 | 35.1166 | 35.048 | 34.7762 | 33.6797 | 31.2689 | 28.9463 | 37.278 | 37.2567 | 37.2329 | 36.1561 | 36.0375 | 35.9127 | 35.7654 | 35.6163 | 35.4447 | 35.3662 | 35.0932 | 33.4725 | 31.202 | 29.016
|  | COWLEY LOCAL | CT |  |  | 39.0996 | 39.0891 | 39.0787 | 38.4404 | 38.387 | 38.3327 | 38.2775 | 38.2209 | 38.1592 | 38.1366 | 38.0648 | 37.2274 | 35.8762 | 33.8335 | 36.9774 | 36.9638 | 36.9483 | 36.2998 | 36.237 | 36.1722 | 36.104 | 36.0284 | 35.9485 | 35.8877 | 35.6893 | 33.866 | 31.3778 | 29.0418 | 37.359 | 37.3427 | 37.3233 | 36.6667 | 36.5963 | 36.5231 | 36.4445 | 36.3597 | 36.2707 | 36.2057 | 36.0061 | 33.6622 | 31.3239 | 29.1161
|  | COWLEY LOCAL | LW |  |  | 39.0159 | 38.9985 | 38.981 | 37.9172 | 37.8103 | 37.6993 | 37.5834 | 37.4626 | 37.3167 | 37.2726 | 37.1274 | 36.8648 | 35.7416 | 33.7123 | 36.8952 | 36.8757 | 36.8547 | 35.7837 | 35.6703 | 35.5516 | 35.4182 | 35.2807 | 35.1166 | 35.048 | 34.7762 | 33.6797 | 31.2689 | 28.9463 | 37.278 | 37.2567 | 37.2329 | 36.1561 | 36.0375 | 35.9127 | 35.7654 | 35.6163 | 35.4447 | 35.3662 | 35.0932 | 33.4725 | 31.202 | 29.016
|  | COWLEY LOCAL | ST |  |  | 39.1415 | 39.1345 | 39.1275 | 38.702 | 38.6664 | 38.63 | 38.593 | 38.5548 | 38.5127 | 38.4953 | 38.4347 | 38.3403 | 38.2122 | 38.1042 | 37.0225 | 37.0146 | 37.0061 | 36.5779 | 36.5397 | 36.4997 | 36.4533 | 36.407 | 36.3551 | 36.3278 | 36.2323 | 35.9846 | 35.3671 | 34.0301 | 37.4066 | 37.398 | 37.3883 | 36.958 | 36.9176 | 36.8746 | 36.8208 | 36.768 | 36.7083 | 36.6731 | 36.5593 | 36.3015 | 35.2492 | 33.8763
|  | COWLEY LOCAL | SP |  |  | 39.1833 | 39.1798 | 39.1763 | 38.9636 | 38.9461 | 38.9286 | 38.9111 | 38.8935 | 38.8758 | 38.8676 | 38.8399 | 38.7997 | 38.753 | 38.6896 | 37.065 | 37.0612 | 37.0571 | 36.8434 | 36.8248 | 36.8057 | 36.7845 | 36.7639 | 36.743 | 36.731 | 36.6919 | 36.6288 | 36.5509 | 36.4261 | 37.4496 | 37.4456 | 37.4409 | 37.2265 | 37.2069 | 37.1866 | 37.1625 | 37.1395 | 37.116 | 37.1009 | 37.0527 | 36.9714 | 36.8781 | 36.7439
BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD | MINIMUM HEADROOM | SU 78275 50779 | YES | 12.5727 | 12.5659 | 12.5569 | 12.5388 | 12.5187 | 12.4978 | 12.4837 | 12.4666 | 12.4389 | 12.4283 | 12.3893 | 12.3103 | 12.1879 | 12.0842 | 11.4201 | 11.3427 | 11.2398 | 11.0337 | 10.8283 | 10.6401 | 10.5584 | 10.4731 | 10.3769 | 10.2928 | 10.0417 | 9.6107 | 9.1314 | 8.7441 | 11.9935 | 11.9879 | 11.9804 | 11.9655 | 11.9484 | 11.9302 | 11.9173 | 11.9013 | 11.8748 | 11.8653 | 11.8298 | 11.7566 | 11.497 | 11.0313
|  | COXMOOR WOOD | CT |  |  | 12.574 | 12.5682 | 12.5605 | 12.5451 | 12.5293 | 12.5145 | 12.4991 | 12.4896 | 12.4767 | 12.4685 | 12.442 | 12.358 | 12.2676 | 12.2031 | 11.4356 | 11.3693 | 11.2811 | 11.1059 | 10.9323 | 10.7774 | 10.6225 | 10.5448 | 10.4634 | 10.3818 | 10.1432 | 9.7071 | 9.2599 | 8.8616 | 11.9947 | 11.9898 | 11.9834 | 11.9707 | 11.9574 | 11.9449 | 11.9319 | 11.9236 | 11.9117 | 11.9047 | 11.8818 | 11.8035 | 11.6364 | 11.1599
|  | COXMOOR WOOD | LW |  |  | 12.5727 | 12.5659 | 12.5569 | 12.5388 | 12.5187 | 12.4978 | 12.4837 | 12.4666 | 12.4389 | 12.4283 | 12.3893 | 12.3103 | 12.1879 | 12.0842 | 11.4201 | 11.3427 | 11.2398 | 11.0337 | 10.8283 | 10.6401 | 10.5584 | 10.4731 | 10.3769 | 10.2928 | 10.0417 | 9.6107 | 9.1314 | 8.7441 | 11.9935 | 11.9879 | 11.9804 | 11.9655 | 11.9484 | 11.9302 | 11.9173 | 11.9013 | 11.8748 | 11.8653 | 11.8298 | 11.7566 | 11.497 | 11.0313
|  | COXMOOR WOOD | ST |  |  | 12.5763 | 12.5723 | 12.5675 | 12.5598 | 12.5498 | 12.5388 | 12.5325 | 12.5256 | 12.5162 | 12.509 | 12.4825 | 12.4433 | 12.3629 | 12.32 | 11.4611 | 11.4159 | 11.3615 | 11.2731 | 11.1649 | 11.0488 | 10.9931 | 10.9366 | 10.8804 | 10.8231 | 10.6532 | 10.3786 | 10.0681 | 9.7992 | 11.9965 | 11.9932 | 11.9893 | 11.9829 | 11.9745 | 11.9652 | 11.9598 | 11.9536 | 11.945 | 11.9386 | 11.9145 | 11.8792 | 11.8025 | 11.7633
|  | COXMOOR WOOD | SP |  |  | 12.585 | 12.5791 | 12.578 | 12.5769 | 12.5741 | 12.5714 | 12.5696 | 12.5678 | 12.5653 | 12.5627 | 12.5528 | 12.5405 | 12.515 | 12.4904 | 11.5607 | 11.493 | 11.4812 | 11.4689 | 11.4366 | 11.4059 | 11.3862 | 11.3664 | 11.3409 | 11.3188 | 11.2534 | 11.1511 | 11.041 | 10.9369 | 12.0038 | 11.9988 | 11.998 | 11.9971 | 11.9947 | 11.9925 | 11.991 | 11.9894 | 11.9874 | 11.9851 | 11.9761 | 11.9653 | 11.9411 | 11.9178
MANNINGTON GSP | LYTCHETT | CREEKMOOR | MINIMUM HEADROOM | SZ 00552 94121 | YES | 25.9883 | 25.8762 | 25.8661 | 25.8486 | 25.5839 | 25.3144 | 25.0408 | 24.7517 | 24.3181 | 24.2429 | 24.0045 | 23.0849 | 22.112 | 21.7624 | 23.7417 | 23.7042 | 23.7008 | 23.695 | 23.4417 | 23.184 | 22.9223 | 22.582 | 22.023 | 21.8142 | 21.1652 | 19.4193 | 17.4887 | 16.173 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.5348 | 23.2831 | 23.0272 | 22.76 | 22.3481 | 22.2959 | 21.981 | 20.2307 | 18.318 | 17.0315
|  | CREEKMOOR | CT |  |  | 25.9883 | 25.8762 | 25.8661 | 25.8486 | 25.5839 | 25.3144 | 25.0408 | 24.7517 | 24.3181 | 24.2429 | 24.0045 | 23.0849 | 22.112 | 21.7624 | 23.7417 | 23.7042 | 23.7008 | 23.695 | 23.4417 | 23.184 | 22.9223 | 22.582 | 22.023 | 21.8142 | 21.1652 | 19.4193 | 17.4887 | 16.173 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.5348 | 23.2831 | 23.0272 | 22.76 | 22.3481 | 22.2959 | 21.981 | 20.2307 | 18.318 | 17.0315
|  | CREEKMOOR | LW |  |  | 25.9916 | 25.882 | 25.8749 | 25.8642 | 25.8203 | 25.7748 | 25.7171 | 25.6581 | 25.5803 | 25.5495 | 25.452 | 25.2683 | 25.022 | 24.8554 | 23.7428 | 23.7061 | 23.7038 | 23.7002 | 23.6635 | 23.6255 | 23.5824 | 23.5381 | 23.4253 | 23.2611 | 22.7529 | 21.743 | 20.5439 | 19.4107 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.7492 | 23.715 | 23.6793 | 23.6423 | 23.5861 | 23.5783 | 23.5516 | 22.5551 | 21.3688 | 20.2649
|  | CREEKMOOR | ST |  |  | 25.9942 | 25.9895 | 25.883 | 25.8784 | 25.8727 | 25.8655 | 25.849 | 25.8328 | 25.818 | 25.8023 | 25.7542 | 25.6571 | 25.5518 | 25.4486 | 23.7436 | 23.7421 | 23.7065 | 23.7049 | 23.703 | 23.7006 | 23.6951 | 23.6897 | 23.6847 | 23.6795 | 23.4696 | 22.8098 | 22.0936 | 21.3893 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.6255 | 22.9061 | 22.2015
|  | CREEKMOOR | SP |  |  | 25.9968 | 25.9944 | 25.8905 | 25.8899 | 25.8808 | 25.8713 | 25.8596 | 25.8478 | 25.8309 | 25.7938 | 25.6771 | 25.5918 | 25.4006 | 25.2326 | 23.7445 | 23.7437 | 23.709 | 23.7088 | 23.701 | 23.6932 | 23.6846 | 23.6759 | 23.6628 | 23.6299 | 23.5255 | 23.4659 | 23.1659 | 22.7376 | 23.7823 | 23.7823 | 23.7823 | 23.7823 | 23.7752 | 23.7682 | 23.7612 | 23.7541 | 23.7429 | 23.712 | 23.6139 | 23.5672 | 23.4201 | 23.2971
MINETY GSP | CIRENCESTER BSP | CRICKLADE | MINIMUM HEADROOM | SU 09400 93270 | NO | 18.3114 | 18.3114 | 18.3114 | 18.3114 | 18.3056 | 18.2998 | 18.294 | 18.2825 | 18.2583 | 18.2524 | 18.1666 | 17.9363 | 17.3723 | 16.9101 | 11.9809 | 11.9777 | 11.9734 | 11.9644 | 11.9531 | 11.9389 | 11.9249 | 11.9076 | 11.8782 | 11.8684 | 11.7101 | 11.0901 | 10.3937 | 9.8014 | 12.1656 | 12.0996 | 12.0118 | 11.8259 | 11.6431 | 11.4591 | 11.3119 | 11.1996 | 11.0843 | 10.9663 | 10.6006 | 9.9817 | 9.2946 | 8.7114
|  | CRICKLADE | CT |  |  | 18.3114 | 18.3114 | 18.3114 | 18.3114 | 18.3106 | 18.3091 | 18.3068 | 18.3035 | 18.2962 | 18.2949 | 18.2879 | 17.9533 | 17.426 | 16.951 | 11.981 | 11.9779 | 11.9737 | 11.965 | 11.9557 | 11.9458 | 11.9352 | 11.9266 | 11.9141 | 11.9072 | 11.7247 | 11.0977 | 10.4382 | 9.8331 | 12.1689 | 12.1038 | 12.0183 | 11.8374 | 11.6613 | 11.4862 | 11.3119 | 11.1996 | 11.0843 | 10.9664 | 10.615 | 9.99 | 9.3397 | 8.7437
|  | CRICKLADE | LW |  |  | 18.3114 | 18.3114 | 18.3114 | 18.3114 | 18.3088 | 18.3032 | 18.2945 | 18.2825 | 18.2583 | 18.2541 | 18.2328 | 17.9363 | 17.3723 | 16.9101 | 11.9809 | 11.9777 | 11.9734 | 11.9644 | 11.9531 | 11.9389 | 11.9249 | 11.9076 | 11.8782 | 11.8684 | 11.7101 | 11.0901 | 10.3937 | 9.8014 | 12.1665 | 12.0996 | 12.0118 | 11.8259 | 11.6431 | 11.4591 | 11.3403 | 11.2193 | 11.087 | 10.9663 | 10.6006 | 9.9817 | 9.2946 | 8.7114
|  | CRICKLADE | ST |  |  | 18.3114 | 18.3114 | 18.3114 | 18.3114 | 18.3109 | 18.3097 | 18.308 | 18.3055 | 18.2999 | 18.2972 | 18.2826 | 18.2636 | 18.0378 | 17.7263 | 11.9809 | 11.9777 | 11.974 | 11.9676 | 11.9593 | 11.9487 | 11.943 | 11.9365 | 11.9273 | 11.9208 | 11.895 | 11.6704 | 11.2271 | 10.8224 | 12.1656 | 12.1006 | 12.0238 | 11.8923 | 11.7301 | 11.5343 | 11.4494 | 11.3648 | 11.2854 | 11.2031 | 10.9567 | 10.5607 | 10.1168 | 9.7181
|  | CRICKLADE | SP |  |  | 18.3114 | 18.3114 | 18.3114 | 18.3114 | 18.3056 | 18.2998 | 18.294 | 18.288 | 18.2787 | 18.2524 | 18.1666 | 18.1241 | 17.9834 | 17.863 | 11.9846 | 11.9843 | 11.984 | 11.9837 | 11.9764 | 11.9689 | 11.9617 | 11.9544 | 11.9433 | 11.9155 | 11.8255 | 11.776 | 11.6288 | 11.5021 | 12.2441 | 12.2371 | 12.2304 | 12.2241 | 12.1883 | 12.1471 | 12.1132 | 12.0795 | 12.0343 | 11.9773 | 11.8021 | 11.617 | 11.3396 | 11.0903
MELKSHAM GSP | FROME BSP | CROCKERTON | MINIMUM HEADROOM | ST 87736 43371 | YES | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6626 | 21.6577 | 21.6527 | 21.6477 | 21.6398 | 21.618 | 21.5486 | 21.5155 | 21.4115 | 21.3245 | 13.0563 | 13.0393 | 13.0365 | 13.0304 | 13.0245 | 13.0187 | 13.0056 | 12.9926 | 12.9797 | 12.8848 | 12.3769 | 11.5449 | 10.688 | 9.8457 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4123 | 13.4073 | 13.4024 | 13.3974 | 13.3895 | 13.3676 | 13.2982 | 13.2652 | 12.8126 | 12.0295
|  | CROCKERTON | CT |  |  | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.4856 | 13.0565 | 13.0397 | 13.0371 | 13.0315 | 13.0261 | 13.0207 | 13.0154 | 13.0024 | 12.9895 | 12.9757 | 12.4989 | 11.6668 | 10.8102 | 9.9685 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 12.9262 | 12.1436
|  | CROCKERTON | LW |  |  | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.3803 | 13.0563 | 13.0393 | 13.0365 | 13.0304 | 13.0245 | 13.0187 | 13.0056 | 12.9926 | 12.9797 | 12.8848 | 12.3769 | 11.5449 | 10.688 | 9.8457 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 12.8126 | 12.0295
|  | CROCKERTON | ST |  |  | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 13.0568 | 13.0551 | 13.0383 | 13.0348 | 13.0306 | 13.0255 | 13.0196 | 13.0138 | 13.0051 | 12.9956 | 12.9119 | 12.3585 | 11.8068 | 11.2588 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.3434
|  | CROCKERTON | SP |  |  | 21.6677 | 21.6677 | 21.6677 | 21.6677 | 21.6626 | 21.6577 | 21.6527 | 21.6477 | 21.6398 | 21.618 | 21.5486 | 21.5155 | 21.4115 | 21.3245 | 13.0588 | 13.0586 | 13.0584 | 13.0582 | 13.0521 | 13.0461 | 13.0393 | 13.0325 | 13.0223 | 12.9967 | 12.9167 | 12.8668 | 12.7468 | 12.6447 | 13.4173 | 13.4173 | 13.4173 | 13.4173 | 13.4123 | 13.4073 | 13.4024 | 13.3974 | 13.3895 | 13.3676 | 13.2982 | 13.2652 | 13.1611 | 13.0741
BRAMLEY (FLEE) | PYESTOCK BSP | Crookham (Church) | MINIMUM HEADROOM | SU 81702 53403 | YES | 33.0002 | 33.0002 | 33.0002 | 33.0002 | 32.9626 | 32.9242 | 32.885 | 32.8442 | 32.7808 | 32.7592 | 32.6886 | 32.6303 | 31.7558 | 30.8402 | 32.3011 | 32.2945 | 32.2858 | 32.2674 | 32.2358 | 31.8782 | 31.4687 | 31.2871 | 31.0976 | 30.9168 | 30.3717 | 29.3386 | 28.208 | 27.1309 | 32.3424 | 32.3424 | 32.3424 | 32.3424 | 32.3048 | 32.1808 | 31.7815 | 31.6042 | 31.419 | 31.2428 | 30.7115 | 29.7038 | 28.5913 | 27.5139
|  | Crookham (Church) | CT |  |  | 33.0002 | 33.0002 | 33.0002 | 33.0002 | 32.9864 | 32.9721 | 32.9575 | 32.942 | 32.9177 | 32.9145 | 32.9037 | 32.7234 | 31.7558 | 30.8402 | 32.3011 | 32.2945 | 32.2858 | 32.2674 | 32.2358 | 31.8782 | 31.4687 | 31.2871 | 31.0976 | 30.9168 | 30.3717 | 29.3386 | 28.208 | 27.1309 | 32.3424 | 32.3424 | 32.3424 | 32.3424 | 32.3286 | 32.1808 | 31.7815 | 31.6042 | 31.419 | 31.2428 | 30.7115 | 29.7038 | 28.5913 | 27.5139
|  | Crookham (Church) | LW |  |  | 33.0002 | 33.0002 | 33.0002 | 33.0002 | 32.9996 | 32.9984 | 32.9964 | 32.9938 | 32.9884 | 32.9875 | 32.9827 | 32.9644 | 32.2683 | 31.3679 | 32.3021 | 32.2962 | 32.2884 | 32.272 | 32.2554 | 32.091 | 31.9218 | 31.7528 | 31.5822 | 31.4039 | 30.8646 | 29.8758 | 28.7835 | 27.7216 | 32.3424 | 32.3424 | 32.3424 | 32.3424 | 32.3418 | 32.3406 | 32.2238 | 32.0592 | 31.8929 | 31.7191 | 31.1937 | 30.2303 | 29.1658 | 28.1048
|  | Crookham (Church) | ST |  |  | 33.0002 | 33.0002 | 33.0002 | 33.0002 | 32.9626 | 32.9242 | 32.885 | 32.8442 | 32.7808 | 32.7592 | 32.6886 | 32.6303 | 32.4374 | 32.36 | 32.3047 | 32.3008 | 32.2963 | 32.2884 | 32.2412 | 32.1913 | 32.1455 | 32.0983 | 32.0299 | 31.934 | 31.5015 | 30.7844 | 29.8968 | 29.1511 | 32.3424 | 32.3424 | 32.3424 | 32.3424 | 32.3048 | 32.2664 | 32.2272 | 32.1864 | 32.1231 | 32.1014 | 31.8065 | 31.1065 | 30.2369 | 29.5089
|  | Crookham (Church) | SP |  |  | 33.0002 | 33.0002 | 33.0002 | 33.0002 | 33.0002 | 33.0002 | 33.0002 | 33.0001 | 33.0001 | 32.9999 | 32.9987 | 32.9978 | 32.9934 | 32.989 | 32.3091 | 32.3085 | 32.3079 | 32.3074 | 32.305 | 32.3021 | 32.2998 | 32.2975 | 32.2945 | 32.2922 | 32.2849 | 32.2726 | 32.256 | 32.2396 | 32.3424 | 32.3424 | 32.3424 | 32.3424 | 32.3424 | 32.3424 | 32.3424 | 32.3423 | 32.3423 | 32.3421 | 32.3409 | 32.34 | 32.3356 | 32.3312
BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE | MINIMUM HEADROOM | SU 84470 64352 | YES | 37.3161 | 37.3039 | 37.2916 | 36.5434 | 36.4792 | 36.4119 | 36.3413 | 36.2671 | 36.1798 | 36.1508 | 35.985 | 34.3663 | 32.9147 | 31.5436 | 35.4383 | 35.3787 | 35.3296 | 34.477 | 34.3032 | 33.9584 | 33.446 | 32.9593 | 32.4518 | 32.016 | 30.6692 | 28.7916 | 27.0954 | 25.5058 | 35.9576 | 35.9453 | 35.933 | 35.1667 | 35.0545 | 34.9373 | 34.8398 | 34.5295 | 34.026 | 33.6007 | 32.2863 | 30.4528 | 28.7983 | 27.2459
|  | CROWTHORNE | CT |  |  | 37.375 | 37.3676 | 37.3603 | 36.9114 | 36.8737 | 36.8353 | 36.796 | 36.7557 | 36.7111 | 36.695 | 36.482 | 34.4426 | 32.9149 | 31.5436 | 35.4998 | 35.4469 | 35.4052 | 34.8647 | 34.7256 | 34.5811 | 33.7993 | 33.3463 | 32.8744 | 32.4514 | 31.1497 | 28.8514 | 27.0954 | 25.5058 | 36.0164 | 36.0091 | 36.0017 | 35.5433 | 35.4612 | 35.3763 | 35.2884 | 34.9122 | 34.4514 | 34.039 | 32.7696 | 30.5154 | 28.7983 | 27.2459
|  | CROWTHORNE | LW |  |  | 37.3161 | 37.3039 | 37.2916 | 36.5434 | 36.4792 | 36.4119 | 36.3413 | 36.2671 | 36.1798 | 36.1508 | 35.985 | 34.3663 | 32.9147 | 31.5568 | 35.4383 | 35.3787 | 35.3296 | 34.477 | 34.3032 | 33.9584 | 33.446 | 32.9593 | 32.4518 | 32.016 | 30.6692 | 28.7916 | 27.1117 | 25.5354 | 35.9576 | 35.9453 | 35.933 | 35.1667 | 35.0545 | 34.9373 | 34.8398 | 34.5295 | 34.026 | 33.6007 | 32.2863 | 30.4528 | 28.8118 | 27.2726
|  | CROWTHORNE | ST |  |  | 37.4044 | 37.3995 | 37.3946 | 37.0953 | 37.0702 | 37.0445 | 37.0181 | 36.9909 | 36.9603 | 36.9476 | 36.9026 | 36.8331 | 36.732 | 35.995 | 35.5379 | 35.5144 | 35.4687 | 35.1355 | 35.0561 | 34.9514 | 34.8763 | 34.8032 | 34.7353 | 34.6867 | 33.8545 | 32.6537 | 31.5838 | 30.5736 | 36.0459 | 36.041 | 36.0361 | 35.7368 | 35.7116 | 35.6561 | 35.6084 | 35.5611 | 35.5142 | 35.4857 | 35.3919 | 34.2396 | 33.1948 | 32.2087
|  | CROWTHORNE | SP |  |  | 37.4339 | 37.4314 | 37.429 | 37.2793 | 37.267 | 37.2547 | 37.2424 | 37.23 | 37.2175 | 37.2116 | 37.1913 | 37.1623 | 37.1262 | 37.0783 | 35.5828 | 35.5744 | 35.547 | 35.3913 | 35.3668 | 35.34 | 35.316 | 35.293 | 35.2686 | 35.254 | 35.2015 | 35.1142 | 35.0307 | 34.9392 | 36.0753 | 36.0729 | 36.0704 | 35.9208 | 35.9085 | 35.8962 | 35.8838 | 35.8715 | 35.8589 | 35.8531 | 35.8327 | 35.7936 | 35.7368 | 35.6698
EALING GSP | EALING (D) | DEAN GARDENS | MINIMUM HEADROOM | TQ 16546 80368 | YES | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.4517 | 13.2742 | 13.0888 | 12.8966 | 12.6048 | 12.5643 | 12.4258 | 12.2181 | 11.4046 | 10.8064 | 13.1721 | 13.1694 | 13.167 | 13.1631 | 12.9935 | 12.8138 | 12.626 | 12.4315 | 12.1373 | 12.0945 | 11.9398 | 11.2144 | 10.1587 | 9.458 | 13.3107 | 13.3073 | 13.3043 | 13.2993 | 13.1304 | 12.95 | 12.7616 | 12.5665 | 12.2717 | 12.2282 | 12.0791 | 11.447 | 10.4446 | 9.7437
|  | DEAN GARDENS | CT |  |  | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.5847 | 13.0223 | 12.4521 | 13.1721 | 13.1694 | 13.167 | 13.1631 | 13.1591 | 13.155 | 13.1508 | 13.1484 | 13.1461 | 13.0995 | 12.9252 | 12.4076 | 11.7441 | 11.0714 | 13.3107 | 13.3073 | 13.3043 | 13.2993 | 13.2943 | 13.289 | 13.2837 | 13.2807 | 13.2778 | 13.2747 | 13.1331 | 12.6572 | 12.0298 | 11.3569
|  | DEAN GARDENS | LW |  |  | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.4517 | 13.2742 | 13.0888 | 12.8966 | 12.6048 | 12.5643 | 12.4258 | 12.2181 | 11.4046 | 10.8064 | 13.1731 | 13.171 | 13.1696 | 13.1676 | 12.9935 | 12.8138 | 12.626 | 12.4315 | 12.1373 | 12.0945 | 11.9398 | 11.2144 | 10.1587 | 9.458 | 13.3119 | 13.3094 | 13.3076 | 13.305 | 13.1304 | 12.95 | 12.7616 | 12.5665 | 12.2717 | 12.2282 | 12.0791 | 11.447 | 10.4446 | 9.7437
|  | DEAN GARDENS | ST |  |  | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.5076 | 13.3897 | 13.2694 | 13.145 | 12.9527 | 12.8874 | 12.6791 | 12.5118 | 12.004 | 11.5992 | 13.1739 | 13.1727 | 13.1721 | 13.1716 | 13.055 | 12.9362 | 12.8137 | 12.6873 | 12.4934 | 12.4265 | 12.2124 | 11.9028 | 10.9546 | 10.3827 | 13.313 | 13.3115 | 13.3107 | 13.3101 | 13.1933 | 13.0743 | 12.9513 | 12.8243 | 12.63 | 12.5627 | 12.347 | 12.1034 | 11.1908 | 10.6533
|  | DEAN GARDENS | SP |  |  | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.6237 | 13.1741 | 13.1733 | 13.1729 | 13.1727 | 13.1723 | 13.1718 | 13.171 | 13.1701 | 13.1692 | 13.1685 | 13.1663 | 13.159 | 13.1489 | 12.9788 | 13.3133 | 13.3122 | 13.3117 | 13.3115 | 13.311 | 13.3103 | 13.3092 | 13.3082 | 13.307 | 13.3062 | 13.3033 | 13.2941 | 13.2813 | 13.1823
COWLEY GSP | YARNTON BSP | DEDDINGTON | MINIMUM HEADROOM | SP 46729 30325 | YES | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.741 | 6.7263 | 6.6664 | 6.6074 | 6.5421 | 6.4897 | 6.3343 | 6.0521 | 5.7537 | 5.4945 | 4.9281 | 4.7769 | 4.7531 | 4.7026 | 4.6424 | 4.5823 | 4.5225 | 4.4767 | 4.4244 | 4.3861 | 4.2711 | 4.059 | 3.8318 | 3.6427 | 6.0935 | 6.0785 | 6.0762 | 6.0712 | 6.0527 | 6.0333 | 6.0146 | 5.9953 | 5.9678 | 5.9609 | 5.9389 | 5.6579 | 5.3218 | 5.0256
|  | DEDDINGTON | CT |  |  | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7439 | 6.7323 | 6.6664 | 6.6074 | 6.5421 | 6.4897 | 6.3343 | 6.0521 | 5.7537 | 5.4945 | 4.9281 | 4.7769 | 4.7531 | 4.7026 | 4.6424 | 4.5823 | 4.5225 | 4.4767 | 4.4244 | 4.3861 | 4.2723 | 4.059 | 3.8318 | 3.6427 | 6.0935 | 6.0785 | 6.0762 | 6.0712 | 6.055 | 6.0386 | 6.0221 | 6.0064 | 5.9842 | 5.9783 | 5.96 | 5.6579 | 5.3218 | 5.0256
|  | DEDDINGTON | LW |  |  | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.741 | 6.7263 | 6.6877 | 6.6249 | 6.5544 | 6.501 | 6.3417 | 6.0804 | 5.796 | 5.5447 | 4.9291 | 4.7786 | 4.7556 | 4.7071 | 4.6457 | 4.5843 | 4.535 | 4.4855 | 4.428 | 4.3888 | 4.2711 | 4.0786 | 3.8654 | 3.6843 | 6.0936 | 6.0787 | 6.0764 | 6.0716 | 6.0527 | 6.0333 | 6.0146 | 5.9953 | 5.9678 | 5.9609 | 5.9389 | 5.6908 | 5.3687 | 5.0804
|  | DEDDINGTON | ST |  |  | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7038 | 6.5414 | 6.3786 | 6.2168 | 4.9689 | 4.9327 | 4.7897 | 4.7726 | 4.7517 | 4.7264 | 4.7019 | 4.6778 | 4.6551 | 4.6306 | 4.5592 | 4.4425 | 4.3256 | 4.2094 | 6.0976 | 6.094 | 6.0798 | 6.0781 | 6.076 | 6.0735 | 6.0711 | 6.0687 | 6.0665 | 6.064 | 6.057 | 6.0454 | 6.0161 | 5.8302
|  | DEDDINGTON | SP |  |  | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 6.7553 | 5 | 4.9475 | 4.9458 | 4.9441 | 4.9363 | 4.9271 | 4.9187 | 4.9105 | 4.8999 | 4.8905 | 4.8629 | 4.819 | 4.7766 | 4.7365 | 6.1013 | 6.0954 | 6.0953 | 6.0951 | 6.0943 | 6.0934 | 6.0926 | 6.0918 | 6.0907 | 6.0898 | 6.0871 | 6.0827 | 6.0785 | 6.0745
IVER 132KV | DENHAM | DENHAM AVENUE | MINIMUM HEADROOM | TQ 03761 86587 | YES | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3067 | 16.2332 | 16.158 | 16.0801 | 15.9591 | 15.9178 | 15.7842 | 15.6746 | 15.3565 | 15.2629 | 12.9071 | 12.9071 | 12.9071 | 12.9071 | 12.835 | 12.7615 | 12.6863 | 12.6084 | 12.4874 | 12.4461 | 12.3125 | 12.2029 | 11.8848 | 11.7912 | 13.4077 | 13.4077 | 13.4077 | 13.4077 | 13.3355 | 13.2621 | 13.1869 | 13.109 | 12.988 | 12.9467 | 12.8131 | 12.7034 | 12.3853 | 12.2918
|  | DENHAM AVENUE | CT |  |  | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3786 | 16.3781 | 16.3774 | 16.3764 | 16.3742 | 16.3738 | 16.3717 | 16.3542 | 16.3347 | 16.3287 | 12.9071 | 12.9071 | 12.9071 | 12.9071 | 12.9069 | 12.9064 | 12.9057 | 12.9047 | 12.9025 | 12.9021 | 12.9 | 12.8825 | 12.863 | 12.857 | 13.4077 | 13.4077 | 13.4077 | 13.4077 | 13.4075 | 13.407 | 13.4063 | 13.4053 | 13.4031 | 13.4027 | 13.4006 | 13.3831 | 13.3636 | 13.3576
|  | DENHAM AVENUE | LW |  |  | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.378 | 16.3763 | 16.3737 | 16.37 | 16.3627 | 16.3614 | 16.355 | 16.3392 | 16.3086 | 16.3065 | 12.9071 | 12.9071 | 12.9071 | 12.9071 | 12.9063 | 12.9046 | 12.902 | 12.8984 | 12.891 | 12.8897 | 12.8833 | 12.8676 | 12.8369 | 12.8348 | 13.4077 | 13.4077 | 13.4077 | 13.4077 | 13.4069 | 13.4052 | 13.4026 | 13.3989 | 13.3916 | 13.3903 | 13.3838 | 13.3681 | 13.3374 | 13.3354
|  | DENHAM AVENUE | ST |  |  | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3067 | 16.2332 | 16.158 | 16.0801 | 15.9591 | 15.9178 | 15.7842 | 15.6746 | 15.3565 | 15.2629 | 12.9071 | 12.9071 | 12.9071 | 12.9071 | 12.835 | 12.7615 | 12.6863 | 12.6084 | 12.4874 | 12.4461 | 12.3125 | 12.2029 | 11.8848 | 11.7912 | 13.4077 | 13.4077 | 13.4077 | 13.4077 | 13.3355 | 13.2621 | 13.1869 | 13.109 | 12.988 | 12.9467 | 12.8131 | 12.7034 | 12.3853 | 12.2918
|  | DENHAM AVENUE | SP |  |  | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3788 | 16.3787 | 16.3787 | 16.3784 | 16.3768 | 16.3755 | 16.3695 | 16.3636 | 12.9071 | 12.9071 | 12.9071 | 12.9071 | 12.9071 | 12.9071 | 12.9071 | 12.9071 | 12.907 | 12.9067 | 12.9051 | 12.9039 | 12.8978 | 12.8919 | 13.4077 | 13.4077 | 13.4077 | 13.4077 | 13.4077 | 13.4077 | 13.4077 | 13.4076 | 13.4076 | 13.4073 | 13.4057 | 13.4044 | 13.3984 | 13.3925
MELKSHAM GSP | NORRINGTON | DEVIZES | MINIMUM HEADROOM | SU 00106 60986 | NO | 30.9761 | 30.9545 | 30.9316 | 29.8773 | 29.777 | 29.6737 | 29.5568 | 29.4205 | 29.2713 | 29.0929 | 28.3197 | 27.0288 | 25.7213 | 24.4493 | 22.28 | 22.2629 | 22.2458 | 21.2037 | 21.1154 | 20.8705 | 20.5299 | 20.188 | 19.8354 | 19.537 | 18.6449 | 17.1585 | 15.6499 | 14.1801 | 27.3577 | 27.2794 | 27.1852 | 25.9799 | 25.7328 | 25.4828 | 25.1429 | 24.8018 | 24.4499 | 24.1523 | 23.2625 | 21.78 | 20.2753 | 18.8094
|  | DEVIZES | CT |  |  | 31.0601 | 31.0467 | 31.0326 | 30.3991 | 30.3156 | 30.231 | 30.1453 | 30.0472 | 29.9182 | 29.851 | 29.2723 | 27.3236 | 25.8111 | 24.5038 | 22.362 | 22.3517 | 22.3415 | 21.7162 | 21.6408 | 21.5643 | 21.4537 | 21.1307 | 20.7921 | 20.5056 | 19.6544 | 17.5102 | 15.7966 | 14.2915 | 27.4662 | 27.4138 | 27.3516 | 26.6163 | 26.4337 | 26.2496 | 26.0656 | 25.7433 | 25.4054 | 25.1198 | 24.2709 | 22.1306 | 20.4209 | 18.9197
|  | DEVIZES | LW |  |  | 30.9761 | 30.9545 | 30.9316 | 29.8773 | 29.777 | 29.6737 | 29.5568 | 29.4205 | 29.2713 | 29.0929 | 28.3197 | 27.0288 | 25.7213 | 24.4493 | 22.28 | 22.2629 | 22.2458 | 21.2037 | 21.1154 | 20.8705 | 20.5299 | 20.188 | 19.8354 | 19.537 | 18.6449 | 17.1585 | 15.6499 | 14.1801 | 27.3577 | 27.2794 | 27.1852 | 25.9799 | 25.7328 | 25.4828 | 25.1429 | 24.8018 | 24.4499 | 24.1523 | 23.2625 | 21.78 | 20.2753 | 18.8094
|  | DEVIZES | ST |  |  | 31.1001 | 31.0895 | 31.0783 | 30.6541 | 30.5661 | 30.4749 | 30.3824 | 30.2876 | 30.1546 | 30.0856 | 29.7738 | 28.9133 | 27.8954 | 27.0338 | 22.403 | 22.3961 | 22.3893 | 21.9725 | 21.8935 | 21.8133 | 21.5937 | 21.3679 | 21.09 | 20.8714 | 20.2187 | 19.2284 | 18.081 | 17.0908 | 27.4935 | 27.4362 | 27.3721 | 26.857 | 26.6573 | 26.4307 | 26.2059 | 25.9806 | 25.7031 | 25.4851 | 24.834 | 23.8462 | 22.7014 | 21.7137
|  | DEVIZES | SP |  |  | 31.1498 | 31.1414 | 31.1376 | 30.9287 | 30.9096 | 30.8901 | 30.8697 | 30.8493 | 30.8277 | 30.8148 | 30.7737 | 30.7113 | 30.6291 | 30.5261 | 22.444 | 22.4405 | 22.4371 | 22.2287 | 22.2116 | 22.1945 | 22.1773 | 22.1601 | 22.1428 | 22.135 | 22.1088 | 21.8027 | 21.4584 | 21.115 | 27.6512 | 27.5811 | 27.5718 | 27.3578 | 27.3143 | 27.2656 | 27.2047 | 27.1444 | 27.0713 | 26.9951 | 26.7701 | 26.4153 | 26.072 | 25.7294
MINETY GSP | TOOTHILL BSP | DORCAN SOUTH | MINIMUM HEADROOM | SU 19288 83540 | YES | 32.454 | 32.4537 | 32.4533 | 32.4526 | 32.3748 | 32.295 | 32.2126 | 32.1273 | 31.9958 | 31.9495 | 31.8015 | 31.6694 | 31.3234 | 31.1091 | 27.6452 | 27.645 | 27.6447 | 27.6443 | 27.5664 | 27.4868 | 27.4048 | 27.3201 | 27.1892 | 27.1437 | 26.9983 | 26.8723 | 26.4859 | 26.0692 | 28.106 | 28.106 | 28.106 | 28.106 | 28.028 | 27.9487 | 27.8678 | 27.7842 | 27.6549 | 27.611 | 27.4699 | 27.3411 | 26.9991 | 26.8869
|  | DORCAN SOUTH | CT |  |  | 32.454 | 32.4537 | 32.4533 | 32.4526 | 32.4519 | 32.4512 | 32.4504 | 32.447 | 32.4437 | 32.4402 | 32.4286 | 32.4003 | 32.2036 | 31.8025 | 27.6452 | 27.645 | 27.6447 | 27.6443 | 27.6438 | 27.6432 | 27.6427 | 27.6404 | 27.6382 | 27.6357 | 27.6279 | 27.6085 | 27.1454 | 26.6374 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.0984 | 28.0748 | 28.0147 | 27.5268
|  | DORCAN SOUTH | LW |  |  | 32.454 | 32.4537 | 32.4533 | 32.4526 | 32.4519 | 32.4512 | 32.4479 | 32.4445 | 32.4412 | 32.4377 | 32.4262 | 32.3978 | 32.1753 | 31.774 | 27.6452 | 27.645 | 27.6447 | 27.6443 | 27.6438 | 27.6432 | 27.641 | 27.6387 | 27.6365 | 27.634 | 27.6262 | 27.6068 | 27.1095 | 26.6014 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.1058 | 28.0963 | 28.0727 | 27.9803 | 27.4922
|  | DORCAN SOUTH | ST |  |  | 32.4541 | 32.4539 | 32.4537 | 32.4533 | 32.3748 | 32.295 | 32.2126 | 32.1273 | 31.9958 | 31.9495 | 31.8015 | 31.6694 | 31.3234 | 31.1091 | 27.6453 | 27.6451 | 27.6449 | 27.6447 | 27.5664 | 27.4868 | 27.4048 | 27.3201 | 27.1892 | 27.1437 | 26.9983 | 26.8723 | 26.4859 | 26.0692 | 28.106 | 28.106 | 28.106 | 28.106 | 28.028 | 27.9487 | 27.8678 | 27.7842 | 27.6549 | 27.611 | 27.4699 | 27.3411 | 26.9991 | 26.8869
|  | DORCAN SOUTH | SP |  |  | 32.4542 | 32.4541 | 32.454 | 32.4539 | 32.4537 | 32.4535 | 32.453 | 32.4525 | 32.4519 | 32.451 | 32.4479 | 32.4398 | 32.4292 | 32.4181 | 27.6453 | 27.6453 | 27.6452 | 27.6451 | 27.645 | 27.6449 | 27.6445 | 27.6442 | 27.6438 | 27.6431 | 27.641 | 27.6355 | 27.6283 | 27.6207 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.106 | 28.0989 | 28.0896
CHICKERELL GSP | CHICKERELL BSP | DORCHESTER TOWN | MINIMUM HEADROOM | SY 69113 90401 | YES | 36.051 | 36.0359 | 36.0207 | 35.0956 | 34.9551 | 34.8109 | 34.6617 | 34.5079 | 34.31 | 34.2623 | 34.1071 | 33.847 | 33.5631 | 32.6924 | 32.5136 | 32.4958 | 32.476 | 31.5443 | 31.3989 | 31.2497 | 31.0886 | 30.9228 | 30.7129 | 30.6523 | 30.4591 | 29.6149 | 28.0505 | 26.6172 | 34.3541 | 34.3389 | 34.3238 | 33.3987 | 33.2582 | 33.1139 | 32.9647 | 32.8085 | 32.596 | 32.5327 | 32.3312 | 31.9978 | 31.2231 | 29.8066
|  | DORCHESTER TOWN | CT |  |  | 36.1238 | 36.1147 | 36.1056 | 35.5506 | 35.5046 | 35.4581 | 35.4112 | 35.3636 | 35.3135 | 35.2945 | 35.2355 | 34.5357 | 34.2611 | 33.381 | 32.5857 | 32.5735 | 32.5591 | 31.996 | 31.9437 | 31.891 | 31.8376 | 31.7779 | 31.7158 | 31.684 | 31.587 | 30.2912 | 28.7366 | 27.3041 | 34.4269 | 34.4178 | 34.4087 | 33.8537 | 33.8076 | 33.7612 | 33.7143 | 33.6636 | 33.5988 | 33.5642 | 33.4589 | 32.6858 | 31.9093 | 30.4936
|  | DORCHESTER TOWN | LW |  |  | 36.051 | 36.0359 | 36.0207 | 35.0956 | 34.9551 | 34.8109 | 34.6617 | 34.5079 | 34.31 | 34.2623 | 34.1071 | 33.847 | 33.5631 | 32.6924 | 32.5136 | 32.4958 | 32.476 | 31.5443 | 31.3989 | 31.2497 | 31.0886 | 30.9228 | 30.7129 | 30.6523 | 30.4591 | 29.6149 | 28.0505 | 26.6172 | 34.3541 | 34.3389 | 34.3238 | 33.3987 | 33.2582 | 33.1139 | 32.9647 | 32.8085 | 32.596 | 32.5327 | 32.3312 | 31.9978 | 31.2231 | 29.8066
|  | DORCHESTER TOWN | ST |  |  | 36.1602 | 36.1542 | 36.1481 | 35.7781 | 35.7474 | 35.7163 | 35.6849 | 35.653 | 35.6191 | 35.6053 | 35.5598 | 35.4871 | 35.4087 | 35.3267 | 32.6227 | 32.6143 | 32.6046 | 32.2299 | 32.1948 | 32.1585 | 32.1187 | 32.0782 | 32.0362 | 32.0136 | 31.9423 | 31.8295 | 31.4122 | 30.5148 | 34.4633 | 34.4572 | 34.4512 | 34.0811 | 34.0504 | 34.0194 | 33.988 | 33.9561 | 33.9222 | 33.8979 | 33.821 | 33.6995 | 33.5731 | 33.4438
|  | DORCHESTER TOWN | SP |  |  | 36.1966 | 36.1936 | 36.1906 | 36.0055 | 35.9904 | 35.9752 | 35.96 | 35.9447 | 35.9294 | 35.9228 | 35.9013 | 35.8683 | 35.8376 | 35.792 | 32.6612 | 32.6575 | 32.6532 | 32.4673 | 32.4513 | 32.4351 | 32.4171 | 32.3991 | 32.3802 | 32.3702 | 32.3387 | 32.2905 | 32.2455 | 32.1864 | 34.4997 | 34.4966 | 34.4936 | 34.3086 | 34.2934 | 34.2782 | 34.263 | 34.2478 | 34.2325 | 34.2258 | 34.2043 | 34.1714 | 34.1297 | 34.0677
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE | MINIMUM HEADROOM | SU 61604 50238 | YES | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 31.5768 | 29.6704 | 27.7922 | 25.7069 | 25.6976 | 25.6854 | 25.6622 | 25.6389 | 25.6148 | 25.5858 | 25.5528 | 25.519 | 25.4827 | 24.6557 | 22.6186 | 20.4482 | 18.31 | 23.9288 | 23.9217 | 23.9125 | 23.8949 | 23.8772 | 23.859 | 23.837 | 23.812 | 23.7864 | 23.7589 | 23.6821 | 21.7288 | 19.5717 | 17.4465
|  | DOWN GRANGE | CT |  |  | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 31.6266 | 29.7204 | 27.8428 | 25.7069 | 25.6976 | 25.6854 | 25.6622 | 25.6389 | 25.6148 | 25.5905 | 25.5575 | 25.5237 | 25.4874 | 24.7133 | 22.6753 | 20.5052 | 18.3676 | 23.9288 | 23.9217 | 23.9125 | 23.8949 | 23.8772 | 23.859 | 23.8406 | 23.8156 | 23.79 | 23.7624 | 23.6857 | 21.7852 | 19.6283 | 17.5037
|  | DOWN GRANGE | LW |  |  | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 31.5768 | 29.6704 | 27.7922 | 25.7073 | 25.6982 | 25.6864 | 25.6639 | 25.6413 | 25.6179 | 25.5858 | 25.5528 | 25.519 | 25.4827 | 24.6557 | 22.6186 | 20.4482 | 18.31 | 23.929 | 23.9222 | 23.9132 | 23.8962 | 23.879 | 23.8613 | 23.837 | 23.812 | 23.7864 | 23.7589 | 23.6821 | 21.7288 | 19.5717 | 17.4465
|  | DOWN GRANGE | ST |  |  | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 32.204 | 30.9925 | 25.7105 | 25.7043 | 25.6971 | 25.6857 | 25.6717 | 25.6547 | 25.6369 | 25.6185 | 25.5955 | 25.5706 | 25.5014 | 24.7423 | 23.3326 | 21.9534 | 23.9315 | 23.9268 | 23.9213 | 23.9127 | 23.9021 | 23.8893 | 23.8757 | 23.8618 | 23.8443 | 23.8255 | 23.7731 | 23.6875 | 22.4385 | 21.0677
|  | DOWN GRANGE | SP |  |  | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 33.1305 | 25.7159 | 25.714 | 25.7121 | 25.7102 | 25.706 | 25.701 | 25.6947 | 25.6882 | 25.6802 | 25.6705 | 25.6435 | 25.5993 | 25.5532 | 25.5081 | 23.9356 | 23.9342 | 23.9327 | 23.9313 | 23.9281 | 23.9243 | 23.9195 | 23.9146 | 23.9086 | 23.9012 | 23.8808 | 23.8472 | 23.8123 | 23.7782
MINETY GSP | STRATTON (2 X 90) | DRAKES WAY | MINIMUM HEADROOM | SU 16899 85647 | YES | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.6875 | 16.0602 | 15.1878 | 15.1873 | 15.1868 | 15.1858 | 15.1848 | 15.1837 | 15.1809 | 15.1781 | 15.1752 | 15.1722 | 15.162 | 15.1347 | 15.1 | 15.0649 | 16.2164 | 16.2158 | 16.2151 | 16.2139 | 16.2126 | 16.2113 | 16.2077 | 16.2041 | 16.2005 | 16.1966 | 16.1838 | 15.8755 | 15.1564 | 14.4297
|  | DRAKES WAY | CT |  |  | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7182 | 16.0909 | 15.1878 | 15.1873 | 15.1868 | 15.1858 | 15.1848 | 15.1837 | 15.1827 | 15.1798 | 15.1769 | 15.1739 | 15.1637 | 15.1364 | 15.1017 | 15.0666 | 16.2164 | 16.2158 | 16.2151 | 16.2139 | 16.2126 | 16.2113 | 16.2099 | 16.2063 | 16.2027 | 16.1988 | 16.186 | 15.9109 | 15.1918 | 14.4652
|  | DRAKES WAY | LW |  |  | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.6875 | 16.0602 | 15.1878 | 15.1873 | 15.1868 | 15.1858 | 15.1848 | 15.1837 | 15.1809 | 15.1781 | 15.1752 | 15.1722 | 15.162 | 15.1347 | 15.1 | 15.0649 | 16.2164 | 16.2158 | 16.2151 | 16.2139 | 16.2126 | 16.2113 | 16.2077 | 16.2041 | 16.2005 | 16.1966 | 16.1838 | 15.8755 | 15.1564 | 14.4297
|  | DRAKES WAY | ST |  |  | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 15.1879 | 15.1876 | 15.1873 | 15.1868 | 15.1862 | 15.1854 | 15.184 | 15.1825 | 15.1806 | 15.1785 | 15.1715 | 15.1525 | 15.1295 | 15.1073 | 16.2165 | 16.2162 | 16.2157 | 16.2151 | 16.2143 | 16.2134 | 16.2116 | 16.2098 | 16.2073 | 16.2047 | 16.1958 | 16.1351 | 15.768 | 15.3074
|  | DRAKES WAY | SP |  |  | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 16.7819 | 15.1881 | 15.1879 | 15.1878 | 15.1877 | 15.1874 | 15.1872 | 15.1867 | 15.1862 | 15.1857 | 15.1849 | 15.1821 | 15.1743 | 15.1635 | 15.152 | 16.2168 | 16.2166 | 16.2164 | 16.2163 | 16.216 | 16.2156 | 16.215 | 16.2144 | 16.2137 | 16.2127 | 16.2092 | 16.1993 | 16.1857 | 16.1287
NURSLING GSP | WINCHESTER | DUNBRIDGE | MINIMUM HEADROOM | SU 31520 26244 | YES | 26.7988 | 26.7988 | 26.7988 | 26.7988 | 26.7252 | 26.6322 | 26.517 | 26.379 | 26.1459 | 26.1103 | 25.9606 | 25.6572 | 24.8273 | 24.3805 | 25.7912 | 25.7382 | 25.6686 | 25.5215 | 25.3432 | 25.1198 | 24.9133 | 24.6847 | 24.3618 | 24.2295 | 23.794 | 23.0191 | 21.9486 | 21.4308 | 26.2993 | 26.2993 | 26.2993 | 26.2993 | 26.2257 | 26.1326 | 26.0175 | 25.8795 | 25.6463 | 25.6108 | 25.4611 | 25.127 | 24.0921 | 23.5856
|  | DUNBRIDGE | CT |  |  | 26.7988 | 26.7988 | 26.7988 | 26.7988 | 26.7938 | 26.7844 | 26.7704 | 26.75 | 26.7098 | 26.7032 | 26.6709 | 26.4213 | 25.8176 | 25.3334 | 25.7912 | 25.7382 | 25.6686 | 25.5215 | 25.3737 | 25.2228 | 25.0688 | 24.958 | 24.828 | 24.7246 | 24.4066 | 23.6854 | 22.9245 | 22.3692 | 26.2993 | 26.2993 | 26.2993 | 26.2993 | 26.2943 | 26.2848 | 26.2708 | 26.2505 | 26.2103 | 26.2037 | 26.1714 | 25.8004 | 25.0735 | 24.5253
|  | DUNBRIDGE | LW |  |  | 26.7988 | 26.7988 | 26.7988 | 26.7988 | 26.7252 | 26.6322 | 26.517 | 26.379 | 26.1459 | 26.1103 | 25.9606 | 25.6572 | 24.8273 | 24.3805 | 25.7969 | 25.7481 | 25.684 | 25.5483 | 25.3432 | 25.1198 | 24.9133 | 24.6847 | 24.3618 | 24.2295 | 23.794 | 23.0191 | 21.9486 | 21.4308 | 26.2993 | 26.2993 | 26.2993 | 26.2993 | 26.2257 | 26.1326 | 26.0175 | 25.8795 | 25.6463 | 25.6108 | 25.4611 | 25.127 | 24.0921 | 23.5856
|  | DUNBRIDGE | ST |  |  | 26.7988 | 26.7988 | 26.7988 | 26.7988 | 26.7846 | 26.7668 | 26.7452 | 26.7181 | 26.6694 | 26.6498 | 26.5635 | 26.465 | 26.1336 | 26.0235 | 25.9818 | 25.8287 | 25.8115 | 25.7818 | 25.7313 | 25.6696 | 25.577 | 25.48 | 25.3699 | 25.2843 | 25.0055 | 24.5934 | 23.9482 | 23.5267 | 26.2993 | 26.2993 | 26.2993 | 26.2993 | 26.2851 | 26.2673 | 26.2456 | 26.2186 | 26.1699 | 26.1502 | 26.064 | 25.9654 | 25.6341 | 25.524
|  | DUNBRIDGE | SP |  |  | 26.7988 | 26.7988 | 26.7988 | 26.7988 | 26.7937 | 26.7885 | 26.783 | 26.7772 | 26.7677 | 26.7392 | 26.6314 | 26.5677 | 26.3167 | 26.0863 | 25.9827 | 25.9235 | 25.8464 | 25.8423 | 25.8185 | 25.7913 | 25.7612 | 25.731 | 25.6898 | 25.6357 | 25.4538 | 25.2716 | 24.9068 | 24.5691 | 26.2993 | 26.2993 | 26.2993 | 26.2993 | 26.2942 | 26.289 | 26.2835 | 26.2777 | 26.2681 | 26.2397 | 26.1319 | 26.0682 | 25.8172 | 25.5868
MANNINGTON GSP | REDHILL BSP | EAST HOWE | MINIMUM HEADROOM | SZ 06789 95116 | YES | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 35.9943 | 34.4251 | 35.0655 | 35.0618 | 35.0587 | 35.0539 | 35.0485 | 35.0425 | 35.0267 | 35.0103 | 34.9933 | 34.976 | 34.9297 | 34.0881 | 32.2811 | 30.4518 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.7614 | 33.9376 | 32.3002 | 30.4361 | 28.5843
|  | EAST HOWE | CT |  |  | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.151 | 34.5823 | 35.0656 | 35.062 | 35.059 | 35.0543 | 35.0492 | 35.0433 | 35.0371 | 35.0207 | 35.0037 | 34.9865 | 34.9401 | 34.2672 | 32.4605 | 30.6373 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.1228 | 32.485 | 30.6211 | 28.7698
|  | EAST HOWE | LW |  |  | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 35.9943 | 34.4251 | 35.0655 | 35.0618 | 35.0587 | 35.0539 | 35.0485 | 35.0425 | 35.0267 | 35.0103 | 34.9933 | 34.976 | 34.9297 | 34.0881 | 32.2811 | 30.4518 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.7614 | 33.9376 | 32.3002 | 30.4361 | 28.5843
|  | EAST HOWE | ST |  |  | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 35.066 | 35.0633 | 35.0612 | 35.0583 | 35.0548 | 35.0504 | 35.04 | 35.0292 | 35.0176 | 35.0059 | 34.9741 | 34.911 | 34.1714 | 33.0223 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.7277 | 33.6067 | 32.3861 | 31.2007
|  | EAST HOWE | SP |  |  | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 36.5564 | 35.0669 | 35.0653 | 35.0644 | 35.0634 | 35.062 | 35.0604 | 35.0572 | 35.0539 | 35.0499 | 35.0453 | 35.0329 | 35.0076 | 34.9781 | 34.9481 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.876 | 34.7987 | 34.2646
MELKSHAM GSP | NORRINGTON | EASTERTON | MINIMUM HEADROOM | SU 01568 54730 | NO | 18.5559 | 18.5394 | 18.5167 | 18.4685 | 18.4207 | 18.3723 | 18.3163 | 18.2224 | 18.1127 | 18.0243 | 17.7515 | 17.2817 | 16.7328 | 16.3198 | 11.796 | 11.7751 | 11.7476 | 11.6896 | 11.6322 | 11.5743 | 11.5109 | 11.4012 | 11.2757 | 11.1704 | 10.8476 | 10.296 | 9.6628 | 9.167 | 12.151 | 12.1316 | 12.1062 | 12.0524 | 11.9991 | 11.9453 | 11.885 | 11.7821 | 11.6634 | 11.5654 | 11.264 | 10.7474 | 10.1503 | 9.69
|  | EASTERTON | CT |  |  | 18.5559 | 18.5394 | 18.5167 | 18.4685 | 18.4207 | 18.3723 | 18.3234 | 18.2416 | 18.1549 | 18.0704 | 17.8173 | 17.3394 | 16.8411 | 16.4107 | 11.796 | 11.7751 | 11.7476 | 11.6896 | 11.6322 | 11.5743 | 11.516 | 11.4183 | 11.3159 | 11.2144 | 10.9114 | 10.3517 | 9.7691 | 9.2561 | 12.151 | 12.1316 | 12.1062 | 12.0524 | 11.9991 | 11.9453 | 11.891 | 11.8001 | 11.7045 | 11.6102 | 11.3286 | 10.804 | 10.2575 | 9.7799
|  | EASTERTON | LW |  |  | 18.5604 | 18.5475 | 18.5298 | 18.4915 | 18.4507 | 18.4063 | 18.3163 | 18.2224 | 18.1127 | 18.0243 | 17.7515 | 17.2817 | 16.7328 | 16.3198 | 11.8018 | 11.7852 | 11.7634 | 11.7173 | 11.6689 | 11.6169 | 11.5109 | 11.4012 | 11.2757 | 11.1704 | 10.8476 | 10.296 | 9.6628 | 9.167 | 12.1565 | 12.1411 | 12.1209 | 12.0781 | 12.0329 | 11.9842 | 11.885 | 11.7821 | 11.6634 | 11.5654 | 11.264 | 10.7474 | 10.1503 | 9.69
|  | EASTERTON | ST |  |  | 18.573 | 18.5692 | 18.5648 | 18.5572 | 18.5471 | 18.5339 | 18.4904 | 18.4466 | 18.3864 | 18.3263 | 18.1422 | 17.8507 | 17.4946 | 17.1985 | 11.8179 | 11.8131 | 11.8074 | 11.7976 | 11.7849 | 11.7689 | 11.717 | 11.6649 | 11.594 | 11.5223 | 11.3045 | 10.9585 | 10.5481 | 10.1981 | 12.1714 | 12.1669 | 12.1616 | 12.1526 | 12.1407 | 12.1257 | 12.0775 | 12.0289 | 11.9626 | 11.8959 | 11.6925 | 11.3699 | 10.9827 | 10.6558
|  | EASTERTON | SP |  |  | 18.5754 | 18.5741 | 18.5727 | 18.5715 | 18.5657 | 18.5494 | 18.5266 | 18.503 | 18.4696 | 18.4047 | 18.2014 | 18.0325 | 17.7112 | 17.4286 | 11.821 | 11.8193 | 11.8176 | 11.816 | 11.8086 | 11.7904 | 11.7638 | 11.7371 | 11.7 | 11.6305 | 11.4142 | 11.2247 | 10.8839 | 10.5828 | 12.1743 | 12.1727 | 12.1711 | 12.1696 | 12.1627 | 12.1452 | 12.1198 | 12.0944 | 12.0588 | 11.9913 | 11.7806 | 11.5999 | 11.2675 | 10.9743
BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD | MINIMUM HEADROOM | SU 86148 67194 | YES | 36.4721 | 36.4721 | 36.4721 | 36.4721 | 36.4537 | 36.4349 | 36.4155 | 36.3953 | 36.3635 | 36.3525 | 36.3158 | 36.284 | 36.164 | 34.8187 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9298 | 34.911 | 34.8916 | 34.8714 | 34.8396 | 34.8286 | 34.7919 | 34.5476 | 32.8433 | 31.1836 | 35.0216 | 35.0216 | 35.0216 | 35.0216 | 35.0032 | 34.9844 | 34.965 | 34.9448 | 34.913 | 34.902 | 34.8653 | 34.8335 | 33.2304 | 31.5633
|  | EASTHAMPSTEAD | CT |  |  | 36.4721 | 36.4721 | 36.4721 | 36.4721 | 36.4719 | 36.4715 | 36.4709 | 36.47 | 36.468 | 36.4676 | 36.4657 | 36.45 | 36.4324 | 35.0856 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.948 | 34.9476 | 34.9469 | 34.946 | 34.944 | 34.9437 | 34.9418 | 34.8432 | 33.1492 | 31.4862 | 35.0216 | 35.0216 | 35.0216 | 35.0216 | 35.0214 | 35.021 | 35.0204 | 35.0195 | 35.0175 | 35.0171 | 35.0152 | 34.9995 | 33.5376 | 31.8672
|  | EASTHAMPSTEAD | LW |  |  | 36.4721 | 36.4721 | 36.4721 | 36.4721 | 36.4714 | 36.4699 | 36.4675 | 36.4642 | 36.4576 | 36.4565 | 36.4507 | 36.4365 | 36.2697 | 34.8187 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9475 | 34.946 | 34.9436 | 34.9403 | 34.9337 | 34.9326 | 34.9267 | 34.5476 | 32.8433 | 31.1836 | 35.0216 | 35.0216 | 35.0216 | 35.0216 | 35.0209 | 35.0194 | 35.017 | 35.0137 | 35.0071 | 35.006 | 35.0002 | 34.9305 | 33.2304 | 31.5633
|  | EASTHAMPSTEAD | ST |  |  | 36.4721 | 36.4721 | 36.4721 | 36.4721 | 36.4537 | 36.4349 | 36.4155 | 36.3953 | 36.3635 | 36.3525 | 36.3158 | 36.284 | 36.1766 | 36.1427 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9298 | 34.911 | 34.8916 | 34.8714 | 34.8396 | 34.8286 | 34.7919 | 34.7601 | 34.5736 | 33.4687 | 35.0216 | 35.0216 | 35.0216 | 35.0216 | 35.0032 | 34.9844 | 34.965 | 34.9448 | 34.913 | 34.902 | 34.8653 | 34.8335 | 34.7261 | 33.8564
|  | EASTHAMPSTEAD | SP |  |  | 36.4721 | 36.4721 | 36.4721 | 36.4721 | 36.4662 | 36.4604 | 36.4546 | 36.4487 | 36.4394 | 36.4136 | 36.331 | 36.2912 | 36.164 | 36.0568 | 34.9482 | 34.9482 | 34.9482 | 34.9482 | 34.9423 | 34.9365 | 34.9307 | 34.9248 | 34.9155 | 34.8897 | 34.807 | 34.7672 | 34.64 | 34.5329 | 35.0216 | 35.0216 | 35.0216 | 35.0216 | 35.0157 | 35.0099 | 35.0041 | 34.9982 | 34.9889 | 34.9631 | 34.8805 | 34.8407 | 34.7135 | 34.6063
NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH | MINIMUM HEADROOM | SU 45426 18958 | YES | 49.5598 | 49.5598 | 49.5598 | 49.5598 | 49.5152 | 49.4696 | 49.423 | 49.3739 | 49.2973 | 49.2874 | 49.2546 | 49.0924 | 48.9222 | 48.5257 | 47.4745 | 47.4646 | 47.4568 | 47.4442 | 47.3898 | 47.3319 | 47.2728 | 47.2042 | 47.1086 | 47.0786 | 46.9908 | 45.2537 | 43.1328 | 41.179 | 47.7504 | 47.7504 | 47.7504 | 47.7504 | 47.7059 | 47.6603 | 47.6137 | 47.5646 | 47.4879 | 47.4781 | 47.4452 | 47.2831 | 47.1129 | 47.0698
|  | EASTLEIGH NORTH | CT |  |  | 49.5598 | 49.5598 | 49.5598 | 49.5598 | 49.5152 | 49.4696 | 49.423 | 49.3739 | 49.2973 | 49.2874 | 49.2546 | 49.0924 | 48.9222 | 48.5257 | 47.475 | 47.4653 | 47.458 | 47.4463 | 47.3898 | 47.3319 | 47.2728 | 47.2042 | 47.1086 | 47.0786 | 46.9908 | 45.2537 | 43.1328 | 41.179 | 47.7504 | 47.7504 | 47.7504 | 47.7504 | 47.7059 | 47.6603 | 47.6137 | 47.5646 | 47.4879 | 47.4781 | 47.4452 | 47.2831 | 47.1129 | 47.0698
|  | EASTLEIGH NORTH | LW |  |  | 49.5598 | 49.5598 | 49.5598 | 49.5598 | 49.5587 | 49.5564 | 49.5528 | 49.5478 | 49.5377 | 49.536 | 49.5272 | 49.5057 | 49.4637 | 48.8811 | 47.4745 | 47.4646 | 47.4568 | 47.4442 | 47.4303 | 47.4149 | 47.3896 | 47.3651 | 47.3361 | 47.3142 | 47.2504 | 45.4036 | 43.4055 | 41.4911 | 47.7504 | 47.7504 | 47.7504 | 47.7504 | 47.7493 | 47.747 | 47.7434 | 47.7384 | 47.7284 | 47.7267 | 47.7178 | 47.6963 | 47.6544 | 47.6515
|  | EASTLEIGH NORTH | ST |  |  | 49.5598 | 49.5598 | 49.5598 | 49.5598 | 49.5595 | 49.5591 | 49.5584 | 49.5573 | 49.555 | 49.5539 | 49.5478 | 49.5399 | 49.5122 | 49.5021 | 47.4753 | 47.471 | 47.4612 | 47.4535 | 47.4443 | 47.4335 | 47.4194 | 47.4063 | 47.3911 | 47.3762 | 47.3329 | 47.2631 | 46.0326 | 44.8075 | 47.7504 | 47.7504 | 47.7504 | 47.7504 | 47.7502 | 47.7497 | 47.749 | 47.748 | 47.7456 | 47.7445 | 47.7385 | 47.7306 | 47.7028 | 47.6927
|  | EASTLEIGH NORTH | SP |  |  | 49.5598 | 49.5598 | 49.5598 | 49.5598 | 49.5598 | 49.5598 | 49.5597 | 49.5597 | 49.5596 | 49.5592 | 49.557 | 49.5553 | 49.547 | 49.5389 | 47.4779 | 47.476 | 47.4739 | 47.4717 | 47.4685 | 47.465 | 47.4603 | 47.4563 | 47.4515 | 47.4458 | 47.4291 | 47.4035 | 47.3718 | 47.3417 | 47.7504 | 47.7504 | 47.7504 | 47.7504 | 47.7504 | 47.7504 | 47.7504 | 47.7503 | 47.7502 | 47.7499 | 47.7477 | 47.746 | 47.7377 | 47.7296
LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY | MINIMUM HEADROOM | SZ 66357 99040 | YES | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.2801 | 31.1452 | 30.0022 | 24.8348 | 24.8338 | 24.8327 | 24.831 | 24.8289 | 24.8264 | 24.8208 | 24.8148 | 24.8088 | 24.8023 | 24.7815 | 24.0796 | 22.7697 | 21.4505 | 24.7311 | 24.7295 | 24.7277 | 24.7248 | 24.7213 | 24.717 | 24.7078 | 24.6977 | 24.6876 | 24.6768 | 24.6419 | 24.4518 | 23.1372 | 21.8133
|  | EASTNEY | CT |  |  | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.3826 | 31.2478 | 30.1051 | 24.8352 | 24.8344 | 24.8335 | 24.8319 | 24.8302 | 24.8284 | 24.8266 | 24.8206 | 24.8145 | 24.8081 | 24.7872 | 24.1979 | 22.8881 | 21.5692 | 24.7317 | 24.7305 | 24.729 | 24.7263 | 24.7235 | 24.7204 | 24.7174 | 24.7073 | 24.6972 | 24.6864 | 24.6515 | 24.5657 | 23.256 | 21.9324
|  | EASTNEY | LW |  |  | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.2801 | 31.1452 | 30.0022 | 24.835 | 24.8341 | 24.833 | 24.831 | 24.829 | 24.8268 | 24.8208 | 24.8148 | 24.8088 | 24.8023 | 24.7815 | 24.0796 | 22.7697 | 21.4505 | 24.7314 | 24.73 | 24.7281 | 24.7248 | 24.7214 | 24.7178 | 24.7078 | 24.6977 | 24.6876 | 24.6768 | 24.6419 | 24.4518 | 23.1372 | 21.8133
|  | EASTNEY | ST |  |  | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.0512 | 31.3245 | 24.8348 | 24.8338 | 24.8327 | 24.831 | 24.8289 | 24.8264 | 24.822 | 24.8176 | 24.8135 | 24.8091 | 24.7948 | 24.6682 | 23.8153 | 22.9766 | 24.7311 | 24.7295 | 24.7277 | 24.7248 | 24.7213 | 24.717 | 24.7097 | 24.7024 | 24.6955 | 24.6881 | 24.6642 | 24.6047 | 24.1866 | 23.3449
|  | EASTNEY | SP |  |  | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 32.7908 | 24.8357 | 24.8354 | 24.8352 | 24.835 | 24.8345 | 24.834 | 24.8325 | 24.831 | 24.8292 | 24.8275 | 24.8219 | 24.8073 | 24.7882 | 24.768 | 24.7326 | 24.7322 | 24.7318 | 24.7314 | 24.7307 | 24.7298 | 24.7273 | 24.7248 | 24.7217 | 24.7188 | 24.7095 | 24.6851 | 24.6532 | 24.6194
LALEHAM | STAINES | EGHAM | MINIMUM HEADROOM | TQ 01030 71404 | YES | 40.8841 | 40.8841 | 40.8841 | 40.8841 | 66.8832 | 66.8814 | 66.8785 | 66.8745 | 66.8665 | 66.8651 | 66.8581 | 66.8409 | 66.8039 | 66.0838 | 38.1375 | 38.1282 | 38.1169 | 38.0993 | 64.0807 | 64.0607 | 64.0401 | 64.022 | 64.0002 | 63.9852 | 63.939 | 63.8234 | 62.7317 | 61.7013 | 38.8305 | 38.8305 | 38.8305 | 38.8305 | 64.8296 | 64.8278 | 64.8249 | 64.8209 | 64.6968 | 64.463 | 63.7909 | 62.6671 | 61.5623 | 60.5193
|  | EGHAM | CT |  |  | 40.8841 | 40.8841 | 40.8841 | 40.8841 | 66.8838 | 66.8833 | 66.8826 | 66.8815 | 66.8791 | 66.8786 | 66.8763 | 66.8573 | 66.8273 | 66.0838 | 38.1375 | 38.1282 | 38.1169 | 38.0993 | 64.0807 | 64.0607 | 64.0401 | 64.0249 | 64.0087 | 63.9946 | 63.9532 | 63.8234 | 62.7317 | 61.7013 | 38.8305 | 38.8305 | 38.8305 | 38.8305 | 64.8302 | 64.8297 | 64.829 | 64.8279 | 64.6968 | 64.463 | 63.7909 | 62.6671 | 61.5623 | 60.5193
|  | EGHAM | LW |  |  | 40.8841 | 40.8841 | 40.8841 | 40.8841 | 66.8832 | 66.8814 | 66.8785 | 66.8745 | 66.8665 | 66.8651 | 66.8581 | 66.8409 | 66.8039 | 66.1211 | 38.1379 | 38.1289 | 38.1179 | 38.1011 | 64.0826 | 64.062 | 64.0402 | 64.022 | 64.0002 | 63.9852 | 63.939 | 63.8573 | 62.7723 | 61.7458 | 38.8305 | 38.8305 | 38.8305 | 38.8305 | 64.8296 | 64.8278 | 64.8249 | 64.8209 | 64.7542 | 64.5196 | 63.8425 | 62.7209 | 61.6037 | 60.5647
|  | EGHAM | ST |  |  | 40.8841 | 40.8841 | 40.8841 | 40.8841 | 66.8839 | 66.8835 | 66.883 | 66.8821 | 66.8803 | 66.8794 | 66.8746 | 66.8683 | 66.8461 | 66.8381 | 38.1415 | 38.1358 | 38.1296 | 38.1222 | 64.1127 | 64.1014 | 64.0868 | 64.0753 | 64.064 | 64.0538 | 64.0224 | 63.9726 | 63.9096 | 63.8623 | 38.8305 | 38.8305 | 38.8305 | 38.8305 | 64.8303 | 64.8299 | 64.8294 | 64.8285 | 64.8267 | 64.8258 | 64.821 | 64.2539 | 63.5313 | 62.8512
|  | EGHAM | SP |  |  | 40.8841 | 40.8841 | 40.8841 | 40.8841 | 66.8841 | 66.8841 | 66.8841 | 66.884 | 66.884 | 66.8836 | 66.8819 | 66.8805 | 66.8739 | 66.8675 | 38.1439 | 38.1407 | 38.1377 | 38.1352 | 64.1311 | 64.1264 | 64.1209 | 64.117 | 64.1122 | 64.1083 | 64.0963 | 64.0781 | 64.0561 | 64.0355 | 38.8305 | 38.8305 | 38.8305 | 38.8305 | 64.8305 | 64.8305 | 64.8305 | 64.8304 | 64.8303 | 64.83 | 64.8283 | 64.8269 | 64.8203 | 64.8139
MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE | MINIMUM HEADROOM | SZ 08757 91379 | YES | 32.5391 | 32.5248 | 32.5178 | 32.5057 | 32.4755 | 32.4474 | 32.4198 | 32.3909 | 32.3518 | 32.3378 | 32.2932 | 32.1878 | 31.1128 | 30.069 | 24.7223 | 24.6464 | 24.6094 | 24.5451 | 24.4546 | 24.3779 | 24.3067 | 24.2313 | 24.1425 | 24.0846 | 23.899 | 23.1327 | 21.9117 | 20.7237 | 24.9743 | 24.9601 | 24.9531 | 24.9411 | 24.876 | 24.7904 | 24.7113 | 24.6273 | 24.5295 | 24.4636 | 24.2582 | 23.7571 | 22.5917 | 21.3663
|  | ELECTRIC HOUSE | CT |  |  | 32.5393 | 32.5252 | 32.5184 | 32.5067 | 32.4931 | 32.4822 | 32.4709 | 32.4601 | 32.4485 | 32.4383 | 32.4067 | 32.325 | 31.2899 | 30.2489 | 24.7234 | 24.6483 | 24.6124 | 24.5504 | 24.4783 | 24.4205 | 24.3605 | 24.3032 | 24.2418 | 24.1878 | 24.017 | 23.2727 | 22.0897 | 20.9045 | 24.9745 | 24.9604 | 24.9537 | 24.9421 | 24.9008 | 24.8344 | 24.7655 | 24.6997 | 24.6293 | 24.5673 | 24.375 | 23.8934 | 22.7699 | 21.5474
|  | ELECTRIC HOUSE | LW |  |  | 32.5391 | 32.5248 | 32.5178 | 32.5057 | 32.4755 | 32.4474 | 32.4198 | 32.3909 | 32.3518 | 32.3378 | 32.2932 | 32.1878 | 31.1128 | 30.069 | 24.7223 | 24.6464 | 24.6094 | 24.5451 | 24.4546 | 24.3779 | 24.3067 | 24.2313 | 24.1425 | 24.0846 | 23.899 | 23.1327 | 21.9117 | 20.7237 | 24.9743 | 24.9601 | 24.9531 | 24.9411 | 24.876 | 24.7904 | 24.7113 | 24.6273 | 24.5295 | 24.4636 | 24.2582 | 23.7571 | 22.5917 | 21.3663
|  | ELECTRIC HOUSE | ST |  |  | 32.5414 | 32.5382 | 32.5255 | 32.5202 | 32.5129 | 32.5065 | 32.4957 | 32.4844 | 32.4767 | 32.4697 | 32.448 | 32.3929 | 32.3281 | 31.6755 | 24.7342 | 24.7174 | 24.6502 | 24.6222 | 24.5831 | 24.5493 | 24.4919 | 24.4324 | 24.3912 | 24.3543 | 24.2392 | 23.9058 | 23.2797 | 22.5286 | 24.9765 | 24.9734 | 24.9608 | 24.9555 | 24.9482 | 24.9419 | 24.9164 | 24.8481 | 24.8007 | 24.7585 | 24.6263 | 24.2909 | 23.8969 | 23.2228
|  | ELECTRIC HOUSE | SP |  |  | 32.5428 | 32.5412 | 32.5307 | 32.529 | 32.5242 | 32.5203 | 32.5149 | 32.5095 | 32.5022 | 32.4933 | 32.4653 | 32.4332 | 32.3736 | 32.3171 | 24.7419 | 24.7335 | 24.6775 | 24.6685 | 24.6494 | 24.6345 | 24.6123 | 24.5894 | 24.5606 | 24.5403 | 24.4763 | 24.3467 | 24.1579 | 23.9646 | 24.978 | 24.9764 | 24.9659 | 24.9642 | 24.9595 | 24.9555 | 24.9502 | 24.9448 | 24.9376 | 24.9287 | 24.9007 | 24.7561 | 24.5438 | 24.3255
BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD | MINIMUM HEADROOM | SU 81057 68532 | YES | 36.3885 | 36.3754 | 36.3623 | 35.5624 | 35.4553 | 35.3463 | 35.2347 | 35.1207 | 34.9802 | 34.9434 | 34.1538 | 32.5643 | 31.0189 | 29.6777 | 34.6234 | 34.599 | 34.558 | 33.7275 | 33.4992 | 32.6761 | 32.2483 | 31.8082 | 31.3199 | 30.9733 | 29.9824 | 28.1809 | 26.4418 | 24.9085 | 34.8668 | 34.8536 | 34.8405 | 34.0406 | 33.9243 | 33.7737 | 33.6436 | 33.5106 | 33.3327 | 32.9879 | 32.0024 | 30.2111 | 28.5031 | 26.9843
|  | ELMS ROAD | CT |  |  | 36.4515 | 36.4436 | 36.4357 | 35.9558 | 35.8762 | 35.7957 | 35.7145 | 35.6311 | 35.5234 | 35.2716 | 34.4315 | 32.5643 | 31.0189 | 29.6777 | 34.6864 | 34.6674 | 34.6318 | 34.1213 | 33.9347 | 33.1446 | 32.3636 | 31.9542 | 31.4988 | 31.1644 | 30.2142 | 28.1809 | 26.4418 | 24.9085 | 34.9297 | 34.9218 | 34.914 | 34.434 | 34.346 | 34.2242 | 34.1022 | 33.9671 | 33.5138 | 33.1813 | 32.2364 | 30.2111 | 28.5031 | 26.9843
|  | ELMS ROAD | LW |  |  | 36.3885 | 36.3754 | 36.3623 | 35.5624 | 35.4553 | 35.3463 | 35.2347 | 35.1207 | 34.9802 | 34.9434 | 34.1538 | 32.8053 | 31.4081 | 30.0996 | 34.6234 | 34.599 | 34.558 | 33.7275 | 33.4992 | 32.6761 | 32.2483 | 31.8082 | 31.3199 | 30.9733 | 29.9824 | 28.4677 | 26.884 | 25.3833 | 34.8668 | 34.8536 | 34.8405 | 34.0406 | 33.9243 | 33.7737 | 33.6436 | 33.5106 | 33.3327 | 32.9879 | 32.0024 | 30.4958 | 28.9359 | 27.4635
|  | ELMS ROAD | ST |  |  | 36.4829 | 36.4777 | 36.4724 | 36.1525 | 36.1261 | 36.0996 | 36.073 | 36.0462 | 36.0187 | 36.0075 | 35.9727 | 35.9158 | 35.3103 | 34.501 | 34.7219 | 34.7088 | 34.6943 | 34.3585 | 34.3111 | 34.2596 | 34.2208 | 34.1523 | 33.8896 | 33.6665 | 33.0328 | 32.0837 | 31.1553 | 30.2386 | 34.9612 | 34.9559 | 34.9507 | 34.6307 | 34.6044 | 34.5779 | 34.5512 | 34.5188 | 34.4775 | 34.4541 | 34.3843 | 34.0975 | 33.1745 | 32.263
|  | ELMS ROAD | SP |  |  | 36.5144 | 36.5118 | 36.5091 | 36.3492 | 36.336 | 36.3229 | 36.3098 | 36.2967 | 36.2835 | 36.278 | 36.2611 | 36.2339 | 36.2135 | 36.1801 | 34.7616 | 34.7574 | 34.7533 | 34.5916 | 34.5722 | 34.5519 | 34.5341 | 34.5163 | 34.4973 | 34.4881 | 34.4605 | 34.4174 | 34.3812 | 34.3327 | 34.9926 | 34.99 | 34.9874 | 34.8274 | 34.8143 | 34.8012 | 34.788 | 34.7749 | 34.7617 | 34.7563 | 34.7393 | 34.7121 | 34.6918 | 34.6584
LOVEDEAN GSP | HAVANT | EMSWORTH | MINIMUM HEADROOM | SU 74861 05807 | YES | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.5312 | 16.435 | 16.3367 | 16.2352 | 16.0783 | 16.025 | 15.855 | 15.7183 | 15.2812 | 15.146 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.5525 | 12.4563 | 12.3581 | 12.2566 | 12.0996 | 12.0463 | 11.8763 | 11.2824 | 10.1744 | 9.1161 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.745 | 12.6488 | 12.5506 | 12.4491 | 12.2921 | 12.2389 | 12.0689 | 11.9321 | 11.4693 | 10.7138
|  | EMSWORTH | CT |  |  | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6145 | 16.6029 | 16.5912 | 16.5789 | 16.56 | 16.5576 | 16.5498 | 16.512 | 16.3217 | 15.4084 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.6358 | 12.6243 | 12.6125 | 12.6002 | 12.5813 | 12.5789 | 12.2903 | 11.2824 | 10.1744 | 9.1161 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8284 | 12.8168 | 12.805 | 12.7927 | 12.7738 | 12.7714 | 12.7637 | 12.6924 | 11.77 | 10.7138
|  | EMSWORTH | LW |  |  | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.5127 | 15.6097 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.4027 | 11.4329 | 10.3704 | 9.3223 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8084 | 11.9659 | 10.9199
|  | EMSWORTH | ST |  |  | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.5312 | 16.435 | 16.3367 | 16.2352 | 16.0783 | 16.025 | 15.855 | 15.7183 | 15.2812 | 15.146 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.5525 | 12.4563 | 12.3581 | 12.2566 | 12.0996 | 12.0463 | 11.8763 | 11.3146 | 10.1859 | 9.3753 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.745 | 12.6488 | 12.5506 | 12.4491 | 12.2921 | 12.2389 | 12.0689 | 11.9321 | 11.4693 | 10.9698
|  | EMSWORTH | SP |  |  | 16.6259 | 16.6259 | 16.6259 | 16.6259 | 16.6247 | 16.6235 | 16.6224 | 16.6212 | 16.6193 | 16.6141 | 16.5977 | 16.5899 | 16.5653 | 16.5447 | 12.6472 | 12.6472 | 12.6472 | 12.6472 | 12.646 | 12.6449 | 12.6437 | 12.6425 | 12.6406 | 12.6355 | 12.619 | 12.6112 | 12.5866 | 12.566 | 12.8398 | 12.8398 | 12.8398 | 12.8398 | 12.8386 | 12.8374 | 12.8362 | 12.835 | 12.8332 | 12.828 | 12.8116 | 12.8038 | 12.7791 | 12.7585
MELKSHAM GSP | AMESBURY | ENFORD | MINIMUM HEADROOM | SU 13728 51712 | YES | 8.8664 | 8.8664 | 8.8664 | 8.8664 | 8.8582 | 8.8498 | 8.8408 | 8.8313 | 8.8157 | 8.81 | 8.7892 | 8.7692 | 8.7026 | 8.6797 | 8.2086 | 8.2086 | 8.2086 | 8.2086 | 8.2005 | 8.192 | 8.183 | 8.1735 | 8.1579 | 8.1522 | 8.1315 | 8.1114 | 8.0448 | 8.0219 | 8.575 | 8.5731 | 8.5706 | 8.5654 | 8.5591 | 8.548 | 8.5121 | 8.4715 | 8.4257 | 8.3864 | 8.2662 | 8.0605 | 7.8261 | 7.6379
|  | ENFORD | CT |  |  | 8.8664 | 8.8664 | 8.8664 | 8.8664 | 8.866 | 8.8653 | 8.8643 | 8.8627 | 8.8594 | 8.8588 | 8.8556 | 8.8292 | 8.7998 | 8.7908 | 8.2086 | 8.2086 | 8.2086 | 8.2086 | 8.2082 | 8.2075 | 8.2065 | 8.2049 | 8.2016 | 8.201 | 8.1978 | 8.1714 | 8.142 | 8.133 | 8.575 | 8.5731 | 8.5706 | 8.5654 | 8.5599 | 8.5542 | 8.5481 | 8.5115 | 8.4735 | 8.4355 | 8.3218 | 8.1133 | 7.8958 | 7.7017
|  | ENFORD | LW |  |  | 8.8664 | 8.8664 | 8.8664 | 8.8664 | 8.8651 | 8.8626 | 8.8586 | 8.8531 | 8.842 | 8.8401 | 8.8304 | 8.8067 | 8.7604 | 8.7573 | 8.2086 | 8.2086 | 8.2086 | 8.2086 | 8.2073 | 8.2048 | 8.2008 | 8.1953 | 8.1842 | 8.1823 | 8.1726 | 8.1489 | 8.1026 | 8.0995 | 8.575 | 8.5731 | 8.5706 | 8.5654 | 8.5591 | 8.5515 | 8.5121 | 8.4715 | 8.4257 | 8.3864 | 8.2662 | 8.0605 | 7.8261 | 7.6379
|  | ENFORD | ST |  |  | 8.8664 | 8.8664 | 8.8664 | 8.8664 | 8.8582 | 8.8498 | 8.8408 | 8.8313 | 8.8157 | 8.81 | 8.7892 | 8.7692 | 8.7026 | 8.6797 | 8.2086 | 8.2086 | 8.2086 | 8.2086 | 8.2005 | 8.192 | 8.183 | 8.1735 | 8.1579 | 8.1522 | 8.1315 | 8.1114 | 8.0448 | 8.0219 | 8.5759 | 8.5747 | 8.5734 | 8.571 | 8.56 | 8.548 | 8.528 | 8.5075 | 8.4682 | 8.437 | 8.3418 | 8.2008 | 8.0131 | 7.8697
|  | ENFORD | SP |  |  | 8.8664 | 8.8664 | 8.8664 | 8.8664 | 8.8664 | 8.8663 | 8.8663 | 8.8663 | 8.8661 | 8.8657 | 8.8633 | 8.8614 | 8.8523 | 8.8434 | 8.2086 | 8.2086 | 8.2086 | 8.2086 | 8.2086 | 8.2085 | 8.2085 | 8.2085 | 8.2084 | 8.2079 | 8.2055 | 8.2036 | 8.1945 | 8.1856 | 8.5772 | 8.577 | 8.5768 | 8.5766 | 8.5758 | 8.5748 | 8.571 | 8.5673 | 8.5623 | 8.552 | 8.5208 | 8.4729 | 8.4196 | 8.3692
COWLEY GSP | YARNTON BSP | EYNSHAM | MINIMUM HEADROOM | SP 42236 10266 | NO | 28.826 | 28.826 | 28.826 | 28.826 | 28.824 | 28.8199 | 28.8135 | 28.8047 | 28.7869 | 28.7719 | 27.9572 | 27.2694 | 26.7198 | 26.2515 | 28.1842 | 28.1842 | 28.1842 | 28.1842 | 28.1823 | 27.8995 | 27.5596 | 27.1765 | 26.7886 | 26.3716 | 25.4021 | 24.5982 | 23.9584 | 23.4086 | 28.5308 | 28.5308 | 28.5308 | 28.5308 | 28.5288 | 28.5247 | 28.5183 | 28.5095 | 28.4917 | 28.3058 | 27.3493 | 26.5556 | 25.9237 | 25.381
|  | EYNSHAM | CT |  |  | 28.826 | 28.826 | 28.826 | 28.826 | 28.8254 | 28.8242 | 28.8226 | 28.8202 | 28.8148 | 28.7719 | 27.9572 | 27.2694 | 26.7198 | 26.2515 | 28.1842 | 28.1842 | 28.1842 | 28.1842 | 28.1836 | 27.8995 | 27.5596 | 27.1765 | 26.7886 | 26.3716 | 25.4021 | 24.5982 | 23.9584 | 23.4086 | 28.5308 | 28.5308 | 28.5308 | 28.5308 | 28.5302 | 28.529 | 28.5274 | 28.525 | 28.5196 | 28.3058 | 27.3493 | 26.5556 | 25.9237 | 25.381
|  | EYNSHAM | LW |  |  | 28.826 | 28.826 | 28.826 | 28.826 | 28.824 | 28.8199 | 28.8135 | 28.8047 | 28.7869 | 28.7839 | 28.0015 | 27.3179 | 26.7414 | 26.2823 | 28.1842 | 28.1842 | 28.1842 | 28.1842 | 28.1823 | 28.0049 | 27.6507 | 27.2611 | 26.8608 | 26.4416 | 25.4616 | 24.662 | 23.9952 | 23.4545 | 28.5308 | 28.5308 | 28.5308 | 28.5308 | 28.5288 | 28.5247 | 28.5183 | 28.5095 | 28.4917 | 28.3746 | 27.4075 | 26.618 | 25.9591 | 25.4256
|  | EYNSHAM | ST |  |  | 28.826 | 28.826 | 28.826 | 28.826 | 28.8256 | 28.8247 | 28.8235 | 28.8216 | 28.8175 | 28.8155 | 28.8048 | 28.4314 | 28.058 | 27.7452 | 28.1842 | 28.1842 | 28.1842 | 28.1842 | 28.1838 | 28.183 | 28.0022 | 27.7403 | 27.4795 | 27.1919 | 26.5034 | 25.966 | 25.533 | 25.1672 | 28.5308 | 28.5308 | 28.5308 | 28.5308 | 28.5303 | 28.5295 | 28.5283 | 28.5264 | 28.5223 | 28.5203 | 28.4357 | 27.9054 | 27.4775 | 27.1164
|  | EYNSHAM | SP |  |  | 28.826 | 28.826 | 28.826 | 28.826 | 28.826 | 28.8259 | 28.8259 | 28.8258 | 28.8256 | 28.825 | 28.8211 | 28.818 | 28.8034 | 28.7891 | 28.1842 | 28.1842 | 28.1842 | 28.1842 | 28.1842 | 28.1842 | 28.1841 | 28.184 | 28.1839 | 28.165 | 27.8929 | 27.6821 | 27.5214 | 27.3839 | 28.5308 | 28.5308 | 28.5308 | 28.5308 | 28.5308 | 28.5307 | 28.5307 | 28.5306 | 28.5304 | 28.5297 | 28.5259 | 28.5228 | 28.5082 | 28.4939
MINETY GSP | CIRENCESTER BSP | FAIRFORD | MINIMUM HEADROOM | SP 14418 00559 | NO | 34.3318 | 34.3318 | 34.3318 | 34.3318 | 34.3294 | 34.327 | 34.3246 | 34.3218 | 34.3134 | 34.3073 | 34.272 | 33.9842 | 33.4856 | 33.0276 | 32.2607 | 32.2597 | 32.2583 | 32.2553 | 32.2522 | 32.2487 | 32.2411 | 32.2324 | 32.2196 | 32.2133 | 31.9511 | 31.4415 | 30.8995 | 30.3988 | 32.7435 | 32.7435 | 32.7435 | 32.7435 | 32.741 | 32.7386 | 32.7362 | 32.7334 | 32.7251 | 32.719 | 32.6836 | 32.6445 | 32.08 | 31.5529
|  | FAIRFORD | CT |  |  | 34.3318 | 34.3318 | 34.3318 | 34.3318 | 34.3315 | 34.331 | 34.3302 | 34.3291 | 34.3265 | 34.3261 | 34.3237 | 33.9993 | 33.5135 | 33.0513 | 32.2607 | 32.2597 | 32.2583 | 32.2553 | 32.2522 | 32.2489 | 32.2453 | 32.2396 | 32.2326 | 32.2273 | 31.9681 | 31.4565 | 30.9272 | 30.4224 | 32.7435 | 32.7435 | 32.7435 | 32.7435 | 32.7432 | 32.7427 | 32.7419 | 32.7407 | 32.7382 | 32.7378 | 32.7353 | 32.6594 | 32.1075 | 31.5763
|  | FAIRFORD | LW |  |  | 34.3318 | 34.3318 | 34.3318 | 34.3318 | 34.3309 | 34.329 | 34.326 | 34.3218 | 34.3134 | 34.3119 | 34.3045 | 33.9842 | 33.4856 | 33.0276 | 32.2609 | 32.26 | 32.2589 | 32.2564 | 32.253 | 32.2487 | 32.2411 | 32.2324 | 32.2196 | 32.2133 | 31.9511 | 31.4415 | 30.8995 | 30.3988 | 32.7435 | 32.7435 | 32.7435 | 32.7435 | 32.7426 | 32.7406 | 32.7376 | 32.7334 | 32.7251 | 32.7236 | 32.7162 | 32.6445 | 32.08 | 31.5529
|  | FAIRFORD | ST |  |  | 34.3318 | 34.3318 | 34.3318 | 34.3318 | 34.3316 | 34.3312 | 34.3306 | 34.3298 | 34.3278 | 34.3269 | 34.3218 | 34.3152 | 34.1231 | 33.8181 | 32.2611 | 32.2604 | 32.2596 | 32.2581 | 32.2561 | 32.2535 | 32.2506 | 32.2475 | 32.2424 | 32.2382 | 32.2236 | 31.9425 | 31.5929 | 31.2601 | 32.7435 | 32.7435 | 32.7435 | 32.7435 | 32.7433 | 32.7429 | 32.7423 | 32.7414 | 32.7395 | 32.7385 | 32.7335 | 32.7269 | 32.7037 | 32.4555
|  | FAIRFORD | SP |  |  | 34.3318 | 34.3318 | 34.3318 | 34.3318 | 34.3294 | 34.327 | 34.3246 | 34.3221 | 34.3182 | 34.3073 | 34.272 | 34.2545 | 34.1973 | 34.1485 | 32.262 | 32.2619 | 32.2618 | 32.2617 | 32.2589 | 32.256 | 32.2528 | 32.2495 | 32.2446 | 32.2324 | 32.1933 | 32.17 | 32.1072 | 32.0531 | 32.7435 | 32.7435 | 32.7435 | 32.7435 | 32.741 | 32.7386 | 32.7362 | 32.7337 | 32.7299 | 32.719 | 32.6836 | 32.6662 | 32.609 | 32.5602
MINETY GSP | STRATTON (2 X 60) | FARINGDON | MINIMUM HEADROOM | SU 28819 94924 | NO | 18.9747 | 18.9747 | 25.3747 | 25.3747 | 25.3393 | 25.3027 | 25.2647 | 25.2246 | 25.1604 | 25.1376 | 25.058 | 24.9853 | 24.4869 | 23.8686 | 13.4427 | 13.4362 | 22.9285 | 22.9144 | 22.8863 | 22.8398 | 22.7953 | 22.7485 | 22.6783 | 22.6495 | 22.4362 | 21.6897 | 20.8925 | 20.1673 | 17.0398 | 17.0331 | 23.4251 | 23.4106 | 23.3827 | 23.3359 | 23.2912 | 23.2099 | 23.0516 | 22.8991 | 22.4568 | 21.6887 | 20.9176 | 20.2178
|  | FARINGDON | CT |  |  | 18.9747 | 18.9747 | 25.3747 | 25.3747 | 25.3737 | 25.3719 | 25.3692 | 25.3652 | 25.3565 | 25.3549 | 25.3466 | 25.1744 | 24.4869 | 23.8686 | 13.4427 | 13.4362 | 22.9285 | 22.9144 | 22.8996 | 22.8837 | 22.8668 | 22.8532 | 22.8358 | 22.8254 | 22.4362 | 21.6897 | 20.8925 | 20.1673 | 17.0398 | 17.0331 | 23.4251 | 23.4106 | 23.3954 | 23.379 | 23.3617 | 23.2099 | 23.0516 | 22.8991 | 22.4568 | 21.6887 | 20.9176 | 20.2178
|  | FARINGDON | LW |  |  | 18.9747 | 18.9747 | 25.3747 | 25.3747 | 25.3674 | 25.3566 | 25.3418 | 25.3228 | 25.287 | 25.2811 | 25.2523 | 25.1856 | 24.4964 | 23.8928 | 13.4434 | 13.4373 | 22.9302 | 22.9173 | 22.8975 | 22.8738 | 22.8496 | 22.8211 | 22.7765 | 22.7617 | 22.511 | 21.7685 | 20.9296 | 20.2191 | 17.0405 | 17.0342 | 23.4269 | 23.4136 | 23.3934 | 23.3693 | 23.3448 | 23.316 | 23.1571 | 23.0002 | 22.5374 | 21.7716 | 20.9482 | 20.2631
|  | FARINGDON | ST |  |  | 18.9747 | 18.9747 | 25.3747 | 25.3747 | 25.3393 | 25.3027 | 25.2647 | 25.2246 | 25.1604 | 25.1376 | 25.058 | 24.9853 | 24.7593 | 24.686 | 13.4452 | 13.4409 | 22.9364 | 22.9297 | 22.8863 | 22.8398 | 22.7953 | 22.7485 | 22.6783 | 22.6495 | 22.5528 | 22.4453 | 21.787 | 21.2885 | 17.0424 | 17.0379 | 23.4333 | 23.4264 | 23.3827 | 23.3359 | 23.2912 | 23.2442 | 23.1738 | 23.1449 | 23.018 | 22.4787 | 21.8055 | 21.2923
|  | FARINGDON | SP |  |  | 18.9747 | 18.9747 | 25.3747 | 25.3747 | 25.3746 | 25.3746 | 25.3745 | 25.3744 | 25.3741 | 25.373 | 25.3667 | 25.3618 | 25.3379 | 25.3147 | 13.4488 | 13.4474 | 22.9463 | 22.9455 | 22.9433 | 22.9407 | 22.9381 | 22.9354 | 22.9323 | 22.9288 | 22.9159 | 22.9005 | 22.8672 | 22.8352 | 17.0461 | 17.0446 | 23.4435 | 23.4427 | 23.4404 | 23.4377 | 23.435 | 23.4323 | 23.429 | 23.4255 | 23.4124 | 23.3967 | 23.3631 | 23.3308
LOVEDEAN GSP | WYMERING BSP | FARLINGTON | MINIMUM HEADROOM | SU 67400 04843 | NO | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4777 | 28.4755 | 28.4705 | 28.4675 | 28.4427 | 27.9835 | 27.2733 | 26.5869 | 22.0025 | 22.002 | 22.0014 | 22.0002 | 21.9983 | 21.9959 | 21.9792 | 21.9551 | 21.9321 | 21.9125 | 21.8491 | 21.2031 | 20.3739 | 19.5684 | 22.073 | 22.0722 | 22.0713 | 22.0696 | 22.0668 | 22.0635 | 22.0561 | 22.0472 | 22.0367 | 22.0271 | 21.755 | 21.11 | 20.3099 | 19.5336
|  | FARLINGTON | CT |  |  | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4773 | 28.4737 | 28.4731 | 28.4522 | 28.0204 | 27.3061 | 26.6121 | 22.0025 | 22.002 | 22.0014 | 22.0002 | 21.9983 | 21.9959 | 21.9905 | 21.9672 | 21.9456 | 21.9264 | 21.8653 | 21.2472 | 20.414 | 19.6009 | 22.073 | 22.0722 | 22.0713 | 22.0696 | 22.0668 | 22.0635 | 22.0602 | 22.0522 | 22.0431 | 22.0368 | 21.8082 | 21.1524 | 20.3482 | 19.5643
|  | FARLINGTON | LW |  |  | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4777 | 28.4755 | 28.4705 | 28.4675 | 28.4427 | 27.9835 | 27.2733 | 26.5869 | 22.0025 | 22.002 | 22.0014 | 22.0002 | 21.9983 | 21.9959 | 21.9792 | 21.9551 | 21.9321 | 21.9125 | 21.8491 | 21.2031 | 20.3739 | 19.5684 | 22.073 | 22.0722 | 22.0713 | 22.0696 | 22.0668 | 22.0635 | 22.0561 | 22.0472 | 22.0367 | 22.0271 | 21.755 | 21.11 | 20.3099 | 19.5336
|  | FARLINGTON | ST |  |  | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4784 | 28.4778 | 28.4763 | 28.4757 | 28.4694 | 28.3901 | 27.9277 | 27.4887 | 22.0028 | 22.0024 | 22.002 | 22.0014 | 22.0002 | 21.9986 | 21.9951 | 21.981 | 21.9673 | 21.954 | 21.9114 | 21.6773 | 21.1364 | 20.6218 | 22.0733 | 22.0727 | 22.0722 | 22.0713 | 22.0696 | 22.0673 | 22.0623 | 22.0568 | 22.0515 | 22.047 | 22.0093 | 21.5677 | 21.046 | 20.5499
|  | FARLINGTON | SP |  |  | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4787 | 28.4786 | 28.4784 | 28.4771 | 28.4762 | 28.4641 | 28.4436 | 22.003 | 22.0028 | 22.0027 | 22.0025 | 22.002 | 22.0013 | 22.0002 | 21.9991 | 21.9979 | 21.9967 | 21.9888 | 21.9489 | 21.8952 | 21.8027 | 22.0737 | 22.0734 | 22.0732 | 22.0729 | 22.0722 | 22.0712 | 22.0697 | 22.068 | 22.0664 | 22.0646 | 22.0586 | 22.0458 | 21.9351 | 21.6887
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH | MINIMUM HEADROOM | SU 88404 53930 | YES | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.1435 | 35.0323 | 34.9162 | 34.7959 | 34.6132 | 34.5879 | 34.0075 | 32.4933 | 30.9813 | 29.7766 | 34.1415 | 34.1308 | 34.1207 | 34.1037 | 33.9798 | 33.851 | 33.4174 | 32.7805 | 32.027 | 31.3932 | 29.9144 | 28.1593 | 26.4288 | 25.017 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.253 | 34.1418 | 33.8544 | 33.2402 | 32.5118 | 31.9047 | 30.4871 | 28.7741 | 27.0778 | 25.6656
|  | FARNBOROUGH | CT |  |  | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2398 | 35.2282 | 35.2164 | 35.2041 | 35.1852 | 35.1828 | 34.8342 | 33.4139 | 32.1199 | 30.9201 | 34.142 | 34.1318 | 34.1222 | 34.1063 | 34.0798 | 34.0516 | 33.8915 | 33.3626 | 32.7729 | 32.1619 | 30.7677 | 29.1065 | 27.5939 | 26.1872 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3493 | 34.3377 | 34.3209 | 33.8147 | 33.2501 | 32.6658 | 31.3356 | 29.7166 | 28.2423 | 26.8358
|  | FARNBOROUGH | LW |  |  | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.1435 | 35.0323 | 34.9162 | 34.7959 | 34.6132 | 34.5879 | 34.0075 | 32.4933 | 30.9813 | 29.7766 | 34.1415 | 34.1308 | 34.1207 | 34.1037 | 33.9798 | 33.851 | 33.4174 | 32.7805 | 32.027 | 31.3932 | 29.9144 | 28.1593 | 26.4288 | 25.017 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.253 | 34.1418 | 33.8544 | 33.2402 | 32.5118 | 31.9047 | 30.4871 | 28.7741 | 27.0778 | 25.6656
|  | FARNBOROUGH | ST |  |  | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 34.4694 | 33.7017 | 34.1434 | 34.1358 | 34.1293 | 34.1197 | 34.1097 | 34.0977 | 34.0821 | 34.0652 | 33.7381 | 33.3208 | 32.3721 | 31.2842 | 30.3262 | 29.4249 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.1757 | 33.7768 | 32.8698 | 31.8377 | 30.9076 | 30.0296
|  | FARNBOROUGH | SP |  |  | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 35.2511 | 34.1457 | 34.1411 | 34.1378 | 34.1339 | 34.1296 | 34.1249 | 34.1188 | 34.1123 | 34.1046 | 34.0971 | 34.08 | 34.0188 | 33.6485 | 33.3043 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.3607 | 34.0901 | 33.761
BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM | MINIMUM HEADROOM | SU 84517 47217 | YES | 31.9305 | 31.9305 | 31.9305 | 31.9305 | 31.9135 | 31.8951 | 31.875 | 31.8533 | 31.8185 | 31.7949 | 31.6047 | 31.5136 | 31.2247 | 30.9823 | 24.2321 | 24.2321 | 24.2321 | 24.2321 | 24.2064 | 24.1622 | 24.1315 | 24.0989 | 24.0545 | 24.0395 | 23.9064 | 23.4994 | 22.4958 | 21.5314 | 24.6269 | 24.6269 | 24.6269 | 24.6269 | 24.5842 | 24.5353 | 24.5026 | 24.468 | 24.4219 | 24.4049 | 24.3011 | 23.9175 | 22.8877 | 21.8922
|  | FARNHAM | CT |  |  | 31.9305 | 31.9305 | 31.9305 | 31.9305 | 31.9302 | 31.9298 | 31.9291 | 31.9281 | 31.9259 | 31.9255 | 31.9234 | 31.9061 | 31.8868 | 31.3621 | 24.2321 | 24.2321 | 24.2321 | 24.2321 | 24.2261 | 24.2008 | 24.1752 | 24.1634 | 24.1516 | 24.1412 | 24.1101 | 23.4994 | 22.4982 | 21.5331 | 24.6269 | 24.6269 | 24.6269 | 24.6269 | 24.6045 | 24.5746 | 24.5444 | 24.5306 | 24.517 | 24.5048 | 24.4683 | 23.9175 | 22.8877 | 21.8922
|  | FARNHAM | LW |  |  | 31.9305 | 31.9305 | 31.9305 | 31.9305 | 31.9135 | 31.8951 | 31.875 | 31.8533 | 31.8185 | 31.8134 | 31.794 | 31.7535 | 31.6739 | 31.3341 | 24.2321 | 24.2321 | 24.2321 | 24.2321 | 24.2064 | 24.1622 | 24.1315 | 24.0989 | 24.0545 | 24.0395 | 23.991 | 23.5574 | 22.4958 | 21.5314 | 24.6269 | 24.6269 | 24.6269 | 24.6269 | 24.5842 | 24.5353 | 24.5026 | 24.468 | 24.4219 | 24.4049 | 24.3511 | 23.9765 | 22.8919 | 21.8972
|  | FARNHAM | ST |  |  | 31.9305 | 31.9305 | 31.9305 | 31.9305 | 31.9214 | 31.912 | 31.9022 | 31.8919 | 31.8754 | 31.8696 | 31.8492 | 31.8301 | 31.7638 | 31.7432 | 24.2321 | 24.2321 | 24.2321 | 24.2321 | 24.223 | 24.2136 | 24.2039 | 24.1922 | 24.1692 | 24.1565 | 24.1165 | 24.0652 | 23.9678 | 23.9166 | 24.6269 | 24.6269 | 24.6269 | 24.6269 | 24.6178 | 24.6084 | 24.5925 | 24.5714 | 24.5472 | 24.5333 | 24.4896 | 24.4324 | 24.3293 | 24.2723
|  | FARNHAM | SP |  |  | 31.9305 | 31.9305 | 31.9305 | 31.9305 | 31.9168 | 31.9033 | 31.8898 | 31.8761 | 31.8547 | 31.7949 | 31.6047 | 31.5136 | 31.2247 | 30.9823 | 24.2321 | 24.2321 | 24.2321 | 24.2321 | 24.2184 | 24.205 | 24.1915 | 24.1778 | 24.1563 | 24.0966 | 23.9064 | 23.8152 | 23.5264 | 23.2839 | 24.6269 | 24.6269 | 24.6269 | 24.6269 | 24.6132 | 24.5997 | 24.5862 | 24.5725 | 24.5511 | 24.4913 | 24.3011 | 24.21 | 23.9211 | 23.6735
IVER 132KV | SLOUGH | FARNHAM ROYAL | MINIMUM HEADROOM | SU 95597 82844 | YES | 50.933 | 50.9174 | 50.9019 | 49.9523 | 49.8734 | 49.7932 | 49.7118 | 49.629 | 49.5412 | 49.5084 | 49.4062 | 49.1123 | 46.8953 | 44.4448 | 33.9125 | 33.897 | 33.8814 | 32.9319 | 32.8529 | 32.7728 | 32.6914 | 32.6086 | 32.5208 | 32.4879 | 32.3857 | 32.0918 | 30.5777 | 27.7686 | 36.9995 | 36.9678 | 36.9385 | 35.959 | 35.8499 | 35.7392 | 35.6283 | 35.5165 | 35.3996 | 35.3357 | 35.1385 | 33.2905 | 30.294 | 27.4755
|  | FARNHAM ROYAL | CT |  |  | 51.0077 | 50.9984 | 50.989 | 50.4193 | 50.3436 | 50.2671 | 50.1898 | 50.1108 | 50.0133 | 49.9881 | 49.9097 | 49.1123 | 46.8953 | 44.4448 | 33.9873 | 33.9779 | 33.9686 | 33.3988 | 33.3231 | 33.2466 | 33.1694 | 33.0903 | 32.9929 | 32.9676 | 32.8893 | 32.0918 | 30.5777 | 27.7686 | 37.0751 | 37.0501 | 37.0279 | 36.4299 | 36.3257 | 36.2202 | 36.1162 | 36.0082 | 35.8817 | 35.8253 | 35.652 | 33.2965 | 30.294 | 27.4755
|  | FARNHAM ROYAL | LW |  |  | 50.933 | 50.9174 | 50.9019 | 49.9523 | 49.8734 | 49.7932 | 49.7118 | 49.629 | 49.5412 | 49.5084 | 49.4062 | 49.2292 | 47.1439 | 44.7246 | 33.9125 | 33.897 | 33.8814 | 32.9319 | 32.8529 | 32.7728 | 32.6914 | 32.6086 | 32.5208 | 32.4879 | 32.3857 | 32.2087 | 30.8093 | 28.0313 | 36.9995 | 36.9678 | 36.9385 | 35.959 | 35.8499 | 35.7392 | 35.6283 | 35.5165 | 35.3996 | 35.3357 | 35.1385 | 33.2905 | 30.5252 | 27.7378
|  | FARNHAM ROYAL | ST |  |  | 51.0451 | 51.0388 | 51.0326 | 50.6528 | 50.59 | 50.5265 | 50.4621 | 50.3962 | 50.3107 | 50.2794 | 50.1797 | 50.0641 | 49.8479 | 49.2807 | 34.0246 | 34.0184 | 34.0122 | 33.6323 | 33.5696 | 33.506 | 33.4416 | 33.3758 | 33.2902 | 33.259 | 33.1592 | 33.0437 | 32.8275 | 32.7019 | 37.1189 | 37.1077 | 37.0898 | 36.6992 | 36.6228 | 36.5429 | 36.4608 | 36.3778 | 36.2724 | 36.22 | 36.0557 | 35.8128 | 34.7013 | 32.9093
|  | FARNHAM ROYAL | SP |  |  | 51.0824 | 51.0793 | 51.0762 | 50.8863 | 50.8707 | 50.8551 | 50.8395 | 50.8239 | 50.8083 | 50.8017 | 50.7808 | 50.748 | 50.721 | 50.6788 | 34.062 | 34.0589 | 34.0557 | 33.8658 | 33.8503 | 33.8347 | 33.8191 | 33.8035 | 33.7878 | 33.7812 | 33.7604 | 33.7275 | 33.7006 | 33.6583 | 37.1608 | 37.1564 | 37.1521 | 36.9603 | 36.9395 | 36.9179 | 36.8964 | 36.8752 | 36.8524 | 36.8376 | 36.7917 | 36.7085 | 36.624 | 36.5236
LALEHAM | EAST BEDFONT A | FELTHAM | MINIMUM HEADROOM | TQ 10628 72811 | YES | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.7565 | 35.6184 | 34.4983 | 28.4795 | 28.4638 | 28.4533 | 28.4351 | 28.4157 | 28.3946 | 28.3743 | 28.3509 | 28.2425 | 28.1299 | 27.8148 | 26.7935 | 25.4527 | 24.1333 | 28.8766 | 28.8509 | 28.8337 | 28.804 | 28.7722 | 28.7375 | 28.7044 | 28.5769 | 28.3587 | 28.1844 | 27.6966 | 26.5888 | 25.2521 | 23.9367
|  | FELTHAM | CT |  |  | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.7905 | 35.6525 | 34.5326 | 28.48 | 28.4646 | 28.4546 | 28.4374 | 28.419 | 28.3987 | 28.3775 | 28.354 | 28.2683 | 28.1557 | 27.8407 | 26.8336 | 25.493 | 24.1737 | 28.8774 | 28.8523 | 28.8358 | 28.8078 | 28.7775 | 28.7444 | 28.7096 | 28.6169 | 28.3987 | 28.2244 | 27.7367 | 26.6288 | 25.2923 | 23.977
|  | FELTHAM | LW |  |  | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.7565 | 35.6184 | 34.4983 | 28.4795 | 28.4638 | 28.4533 | 28.4351 | 28.4157 | 28.3946 | 28.3743 | 28.3509 | 28.2425 | 28.1299 | 27.8148 | 26.7935 | 25.4527 | 24.1333 | 28.8766 | 28.8509 | 28.8337 | 28.804 | 28.7722 | 28.7375 | 28.7044 | 28.5769 | 28.3587 | 28.1844 | 27.6966 | 26.5888 | 25.2521 | 23.9367
|  | FELTHAM | ST |  |  | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.3186 | 28.4816 | 28.4789 | 28.4614 | 28.4518 | 28.4403 | 28.4267 | 28.4136 | 28.3983 | 28.3866 | 28.3771 | 28.3502 | 27.8774 | 27.1143 | 26.2777 | 28.8801 | 28.8757 | 28.8469 | 28.8313 | 28.8125 | 28.7902 | 28.7687 | 28.7437 | 28.7245 | 28.709 | 28.5684 | 27.7935 | 26.9087 | 26.0746
|  | FELTHAM | SP |  |  | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 36.9343 | 28.4837 | 28.4827 | 28.4796 | 28.4758 | 28.4707 | 28.465 | 28.4596 | 28.4535 | 28.4488 | 28.4451 | 28.4345 | 28.4089 | 28.3759 | 28.3092 | 28.8834 | 28.8819 | 28.8768 | 28.8706 | 28.8622 | 28.8528 | 28.844 | 28.834 | 28.8264 | 28.8203 | 28.803 | 28.7611 | 28.707 | 28.462
MANNINGTON GSP | MANNINGTON BSP | FERNDOWN | MINIMUM HEADROOM | SU 06593 00685 | YES | 55.6266 | 55.603 | 55.5794 | 54.1401 | 54.0207 | 53.8996 | 53.7767 | 53.652 | 53.5205 | 53.471 | 53.3175 | 53.0525 | 52.5223 | 51.066 | 53.5303 | 53.5025 | 53.4735 | 52.0228 | 51.8923 | 51.7601 | 51.5987 | 51.4306 | 51.2536 | 51.1545 | 50.8375 | 48.957 | 47.3198 | 45.6442 | 47.6465 | 47.5955 | 47.5359 | 46.021 | 45.8278 | 45.6332 | 45.2545 | 44.8414 | 44.4084 | 44.0298 | 42.7907 | 40.7803 | 39.3533 | 37.8841
|  | FERNDOWN | CT |  |  | 55.7399 | 55.7257 | 55.7116 | 54.848 | 54.7739 | 54.6993 | 54.6243 | 54.5486 | 54.4689 | 54.4393 | 54.3485 | 53.2747 | 52.7032 | 51.2379 | 53.6439 | 53.6258 | 53.6066 | 52.7323 | 52.6477 | 52.5627 | 52.4721 | 52.353 | 52.2279 | 52.1487 | 51.8944 | 49.3801 | 47.5319 | 45.8475 | 47.762 | 47.7221 | 47.674 | 46.7392 | 46.5957 | 46.4519 | 46.2736 | 45.9097 | 45.5286 | 45.1698 | 43.9936 | 41.174 | 39.536 | 38.0579
|  | FERNDOWN | LW |  |  | 55.6266 | 55.603 | 55.5794 | 54.1401 | 54.0207 | 53.8996 | 53.7767 | 53.652 | 53.5205 | 53.471 | 53.3175 | 53.0525 | 52.5223 | 51.066 | 53.5303 | 53.5025 | 53.4735 | 52.0228 | 51.8923 | 51.7601 | 51.5987 | 51.4306 | 51.2536 | 51.1545 | 50.8375 | 48.957 | 47.3198 | 45.6442 | 47.6465 | 47.5955 | 47.5359 | 46.021 | 45.8278 | 45.6332 | 45.2545 | 44.8414 | 44.4084 | 44.0298 | 42.7907 | 40.7803 | 39.3533 | 37.8841
|  | FERNDOWN | ST |  |  | 55.7965 | 55.7871 | 55.7776 | 55.2019 | 55.1544 | 55.1066 | 55.0584 | 55.0098 | 54.9595 | 54.9391 | 54.8743 | 54.7693 | 54.6752 | 54.5577 | 53.6996 | 53.6858 | 53.6712 | 53.0867 | 53.0284 | 52.9675 | 52.8908 | 52.8104 | 52.7293 | 52.675 | 52.4971 | 52.1083 | 51.0859 | 50.0514 | 47.8126 | 47.7742 | 47.7305 | 47.0965 | 46.9773 | 46.8431 | 46.6049 | 46.3456 | 46.0906 | 45.8452 | 45.0294 | 43.7219 | 42.8352 | 41.9347
|  | FERNDOWN | SP |  |  | 55.8531 | 55.8484 | 55.8437 | 55.5558 | 55.5322 | 55.5086 | 55.485 | 55.4613 | 55.4376 | 55.4277 | 55.3964 | 55.3469 | 55.3074 | 55.2446 | 53.7615 | 53.7563 | 53.7511 | 53.4629 | 53.4375 | 53.4117 | 53.3792 | 53.3454 | 53.3089 | 53.2857 | 53.2102 | 53.089 | 53.0053 | 52.9006 | 47.9042 | 47.8965 | 47.8889 | 47.5982 | 47.5626 | 47.5248 | 47.4421 | 47.3512 | 47.2425 | 47.1447 | 46.8195 | 46.2942 | 45.9617 | 45.6204
BRAMLEY (FLEE) | FERNHURST | FIVE OAKS | MINIMUM HEADROOM | TQ 10647 29057 | YES | 15.4279 | 15.3539 | 15.2336 | 15.0164 | 14.789 | 14.5457 | 14.4408 | 14.3199 | 14.1874 | 14.0835 | 13.7762 | 13.2612 | 12.671 | 12.2729 | 13.54 | 13.4528 | 13.3113 | 13.0558 | 12.789 | 12.5044 | 12.3837 | 12.2453 | 12.097 | 11.976 | 11.6212 | 11.0314 | 10.3688 | 9.9025 | 13.8049 | 13.7203 | 13.5827 | 13.3344 | 13.0749 | 12.7981 | 12.6804 | 12.5453 | 12.3999 | 12.2821 | 11.9362 | 11.3604 | 10.7113 | 10.2578
|  | FIVE OAKS | CT |  |  | 15.4415 | 15.3773 | 15.2701 | 15.0802 | 14.8826 | 14.6727 | 14.5189 | 14.4137 | 14.3112 | 14.2123 | 13.9306 | 13.4052 | 12.8806 | 12.4597 | 13.5559 | 13.4804 | 13.3542 | 13.1308 | 12.8985 | 12.652 | 12.4718 | 12.349 | 12.2307 | 12.1148 | 11.7855 | 11.1854 | 10.5883 | 10.0993 | 13.8204 | 13.7471 | 13.6244 | 13.4073 | 13.1815 | 12.9418 | 12.7666 | 12.6471 | 12.5318 | 12.419 | 12.0986 | 11.5125 | 10.9289 | 10.4527
|  | FIVE OAKS | LW |  |  | 15.4279 | 15.3539 | 15.2336 | 15.0164 | 14.789 | 14.5457 | 14.4408 | 14.3199 | 14.1874 | 14.0835 | 13.7762 | 13.2612 | 12.671 | 12.2729 | 13.54 | 13.4528 | 13.3113 | 13.0558 | 12.789 | 12.5044 | 12.3837 | 12.2453 | 12.097 | 11.976 | 11.6212 | 11.0314 | 10.3688 | 9.9025 | 13.8049 | 13.7203 | 13.5827 | 13.3344 | 13.0749 | 12.7981 | 12.6804 | 12.5453 | 12.3999 | 12.2821 | 11.9362 | 11.3604 | 10.7113 | 10.2578
|  | FIVE OAKS | ST |  |  | 15.4388 | 15.3758 | 15.2851 | 15.1459 | 14.9742 | 14.7666 | 14.6848 | 14.5956 | 14.5248 | 14.454 | 14.245 | 13.9275 | 13.5437 | 13.2494 | 13.5527 | 13.4786 | 13.3719 | 13.2081 | 13.0063 | 12.7623 | 12.6666 | 12.5624 | 12.4809 | 12.3985 | 12.1571 | 11.7895 | 11.3589 | 11.0203 | 13.8173 | 13.7453 | 13.6416 | 13.4824 | 13.2862 | 13.0491 | 12.956 | 12.8546 | 12.7751 | 12.6948 | 12.4595 | 12.1013 | 11.6795 | 11.3492
|  | FIVE OAKS | SP |  |  | 15.5029 | 15.4891 | 15.4643 | 15.4389 | 15.3872 | 15.3282 | 15.2972 | 15.2637 | 15.2243 | 15.1831 | 15.0587 | 14.9214 | 14.7223 | 14.5463 | 13.6281 | 13.612 | 13.5828 | 13.5528 | 13.4926 | 13.4238 | 13.3878 | 13.349 | 13.3036 | 13.2579 | 13.1209 | 12.9644 | 12.7481 | 12.5568 | 13.8906 | 13.8749 | 13.8466 | 13.8175 | 13.7589 | 13.6919 | 13.6568 | 13.619 | 13.5747 | 13.5299 | 13.3952 | 13.2423 | 13.0292 | 12.8408
AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH | MINIMUM HEADROOM | SU 90667 89318 | YES | 31.936 | 31.936 | 31.936 | 31.936 | 31.8604 | 31.7835 | 31.7053 | 31.6237 | 31.4979 | 31.4819 | 31.4307 | 31.1943 | 30.9289 | 30.8679 | 29.9155 | 29.8542 | 29.7737 | 29.6044 | 29.3746 | 29.1374 | 28.9002 | 28.6589 | 28.3746 | 28.1881 | 27.6277 | 26.4995 | 25.2801 | 24.2766 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.0475 | 30.9706 | 30.8924 | 30.8108 | 30.685 | 30.6691 | 30.6179 | 30.3636 | 29.1853 | 28.218
|  | FLACKWELL HEATH | CT |  |  | 31.936 | 31.936 | 31.936 | 31.936 | 31.8604 | 31.7835 | 31.7053 | 31.6237 | 31.4979 | 31.4819 | 31.4307 | 31.1943 | 30.9289 | 30.8679 | 29.917 | 29.8567 | 29.7776 | 29.6116 | 29.3746 | 29.1374 | 28.9002 | 28.6589 | 28.3746 | 28.1881 | 27.6277 | 26.4995 | 25.2801 | 24.2766 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.0475 | 30.9706 | 30.8924 | 30.8108 | 30.685 | 30.6691 | 30.6179 | 30.3636 | 29.1853 | 28.218
|  | FLACKWELL HEATH | LW |  |  | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 29.9155 | 29.8542 | 29.7737 | 29.6044 | 29.44 | 29.2766 | 29.1158 | 28.9561 | 28.7977 | 28.6272 | 28.1179 | 27.2261 | 26.272 | 25.329 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.0953 | 30.1778 | 29.271
|  | FLACKWELL HEATH | ST |  |  | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 29.9295 | 29.8801 | 29.8218 | 29.7227 | 29.601 | 29.4543 | 29.3265 | 29.2 | 29.0916 | 28.9753 | 28.6313 | 28.0331 | 27.4155 | 26.8052 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1151 | 30.6906
|  | FLACKWELL HEATH | SP |  |  | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 31.936 | 29.9856 | 29.9788 | 29.9722 | 29.9657 | 29.9381 | 29.9052 | 29.8617 | 29.8186 | 29.7635 | 29.7184 | 29.5854 | 29.3556 | 29.1198 | 28.8903 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231 | 31.1231
NURSLING GSP | ROWNHAMS | FLETCHWOOD | MINIMUM HEADROOM | SU 33800 12142 | YES | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.3925 | 36.3835 | 36.3742 | 36.3647 | 36.3499 | 36.3448 | 36.3023 | 36.2748 | 35.8849 | 34.8686 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3282 | 33.3191 | 33.3099 | 33.3003 | 33.2855 | 33.2805 | 32.1225 | 30.47 | 29.167 | 27.9523 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3818 | 35.3727 | 35.3635 | 35.3539 | 35.3391 | 35.2276 | 34.0623 | 32.4178 | 31.1211 | 29.9123
|  | FLETCHWOOD | CT |  |  | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 35.979 | 34.9631 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 32.235 | 30.5821 | 29.2794 | 28.0653 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3393 | 34.1743 | 32.5294 | 31.2329 | 30.0248
|  | FLETCHWOOD | LW |  |  | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 35.8849 | 34.8686 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.2935 | 32.1225 | 30.47 | 29.167 | 27.9523 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.2276 | 34.0623 | 32.4178 | 31.1211 | 29.9123
|  | FLETCHWOOD | ST |  |  | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.3925 | 36.3835 | 36.3742 | 36.3647 | 36.3499 | 36.3448 | 36.3288 | 36.3159 | 36.2735 | 36.2602 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3282 | 33.3191 | 33.3099 | 33.3003 | 33.2855 | 33.2805 | 33.0154 | 31.8727 | 30.9886 | 30.1851 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3818 | 35.3727 | 35.3635 | 35.3539 | 35.3391 | 35.3341 | 34.9506 | 33.8133 | 32.9333 | 32.1336
|  | FLETCHWOOD | SP |  |  | 36.4015 | 36.4015 | 36.4015 | 36.4015 | 36.3973 | 36.3932 | 36.389 | 36.3848 | 36.3783 | 36.3601 | 36.3023 | 36.2748 | 36.1881 | 36.1156 | 33.3371 | 33.3371 | 33.3371 | 33.3371 | 33.3329 | 33.3288 | 33.3247 | 33.3205 | 33.3139 | 33.2957 | 33.2379 | 33.2104 | 33.1237 | 33.0512 | 35.3907 | 35.3907 | 35.3907 | 35.3907 | 35.3865 | 35.3824 | 35.3783 | 35.3741 | 35.3675 | 35.3493 | 35.2915 | 35.264 | 35.1773 | 35.043
MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE | MINIMUM HEADROOM | SU 14069 15523 | YES | 17.8129 | 17.8129 | 17.8129 | 17.8129 | 17.7682 | 17.7212 | 17.6712 | 17.6184 | 17.5362 | 17.5246 | 17.4823 | 17.3457 | 16.7874 | 16.3674 | 14.9996 | 14.9939 | 14.9767 | 14.943 | 14.8731 | 14.7835 | 14.6316 | 14.4667 | 14.2752 | 14.1541 | 13.7844 | 13.3783 | 12.9417 | 12.6389 | 16.6848 | 16.6842 | 16.6826 | 16.6794 | 16.6323 | 16.5813 | 16.5215 | 16.458 | 16.3654 | 16.3433 | 16.2699 | 16.1314 | 15.4987 | 15.0071
|  | FORDINGBRIDGE | CT |  |  | 17.8129 | 17.8129 | 17.8129 | 17.8129 | 17.8126 | 17.8121 | 17.8113 | 17.8103 | 17.8079 | 17.8075 | 17.8052 | 17.7742 | 17.3268 | 16.9098 | 14.9996 | 14.9939 | 14.9767 | 14.943 | 14.9162 | 14.8727 | 14.8109 | 14.6978 | 14.586 | 14.4761 | 14.1465 | 13.7912 | 13.4655 | 13.1657 | 16.6848 | 16.6842 | 16.6826 | 16.6794 | 16.6766 | 16.672 | 16.6654 | 16.6537 | 16.6408 | 16.63 | 16.5965 | 16.5456 | 16.0478 | 15.5591
|  | FORDINGBRIDGE | LW |  |  | 17.8129 | 17.8129 | 17.8129 | 17.8129 | 17.7682 | 17.7212 | 17.6712 | 17.6184 | 17.5362 | 17.5246 | 17.4823 | 17.3457 | 16.7874 | 16.3674 | 14.9998 | 14.9942 | 14.9773 | 14.9439 | 14.8731 | 14.7835 | 14.6316 | 14.4667 | 14.2752 | 14.1541 | 13.7844 | 13.3783 | 12.9417 | 12.6389 | 16.6848 | 16.6843 | 16.6826 | 16.6795 | 16.6323 | 16.5813 | 16.5215 | 16.458 | 16.3654 | 16.3433 | 16.2699 | 16.1314 | 15.4987 | 15.0071
|  | FORDINGBRIDGE | ST |  |  | 17.8129 | 17.8129 | 17.8129 | 17.8129 | 17.7902 | 17.7669 | 17.7431 | 17.7181 | 17.679 | 17.6655 | 17.6204 | 17.581 | 17.4495 | 17.3568 | 15 | 14.9991 | 14.9882 | 14.9693 | 14.9307 | 14.8787 | 14.7862 | 14.6859 | 14.573 | 14.4846 | 14.212 | 13.9456 | 13.6175 | 13.3849 | 16.685 | 16.6847 | 16.6837 | 16.6819 | 16.6577 | 16.6317 | 16.6013 | 16.5692 | 16.523 | 16.5023 | 16.4355 | 16.3746 | 16.2242 | 16.1453
|  | FORDINGBRIDGE | SP |  |  | 17.8129 | 17.8129 | 17.8129 | 17.8129 | 17.8117 | 17.8105 | 17.8093 | 17.808 | 17.8061 | 17.8006 | 17.7825 | 17.7733 | 17.7422 | 17.7152 | 15 | 15 | 15 | 14.9929 | 14.9854 | 14.9724 | 14.946 | 14.9174 | 14.8862 | 14.8512 | 14.7437 | 14.6471 | 14.5442 | 14.4514 | 16.6854 | 16.6853 | 16.6849 | 16.6841 | 16.6823 | 16.68 | 16.6764 | 16.6726 | 16.6679 | 16.6596 | 16.6329 | 16.6154 | 16.5774 | 16.5442
LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK | MINIMUM HEADROOM | SU 66139 00180 | YES | 42.1266 | 42.1148 | 42.1029 | 41.3819 | 41.2881 | 41.1932 | 41.0967 | 40.9989 | 40.8809 | 40.8491 | 40.7503 | 40.5822 | 38.5018 | 36.0032 | 26.1575 | 26.1143 | 26.098 | 25.3703 | 25.2695 | 25.1665 | 25.0451 | 24.9223 | 24.7789 | 24.72 | 24.5347 | 21.8188 | 18.8552 | 15.9454 | 26.5611 | 26.5157 | 26.4991 | 25.771 | 25.6696 | 25.5661 | 25.4429 | 25.3183 | 25.1731 | 25.1123 | 24.9209 | 23.1733 | 20.2472 | 17.3744
|  | FRATTON PARK | CT |  |  | 42.1833 | 42.1762 | 42.1691 | 41.7365 | 41.6897 | 41.6427 | 41.5954 | 41.5477 | 41.4933 | 41.4767 | 41.4264 | 40.8678 | 38.978 | 36.4754 | 26.2142 | 26.1757 | 26.1642 | 25.7249 | 25.671 | 25.6159 | 25.5607 | 25.488 | 25.4082 | 25.3645 | 25.2278 | 22.4047 | 19.3759 | 16.4621 | 26.6178 | 26.5771 | 26.5653 | 26.1256 | 26.0711 | 26.0155 | 25.9596 | 25.8852 | 25.8036 | 25.758 | 25.6152 | 23.7552 | 20.7639 | 17.8872
|  | FRATTON PARK | LW |  |  | 42.1266 | 42.1148 | 42.1029 | 41.3819 | 41.2881 | 41.1932 | 41.0967 | 40.9989 | 40.8809 | 40.8491 | 40.7503 | 40.5822 | 38.5018 | 36.0032 | 26.1575 | 26.1143 | 26.098 | 25.3703 | 25.2695 | 25.1665 | 25.0451 | 24.9223 | 24.7789 | 24.72 | 24.5347 | 21.8188 | 18.8552 | 15.9454 | 26.5611 | 26.5157 | 26.4991 | 25.771 | 25.6696 | 25.5661 | 25.4429 | 25.3183 | 25.1731 | 25.1123 | 24.9209 | 23.1733 | 20.2472 | 17.3744
|  | FRATTON PARK | ST |  |  | 42.2117 | 42.207 | 42.2022 | 41.9138 | 41.8902 | 41.8665 | 41.8429 | 41.8193 | 41.7956 | 41.7862 | 41.7578 | 41.7105 | 41.6822 | 40.6015 | 26.2412 | 26.2321 | 26.1953 | 25.9 | 25.8681 | 25.8343 | 25.7959 | 25.7575 | 25.7166 | 25.6886 | 25.6008 | 24.7982 | 22.9419 | 21.1095 | 26.6447 | 26.6353 | 26.5962 | 26.3004 | 26.2679 | 26.2335 | 26.194 | 26.1546 | 26.1124 | 26.0831 | 25.9911 | 25.8388 | 24.2961 | 22.4875
|  | FRATTON PARK | SP |  |  | 42.24 | 42.2377 | 42.2353 | 42.0911 | 42.0793 | 42.0675 | 42.0557 | 42.0438 | 42.032 | 42.0273 | 42.0131 | 41.9895 | 41.9753 | 41.9493 | 26.2728 | 26.2688 | 26.2407 | 26.0951 | 26.0814 | 26.0674 | 26.0508 | 26.0344 | 26.0169 | 26.0049 | 25.9675 | 25.9049 | 25.8478 | 25.7787 | 26.6766 | 26.6724 | 26.6425 | 26.4968 | 26.4829 | 26.4688 | 26.4519 | 26.4352 | 26.4172 | 26.4047 | 26.3657 | 26.3004 | 26.2402 | 26.168
COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD | MINIMUM HEADROOM | SP 50426 08256 | YES | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 22.9255 | 22.4557 | 22.0083 | 21.9186 | 21.8051 | 21.6733 | 21.3416 | 20.6458 | 19.8221 | 18.9982 | 17.4619 | 17.4453 | 17.4212 | 17.3737 | 16.9275 | 16.3732 | 15.8454 | 15.7396 | 15.6057 | 15.4502 | 15.0589 | 14.2381 | 13.2663 | 12.2943 | 18.3621 | 18.3503 | 18.3332 | 18.2995 | 18.2677 | 18.1784 | 17.689 | 17.5909 | 17.4668 | 17.3158 | 16.9244 | 16.1032 | 15.1311 | 14.1589
|  | FRENCHAY ROAD | CT |  |  | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 22.9378 | 22.4716 | 22.0083 | 21.9186 | 21.8051 | 21.6733 | 21.3416 | 20.6458 | 19.8221 | 18.9982 | 17.4621 | 17.4456 | 17.4217 | 17.3745 | 16.942 | 16.392 | 15.8454 | 15.7396 | 15.6057 | 15.4502 | 15.0589 | 14.2381 | 13.2663 | 12.2943 | 18.3622 | 18.3505 | 18.3336 | 18.3 | 18.2685 | 18.1957 | 17.689 | 17.5909 | 17.4668 | 17.3158 | 16.9244 | 16.1032 | 15.1311 | 14.1589
|  | FRENCHAY ROAD | LW |  |  | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 22.9255 | 22.4557 | 22.3696 | 22.2799 | 22.1664 | 22.0346 | 21.703 | 21.007 | 20.1833 | 19.3591 | 17.4619 | 17.4453 | 17.4212 | 17.3737 | 16.9275 | 16.3732 | 16.2716 | 16.1658 | 16.0319 | 15.8765 | 15.4852 | 14.6642 | 13.6924 | 12.7201 | 18.3621 | 18.3503 | 18.3332 | 18.2995 | 18.2677 | 18.1784 | 18.0842 | 17.9861 | 17.8619 | 17.7179 | 17.3508 | 16.5295 | 15.5574 | 14.5847
|  | FRENCHAY ROAD | ST |  |  | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 22.6834 | 22.1417 | 21.6164 | 17.475 | 17.4681 | 17.4583 | 17.4433 | 17.4262 | 17.4058 | 17.3972 | 17.3883 | 17.3811 | 17.3727 | 17.2085 | 16.6419 | 16.0028 | 15.3831 | 18.3714 | 18.3665 | 18.3596 | 18.3489 | 18.3368 | 18.3223 | 18.3161 | 18.3099 | 18.3048 | 18.2987 | 18.2836 | 18.2516 | 17.835 | 17.2486
|  | FRENCHAY ROAD | SP |  |  | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 23.1354 | 17.481 | 17.4792 | 17.4764 | 17.474 | 17.4666 | 17.458 | 17.4544 | 17.4508 | 17.4458 | 17.4424 | 17.4341 | 17.4158 | 17.3931 | 17.3695 | 18.3757 | 18.3744 | 18.3724 | 18.3707 | 18.3654 | 18.3593 | 18.3568 | 18.3543 | 18.3506 | 18.3483 | 18.3424 | 18.3294 | 18.3133 | 18.2965
FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER | MINIMUM HEADROOM | SZ 34325 86965 | NO | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.0763 | 16.8925 | 16.6168 | 16.339 | 16.067 | 16.5226 | 16.5206 | 16.5177 | 16.5128 | 16.5075 | 16.5036 | 16.4887 | 16.4735 | 16.4579 | 16.421 | 16.0309 | 15.446 | 14.8565 | 14.2793 | 16.7641 | 16.7633 | 16.762 | 16.7598 | 16.7575 | 16.7558 | 16.7493 | 16.7426 | 16.7358 | 16.7285 | 16.4574 | 15.8734 | 15.2817 | 14.7025
|  | FRESHWATER | CT |  |  | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.115 | 16.9312 | 16.6554 | 16.3777 | 16.1058 | 16.5226 | 16.5206 | 16.5177 | 16.5128 | 16.5075 | 16.5036 | 16.4994 | 16.4842 | 16.4687 | 16.4519 | 16.1129 | 15.5279 | 14.9386 | 14.3617 | 16.7641 | 16.7633 | 16.762 | 16.7598 | 16.7575 | 16.7558 | 16.754 | 16.7473 | 16.7405 | 16.7332 | 16.5387 | 15.9556 | 15.3641 | 14.7852
|  | FRESHWATER | LW |  |  | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.0763 | 16.8925 | 16.6168 | 16.339 | 16.067 | 16.5226 | 16.5206 | 16.5177 | 16.5128 | 16.5075 | 16.5036 | 16.4887 | 16.4735 | 16.4579 | 16.421 | 16.0309 | 15.446 | 14.8565 | 14.2793 | 16.7641 | 16.7633 | 16.762 | 16.7598 | 16.7575 | 16.7558 | 16.7493 | 16.7426 | 16.7358 | 16.7285 | 16.4574 | 15.8734 | 15.2817 | 14.7025
|  | FRESHWATER | ST |  |  | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.0657 | 16.881 | 16.7017 | 16.5253 | 16.5232 | 16.5218 | 16.52 | 16.5174 | 16.5142 | 16.5115 | 16.5034 | 16.4951 | 16.4845 | 16.4731 | 16.3983 | 16.0064 | 15.6261 | 15.2518 | 16.7644 | 16.7638 | 16.763 | 16.7618 | 16.7604 | 16.7593 | 16.7557 | 16.7521 | 16.7475 | 16.7424 | 16.7272 | 16.4332 | 16.0541 | 15.6785
|  | FRESHWATER | SP |  |  | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.1178 | 17.0652 | 16.5239 | 16.5233 | 16.5225 | 16.5217 | 16.5204 | 16.5195 | 16.5173 | 16.515 | 16.512 | 16.5075 | 16.494 | 16.4742 | 16.4557 | 16.3974 | 16.7647 | 16.7644 | 16.7641 | 16.7637 | 16.7632 | 16.7628 | 16.7618 | 16.7608 | 16.7595 | 16.7575 | 16.7516 | 16.743 | 16.7348 | 16.7271
BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY | MINIMUM HEADROOM | SU 87745 57942 | YES | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.2468 | 34.9425 | 34.9368 | 34.9294 | 34.9139 | 34.8988 | 34.8837 | 34.8707 | 34.8578 | 34.8449 | 34.8311 | 34.789 | 34.3123 | 32.7017 | 31.0783 | 35.3319 | 35.3262 | 35.3188 | 35.3032 | 35.2881 | 35.273 | 35.2599 | 35.247 | 35.2341 | 35.2202 | 35.178 | 34.6069 | 33.088 | 31.5763
|  | FRIMLEY | CT |  |  | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.3214 | 34.9432 | 34.938 | 34.9311 | 34.9169 | 34.9031 | 34.8893 | 34.8756 | 34.8627 | 34.8498 | 34.836 | 34.7939 | 34.3978 | 32.7875 | 31.1659 | 35.3326 | 35.3274 | 35.3205 | 35.3063 | 35.2924 | 35.2786 | 35.2648 | 35.2519 | 35.239 | 35.2251 | 35.1829 | 34.6875 | 33.1689 | 31.6579
|  | FRIMLEY | LW |  |  | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.2468 | 34.9425 | 34.9368 | 34.9294 | 34.9139 | 34.8988 | 34.8837 | 34.8707 | 34.8578 | 34.8449 | 34.8311 | 34.789 | 34.3123 | 32.7017 | 31.0783 | 35.3319 | 35.3262 | 35.3188 | 35.3032 | 35.2881 | 35.273 | 35.2599 | 35.247 | 35.2341 | 35.2202 | 35.178 | 34.6069 | 33.088 | 31.5763
|  | FRIMLEY | ST |  |  | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 34.9458 | 34.9427 | 34.939 | 34.9328 | 34.9252 | 34.916 | 34.9058 | 34.8957 | 34.8869 | 34.8775 | 34.8489 | 34.7934 | 34.7333 | 33.7368 | 35.3353 | 35.3322 | 35.3285 | 35.3222 | 35.3146 | 35.3054 | 35.2952 | 35.285 | 35.2762 | 35.2667 | 35.2381 | 35.1824 | 35.0366 | 34.0641
|  | FRIMLEY | SP |  |  | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 36.405 | 34.9489 | 34.9482 | 34.9475 | 34.9468 | 34.9442 | 34.9412 | 34.9377 | 34.9343 | 34.9299 | 34.9262 | 34.9151 | 34.8933 | 34.8686 | 34.8437 | 35.3383 | 35.3376 | 35.337 | 35.3363 | 35.3337 | 35.3306 | 35.3271 | 35.3237 | 35.3193 | 35.3156 | 35.3045 | 35.2826 | 35.2578 | 35.2328
MELKSHAM GSP | FROME BSP | FROME | MINIMUM HEADROOM | ST 78850 48051 | YES | 71.7621 | 71.7392 | 71.7163 | 70.3178 | 70.187 | 70.039 | 69.872 | 69.6849 | 69.4361 | 69.3684 | 69.1272 | 67.5098 | 65.3357 | 63.5354 | 67.5947 | 67.5568 | 67.4835 | 66.0666 | 65.9177 | 65.7515 | 65.5633 | 65.3548 | 65.0349 | 64.444 | 62.5432 | 59.6986 | 57.2959 | 55.2768 | 68.881 | 68.8581 | 68.8352 | 67.4367 | 67.3059 | 67.1499 | 66.9491 | 66.3489 | 65.6664 | 65.1364 | 63.4289 | 60.802 | 58.4791 | 56.4719
|  | FROME | CT |  |  | 71.8722 | 71.8584 | 71.8447 | 71.0056 | 70.9319 | 70.8539 | 70.7715 | 70.6828 | 70.5744 | 70.5403 | 70.4253 | 68.2071 | 65.988 | 64.1393 | 67.7053 | 67.6768 | 67.6132 | 66.7567 | 66.6659 | 66.5707 | 66.4727 | 66.3627 | 66.2318 | 65.8332 | 64.059 | 60.4232 | 57.9756 | 55.9083 | 68.9911 | 68.9773 | 68.9636 | 68.1245 | 68.0508 | 67.9704 | 67.8676 | 67.5389 | 66.9968 | 66.5004 | 64.9193 | 61.5171 | 59.1493 | 57.1043
|  | FROME | LW |  |  | 71.7621 | 71.7392 | 71.7163 | 70.3178 | 70.187 | 70.039 | 69.872 | 69.6849 | 69.4361 | 69.3684 | 69.1272 | 67.5098 | 65.3357 | 63.5354 | 67.5947 | 67.5568 | 67.4835 | 66.0666 | 65.9177 | 65.7515 | 65.5633 | 65.3548 | 65.0349 | 64.444 | 62.5432 | 59.6986 | 57.2959 | 55.2768 | 68.881 | 68.8581 | 68.8352 | 67.4367 | 67.3059 | 67.1499 | 66.9491 | 66.3489 | 65.6664 | 65.1364 | 63.4289 | 60.802 | 58.4791 | 56.4719
|  | FROME | ST |  |  | 71.9272 | 71.918 | 71.9089 | 71.3495 | 71.2979 | 71.243 | 71.1846 | 71.1211 | 71.041 | 71.0078 | 70.8814 | 70.7024 | 70.3529 | 69.8335 | 67.7608 | 67.7454 | 67.7215 | 67.1504 | 67.0857 | 67.0158 | 66.9442 | 66.8675 | 66.7722 | 66.7226 | 66.5437 | 64.9953 | 63.4737 | 62.1422 | 69.0461 | 69.0369 | 69.0278 | 68.4684 | 68.4169 | 68.3619 | 68.3035 | 68.24 | 68.1599 | 68.1218 | 67.3985 | 65.7789 | 64.3938 | 63.1941
|  | FROME | SP |  |  | 71.9822 | 71.9776 | 71.9731 | 71.6934 | 71.6703 | 71.6471 | 71.6236 | 71.6 | 71.5754 | 71.5597 | 71.4948 | 71.4193 | 71.2499 | 71.061 | 67.82 | 67.8129 | 67.7983 | 67.5153 | 67.4879 | 67.4601 | 67.4321 | 67.404 | 67.3738 | 67.3517 | 67.2663 | 67.1617 | 66.9726 | 66.7659 | 69.1011 | 69.0965 | 69.092 | 68.8123 | 68.7892 | 68.766 | 68.7425 | 68.7189 | 68.6943 | 68.6786 | 68.6138 | 68.5382 | 68.3688 | 68.162
COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE | MINIMUM HEADROOM | SU 84935 93873 | YES | 30.7647 | 30.7443 | 30.7221 | 29.8146 | 29.7272 | 29.6405 | 29.5522 | 29.4639 | 29.3758 | 29.3304 | 29.1951 | 28.9684 | 28.7969 | 28.2328 | 22.8302 | 22.8048 | 22.7761 | 21.856 | 21.7565 | 21.6583 | 21.5572 | 21.4562 | 21.3553 | 21.2963 | 21.0249 | 19.7255 | 18.4379 | 17.0979 | 23.3066 | 23.2872 | 23.2665 | 22.3619 | 22.2772 | 22.1931 | 22.1077 | 22.0224 | 21.9371 | 21.8948 | 21.7687 | 21.5574 | 20.3657 | 19.028
|  | FRYERS LANE | CT |  |  | 30.8361 | 30.8222 | 30.8069 | 30.2586 | 30.2026 | 30.1472 | 30.0921 | 30.0331 | 29.9742 | 29.9405 | 29.8404 | 29.1197 | 28.8101 | 28.3948 | 22.9024 | 22.8843 | 22.8635 | 22.3044 | 22.238 | 22.173 | 22.1084 | 22.0366 | 21.965 | 21.9177 | 21.7773 | 20.0534 | 18.6279 | 17.2885 | 23.3777 | 23.3648 | 23.3508 | 22.805 | 22.7512 | 22.6981 | 22.6451 | 22.589 | 22.533 | 22.5024 | 22.4114 | 21.7062 | 20.5554 | 19.2182
|  | FRYERS LANE | LW |  |  | 30.7647 | 30.7443 | 30.7221 | 29.8146 | 29.7272 | 29.6405 | 29.5522 | 29.4639 | 29.3758 | 29.3304 | 29.1951 | 28.9684 | 28.7969 | 28.2328 | 22.8302 | 22.8048 | 22.7761 | 21.856 | 21.7565 | 21.6583 | 21.5572 | 21.4562 | 21.3553 | 21.2963 | 21.0249 | 19.7255 | 18.4379 | 17.0979 | 23.3066 | 23.2872 | 23.2665 | 22.3619 | 22.2772 | 22.1931 | 22.1077 | 22.0224 | 21.9371 | 21.8948 | 21.7687 | 21.5574 | 20.3657 | 19.028
|  | FRYERS LANE | ST |  |  | 30.8711 | 30.8604 | 30.8489 | 30.4827 | 30.4425 | 30.4006 | 30.3612 | 30.3218 | 30.2823 | 30.2596 | 30.1924 | 30.0801 | 29.9909 | 29.8732 | 22.9373 | 22.9226 | 22.9063 | 22.5323 | 22.4829 | 22.4303 | 22.3823 | 22.3344 | 22.2862 | 22.2542 | 22.1598 | 21.8501 | 21.0402 | 20.211 | 23.4127 | 23.403 | 23.3925 | 23.0281 | 22.99 | 22.9506 | 22.9131 | 22.8757 | 22.8381 | 22.8175 | 22.7565 | 22.6545 | 22.5757 | 22.1374
|  | FRYERS LANE | SP |  |  | 30.9111 | 30.9071 | 30.9032 | 30.7237 | 30.7064 | 30.6891 | 30.671 | 30.6529 | 30.6339 | 30.6238 | 30.5938 | 30.544 | 30.5063 | 30.4549 | 22.9815 | 22.9767 | 22.9719 | 22.7915 | 22.7721 | 22.7524 | 22.7314 | 22.7105 | 22.6877 | 22.674 | 22.6335 | 22.5663 | 22.5115 | 22.4438 | 23.4518 | 23.448 | 23.4443 | 23.265 | 23.2482 | 23.2314 | 23.214 | 23.1966 | 23.1784 | 23.1691 | 23.1415 | 23.0956 | 23.0618 | 23.0141
COWLEY GSP | DRAYTON BSP | FULSCOT | MINIMUM HEADROOM | SU 54413 89511 | NO | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 25.7648 | 24.898 | 24.0513 | 24.5156 | 24.5031 | 24.4928 | 24.4758 | 24.4589 | 24.4393 | 24.4188 | 24.3993 | 24.381 | 24.0643 | 23.1676 | 22.0218 | 20.9615 | 19.9626 | 21.2353 | 20.9711 | 20.7558 | 20.3994 | 20.0447 | 19.6342 | 19.2027 | 18.7937 | 18.4107 | 18.0347 | 17.1378 | 15.9915 | 14.9309 | 13.9317
|  | FULSCOT | CT |  |  | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 25.7648 | 24.898 | 24.0513 | 24.5156 | 24.5031 | 24.4928 | 24.4758 | 24.4589 | 24.4393 | 24.4188 | 24.3993 | 24.381 | 24.0643 | 23.1676 | 22.0218 | 20.9615 | 19.9626 | 21.2353 | 20.9711 | 20.7558 | 20.3994 | 20.0447 | 19.6342 | 19.2027 | 18.7937 | 18.4107 | 18.0347 | 17.1378 | 15.9915 | 14.9309 | 13.9317
|  | FULSCOT | LW |  |  | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 25.8366 | 24.9847 | 24.1375 | 24.516 | 24.5037 | 24.4937 | 24.4774 | 24.4612 | 24.4423 | 24.4236 | 24.4041 | 24.3859 | 24.1668 | 23.2701 | 22.124 | 21.0638 | 20.0643 | 21.2427 | 20.9838 | 20.7755 | 20.4336 | 20.093 | 19.6964 | 19.305 | 18.896 | 18.5131 | 18.1373 | 17.2403 | 16.0938 | 15.0332 | 14.0334
|  | FULSCOT | ST |  |  | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.1898 | 24.521 | 24.5139 | 24.5036 | 24.4959 | 24.4872 | 24.4758 | 24.4629 | 24.4494 | 24.4371 | 24.4248 | 24.3953 | 23.9615 | 23.275 | 22.6273 | 21.3468 | 21.1989 | 20.9834 | 20.8215 | 20.639 | 20.3989 | 20.1278 | 19.8456 | 19.5872 | 19.3297 | 18.7105 | 17.9319 | 17.2452 | 16.5972
|  | FULSCOT | SP |  |  | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 26.2209 | 24.523 | 24.5204 | 24.511 | 24.5082 | 24.5044 | 24.4997 | 24.4946 | 24.4894 | 24.4841 | 24.4793 | 24.4677 | 24.4532 | 24.4407 | 24.4294 | 21.3903 | 21.3354 | 21.1374 | 21.079 | 21.0001 | 20.9009 | 20.7933 | 20.6849 | 20.5738 | 20.4724 | 20.2296 | 19.9249 | 19.6627 | 19.4255
COWLEY GSP | WITNEY BSP | FYFIELD | MINIMUM HEADROOM | SU 42256 99551 | NO | 18.3852 | 18.3852 | 18.3852 | 18.3852 | 18.3251 | 18.2631 | 18.1989 | 18.1314 | 18.0244 | 17.9868 | 17.8577 | 17.518 | 16.8821 | 16.4926 | 13.6614 | 13.6583 | 13.6535 | 13.6432 | 13.5943 | 13.5121 | 13.2967 | 13.1459 | 12.9536 | 12.8334 | 12.4891 | 11.9121 | 11.2133 | 10.7637 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4398 | 11.3778 | 11.3137 | 11.2462 | 11.1391 | 11.1016 | 10.9724 | 10.8572 | 10.4857 | 10.3705
|  | FYFIELD | CT |  |  | 18.3852 | 18.3852 | 18.3852 | 18.3852 | 18.384 | 18.3816 | 18.3781 | 18.3729 | 18.3615 | 18.3595 | 18.1539 | 17.6684 | 17.1765 | 16.7719 | 13.6614 | 13.6583 | 13.6535 | 13.6432 | 13.6315 | 13.5121 | 13.2967 | 13.1459 | 13.0035 | 12.8945 | 12.5854 | 12.0363 | 11.4816 | 11.0169 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4987 | 11.4963 | 11.4928 | 11.4877 | 11.4763 | 11.4742 | 11.4634 | 11.3735 | 11.2733 | 11.2424
|  | FYFIELD | LW |  |  | 18.3852 | 18.3852 | 18.3852 | 18.3852 | 18.3525 | 18.3145 | 18.2701 | 18.2195 | 18.1334 | 18.1202 | 18.0321 | 17.518 | 16.8821 | 16.4926 | 13.662 | 13.6593 | 13.6551 | 13.646 | 13.604 | 13.5443 | 13.3672 | 13.1708 | 12.9536 | 12.8334 | 12.4891 | 11.9121 | 11.2133 | 10.7637 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4673 | 11.4292 | 11.3849 | 11.3343 | 11.2481 | 11.2349 | 11.1787 | 11.0601 | 10.8159 | 10.8002
|  | FYFIELD | ST |  |  | 18.3852 | 18.3852 | 18.3852 | 18.3852 | 18.3251 | 18.2631 | 18.1989 | 18.1314 | 18.0244 | 17.9868 | 17.8577 | 17.7424 | 17.3709 | 17.0979 | 13.6642 | 13.6632 | 13.6615 | 13.6583 | 13.5943 | 13.5276 | 13.4587 | 13.386 | 13.2744 | 13.2331 | 12.9766 | 12.5718 | 11.9243 | 11.5354 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4398 | 11.3778 | 11.3137 | 11.2462 | 11.1391 | 11.1016 | 10.9724 | 10.8572 | 10.4857 | 10.3705
|  | FYFIELD | SP |  |  | 18.3852 | 18.3852 | 18.3852 | 18.3852 | 18.3852 | 18.3851 | 18.385 | 18.3849 | 18.3845 | 18.3831 | 18.3749 | 18.3684 | 18.3373 | 18.3069 | 13.6651 | 13.6649 | 13.6643 | 13.6634 | 13.6616 | 13.6595 | 13.6575 | 13.6554 | 13.653 | 13.6501 | 13.638 | 13.6258 | 13.5895 | 13.5545 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4999 | 11.4998 | 11.4996 | 11.4993 | 11.4978 | 11.4897 | 11.4831 | 11.452 | 11.4217
LOVEDEAN GSP | HAVANT | GABLE HEAD | MINIMUM HEADROOM | SZ 72204 99904 | YES | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.488 | 34.4868 | 34.4856 | 34.4845 | 34.4826 | 34.4774 | 34.461 | 33.6773 | 32.7221 | 31.7878 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6703 | 25.6691 | 25.6679 | 25.6667 | 25.6649 | 25.6263 | 24.9495 | 23.855 | 22.7281 | 21.6258 | 25.8053 | 25.8023 | 25.7977 | 25.7896 | 25.7839 | 25.7779 | 25.7638 | 25.7489 | 25.735 | 25.7205 | 25.1966 | 24.1017 | 22.9745 | 21.8718
|  | GABLE HEAD | CT |  |  | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 33.9312 | 32.9759 | 32.0421 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.2491 | 24.1545 | 23.0275 | 21.9258 | 25.8067 | 25.8044 | 25.8004 | 25.7944 | 25.7908 | 25.7867 | 25.7807 | 25.7658 | 25.7519 | 25.7375 | 25.4964 | 24.4013 | 23.274 | 22.1719
|  | GABLE HEAD | LW |  |  | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 33.6773 | 32.7221 | 31.7878 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6263 | 24.9495 | 23.855 | 22.7281 | 21.6258 | 25.8057 | 25.8027 | 25.7977 | 25.7896 | 25.7839 | 25.7779 | 25.7638 | 25.7489 | 25.735 | 25.7205 | 25.1966 | 24.1017 | 22.9745 | 21.8718
|  | GABLE HEAD | ST |  |  | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.4375 | 33.8182 | 33.2142 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.4898 | 24.7517 | 24.0212 | 23.3086 | 25.8053 | 25.8023 | 25.798 | 25.7917 | 25.7861 | 25.7791 | 25.7689 | 25.7582 | 25.7488 | 25.7389 | 25.7128 | 24.9988 | 24.268 | 23.5552
|  | GABLE HEAD | SP |  |  | 34.4892 | 34.4892 | 34.4892 | 34.4892 | 34.488 | 34.4868 | 34.4856 | 34.4845 | 34.4826 | 34.4774 | 34.461 | 34.4532 | 34.4286 | 34.408 | 25.6715 | 25.6715 | 25.6715 | 25.6715 | 25.6703 | 25.6691 | 25.6679 | 25.6667 | 25.6649 | 25.6597 | 25.6433 | 25.6355 | 25.6109 | 25.5903 | 25.8078 | 25.8068 | 25.8053 | 25.8036 | 25.8012 | 25.7986 | 25.794 | 25.7891 | 25.7833 | 25.7742 | 25.7477 | 25.7236 | 25.683 | 25.647
LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD | MINIMUM HEADROOM | SU 64771 01769 | NO | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.2344 | 36.0951 | 35.9496 | 35.7988 | 35.5697 | 35.538 | 35.4292 | 34.2629 | 32.1503 | 30.4934 | 28.7261 | 28.6923 | 28.6736 | 28.627 | 28.4427 | 28.2241 | 27.9287 | 27.6142 | 27.2057 | 26.9827 | 25.6262 | 22.0307 | 19.4773 | 17.426 | 28.4356 | 28.4293 | 28.4259 | 28.4172 | 28.2731 | 28.1191 | 27.9458 | 27.7647 | 27.5024 | 27.4352 | 26.5708 | 22.9629 | 20.4013 | 18.3427
|  | GAMBLE ROAD | CT |  |  | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 35.5309 | 33.6981 | 32.059 | 28.7261 | 28.6923 | 28.6736 | 28.627 | 28.5777 | 28.4984 | 28.4138 | 28.2503 | 28.0708 | 27.8795 | 26.7694 | 23.3385 | 21.0648 | 19.0315 | 28.4356 | 28.4293 | 28.4259 | 28.4172 | 28.4081 | 28.3934 | 28.3777 | 28.3474 | 28.3142 | 28.2788 | 27.7169 | 24.2715 | 21.9896 | 19.949
|  | GAMBLE ROAD | LW |  |  | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.2344 | 36.0951 | 35.9496 | 35.7988 | 35.5697 | 35.538 | 35.4292 | 34.2629 | 32.1503 | 30.4934 | 28.7261 | 28.6923 | 28.6736 | 28.627 | 28.4427 | 28.2241 | 27.9287 | 27.6142 | 27.2057 | 26.9827 | 25.6262 | 22.0307 | 19.4773 | 17.426 | 28.4356 | 28.4293 | 28.4259 | 28.4172 | 28.2731 | 28.1191 | 27.9458 | 27.7647 | 27.5024 | 27.4352 | 26.5708 | 22.9629 | 20.4013 | 18.3427
|  | GAMBLE ROAD | ST |  |  | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3605 | 36.3514 | 36.3421 | 36.3326 | 36.3178 | 36.3128 | 36.2967 | 36.2829 | 36.2347 | 35.1696 | 28.7293 | 28.7203 | 28.6876 | 28.6602 | 28.62 | 28.5577 | 28.4738 | 28.3802 | 28.2444 | 28.1082 | 27.6207 | 25.7827 | 24.2435 | 22.9254 | 28.4362 | 28.4345 | 28.4285 | 28.4234 | 28.4087 | 28.3897 | 28.3666 | 28.3415 | 28.3043 | 28.275 | 28.1716 | 26.7247 | 25.1802 | 23.8574
|  | GAMBLE ROAD | SP |  |  | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 36.3694 | 28.7335 | 28.7291 | 28.7028 | 28.6904 | 28.6761 | 28.6527 | 28.6259 | 28.5963 | 28.5616 | 28.5099 | 28.3237 | 28.0061 | 27.8031 | 27.6227 | 28.437 | 28.4361 | 28.4313 | 28.429 | 28.4263 | 28.422 | 28.417 | 28.4115 | 28.4051 | 28.3955 | 28.361 | 28.3022 | 28.2646 | 28.2312
IVER 132KV | DENHAM | GERRARDS CROSS | MINIMUM HEADROOM | SU 99973 87964 | YES | 20.3383 | 20.3383 | 20.3383 | 20.3383 | 20.3136 | 20.2882 | 20.262 | 20.2343 | 20.1906 | 20.1849 | 19.9701 | 19.3615 | 18.704 | 18.1395 | 13.0411 | 13.0336 | 13.0237 | 13.0029 | 12.8726 | 12.4322 | 12.123 | 11.9955 | 11.8527 | 11.7404 | 11.4014 | 10.7209 | 9.9858 | 9.3445 | 14.3908 | 14.3818 | 14.3692 | 14.3427 | 14.2995 | 14.2507 | 14.2013 | 14.1678 | 14.1183 | 14.1064 | 14.0683 | 13.4884 | 12.757 | 12.1195
|  | GERRARDS CROSS | CT |  |  | 20.3383 | 20.3383 | 20.3383 | 20.3383 | 20.3136 | 20.2882 | 20.262 | 20.2343 | 20.1906 | 20.1849 | 19.9701 | 19.3615 | 18.704 | 18.1395 | 13.042 | 13.0351 | 13.026 | 13.0069 | 12.9637 | 12.5468 | 12.123 | 11.9955 | 11.8527 | 11.7404 | 11.4014 | 10.7209 | 9.9858 | 9.3445 | 14.3908 | 14.3837 | 14.3722 | 14.3478 | 14.2995 | 14.2507 | 14.2013 | 14.1678 | 14.1183 | 14.1064 | 14.0683 | 13.4884 | 12.757 | 12.1195
|  | GERRARDS CROSS | LW |  |  | 20.3383 | 20.3383 | 20.3383 | 20.3383 | 20.3372 | 20.3348 | 20.331 | 20.3258 | 20.3153 | 20.3135 | 20.2279 | 19.7067 | 19.1236 | 18.5868 | 13.0411 | 13.0336 | 13.0237 | 13.0029 | 12.8726 | 12.4322 | 12.328 | 12.223 | 12.1134 | 12.0051 | 11.6762 | 11.0832 | 10.4225 | 9.8089 | 14.3908 | 14.3818 | 14.3692 | 14.3427 | 14.3158 | 14.2878 | 14.2782 | 14.2672 | 14.2509 | 14.2429 | 14.2151 | 13.8499 | 13.1929 | 12.5831
|  | GERRARDS CROSS | ST |  |  | 20.3383 | 20.3383 | 20.3383 | 20.3383 | 20.3381 | 20.3376 | 20.3369 | 20.3358 | 20.3333 | 20.3321 | 20.3258 | 20.3176 | 20.2886 | 20.2781 | 13.047 | 13.0438 | 13.04 | 13.0335 | 13.0254 | 13.0154 | 13.0098 | 13.0039 | 12.9984 | 12.9939 | 12.9777 | 12.6342 | 12.2055 | 11.8004 | 14.3908 | 14.3908 | 14.39 | 14.3817 | 14.3714 | 14.3588 | 14.3519 | 14.3447 | 14.3383 | 14.3329 | 14.314 | 14.2834 | 14.2312 | 14.1977
|  | GERRARDS CROSS | SP |  |  | 20.3383 | 20.3383 | 20.3383 | 20.3383 | 20.3383 | 20.3383 | 20.3383 | 20.3382 | 20.3381 | 20.3377 | 20.3354 | 20.3336 | 20.325 | 20.3166 | 13.0499 | 13.0492 | 13.0485 | 13.0478 | 13.0447 | 13.0409 | 13.0392 | 13.0374 | 13.0351 | 13.0334 | 13.0273 | 13.0188 | 13.003 | 12.9876 | 14.3908 | 14.3908 | 14.3908 | 14.3908 | 14.3908 | 14.3908 | 14.3889 | 14.3867 | 14.3838 | 14.3817 | 14.3746 | 14.3642 | 14.3465 | 14.3292
MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM | MINIMUM HEADROOM | ST 80185 25765 | YES | 31.9253 | 31.9253 | 31.9253 | 31.9253 | 31.9246 | 31.9232 | 31.9211 | 31.9181 | 31.8649 | 31.6875 | 31.1112 | 30.2339 | 29.8433 | 29.5051 | 31.2824 | 31.0991 | 31.0679 | 30.9961 | 30.9039 | 30.7841 | 30.6027 | 30.4312 | 30.2206 | 30.0095 | 29.3239 | 28.2811 | 27.8206 | 27.4179 | 30.816 | 30.3884 | 30.3577 | 30.2869 | 30.1961 | 30.0781 | 29.8993 | 29.7302 | 29.5227 | 29.3146 | 28.6391 | 27.6114 | 27.1573 | 26.7606
|  | GILLINGHAM | CT |  |  | 31.9253 | 31.9253 | 31.9253 | 31.9253 | 31.9251 | 31.9247 | 31.9241 | 31.9233 | 31.9161 | 31.7394 | 31.1667 | 30.2878 | 29.9063 | 29.5649 | 31.2824 | 31.0991 | 31.0679 | 30.9961 | 30.9043 | 30.7856 | 30.6556 | 30.4862 | 30.2798 | 30.0694 | 29.3874 | 28.343 | 27.8915 | 27.4857 | 30.816 | 30.3884 | 30.3577 | 30.2869 | 30.1965 | 30.0795 | 29.9514 | 29.7845 | 29.5812 | 29.3738 | 28.7018 | 27.6726 | 27.2275 | 26.8276
|  | GILLINGHAM | LW |  |  | 31.9253 | 31.9253 | 31.9253 | 31.9253 | 31.9246 | 31.9232 | 31.9211 | 31.9181 | 31.8649 | 31.6875 | 31.1112 | 30.2339 | 29.8433 | 29.5051 | 31.2824 | 31.0991 | 31.0679 | 30.9961 | 30.9039 | 30.7841 | 30.6027 | 30.4312 | 30.2206 | 30.0095 | 29.3239 | 28.2811 | 27.8206 | 27.4179 | 30.816 | 30.3884 | 30.3577 | 30.2869 | 30.1961 | 30.0781 | 29.8993 | 29.7302 | 29.5227 | 29.3146 | 28.6391 | 27.6114 | 27.1573 | 26.7606
|  | GILLINGHAM | ST |  |  | 31.9253 | 31.9253 | 31.9253 | 31.9253 | 31.9251 | 31.9248 | 31.9244 | 31.9238 | 31.9224 | 31.9217 | 31.6234 | 31.0062 | 30.7524 | 30.5288 | 31.2827 | 31.282 | 31.0881 | 31.0442 | 30.9848 | 30.9052 | 30.7995 | 30.7007 | 30.5618 | 30.4171 | 29.9317 | 29.1973 | 28.8981 | 28.6328 | 30.8204 | 30.8087 | 30.3776 | 30.3343 | 30.2758 | 30.1974 | 30.0932 | 29.9958 | 29.859 | 29.7164 | 29.2381 | 28.5145 | 28.2194 | 27.958
|  | GILLINGHAM | SP |  |  | 31.9253 | 31.9253 | 31.9253 | 31.9253 | 31.9253 | 31.9252 | 31.9252 | 31.9252 | 31.9251 | 31.9249 | 31.9236 | 31.9226 | 31.87 | 31.7834 | 31.283 | 31.2826 | 31.1066 | 31.0866 | 31.0575 | 31.0216 | 30.9788 | 30.941 | 30.8922 | 30.835 | 30.6432 | 30.341 | 30.2257 | 30.1234 | 30.8258 | 30.8194 | 30.3978 | 30.3761 | 30.3475 | 30.3121 | 30.2699 | 30.2327 | 30.1846 | 30.1283 | 29.9392 | 29.6414 | 29.5277 | 29.4269
BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING | MINIMUM HEADROOM | SU 96743 44375 | YES | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.1093 | 35.0398 | 33.9879 | 34.8074 | 34.7882 | 34.7643 | 34.7154 | 34.669 | 34.6228 | 34.066 | 33.8434 | 33.623 | 33.3872 | 32.6893 | 31.5101 | 30.2867 | 29.0833 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9427 | 34.9101 | 34.8971 | 34.8843 | 34.8615 | 34.1943 | 32.9903 | 31.7283 | 30.4869
|  | GODALMING | CT |  |  | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.1093 | 35.0398 | 33.9879 | 34.8074 | 34.7882 | 34.7643 | 34.7154 | 34.669 | 34.6228 | 34.066 | 33.8434 | 33.623 | 33.3872 | 32.6893 | 31.5101 | 30.2867 | 29.0833 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9427 | 34.9101 | 34.8971 | 34.8843 | 34.8615 | 34.1943 | 32.9903 | 31.7283 | 30.4869
|  | GODALMING | LW |  |  | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 35.5278 | 34.4749 | 34.8096 | 34.7919 | 34.77 | 34.7255 | 34.6832 | 34.6411 | 34.6227 | 34.4017 | 34.1812 | 33.9455 | 33.2476 | 32.0684 | 30.8449 | 29.6404 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9426 | 34.9296 | 34.9168 | 34.9031 | 34.728 | 33.5663 | 32.3041 | 31.0616
|  | GODALMING | ST |  |  | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 34.8263 | 34.8089 | 34.7979 | 34.7798 | 34.7584 | 34.7325 | 34.7166 | 34.7009 | 34.6886 | 34.6754 | 34.6367 | 34.0079 | 33.2184 | 32.4363 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9067 | 34.7001 | 33.9458
|  | GODALMING | SP |  |  | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 36.584 | 34.8352 | 34.8253 | 34.8231 | 34.8212 | 34.8142 | 34.8057 | 34.8 | 34.7943 | 34.7871 | 34.782 | 34.767 | 34.7423 | 34.7183 | 34.6953 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495 | 34.9495
WILLESDEN GSP | ACTON LANE | GOLDSMITHS | MINIMUM HEADROOM | TQ 21089 80758 | YES | 17.6898 | 17.6875 | 17.684 | 17.6774 | 17.6705 | 17.6629 | 17.6523 | 17.6429 | 17.634 | 17.625 | 17.5973 | 17.5384 | 16.8655 | 16.0687 | 14.405 | 14.4032 | 14.4005 | 14.3954 | 14.39 | 14.3842 | 14.3759 | 14.3686 | 14.3618 | 14.3548 | 14.3334 | 13.6788 | 12.7817 | 11.866 | 14.602 | 14.5995 | 14.5956 | 14.5884 | 14.5808 | 14.5725 | 14.5608 | 14.5505 | 14.5408 | 14.5309 | 14.4939 | 14.1002 | 13.3428 | 12.4071
|  | GOLDSMITHS | CT |  |  | 17.6898 | 17.6876 | 17.6842 | 17.6777 | 17.6709 | 17.6634 | 17.6558 | 17.6464 | 17.6376 | 17.6286 | 17.6009 | 17.5419 | 16.9074 | 16.1106 | 14.405 | 14.4033 | 14.4006 | 14.3956 | 14.3903 | 14.3845 | 14.3787 | 14.3714 | 14.3646 | 14.3576 | 14.3361 | 13.7257 | 12.8286 | 11.9153 | 14.602 | 14.5996 | 14.5958 | 14.5887 | 14.5812 | 14.5731 | 14.5648 | 14.5545 | 14.5448 | 14.5349 | 14.5045 | 14.1243 | 13.392 | 12.4562
|  | GOLDSMITHS | LW |  |  | 17.6898 | 17.6875 | 17.684 | 17.6774 | 17.6705 | 17.6629 | 17.6523 | 17.6429 | 17.634 | 17.625 | 17.5973 | 17.5384 | 16.8655 | 16.0687 | 14.405 | 14.4032 | 14.4005 | 14.3954 | 14.39 | 14.3842 | 14.3759 | 14.3686 | 14.3618 | 14.3548 | 14.3334 | 13.6788 | 12.7817 | 11.866 | 14.602 | 14.5995 | 14.5956 | 14.5884 | 14.5808 | 14.5725 | 14.5608 | 14.5505 | 14.5408 | 14.5309 | 14.4939 | 14.1002 | 13.3428 | 12.4071
|  | GOLDSMITHS | ST |  |  | 17.6907 | 17.6892 | 17.6871 | 17.6836 | 17.6793 | 17.6741 | 17.6664 | 17.6596 | 17.6536 | 17.6475 | 17.6286 | 17.5882 | 17.5432 | 17.2161 | 14.4057 | 14.4045 | 14.4028 | 14.4002 | 14.3969 | 14.3928 | 14.3869 | 14.3816 | 14.377 | 14.3722 | 14.3576 | 14.3263 | 13.7422 | 13.1736 | 14.603 | 14.6014 | 14.599 | 14.5952 | 14.5905 | 14.5848 | 14.5764 | 14.5689 | 14.5623 | 14.5556 | 14.5349 | 14.4346 | 14.1328 | 13.7545
|  | GOLDSMITHS | SP |  |  | 17.692 | 17.6914 | 17.6906 | 17.6896 | 17.688 | 17.6858 | 17.6825 | 17.6796 | 17.6762 | 17.6725 | 17.6611 | 17.6429 | 17.6172 | 17.592 | 14.4067 | 14.4063 | 14.4056 | 14.4048 | 14.4036 | 14.4018 | 14.3992 | 14.3969 | 14.3941 | 14.391 | 14.3812 | 14.3667 | 14.3454 | 14.3247 | 14.6044 | 14.6038 | 14.6029 | 14.6018 | 14.6 | 14.5977 | 14.5941 | 14.5909 | 14.5872 | 14.5833 | 14.5712 | 14.5514 | 14.5238 | 14.4967
NURSLING GSP | WINCHESTER | GORDON ROAD | MINIMUM HEADROOM | SU 48217 29991 | YES | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.3389 | 37.2683 | 37.1993 | 28.6335 | 28.4839 | 28.2872 | 27.8632 | 27.4275 | 26.974 | 26.5032 | 26.248 | 26.0202 | 25.8053 | 25.1925 | 24.2104 | 23.2006 | 22.2149 | 25.8082 | 25.8082 | 25.8082 | 25.6477 | 25.2774 | 24.8404 | 24.3818 | 24.1333 | 23.9113 | 23.702 | 23.0992 | 22.1303 | 21.134 | 20.1614
|  | GORDON ROAD | CT |  |  | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.3389 | 37.2683 | 37.1993 | 28.6335 | 28.4839 | 28.2872 | 27.8632 | 27.4275 | 26.974 | 26.5032 | 26.248 | 26.0202 | 25.8053 | 25.1925 | 24.2104 | 23.2006 | 22.2149 | 25.8082 | 25.8082 | 25.8082 | 25.6477 | 25.2774 | 24.8404 | 24.3818 | 24.1333 | 23.9113 | 23.702 | 23.0992 | 22.1303 | 21.134 | 20.1614
|  | GORDON ROAD | LW |  |  | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.2966 | 37.2277 | 28.6561 | 28.5227 | 28.3474 | 27.9689 | 27.5772 | 27.1673 | 26.9091 | 26.654 | 26.4261 | 26.2112 | 25.5983 | 24.6163 | 23.6063 | 22.6204 | 25.8082 | 25.8082 | 25.8082 | 25.7375 | 25.4047 | 25.0287 | 24.7772 | 24.5287 | 24.3067 | 24.0974 | 23.4996 | 22.5308 | 21.5343 | 20.5616
|  | GORDON ROAD | ST |  |  | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 28.7439 | 28.6762 | 28.5966 | 28.4548 | 28.2655 | 28.0275 | 27.8287 | 27.6331 | 27.4783 | 27.3318 | 26.9179 | 26.2631 | 25.6121 | 24.9719 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.7873 | 25.6184 | 25.4521 | 25.3206 | 25.1889 | 24.7858 | 24.1479 | 23.5133 | 22.8816
|  | GORDON ROAD | SP |  |  | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 37.34 | 28.8109 | 28.797 | 28.7837 | 28.7679 | 28.6971 | 28.6094 | 28.5335 | 28.4599 | 28.3792 | 28.3227 | 28.1635 | 27.9155 | 27.6774 | 27.4537 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.8082 | 25.6922 | 25.4898 | 25.2997
BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING | MINIMUM HEADROOM | SU 60305 82895 | YES | 16.489 | 16.4611 | 16.4245 | 16.3476 | 16.2729 | 16.1989 | 16.1255 | 16.0864 | 16.0475 | 16.0057 | 15.8803 | 15.6549 | 15.4103 | 15.1683 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963
|  | GORING | CT |  |  | 16.489 | 16.4611 | 16.4245 | 16.3476 | 16.2729 | 16.1989 | 16.1255 | 16.0864 | 16.0475 | 16.0057 | 15.8803 | 15.6549 | 15.4103 | 15.1683 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963
|  | GORING | LW |  |  | 16.5077 | 16.4934 | 16.4746 | 16.4352 | 16.397 | 16.3589 | 16.3196 | 16.2804 | 16.2416 | 16.1998 | 16.0744 | 15.8489 | 15.6042 | 15.3619 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963
|  | GORING | ST |  |  | 16.5168 | 16.5095 | 16.5008 | 16.4861 | 16.4679 | 16.4461 | 16.4155 | 16.3853 | 16.3587 | 16.3302 | 16.2455 | 16.0938 | 15.9349 | 15.7779 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963
|  | GORING | SP |  |  | 16.5248 | 16.5236 | 16.5223 | 16.5211 | 16.5164 | 16.5107 | 16.4997 | 16.4886 | 16.4744 | 16.4632 | 16.4303 | 16.3718 | 16.31 | 16.2491 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.322 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963 | 16.2963
IVER 132KV | DENHAM | GRASSINGHAM ROAD | MINIMUM HEADROOM | TQ 00165 90988 | YES | 31.5567 | 31.5567 | 31.5567 | 31.5567 | 31.5362 | 31.515 | 31.4932 | 31.4698 | 31.4327 | 31.4278 | 31.366 | 31.3119 | 30.8106 | 30.1013 | 24.6714 | 24.6714 | 24.6714 | 24.6714 | 24.651 | 24.6298 | 24.6079 | 24.5846 | 24.5474 | 24.5425 | 24.4422 | 23.5905 | 22.6856 | 21.8783 | 23.8601 | 23.8601 | 23.8601 | 23.8601 | 23.8397 | 23.8185 | 23.7966 | 23.7733 | 23.7361 | 23.7312 | 23.6695 | 23.6154 | 23.4414 | 22.7758
|  | GRASSINGHAM ROAD | CT |  |  | 31.5567 | 31.5567 | 31.5567 | 31.5567 | 31.5362 | 31.515 | 31.4932 | 31.4698 | 31.4327 | 31.4278 | 31.4106 | 31.3139 | 30.8106 | 30.1013 | 24.6714 | 24.6714 | 24.6714 | 24.6714 | 24.651 | 24.6298 | 24.6079 | 24.5846 | 24.5474 | 24.5425 | 24.4422 | 23.5905 | 22.6856 | 21.8783 | 23.8601 | 23.8601 | 23.8601 | 23.8601 | 23.8397 | 23.8185 | 23.7966 | 23.7733 | 23.7361 | 23.7312 | 23.714 | 23.6174 | 23.5031 | 22.7758
|  | GRASSINGHAM ROAD | LW |  |  | 31.5567 | 31.5567 | 31.5567 | 31.5567 | 31.5553 | 31.5524 | 31.5478 | 31.5416 | 31.5289 | 31.5268 | 31.5157 | 31.4886 | 31.1249 | 30.4403 | 24.6714 | 24.6714 | 24.6714 | 24.6714 | 24.67 | 24.6671 | 24.6626 | 24.6563 | 24.6437 | 24.6415 | 24.6304 | 23.8547 | 23.0112 | 22.2285 | 23.8601 | 23.8601 | 23.8601 | 23.8601 | 23.8587 | 23.8559 | 23.8513 | 23.845 | 23.8324 | 23.8302 | 23.8191 | 23.7921 | 23.7394 | 23.1254
|  | GRASSINGHAM ROAD | ST |  |  | 31.5567 | 31.5567 | 31.5567 | 31.5567 | 31.5564 | 31.5558 | 31.5549 | 31.5536 | 31.5506 | 31.5492 | 31.5416 | 31.5317 | 31.4968 | 31.4841 | 24.6714 | 24.6714 | 24.6714 | 24.6714 | 24.6711 | 24.6705 | 24.6697 | 24.6683 | 24.6654 | 24.664 | 24.6564 | 24.6465 | 24.4301 | 23.9116 | 23.8601 | 23.8601 | 23.8601 | 23.8601 | 23.8598 | 23.8593 | 23.8584 | 23.8571 | 23.8541 | 23.8527 | 23.8451 | 23.8352 | 23.8003 | 23.7876
|  | GRASSINGHAM ROAD | SP |  |  | 31.5567 | 31.5567 | 31.5567 | 31.5567 | 31.5487 | 31.5409 | 31.5331 | 31.5251 | 31.5127 | 31.4778 | 31.366 | 31.3119 | 31.1379 | 30.991 | 24.6714 | 24.6714 | 24.6714 | 24.6714 | 24.6635 | 24.6557 | 24.6479 | 24.6399 | 24.6274 | 24.5926 | 24.4808 | 24.4266 | 24.2527 | 24.1057 | 23.8601 | 23.8601 | 23.8601 | 23.8601 | 23.8522 | 23.8444 | 23.8366 | 23.8286 | 23.8161 | 23.7813 | 23.6695 | 23.6154 | 23.4414 | 23.2945
LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET | MINIMUM HEADROOM | SU 64445 00178 | YES | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.7066 | 34.6102 | 34.5122 | 34.4099 | 34.2522 | 34.2322 | 34.168 | 33.8716 | 33.5632 | 33.1724 | 26.6408 | 26.6398 | 26.6384 | 26.6354 | 26.5374 | 26.4372 | 26.3357 | 26.2287 | 26.0668 | 26.0426 | 25.9542 | 24.8774 | 23.5226 | 22.3545 | 26.9247 | 26.9235 | 26.9219 | 26.9183 | 26.8197 | 26.7188 | 26.6167 | 26.5088 | 26.3461 | 26.3211 | 26.2401 | 25.8964 | 25.5267 | 25.3905
|  | GREETHAM STREET | CT |  |  | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.7066 | 34.6102 | 34.5122 | 34.4099 | 34.2522 | 34.2322 | 34.168 | 33.8716 | 33.5632 | 33.1724 | 26.6408 | 26.6398 | 26.6384 | 26.6354 | 26.5374 | 26.4372 | 26.3357 | 26.2287 | 26.0668 | 26.0426 | 25.9542 | 24.8774 | 23.5226 | 22.3545 | 26.9247 | 26.9235 | 26.9219 | 26.9183 | 26.8197 | 26.7188 | 26.6167 | 26.5088 | 26.3461 | 26.3211 | 26.2401 | 25.8964 | 25.5267 | 25.3905
|  | GREETHAM STREET | LW |  |  | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.4684 | 26.6408 | 26.6398 | 26.6384 | 26.6354 | 26.6321 | 26.6284 | 26.6239 | 26.6192 | 26.615 | 26.6108 | 26.5693 | 25.7889 | 24.7418 | 23.6474 | 26.9247 | 26.9235 | 26.9219 | 26.9183 | 26.9144 | 26.9099 | 26.9047 | 26.8991 | 26.8941 | 26.8891 | 26.8723 | 26.825 | 26.7638 | 26.702
|  | GREETHAM STREET | ST |  |  | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 26.6436 | 26.6406 | 26.6398 | 26.6381 | 26.6362 | 26.6336 | 26.6308 | 26.6278 | 26.625 | 26.6221 | 26.6124 | 26.3311 | 25.6602 | 24.99 | 26.928 | 26.9244 | 26.9235 | 26.9215 | 26.9192 | 26.9162 | 26.9129 | 26.9093 | 26.906 | 26.9026 | 26.891 | 26.8578 | 26.8173 | 26.7782
|  | GREETHAM STREET | SP |  |  | 34.8013 | 34.8013 | 34.8013 | 34.8013 | 34.8001 | 34.7989 | 34.7978 | 34.7966 | 34.7947 | 34.7896 | 34.7731 | 34.7653 | 34.7407 | 34.7201 | 26.6442 | 26.6439 | 26.6413 | 26.6408 | 26.6389 | 26.6367 | 26.6346 | 26.6323 | 26.6294 | 26.6231 | 26.6029 | 26.5834 | 26.5425 | 26.2751 | 26.9287 | 26.9284 | 26.9253 | 26.9247 | 26.9226 | 26.9203 | 26.918 | 26.9155 | 26.9124 | 26.9059 | 26.885 | 26.8634 | 26.8195 | 26.7782
COWLEY GSP | DRAYTON BSP | GROVE | MINIMUM HEADROOM | SU 39515 89611 | YES | 21.5095 | 21.4989 | 21.4883 | 20.8435 | 20.789 | 20.7326 | 20.6743 | 20.614 | 20.5459 | 20.5222 | 19.7364 | 18.1813 | 17.237 | 16.4943 | 14.8737 | 14.823 | 14.7582 | 14.033 | 13.8985 | 13.7531 | 13.5547 | 13.3393 | 13.0704 | 12.8754 | 12.2991 | 11.3189 | 10.7063 | 10.216 | 20.2419 | 20.2313 | 20.2208 | 19.5759 | 19.5214 | 19.4651 | 19.4068 | 19.3464 | 19.2353 | 18.8662 | 17.7762 | 15.9298 | 14.8175 | 13.947
|  | GROVE | CT |  |  | 21.5602 | 21.5539 | 21.5475 | 21.1606 | 21.1284 | 21.0957 | 21.0626 | 21.0288 | 20.9925 | 20.979 | 20.2362 | 18.3205 | 17.2995 | 16.5492 | 14.9213 | 14.8727 | 14.8091 | 14.3357 | 14.2176 | 14.0898 | 13.948 | 13.7593 | 13.5222 | 13.3374 | 12.7955 | 11.4547 | 10.7654 | 10.2673 | 20.2927 | 20.2863 | 20.28 | 19.8931 | 19.8608 | 19.8282 | 19.795 | 19.7613 | 19.6915 | 19.3334 | 18.2778 | 16.0708 | 14.8818 | 14.0038
|  | GROVE | LW |  |  | 21.5095 | 21.4989 | 21.4883 | 20.8435 | 20.789 | 20.7326 | 20.6743 | 20.614 | 20.5459 | 20.5222 | 19.7364 | 18.1813 | 17.237 | 16.4943 | 14.8737 | 14.823 | 14.7582 | 14.033 | 13.8985 | 13.7531 | 13.5547 | 13.3393 | 13.0704 | 12.8754 | 12.2991 | 11.3189 | 10.7063 | 10.216 | 20.2419 | 20.2313 | 20.2208 | 19.5759 | 19.5214 | 19.4651 | 19.4068 | 19.3464 | 19.2353 | 18.8662 | 17.7762 | 15.9298 | 14.8175 | 13.947
|  | GROVE | ST |  |  | 21.5856 | 21.5814 | 21.5771 | 21.3192 | 21.2786 | 21.2373 | 21.1953 | 21.1521 | 21.0958 | 21.0749 | 21.0061 | 20.0903 | 19.3947 | 18.8994 | 14.9591 | 14.9271 | 14.8879 | 14.5852 | 14.4961 | 14.3962 | 14.2659 | 14.1244 | 13.9331 | 13.7948 | 13.376 | 12.7031 | 12.2244 | 11.8934 | 20.318 | 20.3138 | 20.3096 | 20.0516 | 20.011 | 19.9698 | 19.9278 | 19.8846 | 19.8282 | 19.8073 | 19.3838 | 18.1048 | 17.2993 | 16.7207
|  | GROVE | SP |  |  | 21.611 | 21.6088 | 21.6067 | 21.4778 | 21.4672 | 21.4566 | 21.446 | 21.4353 | 21.4246 | 21.4198 | 21.4038 | 21.3801 | 21.3549 | 21.3194 | 14.9939 | 14.9754 | 14.9547 | 14.8065 | 14.774 | 14.739 | 14.693 | 14.6441 | 14.5798 | 14.5287 | 14.3747 | 14.1084 | 13.9581 | 13.8397 | 20.3434 | 20.3413 | 20.3392 | 20.2102 | 20.1996 | 20.189 | 20.1784 | 20.1678 | 20.157 | 20.1522 | 20.1363 | 20.1125 | 20.0873 | 20.001
MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL | MINIMUM HEADROOM | ST 98638 11417 | YES | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.1914 | 5.1905 | 5.1895 | 5.1871 | 5.1849 | 5.1826 | 5.1765 | 5.1704 | 5.1644 | 5.1579 | 5.1386 | 5.1064 | 5.0728 | 5.0396 | 5.216 | 5.2156 | 5.215 | 5.2139 | 5.2127 | 5.2116 | 5.2085 | 5.2054 | 5.2024 | 5.1991 | 5.1893 | 5.173 | 5.156 | 5.1393
|  | GUSSAGE ST MICHAEL | CT |  |  | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.1914 | 5.1905 | 5.1895 | 5.1871 | 5.1849 | 5.1826 | 5.1804 | 5.1743 | 5.1683 | 5.1618 | 5.1425 | 5.1103 | 5.0767 | 5.0435 | 5.216 | 5.2156 | 5.215 | 5.2139 | 5.2127 | 5.2116 | 5.2105 | 5.2074 | 5.2043 | 5.201 | 5.1913 | 5.175 | 5.158 | 5.1412
|  | GUSSAGE ST MICHAEL | LW |  |  | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.1914 | 5.1905 | 5.1895 | 5.1871 | 5.1849 | 5.1826 | 5.1765 | 5.1704 | 5.1644 | 5.1579 | 5.1386 | 5.1064 | 5.0728 | 5.0396 | 5.216 | 5.2156 | 5.215 | 5.2139 | 5.2127 | 5.2116 | 5.2085 | 5.2054 | 5.2024 | 5.1991 | 5.1893 | 5.173 | 5.156 | 5.1393
|  | GUSSAGE ST MICHAEL | ST |  |  | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.1918 | 5.1913 | 5.1907 | 5.1896 | 5.1883 | 5.1868 | 5.1846 | 5.1824 | 5.1783 | 5.1739 | 5.1609 | 5.1394 | 5.1178 | 5.0964 | 5.2162 | 5.216 | 5.2156 | 5.2151 | 5.2145 | 5.2137 | 5.2126 | 5.2115 | 5.2094 | 5.2071 | 5.2006 | 5.1897 | 5.1788 | 5.168
|  | GUSSAGE ST MICHAEL | SP |  |  | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.3971 | 5.1923 | 5.1923 | 5.1922 | 5.1921 | 5.1917 | 5.1913 | 5.1906 | 5.1899 | 5.189 | 5.1873 | 5.1823 | 5.1741 | 5.1662 | 5.1586 | 5.2165 | 5.2165 | 5.2164 | 5.2164 | 5.2162 | 5.216 | 5.2156 | 5.2153 | 5.2148 | 5.2139 | 5.2114 | 5.2073 | 5.2033 | 5.1994
BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE | MINIMUM HEADROOM | SU 47370 08794 | YES | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.3379 | 35.6502 | 36.0441 | 36.0317 | 36.0294 | 36.0246 | 36.0199 | 36.0152 | 36.0104 | 36.0049 | 35.9994 | 35.896 | 35.5079 | 34.7855 | 33.9876 | 33.1954 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 35.556 | 34.7388
|  | HAMBLE | CT |  |  | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.3408 | 35.6534 | 36.0441 | 36.0317 | 36.0294 | 36.0246 | 36.0199 | 36.0152 | 36.0106 | 36.0051 | 35.9996 | 35.8996 | 35.5116 | 34.7889 | 33.9912 | 33.1991 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 35.5597 | 34.7426
|  | HAMBLE | LW |  |  | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.3379 | 35.6502 | 36.0442 | 36.0318 | 36.0296 | 36.025 | 36.0204 | 36.0159 | 36.0104 | 36.0049 | 35.9994 | 35.896 | 35.5079 | 34.7855 | 33.9876 | 33.1954 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 35.556 | 34.7388
|  | HAMBLE | ST |  |  | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.647 | 36.0445 | 36.0431 | 36.0308 | 36.028 | 36.0246 | 36.0205 | 36.0166 | 36.0127 | 36.009 | 36.005 | 35.8828 | 35.3952 | 34.8766 | 34.3658 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 35.9462
|  | HAMBLE | SP |  |  | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.7835 | 36.0461 | 36.0459 | 36.035 | 36.0348 | 36.0341 | 36.0331 | 36.0319 | 36.0306 | 36.029 | 36.0274 | 36.0228 | 36.0141 | 36.0046 | 35.9314 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242 | 36.242
MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY | MINIMUM HEADROOM | SZ 00104 90800 | YES | 35.5816 | 27.1494 | 27.1383 | 26.4608 | 26.4033 | 26.3435 | 26.2814 | 26.2167 | 26.1427 | 26.1173 | 26.0344 | 25.7272 | 24.3393 | 23.0104 | 34.1125 | 25.6804 | 25.6692 | 24.9918 | 24.9342 | 24.8744 | 24.7921 | 24.695 | 24.586 | 24.1484 | 22.8987 | 21.2538 | 19.6423 | 18.0974 | 34.423 | 25.9843 | 25.965 | 25.2807 | 25.2105 | 25.1359 | 25.0515 | 24.9637 | 24.508 | 24.0322 | 22.8248 | 21.2339 | 19.6449 | 18.1189
|  | HAMWORTHY | CT |  |  | 35.6349 | 35.6282 | 35.6216 | 35.2151 | 35.1811 | 35.1467 | 35.1116 | 35.0758 | 35.0369 | 35.0226 | 34.9773 | 34.3961 | 32.9315 | 31.5926 | 34.1658 | 34.1592 | 34.1525 | 33.746 | 33.7121 | 33.6776 | 33.6322 | 33.564 | 33.4901 | 33.1781 | 31.9661 | 29.9416 | 28.2534 | 26.6986 | 34.4763 | 34.4631 | 34.4482 | 34.0349 | 33.9884 | 33.939 | 33.8887 | 33.8299 | 33.5222 | 33.0573 | 31.8876 | 29.9173 | 28.2544 | 26.7185
|  | HAMWORTHY | LW |  |  | 35.5816 | 27.1494 | 27.1383 | 26.4608 | 26.4033 | 26.3435 | 26.2814 | 26.2167 | 26.1427 | 26.1173 | 26.0344 | 25.7272 | 24.3393 | 23.0104 | 34.1125 | 25.6804 | 25.6692 | 24.9918 | 24.9342 | 24.8744 | 24.7921 | 24.695 | 24.586 | 24.1484 | 22.8987 | 21.2538 | 19.6423 | 18.0974 | 34.423 | 25.9843 | 25.965 | 25.2807 | 25.2105 | 25.1359 | 25.0515 | 24.9637 | 24.508 | 24.0322 | 22.8248 | 21.2339 | 19.6449 | 18.1189
|  | HAMWORTHY | ST |  |  | 35.6616 | 35.6571 | 35.6527 | 35.3817 | 35.359 | 35.336 | 35.3125 | 35.2883 | 35.2618 | 35.2509 | 35.2131 | 35.1542 | 35.0766 | 34.6415 | 34.1925 | 34.188 | 34.1836 | 33.9126 | 33.89 | 33.8669 | 33.8434 | 33.8071 | 33.757 | 33.7206 | 33.2325 | 32.1447 | 31.1075 | 30.1301 | 34.5035 | 34.494 | 34.4836 | 34.208 | 34.1763 | 34.1422 | 34.1037 | 34.0641 | 34.0209 | 33.9364 | 33.1167 | 32.0662 | 31.0637 | 30.1164
|  | HAMWORTHY | SP |  |  | 35.6882 | 35.686 | 35.6838 | 35.5483 | 35.5371 | 35.526 | 35.5148 | 35.5037 | 35.4924 | 35.4872 | 35.4699 | 35.4445 | 35.416 | 35.3767 | 34.2191 | 34.2169 | 34.2147 | 34.0792 | 34.0681 | 34.0569 | 34.0458 | 34.0346 | 34.0233 | 34.0182 | 34.0008 | 33.943 | 33.8824 | 33.7728 | 34.5318 | 34.5264 | 34.521 | 34.3839 | 34.3687 | 34.353 | 34.3364 | 34.3198 | 34.3022 | 34.2899 | 34.2546 | 34.2059 | 34.0615 | 33.6434
IVER 132KV | DENHAM | HAREFIELD | MINIMUM HEADROOM | TQ 04001 91227 | YES | 14.723 | 14.723 | 14.723 | 14.723 | 14.7224 | 14.7212 | 14.7193 | 14.7167 | 14.7114 | 14.7105 | 14.7059 | 14.6946 | 14.6543 | 14.6287 | 15.3396 | 15.3396 | 15.3396 | 15.3396 | 15.339 | 15.3378 | 15.3359 | 15.3333 | 15.328 | 15.3271 | 15.3225 | 15.3112 | 15.216 | 14.8745 | 15.4894 | 15.4894 | 15.4894 | 15.4894 | 15.4888 | 15.4876 | 15.4857 | 15.4831 | 15.4779 | 15.4769 | 15.4723 | 15.461 | 15.3661 | 15.0194
|  | HAREFIELD | CT |  |  | 14.723 | 14.723 | 14.723 | 14.723 | 14.7228 | 14.7225 | 14.722 | 14.7212 | 14.7197 | 14.7194 | 14.7178 | 14.7053 | 14.6757 | 14.6473 | 15.3396 | 15.3396 | 15.3396 | 15.3396 | 15.3394 | 15.3391 | 15.3386 | 15.3379 | 15.3363 | 15.336 | 15.3345 | 15.3219 | 15.2715 | 14.9284 | 15.4894 | 15.4894 | 15.4894 | 15.4894 | 15.4892 | 15.4889 | 15.4884 | 15.4877 | 15.4861 | 15.4858 | 15.4843 | 15.4718 | 15.4227 | 15.0733
|  | HAREFIELD | LW |  |  | 14.723 | 14.723 | 14.723 | 14.723 | 14.7224 | 14.7212 | 14.7193 | 14.7167 | 14.7114 | 14.7105 | 14.7059 | 14.6946 | 14.6543 | 14.6287 | 15.3396 | 15.3396 | 15.3396 | 15.3396 | 15.339 | 15.3378 | 15.3359 | 15.3333 | 15.328 | 15.3271 | 15.3225 | 15.3112 | 15.216 | 14.8745 | 15.4894 | 15.4894 | 15.4894 | 15.4894 | 15.4888 | 15.4876 | 15.4857 | 15.4831 | 15.4779 | 15.4769 | 15.4723 | 15.461 | 15.3661 | 15.0194
|  | HAREFIELD | ST |  |  | 14.723 | 14.723 | 14.723 | 14.723 | 14.7228 | 14.7226 | 14.7222 | 14.7217 | 14.7204 | 14.7199 | 14.7167 | 14.7126 | 14.698 | 14.6872 | 15.3396 | 15.3396 | 15.3396 | 15.3396 | 15.3395 | 15.3392 | 15.3389 | 15.3383 | 15.3371 | 15.3365 | 15.3333 | 15.3292 | 15.3146 | 15.3093 | 15.4894 | 15.4894 | 15.4894 | 15.4894 | 15.4893 | 15.489 | 15.4887 | 15.4881 | 15.4869 | 15.4863 | 15.4831 | 15.479 | 15.4644 | 15.4592
|  | HAREFIELD | SP |  |  | 14.723 | 14.723 | 14.723 | 14.723 | 14.723 | 14.723 | 14.7229 | 14.7229 | 14.7229 | 14.7227 | 14.7215 | 14.7206 | 14.7163 | 14.712 | 15.3396 | 15.3396 | 15.3396 | 15.3396 | 15.3396 | 15.3396 | 15.3396 | 15.3395 | 15.3395 | 15.3393 | 15.3381 | 15.3372 | 15.3329 | 15.3287 | 15.4894 | 15.4894 | 15.4894 | 15.4894 | 15.4894 | 15.4894 | 15.4894 | 15.4894 | 15.4893 | 15.4891 | 15.488 | 15.4871 | 15.4827 | 15.4785
NURSLING GSP | WINCHESTER | HARESTOCK | MINIMUM HEADROOM | SU 45908 31300 | YES | 36.3946 | 36.3946 | 31.1315 | 31.1315 | 31.1303 | 31.1279 | 31.1232 | 31.116 | 31.1005 | 31.0978 | 30.5578 | 29.1861 | 28.2163 | 27.3292 | 34.7105 | 34.6458 | 29.1188 | 28.5898 | 28.0571 | 27.5112 | 26.9598 | 26.6453 | 26.3004 | 25.9284 | 24.7085 | 23.1074 | 21.9805 | 20.9428 | 35.3009 | 35.3009 | 30.0377 | 30.0377 | 29.7584 | 29.2365 | 28.7093 | 28.4085 | 28.0829 | 27.7379 | 26.6065 | 25.1182 | 24.0585 | 23.0471
|  | HARESTOCK | CT |  |  | 36.3946 | 36.3946 | 31.1315 | 31.1315 | 31.1311 | 31.1305 | 31.1295 | 31.1266 | 31.1194 | 31.1181 | 30.5578 | 29.1861 | 28.2163 | 27.3292 | 34.7105 | 34.6458 | 29.1188 | 28.5898 | 28.0571 | 27.5112 | 26.9598 | 26.6453 | 26.3004 | 25.9284 | 24.7085 | 23.1074 | 21.9805 | 20.9428 | 35.3009 | 35.3009 | 30.0377 | 30.0377 | 29.7584 | 29.2365 | 28.7093 | 28.4085 | 28.0829 | 27.7379 | 26.6065 | 25.1182 | 24.0585 | 23.0471
|  | HARESTOCK | LW |  |  | 36.3946 | 36.3946 | 31.1315 | 31.1315 | 31.1303 | 31.1279 | 31.1232 | 31.116 | 31.1005 | 31.0978 | 30.7978 | 29.444 | 28.4685 | 27.597 | 34.7105 | 34.6546 | 29.1328 | 28.6151 | 28.0921 | 27.5551 | 27.2597 | 26.9408 | 26.5922 | 26.2237 | 24.9953 | 23.4121 | 22.2795 | 21.2572 | 35.3009 | 35.3009 | 30.0377 | 30.0377 | 29.7919 | 29.2783 | 28.9958 | 28.6906 | 28.3566 | 28.0102 | 26.8703 | 25.3999 | 24.3445 | 23.3534
|  | HARESTOCK | ST |  |  | 36.3946 | 36.3946 | 36.3946 | 36.3946 | 31.1312 | 31.1307 | 31.1297 | 31.1281 | 31.1242 | 31.1224 | 31.1134 | 31.1017 | 30.6078 | 30.0295 | 34.7105 | 34.7105 | 34.6019 | 34.3324 | 28.7279 | 28.3119 | 28.1055 | 27.8852 | 27.6559 | 27.408 | 26.577 | 25.501 | 24.7762 | 24.0999 | 35.3009 | 35.3009 | 35.3009 | 35.3009 | 30.0375 | 30.0021 | 29.8047 | 29.594 | 29.3746 | 29.1375 | 28.3426 | 27.3405 | 26.6655 | 26.0374
|  | HARESTOCK | SP |  |  | 36.3946 | 36.3946 | 36.3946 | 36.3946 | 36.3946 | 36.3946 | 36.3946 | 31.1313 | 31.1312 | 31.1306 | 31.1271 | 31.1245 | 31.1129 | 31.1018 | 34.7105 | 34.7105 | 34.7105 | 34.7105 | 34.7104 | 34.7104 | 34.641 | 29.2974 | 29.1992 | 29.1055 | 28.7826 | 28.3715 | 28.1169 | 27.8847 | 35.3009 | 35.3009 | 35.3009 | 35.3009 | 35.3009 | 35.3008 | 35.3008 | 30.0376 | 30.0374 | 30.0368 | 30.0333 | 30.0307 | 29.8149 | 29.5923
EALING GSP | EALING (D) | HARVARD LANE | MINIMUM HEADROOM | TQ 20021 78030 | YES | 44.1486 | 44.1486 | 44.1486 | 59.5486 | 59.357 | 59.1592 | 58.9527 | 58.7386 | 58.4135 | 58.3684 | 58.2141 | 57.9832 | 57.2424 | 55.3621 | 33.5513 | 33.5513 | 33.5513 | 56.5513 | 56.093 | 55.0575 | 54.267 | 54.0221 | 53.6083 | 53.3385 | 52.4746 | 50.5349 | 47.8576 | 45.7216 | 39.6796 | 39.6327 | 39.6054 | 54.9498 | 54.6349 | 53.5543 | 52.7431 | 52.4939 | 52.0928 | 51.8191 | 50.9428 | 48.9732 | 46.2593 | 44.0866
|  | HARVARD LANE | CT |  |  | 44.1486 | 44.1486 | 44.1486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 58.5577 | 56.7113 | 33.5513 | 33.5513 | 33.5513 | 56.5513 | 56.1175 | 55.195 | 54.267 | 54.0221 | 53.7962 | 53.5714 | 52.8619 | 51.153 | 49.0578 | 46.9557 | 39.6796 | 39.6327 | 39.6054 | 54.9498 | 54.6349 | 53.6874 | 52.7431 | 52.4939 | 52.2642 | 52.0354 | 51.3135 | 49.5748 | 47.4429 | 45.3042
|  | HARVARD LANE | LW |  |  | 44.1486 | 44.1486 | 44.1486 | 59.5486 | 59.357 | 59.1592 | 58.9527 | 58.7386 | 58.4135 | 58.3684 | 58.2141 | 57.9832 | 57.2424 | 55.3621 | 33.5513 | 33.5513 | 33.5513 | 56.5513 | 56.093 | 55.0575 | 54.6182 | 54.1593 | 53.6083 | 53.3385 | 52.4746 | 50.5349 | 47.8576 | 45.7216 | 39.6813 | 39.6357 | 39.61 | 54.9579 | 54.6419 | 53.5543 | 53.1109 | 52.6477 | 52.0928 | 51.8191 | 50.9428 | 48.9732 | 46.2593 | 44.0866
|  | HARVARD LANE | ST |  |  | 44.1486 | 44.1486 | 44.1486 | 59.5486 | 59.5329 | 59.5169 | 59.5006 | 59.4838 | 59.4577 | 59.4489 | 59.4207 | 59.3972 | 59.3159 | 59.2924 | 33.5513 | 33.5513 | 33.5513 | 56.5513 | 56.5356 | 56.5197 | 56.5034 | 56.4865 | 56.4605 | 56.4517 | 56.2247 | 55.0656 | 53.6028 | 52.243 | 39.6914 | 39.6876 | 39.6507 | 55.0343 | 54.9987 | 54.9586 | 54.9263 | 54.893 | 54.8581 | 54.8403 | 54.7838 | 53.5583 | 52.0714 | 50.6882
|  | HARVARD LANE | SP |  |  | 44.1486 | 44.1486 | 44.1486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 59.5486 | 33.5513 | 33.5513 | 33.5513 | 56.5513 | 56.5513 | 56.5513 | 56.5513 | 56.5513 | 56.5513 | 56.5513 | 56.5513 | 56.5513 | 56.5513 | 56.3698 | 39.6914 | 39.6914 | 39.671 | 55.0684 | 55.0601 | 55.0503 | 55.0442 | 55.038 | 55.0307 | 55.0272 | 55.0162 | 54.9881 | 54.9514 | 54.9129
BRAMLEY (FLEE) | FERNHURST | HASLEMERE | MINIMUM HEADROOM | SU 89300 31710 | YES | 32.2526 | 32.2526 | 32.2526 | 35.3526 | 35.2783 | 35.2027 | 35.1254 | 35.0453 | 34.9208 | 34.8785 | 34.7427 | 34.6325 | 34.3059 | 34.2076 | 19.8434 | 19.7264 | 19.5734 | 26.8547 | 26.5607 | 26.2681 | 25.9778 | 25.7911 | 25.6033 | 25.4054 | 24.8186 | 23.799 | 22.7249 | 21.6897 | 25.8439 | 25.7273 | 25.5747 | 26.857 | 26.5639 | 26.2722 | 25.9827 | 25.7966 | 25.6093 | 25.4121 | 24.827 | 23.8104 | 22.7395 | 21.7075
|  | HASLEMERE | CT |  |  | 32.2526 | 32.2526 | 32.2526 | 35.3526 | 35.3526 | 35.3526 | 35.3526 | 35.3513 | 35.3478 | 35.3472 | 35.3442 | 35.3194 | 35.2853 | 34.6581 | 19.8434 | 19.7264 | 19.5734 | 26.8547 | 26.5607 | 26.2681 | 25.9778 | 25.7911 | 25.6033 | 25.4054 | 24.8186 | 23.799 | 22.7249 | 21.6897 | 25.8439 | 25.7273 | 25.5747 | 26.857 | 26.5639 | 26.2722 | 25.9827 | 25.7966 | 25.6093 | 25.4121 | 24.827 | 23.8104 | 22.7395 | 21.7075
|  | HASLEMERE | LW |  |  | 32.2526 | 32.2526 | 32.2526 | 35.3526 | 35.3526 | 35.3526 | 35.3518 | 35.35 | 35.3457 | 35.3449 | 35.34 | 35.3282 | 35.3031 | 34.8157 | 19.8493 | 19.7367 | 19.5894 | 26.8825 | 26.6001 | 26.319 | 26.1323 | 25.9451 | 25.7564 | 25.5585 | 24.9695 | 23.9634 | 22.8978 | 21.8713 | 25.8498 | 25.7375 | 25.5906 | 26.8847 | 26.6032 | 26.3229 | 26.1367 | 25.9501 | 25.762 | 25.5647 | 24.9775 | 23.9744 | 22.912 | 21.8886
|  | HASLEMERE | ST |  |  | 32.2526 | 32.2526 | 32.2526 | 35.3526 | 35.2783 | 35.2027 | 35.1254 | 35.0453 | 34.9208 | 34.8785 | 34.7427 | 34.6325 | 34.3059 | 34.2076 | 19.9316 | 19.8813 | 19.8221 | 27.3216 | 27.137 | 26.9278 | 26.6979 | 26.4661 | 26.2157 | 26.039 | 25.509 | 24.734 | 23.7357 | 22.9729 | 25.9318 | 25.8817 | 25.8227 | 27.3225 | 27.1382 | 26.9294 | 26.6999 | 26.4686 | 26.2186 | 26.0423 | 25.5135 | 24.7405 | 23.7443 | 22.9835
|  | HASLEMERE | SP |  |  | 32.2526 | 32.2526 | 32.2526 | 35.3526 | 35.3494 | 35.3462 | 35.343 | 35.3398 | 35.3347 | 35.3206 | 35.2752 | 35.2533 | 35.1843 | 35.1264 | 19.9736 | 19.959 | 19.9443 | 27.528 | 27.4806 | 27.4248 | 27.369 | 27.3135 | 27.2416 | 27.1753 | 26.9778 | 26.7023 | 26.3821 | 26.0835 | 25.9737 | 25.9591 | 25.9445 | 27.5283 | 27.4809 | 27.4253 | 27.3697 | 27.3143 | 27.2426 | 27.1765 | 26.9794 | 26.7047 | 26.3853 | 26.0874
BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE | MINIMUM HEADROOM | SU 98188 20276 | YES | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.3903 | 12.3066 | 12.2193 | 12.1287 | 11.9912 | 11.9721 | 11.9068 | 11.8092 | 11.2714 | 10.898 | 10.8006 | 10.7963 | 10.7907 | 10.7788 | 10.6862 | 10.5911 | 10.4666 | 10.3392 | 10.1652 | 10.1068 | 9.9254 | 9.6374 | 9.195 | 8.9878 | 10.8077 | 10.7977 | 10.7846 | 10.7567 | 10.6485 | 10.5378 | 10.3632 | 10.1862 | 9.9629 | 9.8514 | 9.5133 | 8.9682 | 8.2611 | 7.7934
|  | HASLINGBOURNE | CT |  |  | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.2277 | 11.8689 | 10.8006 | 10.7963 | 10.7907 | 10.7788 | 10.7673 | 10.7558 | 10.7444 | 10.7076 | 10.6711 | 10.6317 | 10.5156 | 10.3253 | 10.1291 | 9.9364 | 10.8077 | 10.7977 | 10.7846 | 10.7567 | 10.7295 | 10.7025 | 10.6757 | 10.5893 | 10.5035 | 10.411 | 10.1381 | 9.6908 | 9.23 | 8.777
|  | HASLINGBOURNE | LW |  |  | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.3903 | 12.3066 | 12.2193 | 12.1287 | 11.9912 | 11.9721 | 11.9068 | 11.8092 | 11.2714 | 10.898 | 10.8006 | 10.7963 | 10.7907 | 10.7788 | 10.6862 | 10.5911 | 10.4666 | 10.3392 | 10.1652 | 10.1068 | 9.9254 | 9.6374 | 9.195 | 8.9878 | 10.8077 | 10.7977 | 10.7846 | 10.7567 | 10.6485 | 10.5378 | 10.3632 | 10.1862 | 9.9629 | 9.8514 | 9.5133 | 8.9682 | 8.2611 | 7.7934
|  | HASLINGBOURNE | ST |  |  | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4211 | 10.8027 | 10.8 | 10.7969 | 10.7916 | 10.785 | 10.7771 | 10.759 | 10.7411 | 10.7163 | 10.6894 | 10.6112 | 10.4848 | 10.3586 | 10.233 | 10.8127 | 10.8065 | 10.7992 | 10.7866 | 10.7712 | 10.7526 | 10.7101 | 10.6681 | 10.6096 | 10.5466 | 10.3628 | 10.0657 | 9.7692 | 9.474
|  | HASLINGBOURNE | SP |  |  | 12.4713 | 12.4713 | 12.4713 | 12.4713 | 12.4688 | 12.4663 | 12.4638 | 12.4612 | 12.4572 | 12.4462 | 12.411 | 12.3943 | 12.3416 | 12.2976 | 10.8055 | 10.8051 | 10.8047 | 10.8043 | 10.7999 | 10.7953 | 10.7864 | 10.7775 | 10.7652 | 10.7438 | 10.6785 | 10.6141 | 10.516 | 10.429 | 10.8193 | 10.8184 | 10.8174 | 10.8165 | 10.8097 | 10.8022 | 10.7847 | 10.7671 | 10.7437 | 10.7083 | 10.6023 | 10.4735 | 10.3141 | 10.1692
MELKSHAM GSP | FROME BSP | HAWKERIDGE | MINIMUM HEADROOM | ST 86422 53026 | YES | 17.7413 | 17.7295 | 17.7178 | 16.9995 | 16.8175 | 16.6315 | 16.4399 | 16.2435 | 15.9757 | 15.9232 | 15.7534 | 15.4873 | 15.1673 | 15.0233 | 17.0692 | 17.0574 | 17.0456 | 16.3273 | 16.1453 | 15.9594 | 15.7678 | 15.5713 | 15.3036 | 15.2511 | 15.0812 | 14.8151 | 14.4952 | 14.3512 | 17.9635 | 17.9258 | 17.9067 | 17.1696 | 16.9693 | 16.7653 | 16.5643 | 16.3587 | 16.0817 | 16.0192 | 15.7959 | 15.3921 | 14.9275 | 14.6407
|  | HAWKERIDGE | CT |  |  | 17.7978 | 17.7908 | 17.7837 | 17.3527 | 17.3174 | 17.2821 | 17.2468 | 17.2114 | 17.1761 | 17.162 | 17.1196 | 16.6043 | 16.4225 | 16.293 | 17.1257 | 17.1186 | 17.1116 | 16.6806 | 16.6453 | 16.6099 | 16.5746 | 16.5393 | 16.504 | 16.4898 | 16.4474 | 15.9322 | 15.7503 | 15.6208 | 18.0211 | 17.9889 | 17.9772 | 17.531 | 17.4808 | 17.4307 | 17.3808 | 17.3362 | 17.2917 | 17.2676 | 17.1886 | 16.5356 | 16.2091 | 15.9368
|  | HAWKERIDGE | LW |  |  | 17.7413 | 17.7295 | 17.7178 | 16.9995 | 16.8175 | 16.6315 | 16.4399 | 16.2435 | 15.9757 | 15.9232 | 15.7534 | 15.4873 | 15.1673 | 15.0233 | 17.0692 | 17.0574 | 17.0456 | 16.3273 | 16.1453 | 15.9594 | 15.7678 | 15.5713 | 15.3036 | 15.2511 | 15.0812 | 14.8151 | 14.4952 | 14.3512 | 17.9635 | 17.9258 | 17.9067 | 17.1696 | 16.9693 | 16.7653 | 16.5643 | 16.3587 | 16.0817 | 16.0192 | 15.7959 | 15.3921 | 14.9275 | 14.6407
|  | HAWKERIDGE | ST |  |  | 17.8261 | 17.8214 | 17.8167 | 17.5294 | 17.5058 | 17.4823 | 17.4587 | 17.4352 | 17.4116 | 17.4022 | 17.3739 | 17.3268 | 17.2986 | 17.2468 | 17.1539 | 17.1492 | 17.1445 | 16.8572 | 16.8337 | 16.8101 | 16.7866 | 16.763 | 16.7395 | 16.73 | 16.7018 | 16.6547 | 16.6264 | 16.5746 | 18.0491 | 18.0407 | 18.0099 | 17.7109 | 17.673 | 17.6323 | 17.6015 | 17.5708 | 17.541 | 17.5248 | 17.4768 | 17.3776 | 17.2561 | 17.1117
|  | HAWKERIDGE | SP |  |  | 17.8544 | 17.852 | 17.8497 | 17.706 | 17.6942 | 17.6824 | 17.6707 | 17.6589 | 17.6471 | 17.6424 | 17.6283 | 17.6047 | 17.5906 | 17.5647 | 17.1822 | 17.1799 | 17.1775 | 17.0338 | 17.0221 | 17.0103 | 16.9985 | 16.9867 | 16.975 | 16.9703 | 16.9561 | 16.9326 | 16.9184 | 16.8925 | 18.0816 | 18.0788 | 18.0543 | 17.9102 | 17.8965 | 17.8824 | 17.8692 | 17.8559 | 17.8423 | 17.8359 | 17.8142 | 17.7781 | 17.7515 | 17.7136
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY | MINIMUM HEADROOM | SU 85973 57691 | YES | 33.3018 | 33.3 | 33.2981 | 33.2951 | 33.2921 | 33.2887 | 33.2808 | 33.2683 | 33.2558 | 33.2426 | 33.201 | 33.1104 | 32.77 | 31.5558 | 32.5959 | 32.5946 | 32.5934 | 32.5914 | 32.5893 | 32.587 | 32.5816 | 32.573 | 32.5645 | 32.5555 | 32.5272 | 32.2958 | 30.8123 | 29.3266 | 32.669 | 32.6675 | 32.666 | 32.6636 | 32.6611 | 32.6584 | 32.6519 | 32.6419 | 32.6318 | 32.6211 | 32.5875 | 32.5143 | 31.3702 | 29.8936
|  | HAWLEY | CT |  |  | 33.3018 | 33.3 | 33.2981 | 33.2951 | 33.2921 | 33.2887 | 33.2853 | 33.2729 | 33.2604 | 33.2472 | 33.2056 | 33.115 | 32.822 | 31.6082 | 32.5959 | 32.5946 | 32.5934 | 32.5914 | 32.5893 | 32.587 | 32.5847 | 32.5762 | 32.5677 | 32.5586 | 32.5303 | 32.3595 | 30.876 | 29.3907 | 32.669 | 32.6675 | 32.666 | 32.6636 | 32.6611 | 32.6584 | 32.6556 | 32.6456 | 32.6355 | 32.6248 | 32.5912 | 32.518 | 31.4335 | 29.9573
|  | HAWLEY | LW |  |  | 33.3023 | 33.3009 | 33.2995 | 33.2976 | 33.2956 | 33.2932 | 33.2808 | 33.2683 | 33.2558 | 33.2426 | 33.201 | 33.1104 | 32.77 | 31.5558 | 32.5963 | 32.5953 | 32.5944 | 32.5931 | 32.5917 | 32.5901 | 32.5816 | 32.573 | 32.5645 | 32.5555 | 32.5272 | 32.2958 | 30.8123 | 29.3266 | 32.6694 | 32.6682 | 32.6671 | 32.6656 | 32.6639 | 32.662 | 32.6519 | 32.6419 | 32.6318 | 32.6211 | 32.5875 | 32.5143 | 31.3702 | 29.8936
|  | HAWLEY | ST |  |  | 33.3019 | 33.3002 | 33.2987 | 33.2965 | 33.2937 | 33.2904 | 33.285 | 33.2796 | 33.2711 | 33.262 | 33.2337 | 33.1715 | 33.1013 | 33.0328 | 32.596 | 32.5948 | 32.5938 | 32.5923 | 32.5904 | 32.5881 | 32.5844 | 32.5808 | 32.575 | 32.5688 | 32.5494 | 32.507 | 32.1702 | 31.2201 | 32.669 | 32.6677 | 32.6664 | 32.6647 | 32.6624 | 32.6597 | 32.6554 | 32.651 | 32.6441 | 32.6368 | 32.6139 | 32.5637 | 32.5069 | 31.7755
|  | HAWLEY | SP |  |  | 33.3032 | 33.3026 | 33.3022 | 33.3019 | 33.3014 | 33.3008 | 33.2991 | 33.2974 | 33.2952 | 33.2917 | 33.2806 | 33.2556 | 33.225 | 33.1934 | 32.5968 | 32.5964 | 32.5962 | 32.596 | 32.5956 | 32.5952 | 32.5941 | 32.5929 | 32.5914 | 32.589 | 32.5815 | 32.5644 | 32.5435 | 32.522 | 32.67 | 32.6696 | 32.6693 | 32.669 | 32.6686 | 32.6682 | 32.6668 | 32.6654 | 32.6636 | 32.6608 | 32.6518 | 32.6316 | 32.6069 | 32.5813
COWLEY GSP | HEADINGTON BSP | HEADINGTON | MINIMUM HEADROOM | SP 54440 08085 | NO | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.1951 | 43.9474 | 42.7319 | 44.5923 | 44.585 | 44.5755 | 44.5539 | 44.5285 | 44.5024 | 44.4779 | 44.4597 | 44.4396 | 44.4174 | 44.1595 | 42.8254 | 41.405 | 40.0212 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1045 | 43.7694 | 42.9422 | 41.7161 | 40.3696 | 39.0579
|  | HEADINGTON | CT |  |  | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.1951 | 43.9474 | 42.7319 | 44.5923 | 44.585 | 44.5755 | 44.5539 | 44.5285 | 44.5024 | 44.4779 | 44.4597 | 44.4396 | 44.4174 | 44.1595 | 42.8254 | 41.405 | 40.0212 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1045 | 43.7694 | 42.9422 | 41.7161 | 40.3696 | 39.0579
|  | HEADINGTON | LW |  |  | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.4264 | 44.1784 | 42.9629 | 44.5932 | 44.5866 | 44.578 | 44.5583 | 44.5347 | 44.5104 | 44.4932 | 44.475 | 44.4549 | 44.4327 | 44.3778 | 43.0887 | 41.668 | 40.2841 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.0001 | 43.1727 | 41.9657 | 40.6189 | 39.3071
|  | HEADINGTON | ST |  |  | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.6689 | 44.5986 | 44.5961 | 44.5932 | 44.5869 | 44.5768 | 44.5654 | 44.5541 | 44.5421 | 44.5285 | 44.5133 | 44.4752 | 44.4219 | 44.2506 | 43.3648 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 43.8379 | 43.0223 | 42.2274
|  | HEADINGTON | SP |  |  | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 45.9683 | 44.6002 | 44.5991 | 44.5981 | 44.596 | 44.5908 | 44.5852 | 44.5806 | 44.5759 | 44.5702 | 44.5642 | 44.5492 | 44.5278 | 44.5046 | 44.4815 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072 | 44.1072
NURSLING GSP | VELMORE BSP | HEDGE END | MINIMUM HEADROOM | SU 49035 15685 | YES | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 29.9074 | 29.7706 | 29.6316 | 29.4864 | 29.2625 | 29.2341 | 29.143 | 28.7223 | 28.1803 | 28.0557 | 32.0412 | 32.0294 | 32.0121 | 31.9834 | 31.8267 | 31.628 | 31.1733 | 30.7893 | 30.389 | 30.2027 | 29.7102 | 28.6196 | 27.4133 | 26.6724 | 32.186 | 32.1776 | 32.1653 | 32.145 | 31.9947 | 31.5704 | 31.1174 | 30.7397 | 30.3441 | 30.1614 | 29.6596 | 28.5535 | 27.3319 | 26.5755
|  | HEDGE END | CT |  |  | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 29.9074 | 29.7706 | 29.6316 | 29.4864 | 29.2625 | 29.2341 | 29.143 | 28.7223 | 28.1803 | 28.0557 | 32.0424 | 32.0315 | 32.0154 | 31.9892 | 31.8267 | 31.628 | 31.1733 | 30.7893 | 30.389 | 30.2027 | 29.7102 | 28.6196 | 27.4133 | 26.6724 | 32.1868 | 32.1791 | 32.1676 | 32.149 | 31.9947 | 31.5704 | 31.1174 | 30.7397 | 30.3441 | 30.1614 | 29.6596 | 28.5535 | 27.3319 | 26.5755
|  | HEDGE END | LW |  |  | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 32.0412 | 32.0294 | 32.0121 | 31.9834 | 31.9531 | 31.7801 | 31.5488 | 31.3099 | 31.1335 | 30.9755 | 30.5741 | 29.9043 | 29.2399 | 28.6236 | 32.186 | 32.1776 | 32.1653 | 32.145 | 32.0888 | 31.7191 | 31.4939 | 31.2613 | 31.0894 | 30.9334 | 30.5226 | 29.8375 | 29.1578 | 28.5248
|  | HEDGE END | ST |  |  | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 32.0436 | 32.0348 | 32.023 | 32.0061 | 31.9856 | 31.9616 | 31.941 | 31.9032 | 31.8047 | 31.6964 | 31.4193 | 30.9593 | 30.525 | 30.1289 | 32.1877 | 32.1815 | 32.173 | 32.1611 | 32.1465 | 32.1294 | 32.0256 | 31.8589 | 31.743 | 31.6376 | 31.3677 | 30.9168 | 30.4725 | 30.0673
|  | HEDGE END | SP |  |  | 30.0419 | 30.0419 | 30.0419 | 30.0419 | 30.0398 | 30.0378 | 30.0357 | 30.0336 | 30.0303 | 30.0212 | 29.9923 | 29.9786 | 29.9352 | 29.899 | 32.0494 | 32.0458 | 32.0412 | 32.0362 | 32.0268 | 32.0168 | 32.0091 | 32.0014 | 31.9935 | 31.9808 | 31.9428 | 31.9136 | 31.8551 | 31.7985 | 32.1918 | 32.1893 | 32.186 | 32.1825 | 32.1752 | 32.1675 | 32.1614 | 32.1553 | 32.1488 | 32.1371 | 32.1018 | 32.077 | 32.0229 | 31.8849
BRAMLEY (FLEE) | READING BSP | HENLEY | MINIMUM HEADROOM | SU 76070 82422 | YES | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1334 | 36.0927 | 36.0502 | 36.0062 | 35.9393 | 35.93 | 35.6915 | 34.7601 | 33.8601 | 33.0615 | 34.4801 | 34.4686 | 34.4609 | 34.4438 | 34.3928 | 34.3339 | 34.2787 | 34.221 | 34.1392 | 34.1137 | 33.0109 | 31.9653 | 30.9973 | 30.0891 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.5812 | 34.5405 | 34.498 | 34.454 | 34.3871 | 34.3778 | 34.0183 | 33.0133 | 32.0744 | 31.2126
|  | HENLEY | CT |  |  | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 35.6915 | 34.7601 | 33.9384 | 33.1468 | 34.4801 | 34.4686 | 34.4609 | 34.4438 | 34.425 | 34.4046 | 34.3841 | 34.3704 | 34.3555 | 34.2343 | 33.0109 | 31.9653 | 31.0298 | 30.1257 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.0183 | 33.0133 | 32.1265 | 31.2503
|  | HENLEY | LW |  |  | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1334 | 36.0927 | 36.0502 | 36.0062 | 35.9393 | 35.93 | 35.7483 | 34.7698 | 33.8601 | 33.0615 | 34.4813 | 34.4705 | 34.4638 | 34.4489 | 34.3928 | 34.3339 | 34.2787 | 34.221 | 34.1392 | 34.1137 | 33.1068 | 32.0186 | 30.9973 | 30.0891 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.5812 | 34.5405 | 34.498 | 34.454 | 34.3871 | 34.3778 | 34.1014 | 33.0492 | 32.0744 | 31.2126
|  | HENLEY | ST |  |  | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 35.7161 | 34.4851 | 34.4828 | 34.4745 | 34.4694 | 34.4619 | 34.4521 | 34.4424 | 34.432 | 34.422 | 34.4108 | 34.3708 | 34.207 | 33.6133 | 33.0384 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.5863 | 34.0449
|  | HENLEY | SP |  |  | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 36.1728 | 34.4873 | 34.4868 | 34.4807 | 34.4799 | 34.4769 | 34.4731 | 34.4693 | 34.4654 | 34.4606 | 34.4562 | 34.4404 | 34.4277 | 34.4174 | 34.4079 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206 | 34.6206
AXMINSTER | YEOVIL BSP | HENSTRIDGE | MINIMUM HEADROOM | ST 72676 19263 | YES | 24.1295 | 24.1131 | 24.0823 | 24.0488 | 23.9542 | 23.8527 | 23.7469 | 23.571 | 23.3577 | 23.2198 | 22.8699 | 22.244 | 21.5807 | 21.1107 | 24.1278 | 24.1046 | 24.0609 | 24.0134 | 23.9029 | 23.7832 | 23.6577 | 23.4565 | 23.2194 | 23.0562 | 22.6459 | 21.9394 | 21.1981 | 20.6531 | 23.9194 | 23.8967 | 23.8539 | 23.8075 | 23.6982 | 23.5798 | 23.4558 | 23.2576 | 23.0237 | 22.8639 | 22.4633 | 21.7705 | 21.0425 | 20.5103
|  | HENSTRIDGE | CT |  |  | 24.1295 | 24.1131 | 24.0823 | 24.0488 | 23.9542 | 23.8527 | 23.7469 | 23.571 | 23.3577 | 23.2198 | 22.8699 | 22.244 | 21.5807 | 21.1107 | 24.1278 | 24.1046 | 24.0609 | 24.0134 | 23.9029 | 23.7832 | 23.6577 | 23.4565 | 23.2194 | 23.0562 | 22.6459 | 21.9394 | 21.1981 | 20.6531 | 23.9194 | 23.8967 | 23.8539 | 23.8075 | 23.6982 | 23.5798 | 23.4558 | 23.2576 | 23.0237 | 22.8639 | 22.4633 | 21.7705 | 21.0425 | 20.5103
|  | HENSTRIDGE | LW |  |  | 24.1295 | 24.1132 | 24.0824 | 24.049 | 24.0113 | 23.9678 | 23.8617 | 23.7452 | 23.6266 | 23.5007 | 23.188 | 22.74 | 22.3058 | 21.8883 | 24.1279 | 24.1047 | 24.061 | 24.0137 | 23.9601 | 23.8984 | 23.7583 | 23.6184 | 23.4761 | 23.3246 | 22.9528 | 22.4243 | 21.9121 | 21.4195 | 23.9194 | 23.8968 | 23.854 | 23.8078 | 23.7554 | 23.695 | 23.558 | 23.4212 | 23.282 | 23.1343 | 22.772 | 22.2573 | 21.7584 | 21.2785
|  | HENSTRIDGE | ST |  |  | 24.3571 | 24.1217 | 24.101 | 24.0814 | 24.0574 | 24.028 | 23.9704 | 23.9128 | 23.8332 | 23.7471 | 23.5361 | 23.2385 | 22.9583 | 22.6872 | 24.3347 | 24.1168 | 24.0874 | 24.0597 | 24.0256 | 23.9839 | 23.9022 | 23.8204 | 23.7241 | 23.6208 | 23.3673 | 23.0123 | 22.6819 | 22.362 | 24.2352 | 23.9086 | 23.8798 | 23.8527 | 23.8194 | 23.7786 | 23.6987 | 23.6188 | 23.5246 | 23.4235 | 23.1758 | 22.8301 | 22.5082 | 22.1966
|  | HENSTRIDGE | SP |  |  | 24.3615 | 24.1309 | 24.119 | 24.1104 | 24.0895 | 24.0674 | 24.0382 | 24.0094 | 23.9725 | 23.9008 | 23.6946 | 23.5193 | 23.2125 | 22.9474 | 24.338 | 24.1298 | 24.113 | 24.1007 | 24.0753 | 24.048 | 24.0106 | 23.974 | 23.928 | 23.8444 | 23.609 | 23.4073 | 23.0802 | 22.7962 | 24.2413 | 23.9213 | 23.9049 | 23.8929 | 23.8678 | 23.8408 | 23.8041 | 23.7681 | 23.7228 | 23.64 | 23.4069 | 23.2082 | 22.8837 | 22.6023
BRAMLEY (FLEE) | ALTON | HERRIARD | MINIMUM HEADROOM | SU 66770 44972 | YES | 3.1171 | 3.1063 | 3.0921 | 3.062 | 3.0329 | 3.004 | 2.9913 | 2.9788 | 2.9663 | 2.9528 | 2.913 | 2.8471 | 2.7789 | 2.7118 | 1.4466 | 1.4314 | 1.4115 | 1.3695 | 1.3287 | 1.2882 | 1.2704 | 1.2528 | 1.2353 | 1.2164 | 1.1606 | 1.0684 | 0.97288 | 0.87886 | 1.9717 | 1.9562 | 1.936 | 1.8932 | 1.8517 | 1.8105 | 1.7924 | 1.7745 | 1.7567 | 1.7375 | 1.6807 | 1.5868 | 1.4896 | 1.394
|  | HERRIARD | CT |  |  | 3.1195 | 3.1104 | 3.0984 | 3.0732 | 3.0487 | 3.0244 | 3.0004 | 2.9878 | 2.9753 | 2.9618 | 2.922 | 2.8561 | 2.7879 | 2.7209 | 1.4499 | 1.4371 | 1.4204 | 1.385 | 1.3507 | 1.3168 | 1.2831 | 1.2655 | 1.248 | 1.2291 | 1.1733 | 1.081 | 0.98556 | 0.89162 | 1.9751 | 1.962 | 1.945 | 1.909 | 1.8741 | 1.8395 | 1.8053 | 1.7874 | 1.7696 | 1.7503 | 1.6936 | 1.5997 | 1.5025 | 1.407
|  | HERRIARD | LW |  |  | 3.1171 | 3.1063 | 3.0921 | 3.062 | 3.0329 | 3.004 | 2.9913 | 2.9788 | 2.9663 | 2.9528 | 2.913 | 2.8471 | 2.7789 | 2.7118 | 1.4466 | 1.4314 | 1.4115 | 1.3695 | 1.3287 | 1.2882 | 1.2704 | 1.2528 | 1.2353 | 1.2164 | 1.1606 | 1.0684 | 0.97288 | 0.87886 | 1.9717 | 1.9562 | 1.936 | 1.8932 | 1.8517 | 1.8105 | 1.7924 | 1.7745 | 1.7567 | 1.7375 | 1.6807 | 1.5868 | 1.4896 | 1.394
|  | HERRIARD | ST |  |  | 3.123 | 3.1167 | 3.1093 | 3.0965 | 3.0809 | 3.062 | 3.0542 | 3.0466 | 3.0381 | 3.0289 | 3.002 | 2.9582 | 2.9143 | 2.8705 | 1.4549 | 1.4461 | 1.4356 | 1.4178 | 1.3959 | 1.3694 | 1.3585 | 1.3478 | 1.3359 | 1.323 | 1.2854 | 1.2241 | 1.1625 | 1.1012 | 1.9801 | 1.9711 | 1.9605 | 1.9423 | 1.92 | 1.8931 | 1.8821 | 1.8711 | 1.859 | 1.8459 | 1.8076 | 1.7452 | 1.6826 | 1.6203
|  | HERRIARD | SP |  |  | 3.1296 | 3.1285 | 3.1274 | 3.1264 | 3.1215 | 3.1157 | 3.113 | 3.1103 | 3.107 | 3.1034 | 3.0931 | 3.0766 | 3.0606 | 3.0455 | 1.4641 | 1.4625 | 1.461 | 1.4595 | 1.4527 | 1.4446 | 1.4408 | 1.4371 | 1.4324 | 1.4274 | 1.4129 | 1.3898 | 1.3675 | 1.3463 | 1.9894 | 1.9879 | 1.9863 | 1.9848 | 1.9779 | 1.9696 | 1.9658 | 1.962 | 1.9572 | 1.9522 | 1.9374 | 1.9139 | 1.8912 | 1.8696
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE | MINIMUM HEADROOM | SU 84733 92200 | YES | 37.4776 | 37.461 | 37.4444 | 36.4323 | 36.3493 | 36.2664 | 36.1834 | 36.1004 | 36.0175 | 35.9843 | 35.8847 | 35.7188 | 35.1734 | 34.2875 | 36.1268 | 36.1029 | 36.0766 | 35.0442 | 34.9415 | 34.839 | 34.7376 | 34.6363 | 34.5351 | 34.4823 | 34.3238 | 33.9511 | 33.2704 | 32.3659 | 36.2972 | 36.277 | 36.2556 | 35.2334 | 35.1406 | 35.0479 | 34.9558 | 34.8638 | 34.7718 | 34.7288 | 34.2854 | 33.3231 | 32.3567 | 31.3152
|  | HIGH WYCOMBE | CT |  |  | 37.5572 | 37.5473 | 37.5373 | 36.9301 | 36.8803 | 36.8305 | 36.7807 | 36.7309 | 36.6812 | 36.6613 | 36.6015 | 35.8754 | 35.1821 | 34.298 | 36.2067 | 36.1896 | 36.1702 | 35.5431 | 35.4741 | 35.4052 | 35.3364 | 35.2683 | 35.2003 | 35.1608 | 35.0421 | 34.1153 | 33.2782 | 32.3783 | 36.377 | 36.3635 | 36.3488 | 35.7317 | 35.6724 | 35.6131 | 35.5539 | 35.495 | 35.4362 | 35.4066 | 35.0139 | 33.4912 | 32.3684 | 31.3271
|  | HIGH WYCOMBE | LW |  |  | 37.4776 | 37.461 | 37.4444 | 36.4323 | 36.3493 | 36.2664 | 36.1834 | 36.1004 | 36.0175 | 35.9843 | 35.8847 | 35.7188 | 35.1734 | 34.2875 | 36.1268 | 36.1029 | 36.0766 | 35.0442 | 34.9415 | 34.839 | 34.7376 | 34.6363 | 34.5351 | 34.4823 | 34.3238 | 33.9511 | 33.2704 | 32.3659 | 36.2972 | 36.277 | 36.2556 | 35.2334 | 35.1406 | 35.0479 | 34.9558 | 34.8638 | 34.7718 | 34.7288 | 34.2854 | 33.3231 | 32.3567 | 31.3152
|  | HIGH WYCOMBE | ST |  |  | 37.5971 | 37.5904 | 37.5838 | 37.1789 | 37.1458 | 37.1126 | 37.0794 | 37.0462 | 37.013 | 36.9997 | 36.9599 | 36.8935 | 36.8537 | 36.712 | 36.2484 | 36.2362 | 36.223 | 35.807 | 35.7601 | 35.7103 | 35.6638 | 35.6174 | 35.5718 | 35.5451 | 35.4655 | 35.3274 | 35.2123 | 34.7723 | 36.4177 | 36.4083 | 36.3984 | 35.988 | 35.948 | 35.9066 | 35.8668 | 35.8271 | 35.7877 | 35.7678 | 35.7082 | 35.2555 | 34.6536 | 34.026
|  | HIGH WYCOMBE | SP |  |  | 37.6369 | 37.6336 | 37.6302 | 37.4278 | 37.4112 | 37.3946 | 37.378 | 37.3615 | 37.3449 | 37.3382 | 37.3183 | 37.2851 | 37.2652 | 37.2287 | 36.2944 | 36.2903 | 36.2861 | 36.0829 | 36.0629 | 36.0424 | 36.0214 | 36.0004 | 35.9783 | 35.9665 | 35.9312 | 35.8703 | 35.821 | 35.7555 | 36.4606 | 36.4569 | 36.4531 | 36.2503 | 36.2321 | 36.2135 | 36.1947 | 36.176 | 36.1566 | 36.1474 | 36.1199 | 36.0729 | 36.0384 | 35.9875
COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN | MINIMUM HEADROOM | SU 86304 92972 | YES | 67.8251 | 67.8116 | 67.7981 | 66.9737 | 66.9061 | 66.8385 | 66.771 | 66.7034 | 66.6358 | 66.6088 | 66.5277 | 65.6722 | 65.1849 | 64.9722 | 65.8156 | 65.7988 | 65.7811 | 64.9481 | 64.872 | 64.7958 | 64.7164 | 64.6369 | 64.5574 | 64.5176 | 64.3965 | 63.1976 | 61.8704 | 60.5928 | 66.6063 | 66.5928 | 66.5793 | 65.7549 | 65.6873 | 65.6197 | 65.5521 | 65.4846 | 65.417 | 65.39 | 65.3089 | 64.4533 | 63.9048 | 63.5787
|  | HIGH WYCOMBE TOWN | CT |  |  | 67.89 | 67.8819 | 67.8738 | 67.3791 | 67.2522 | 67.1237 | 66.9938 | 66.86 | 66.6756 | 66.6411 | 66.5339 | 65.6722 | 65.1849 | 64.9722 | 65.8803 | 65.8688 | 65.8563 | 65.3528 | 65.217 | 65.0797 | 64.9409 | 64.7952 | 64.5988 | 64.5517 | 64.4045 | 63.1976 | 61.8704 | 60.5928 | 66.6712 | 66.6631 | 66.6549 | 66.1603 | 66.0333 | 65.9049 | 65.775 | 65.6411 | 65.4567 | 65.4223 | 65.3151 | 64.4533 | 63.9048 | 63.5787
|  | HIGH WYCOMBE TOWN | LW |  |  | 67.8251 | 67.8116 | 67.7981 | 66.9737 | 66.9061 | 66.8385 | 66.771 | 66.7034 | 66.6358 | 66.6088 | 66.5277 | 66.3926 | 66.3115 | 66.1628 | 65.8156 | 65.7988 | 65.7811 | 64.9481 | 64.872 | 64.7958 | 64.7164 | 64.6369 | 64.5574 | 64.5176 | 64.3965 | 63.9039 | 62.9829 | 61.7613 | 66.6063 | 66.5928 | 66.5793 | 65.7549 | 65.6873 | 65.6197 | 65.5521 | 65.4846 | 65.417 | 65.39 | 65.3089 | 65.1737 | 65.0302 | 64.7475
|  | HIGH WYCOMBE TOWN | ST |  |  | 67.9224 | 67.917 | 67.9116 | 67.5819 | 67.5548 | 67.5278 | 67.5008 | 67.4737 | 67.4467 | 67.4359 | 67.4035 | 67.3494 | 67.317 | 67.2575 | 65.9177 | 65.9064 | 65.8983 | 65.564 | 65.5316 | 65.4979 | 65.4612 | 65.4246 | 65.3894 | 65.3699 | 65.3103 | 65.1965 | 64.8099 | 64.2124 | 66.7036 | 66.6982 | 66.6928 | 66.363 | 66.336 | 66.309 | 66.2819 | 66.2549 | 66.2279 | 66.2171 | 66.1846 | 66.1306 | 66.0981 | 66.001
|  | HIGH WYCOMBE TOWN | SP |  |  | 67.9549 | 67.9522 | 67.9495 | 67.7846 | 67.7711 | 67.7576 | 67.744 | 67.7305 | 67.717 | 67.7116 | 67.6954 | 67.6684 | 67.6521 | 67.6224 | 65.9524 | 65.9456 | 65.9424 | 65.777 | 65.762 | 65.7467 | 65.7298 | 65.713 | 65.6953 | 65.6865 | 65.6598 | 65.6089 | 65.5633 | 65.503 | 66.736 | 66.7333 | 66.7306 | 66.5658 | 66.5522 | 66.5387 | 66.5252 | 66.5117 | 66.4982 | 66.4928 | 66.4766 | 66.4495 | 66.4333 | 66.4036
LOVEDEAN GSP | WYMERING BSP | HILSEA | MINIMUM HEADROOM | SU 66394 03806 | NO | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.9558 | 31.9554 | 31.9548 | 31.9537 | 31.9526 | 31.9515 | 31.9496 | 31.9477 | 31.9458 | 31.9438 | 31.9375 | 31.9249 | 31.9103 | 31.8958
|  | HILSEA | CT |  |  | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.9558 | 31.9554 | 31.9548 | 31.9537 | 31.9526 | 31.9515 | 31.9503 | 31.9485 | 31.9466 | 31.9445 | 31.9383 | 31.9256 | 31.9111 | 31.8965
|  | HILSEA | LW |  |  | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.9558 | 31.9554 | 31.9548 | 31.9537 | 31.9526 | 31.9515 | 31.9496 | 31.9477 | 31.9458 | 31.9438 | 31.9375 | 31.9249 | 31.9103 | 31.8958
|  | HILSEA | ST |  |  | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.956 | 31.9557 | 31.9554 | 31.9549 | 31.9542 | 31.9535 | 31.9521 | 31.9507 | 31.9495 | 31.9481 | 31.9439 | 31.9352 | 31.9257 | 31.9164
|  | HILSEA | SP |  |  | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 32.3915 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.8922 | 31.9562 | 31.9562 | 31.9561 | 31.956 | 31.9559 | 31.9556 | 31.9552 | 31.9548 | 31.9542 | 31.9536 | 31.952 | 31.9486 | 31.9447 | 31.9406
MANNINGTON GSP | ARNEWOOD | HINCHELSEA | MINIMUM HEADROOM | SU 27805 00447 | YES | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.1154 | 16.8921 | 16.8914 | 16.8904 | 16.8883 | 16.8863 | 16.8843 | 16.8814 | 16.878 | 16.8746 | 16.871 | 16.8602 | 16.8425 | 16.7751 | 16.3765 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.6153 | 16.2028 | 15.7972
|  | HINCHELSEA | CT |  |  | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.1322 | 16.8921 | 16.8914 | 16.8904 | 16.8883 | 16.8863 | 16.8843 | 16.8823 | 16.8789 | 16.8755 | 16.8718 | 16.861 | 16.8433 | 16.7943 | 16.3959 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.6347 | 16.2223 | 15.8169
|  | HINCHELSEA | LW |  |  | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.1154 | 16.8922 | 16.8915 | 16.8906 | 16.8886 | 16.8867 | 16.8849 | 16.8814 | 16.878 | 16.8746 | 16.871 | 16.8602 | 16.8425 | 16.7751 | 16.3765 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.6153 | 16.2028 | 15.7972
|  | HINCHELSEA | ST |  |  | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 16.8924 | 16.8919 | 16.8912 | 16.8901 | 16.8888 | 16.8872 | 16.8845 | 16.8819 | 16.8796 | 16.8771 | 16.8698 | 16.8581 | 16.8463 | 16.8346 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.7014 | 16.4373
|  | HINCHELSEA | SP |  |  | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 17.3905 | 16.893 | 16.8929 | 16.8929 | 16.8928 | 16.8925 | 16.8921 | 16.8913 | 16.8904 | 16.8894 | 16.8884 | 16.8856 | 16.8811 | 16.8769 | 16.8729 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413 | 16.9413
BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD | MINIMUM HEADROOM | SU 88631 36479 | YES | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5007 | 34.4882 | 34.4776 | 34.4644 | 34.4541 | 34.4222 | 34.3459 | 34.258 | 34.197 | 33.1258 | 33.1122 | 33.0944 | 33.0566 | 33.0201 | 32.9838 | 32.9478 | 32.9205 | 32.8905 | 32.8623 | 32.7773 | 32.4687 | 31.812 | 31.1644 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1947 | 33.192 | 33.1857 | 33.1846 | 33.1778 | 33.1566 | 32.9574 | 32.3257
|  | HINDHEAD | CT |  |  | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5007 | 34.4882 | 34.4776 | 34.4644 | 34.4541 | 34.4222 | 34.3459 | 34.258 | 34.197 | 33.1258 | 33.1122 | 33.0944 | 33.0566 | 33.0201 | 32.9838 | 32.9478 | 32.9205 | 32.8905 | 32.8623 | 32.7773 | 32.4687 | 31.812 | 31.1644 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1942 | 33.1898 | 33.189 | 33.1854 | 33.1566 | 32.9574 | 32.3257
|  | HINDHEAD | LW |  |  | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.4972 | 34.4856 | 34.4705 | 34.4598 | 34.4249 | 34.3615 | 34.2783 | 34.2266 | 33.1281 | 33.1161 | 33.1004 | 33.0673 | 33.0351 | 33.0032 | 32.976 | 32.9477 | 32.916 | 32.8874 | 32.7993 | 32.601 | 31.9489 | 31.321 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1947 | 33.192 | 33.1857 | 33.1846 | 33.1778 | 33.1619 | 33.0965 | 32.4734
|  | HINDHEAD | ST |  |  | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5048 | 34.504 | 34.4989 | 34.4917 | 34.4693 | 34.4334 | 34.3863 | 34.3494 | 33.1324 | 33.1238 | 33.1138 | 33.0966 | 33.0755 | 33.05 | 33.0268 | 33.0034 | 32.9841 | 32.9647 | 32.9065 | 32.8108 | 32.703 | 32.4185 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1956 | 33.1949 | 33.193 | 33.1923 | 33.1889 | 33.1848 | 33.1698 | 33.1648
|  | HINDHEAD | SP |  |  | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.5051 | 34.505 | 34.5047 | 34.5031 | 34.502 | 34.4981 | 34.4851 | 33.1419 | 33.1406 | 33.1394 | 33.1382 | 33.1328 | 33.1265 | 33.1182 | 33.1099 | 33.0993 | 33.0917 | 33.069 | 33.033 | 32.9948 | 32.9585 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1959 | 33.1958 | 33.1955 | 33.1939 | 33.1928 | 33.1889 | 33.1854
MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL | MINIMUM HEADROOM | SU 00702 06030 | YES | 6.5485 | 6.5401 | 6.529 | 6.5056 | 6.3953 | 6.2658 | 6.1418 | 6.0139 | 5.8263 | 5.7547 | 5.5267 | 5.3125 | 4.683 | 4.4609 | 5.0694 | 5.0651 | 5.0596 | 5.0478 | 4.9398 | 4.8211 | 4.704 | 4.5829 | 4.4004 | 4.3343 | 4.112 | 3.8913 | 3.2552 | 3.0265 | 5.3642 | 5.3557 | 5.3445 | 5.3209 | 5.2105 | 5.0808 | 4.9566 | 4.8286 | 4.6409 | 4.5692 | 4.3408 | 4.1261 | 3.496 | 3.2733
|  | HINTON MARTELL | CT |  |  | 6.5503 | 6.5432 | 6.5338 | 6.5141 | 6.4947 | 6.4751 | 6.4553 | 6.4388 | 6.4206 | 6.4039 | 6.3531 | 6.2472 | 6.1348 | 6.0437 | 5.0703 | 5.0667 | 5.062 | 5.0521 | 5.0421 | 5.032 | 5.0215 | 5.0125 | 5.0017 | 4.9909 | 4.9342 | 4.8185 | 4.6957 | 4.5945 | 5.3661 | 5.3589 | 5.3494 | 5.3295 | 5.3099 | 5.2901 | 5.2701 | 5.2534 | 5.235 | 5.2182 | 5.1669 | 5.0601 | 4.9468 | 4.8548
|  | HINTON MARTELL | LW |  |  | 6.5485 | 6.5401 | 6.529 | 6.5056 | 6.4817 | 6.4567 | 6.4376 | 6.4172 | 6.3913 | 6.3734 | 6.3161 | 6.2129 | 6.0839 | 5.9986 | 5.0694 | 5.0651 | 5.0596 | 5.0478 | 5.0352 | 5.0214 | 5.0099 | 4.9969 | 4.9785 | 4.9588 | 4.8957 | 4.7826 | 4.6433 | 4.5478 | 5.3642 | 5.3557 | 5.3445 | 5.3209 | 5.2967 | 5.2715 | 5.2522 | 5.2316 | 5.2056 | 5.1875 | 5.1298 | 5.0257 | 4.8958 | 4.8095
|  | HINTON MARTELL | ST |  |  | 6.5498 | 6.5425 | 6.5339 | 6.5192 | 6.3953 | 6.2658 | 6.1418 | 6.0139 | 5.8263 | 5.7547 | 5.5267 | 5.3125 | 4.683 | 4.4609 | 5.07 | 5.0663 | 5.062 | 5.0546 | 4.9398 | 4.8211 | 4.704 | 4.5829 | 4.4004 | 4.3343 | 4.112 | 3.8913 | 3.2552 | 3.0265 | 5.3655 | 5.3582 | 5.3494 | 5.3346 | 5.2105 | 5.0808 | 4.9566 | 4.8286 | 4.6409 | 4.5692 | 4.3408 | 4.1261 | 3.496 | 3.2733
|  | HINTON MARTELL | SP |  |  | 6.5582 | 6.5573 | 6.5564 | 6.5556 | 6.5517 | 6.5472 | 6.5424 | 6.5376 | 6.5314 | 6.5268 | 6.512 | 6.4899 | 6.461 | 6.4333 | 5.0742 | 5.0738 | 5.0733 | 5.0729 | 5.0709 | 5.0687 | 5.0662 | 5.0638 | 5.0607 | 5.0581 | 5.0495 | 5.0375 | 5.0185 | 5.0003 | 5.3741 | 5.3732 | 5.3723 | 5.3714 | 5.3675 | 5.3629 | 5.3581 | 5.3532 | 5.347 | 5.3423 | 5.3274 | 5.305 | 5.276 | 5.2481
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE | MINIMUM HEADROOM | SU 79461 54769 | YES | 48.3328 | 48.3328 | 48.3328 | 48.3328 | 48.2817 | 48.2075 | 48.1077 | 47.9809 | 47.7747 | 47.7443 | 47.1121 | 45.8033 | 44.3653 | 43.3479 | 44.8743 | 44.4581 | 44.1251 | 43.4513 | 42.7324 | 41.9797 | 41.6075 | 41.188 | 40.6706 | 40.2883 | 39.1502 | 37.6612 | 36.0535 | 34.8714 | 45.6316 | 45.2174 | 44.886 | 44.2154 | 43.4998 | 42.7503 | 42.3795 | 41.9614 | 41.4491 | 41.0887 | 40.0138 | 38.5592 | 36.9373 | 35.7416
|  | HITCHES LANE | CT |  |  | 48.3328 | 48.3328 | 48.3328 | 48.3328 | 48.3265 | 48.3147 | 48.2972 | 48.2718 | 48.2275 | 48.221 | 47.6253 | 46.3583 | 45.1375 | 44.0931 | 44.9065 | 44.5139 | 44.2112 | 43.6021 | 42.9908 | 42.3625 | 41.7345 | 41.4165 | 41.0571 | 40.6987 | 39.6539 | 38.2068 | 36.8161 | 35.6072 | 45.6637 | 45.2729 | 44.9717 | 44.3655 | 43.7571 | 43.1318 | 42.5068 | 42.1902 | 41.8397 | 41.5031 | 40.5217 | 39.1039 | 37.6992 | 36.4766
|  | HITCHES LANE | LW |  |  | 48.3328 | 48.3328 | 48.3328 | 48.3328 | 48.2817 | 48.2075 | 48.1077 | 47.9809 | 47.7747 | 47.7443 | 47.1121 | 45.8033 | 44.3653 | 43.3479 | 44.8743 | 44.4581 | 44.1251 | 43.4513 | 42.7324 | 41.9797 | 41.6075 | 41.188 | 40.6706 | 40.2883 | 39.1502 | 37.6612 | 36.0535 | 34.8714 | 45.6316 | 45.2174 | 44.886 | 44.2154 | 43.4998 | 42.7503 | 42.3795 | 41.9614 | 41.4491 | 41.0887 | 40.0138 | 38.5592 | 36.9373 | 35.7416
|  | HITCHES LANE | ST |  |  | 48.3328 | 48.3328 | 48.3328 | 48.3328 | 48.3284 | 48.3198 | 48.3066 | 48.2872 | 48.2531 | 48.2398 | 48.1835 | 48.1214 | 47.5493 | 46.8378 | 44.9781 | 44.7962 | 44.4457 | 44.1125 | 43.6959 | 43.1858 | 42.9386 | 42.6726 | 42.4301 | 42.1899 | 41.4737 | 40.5829 | 39.6111 | 38.7926 | 45.7349 | 45.5539 | 45.205 | 44.8735 | 44.4588 | 43.9511 | 43.7051 | 43.4403 | 43.1988 | 42.9597 | 42.2467 | 41.3883 | 40.4644 | 39.6926
|  | HITCHES LANE | SP |  |  | 48.3328 | 48.3328 | 48.3328 | 48.3328 | 48.3326 | 48.3323 | 48.3317 | 48.3308 | 48.3288 | 48.321 | 48.2762 | 48.2406 | 48.0705 | 47.9046 | 45.1516 | 45.1072 | 44.9222 | 44.8864 | 44.7688 | 44.6286 | 44.5412 | 44.449 | 44.3338 | 44.2372 | 43.9347 | 43.5913 | 43.1566 | 42.7455 | 45.9075 | 45.8633 | 45.6792 | 45.6436 | 45.5266 | 45.3871 | 45.3 | 45.2083 | 45.0937 | 44.9975 | 44.6962 | 44.3543 | 43.9209 | 43.511
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD | MINIMUM HEADROOM | SU 57855 04433 | YES | 19.3246 | 19.2635 | 19.2014 | 18.464 | 18.3499 | 18.234 | 17.9995 | 17.763 | 17.518 | 17.3214 | 16.703 | 15.3409 | 13.6942 | 12.0846 | 14.8173 | 14.7473 | 14.6762 | 13.929 | 13.8074 | 13.6835 | 13.4202 | 13.1546 | 12.8807 | 12.6537 | 11.9394 | 10.3588 | 8.4727 | 6.603 | 14.8236 | 14.7538 | 14.6828 | 13.9358 | 13.8144 | 13.6907 | 13.4279 | 13.1629 | 12.8895 | 12.6632 | 11.9508 | 10.3746 | 8.4933 | 6.6289
|  | HOEFORD | CT |  |  | 19.3784 | 19.3217 | 19.2641 | 18.7998 | 18.6959 | 18.5901 | 18.4796 | 18.2527 | 18.0103 | 17.8204 | 17.2225 | 15.4183 | 13.6942 | 12.0846 | 14.8711 | 14.8055 | 14.7389 | 14.2649 | 14.1534 | 14.0397 | 13.9206 | 13.6647 | 13.3932 | 13.173 | 12.4792 | 10.4564 | 8.4727 | 6.603 | 14.8773 | 14.812 | 14.7455 | 14.2717 | 14.1603 | 14.0468 | 13.9279 | 13.6725 | 13.4017 | 13.182 | 12.4902 | 10.4718 | 8.4933 | 6.6289
|  | HOEFORD | LW |  |  | 19.3246 | 19.2635 | 19.2014 | 18.464 | 18.3499 | 18.234 | 17.9995 | 17.763 | 17.518 | 17.3214 | 16.703 | 15.3409 | 13.7686 | 12.1815 | 14.8173 | 14.7473 | 14.6762 | 13.929 | 13.8074 | 13.6835 | 13.4202 | 13.1546 | 12.8807 | 12.6537 | 11.9394 | 10.3588 | 8.5269 | 6.6796 | 14.8236 | 14.7538 | 14.6828 | 13.9358 | 13.8144 | 13.6907 | 13.4279 | 13.1629 | 12.8895 | 12.6632 | 11.9508 | 10.3746 | 8.5479 | 6.7059
|  | HOEFORD | ST |  |  | 19.413 | 19.3723 | 19.334 | 19.0303 | 18.9821 | 18.9297 | 18.8387 | 18.7466 | 18.6133 | 18.4878 | 18.0925 | 17.2016 | 16.2161 | 15.2348 | 14.9071 | 14.86 | 14.8157 | 14.5065 | 14.4536 | 14.3959 | 14.2928 | 14.1882 | 14.0352 | 13.8889 | 13.428 | 12.3865 | 11.2303 | 10.0832 | 14.9133 | 14.8663 | 14.8221 | 14.5131 | 14.4603 | 14.4027 | 14.2998 | 14.1955 | 14.0429 | 13.897 | 13.4375 | 12.399 | 11.2463 | 10.1025
|  | HOEFORD | SP |  |  | 19.4487 | 19.4233 | 19.4025 | 19.254 | 19.2328 | 19.2109 | 19.1799 | 19.1486 | 19.1135 | 19.0637 | 18.907 | 18.5412 | 18.102 | 17.6333 | 14.9443 | 14.9148 | 14.8908 | 14.74 | 14.7171 | 14.6933 | 14.6587 | 14.6239 | 14.5846 | 14.5267 | 14.3444 | 13.9175 | 13.4026 | 12.8548 | 14.9505 | 14.9211 | 14.8971 | 14.7464 | 14.7236 | 14.6998 | 14.6653 | 14.6305 | 14.5913 | 14.5335 | 14.3518 | 13.9261 | 13.4127 | 12.8665
MANNINGTON GSP | LYTCHETT | HOLES BAY | MINIMUM HEADROOM | SZ 00725 91955 | YES | 29.8065 | 29.7611 | 29.7426 | 28.7073 | 28.6173 | 28.5273 | 28.4321 | 28.3368 | 28.2416 | 28.1963 | 28.0594 | 27.818 | 27.6331 | 27.3639 | 30.4093 | 30.3924 | 30.3755 | 29.3443 | 29.2598 | 29.1753 | 29.0908 | 29.0062 | 28.9217 | 28.8879 | 28.7865 | 28.6174 | 28.516 | 28.3301 | 30.5513 | 30.48 | 30.4601 | 29.423 | 29.3326 | 29.2421 | 29.1459 | 29.0496 | 28.9534 | 28.9071 | 28.767 | 28.5191 | 28.3268 | 27.7636
|  | HOLES BAY | CT |  |  | 29.8876 | 29.849 | 29.8373 | 29.2144 | 29.1583 | 29.1021 | 29.0459 | 28.9845 | 28.923 | 28.8913 | 28.7949 | 27.9828 | 27.6384 | 27.3692 | 30.4905 | 30.4803 | 30.4702 | 29.8515 | 29.8008 | 29.75 | 29.6993 | 29.6486 | 29.5979 | 29.5776 | 29.5168 | 28.777 | 28.516 | 28.3301 | 30.6324 | 30.5679 | 30.5548 | 29.9301 | 29.8735 | 29.8168 | 29.7602 | 29.6977 | 29.6353 | 29.6026 | 29.503 | 28.6844 | 28.3325 | 27.7992
|  | HOLES BAY | LW |  |  | 29.8065 | 29.7611 | 29.7426 | 28.7073 | 28.6173 | 28.5273 | 28.4321 | 28.3368 | 28.2416 | 28.1963 | 28.0594 | 27.818 | 27.6331 | 27.3639 | 30.4093 | 30.3924 | 30.3755 | 29.3443 | 29.2598 | 29.1753 | 29.0908 | 29.0062 | 28.9217 | 28.8879 | 28.7865 | 28.6174 | 28.516 | 28.3301 | 30.5513 | 30.48 | 30.4601 | 29.423 | 29.3326 | 29.2421 | 29.1459 | 29.0496 | 28.9534 | 28.9071 | 28.767 | 28.5191 | 28.3268 | 27.7636
|  | HOLES BAY | ST |  |  | 29.9362 | 29.9212 | 29.8863 | 29.4723 | 29.3921 | 29.3093 | 29.2212 | 29.1317 | 29.0167 | 28.9702 | 28.8255 | 28.6442 | 28.3184 | 28.1238 | 30.531 | 30.5243 | 30.5175 | 30.105 | 30.0266 | 29.9474 | 29.8673 | 29.7857 | 29.6779 | 29.6393 | 29.5186 | 29.3866 | 29.1152 | 28.974 | 30.6882 | 30.6658 | 30.6052 | 30.19 | 30.1082 | 30.0249 | 29.9362 | 29.846 | 29.7302 | 29.6831 | 29.5362 | 29.3505 | 29.0198 | 28.8204
|  | HOLES BAY | SP |  |  | 29.9774 | 29.9739 | 29.9356 | 29.7292 | 29.7117 | 29.6942 | 29.6759 | 29.6576 | 29.6385 | 29.6288 | 29.5992 | 29.546 | 29.5028 | 29.4423 | 30.5716 | 30.5682 | 30.5648 | 30.3586 | 30.3417 | 30.3248 | 30.3079 | 30.291 | 30.2741 | 30.2673 | 30.247 | 30.2132 | 30.1929 | 30.1557 | 30.7301 | 30.7264 | 30.6563 | 30.4498 | 30.4318 | 30.4137 | 30.3942 | 30.3747 | 30.3544 | 30.3444 | 30.314 | 30.259 | 30.2138 | 30.1512
MELKSHAM GSP | FROME BSP | HOLWELL | MINIMUM HEADROOM | ST 72191 44633 | YES | 16.6846 | 16.6846 | 16.6846 | 16.6846 | 16.6716 | 16.6447 | 16.6024 | 16.544 | 16.4377 | 16.4206 | 16.3412 | 16.1639 | 15.8294 | 15.8083 | 15.734 | 15.734 | 15.734 | 15.734 | 15.721 | 15.6941 | 15.6518 | 15.5934 | 15.4871 | 15.47 | 15.3906 | 15.2133 | 14.8788 | 14.8577 | 15.7581 | 15.7581 | 15.7581 | 15.7581 | 15.7451 | 15.7181 | 15.6759 | 15.6174 | 15.5112 | 15.4941 | 15.4147 | 15.2346 | 14.7923 | 14.6649
|  | HOLWELL | CT |  |  | 16.6846 | 16.6846 | 16.6846 | 16.6846 | 16.6806 | 16.6732 | 16.6622 | 16.6462 | 16.6149 | 16.6098 | 16.5853 | 16.3974 | 16.1921 | 16.1362 | 15.734 | 15.734 | 15.734 | 15.734 | 15.73 | 15.7226 | 15.7116 | 15.6956 | 15.6643 | 15.6592 | 15.6347 | 15.4468 | 15.2415 | 15.1857 | 15.7581 | 15.7581 | 15.7581 | 15.7581 | 15.7541 | 15.7467 | 15.7357 | 15.7196 | 15.6884 | 15.6833 | 15.6588 | 15.4693 | 15.1697 | 15.0077
|  | HOLWELL | LW |  |  | 16.6846 | 16.6846 | 16.6846 | 16.6846 | 16.6716 | 16.6447 | 16.6024 | 16.544 | 16.4377 | 16.4206 | 16.3412 | 16.1639 | 15.8294 | 15.8083 | 15.734 | 15.734 | 15.734 | 15.734 | 15.721 | 15.6941 | 15.6518 | 15.5934 | 15.4871 | 15.47 | 15.3906 | 15.2133 | 14.8788 | 14.8577 | 15.7581 | 15.7581 | 15.7581 | 15.7581 | 15.7451 | 15.7181 | 15.6759 | 15.6174 | 15.5112 | 15.4941 | 15.4147 | 15.2346 | 14.7923 | 14.6649
|  | HOLWELL | ST |  |  | 16.6846 | 16.6846 | 16.6846 | 16.6846 | 16.6818 | 16.6764 | 16.6681 | 16.6558 | 16.6318 | 16.6213 | 16.5704 | 16.5078 | 16.2979 | 16.2287 | 15.734 | 15.734 | 15.734 | 15.734 | 15.7312 | 15.7258 | 15.7175 | 15.7052 | 15.6812 | 15.6707 | 15.6198 | 15.5572 | 15.3473 | 15.2781 | 15.7581 | 15.7581 | 15.7581 | 15.7581 | 15.7553 | 15.7499 | 15.7416 | 15.7293 | 15.7053 | 15.6948 | 15.6439 | 15.5797 | 15.3149 | 15.1763
|  | HOLWELL | SP |  |  | 16.6846 | 16.6846 | 16.6846 | 16.6846 | 16.6845 | 16.6842 | 16.6838 | 16.6832 | 16.6818 | 16.6764 | 16.6452 | 16.6204 | 16.5018 | 16.3861 | 15.734 | 15.734 | 15.734 | 15.734 | 15.7339 | 15.7337 | 15.7332 | 15.7326 | 15.7312 | 15.7258 | 15.6946 | 15.6698 | 15.5512 | 15.4355 | 15.7581 | 15.7581 | 15.7581 | 15.7581 | 15.758 | 15.7577 | 15.7573 | 15.7567 | 15.7553 | 15.7498 | 15.7186 | 15.6938 | 15.5752 | 15.4596
MANNINGTON GSP | SALISBURY | HOMINGTON | MINIMUM HEADROOM | SU 11742 26037 | YES | 16.3862 | 16.3862 | 16.3862 | 16.3862 | 16.3182 | 16.2489 | 16.1781 | 16.1046 | 15.9903 | 15.9513 | 15.8248 | 15.7206 | 15.4179 | 15.3286 | 16.6425 | 16.6421 | 16.6417 | 16.6409 | 16.5733 | 16.5035 | 16.4307 | 16.3553 | 16.2386 | 16.1969 | 16.0625 | 15.9458 | 15.6304 | 15.5286 | 16.6939 | 16.6937 | 16.6933 | 16.6927 | 16.625 | 16.5553 | 16.483 | 16.4081 | 16.292 | 16.2509 | 16.1185 | 16.0048 | 15.6925 | 15.5524
|  | HOMINGTON | CT |  |  | 16.3862 | 16.3862 | 16.3862 | 16.3862 | 16.3859 | 16.3854 | 16.3847 | 16.3836 | 16.3811 | 16.3807 | 16.3784 | 16.3592 | 16.3379 | 16.3313 | 16.6425 | 16.6421 | 16.6417 | 16.6409 | 16.6397 | 16.6384 | 16.6368 | 16.632 | 16.626 | 16.6216 | 16.6077 | 16.5696 | 16.5286 | 16.5027 | 16.6939 | 16.6937 | 16.6933 | 16.6927 | 16.6918 | 16.6906 | 16.6892 | 16.6854 | 16.6802 | 16.6768 | 16.6657 | 16.6321 | 16.4456 | 16.1969
|  | HOMINGTON | LW |  |  | 16.3862 | 16.3862 | 16.3862 | 16.3862 | 16.3853 | 16.3835 | 16.3806 | 16.3766 | 16.3685 | 16.3671 | 16.3601 | 16.3428 | 16.3092 | 16.307 | 16.6425 | 16.6421 | 16.6417 | 16.6409 | 16.6391 | 16.6364 | 16.6298 | 16.6222 | 16.6105 | 16.6052 | 16.5865 | 16.5503 | 16.4971 | 16.4756 | 16.6939 | 16.6937 | 16.6933 | 16.6927 | 16.6912 | 16.6887 | 16.683 | 16.6762 | 16.6654 | 16.661 | 16.6452 | 16.6136 | 16.381 | 16.1364
|  | HOMINGTON | ST |  |  | 16.3862 | 16.3862 | 16.3862 | 16.3862 | 16.3182 | 16.2489 | 16.1781 | 16.1046 | 15.9903 | 15.9513 | 15.8248 | 15.7206 | 15.4179 | 15.3286 | 16.6426 | 16.6424 | 16.6422 | 16.6418 | 16.5733 | 16.5035 | 16.4307 | 16.3553 | 16.2386 | 16.1969 | 16.0625 | 15.9458 | 15.6304 | 15.5286 | 16.694 | 16.6939 | 16.6937 | 16.6934 | 16.625 | 16.5553 | 16.483 | 16.4081 | 16.292 | 16.2509 | 16.1185 | 16.0048 | 15.6925 | 15.5524
|  | HOMINGTON | SP |  |  | 16.3862 | 16.3862 | 16.3862 | 16.3862 | 16.3862 | 16.3862 | 16.3861 | 16.3861 | 16.386 | 16.3857 | 16.384 | 16.3826 | 16.376 | 16.3695 | 16.6428 | 16.6428 | 16.6428 | 16.6427 | 16.6426 | 16.6424 | 16.6417 | 16.6411 | 16.6401 | 16.6388 | 16.6341 | 16.6279 | 16.6167 | 16.6059 | 16.6942 | 16.6941 | 16.6941 | 16.6941 | 16.694 | 16.6939 | 16.6933 | 16.6928 | 16.6921 | 16.691 | 16.687 | 16.682 | 16.6719 | 16.6622
BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK | MINIMUM HEADROOM | SU 72602 53780 | YES | 35.0186 | 35.0186 | 35.0186 | 35.0186 | 34.9832 | 34.941 | 34.8911 | 34.8334 | 34.7337 | 34.7182 | 34.6511 | 34.5105 | 34.0862 | 33.3756 | 33.5864 | 33.5864 | 33.5864 | 33.5864 | 33.551 | 33.5089 | 33.459 | 33.4012 | 33.3015 | 33.2861 | 32.9882 | 32.0466 | 30.9467 | 30.113 | 33.9025 | 33.8938 | 33.8825 | 33.8584 | 33.8021 | 33.7375 | 33.6777 | 33.6101 | 33.5008 | 33.4749 | 33.3769 | 32.7171 | 31.631 | 30.811
|  | HOOK | CT |  |  | 35.0186 | 35.0186 | 35.0186 | 35.0186 | 35.0169 | 35.0139 | 35.0093 | 35.0026 | 34.9879 | 34.9853 | 34.9712 | 34.8552 | 34.3554 | 33.6244 | 33.5864 | 33.5864 | 33.5864 | 33.5864 | 33.5848 | 33.5817 | 33.5772 | 33.5705 | 33.5558 | 33.5184 | 33.0518 | 32.1344 | 31.1771 | 30.3231 | 33.9025 | 33.8938 | 33.8825 | 33.8584 | 33.8333 | 33.807 | 33.7795 | 33.763 | 33.7386 | 33.7256 | 33.6807 | 32.8092 | 31.8658 | 31.0254
|  | HOOK | LW |  |  | 35.0186 | 35.0186 | 35.0186 | 35.0186 | 34.9832 | 34.941 | 34.8911 | 34.8334 | 34.7337 | 34.7182 | 34.6511 | 34.5105 | 34.0862 | 33.3756 | 33.5864 | 33.5864 | 33.5864 | 33.5864 | 33.551 | 33.5089 | 33.459 | 33.4012 | 33.3015 | 33.2861 | 32.9882 | 32.0466 | 30.9467 | 30.113 | 33.9029 | 33.8945 | 33.8835 | 33.8602 | 33.8021 | 33.7375 | 33.6777 | 33.6101 | 33.5008 | 33.4749 | 33.3769 | 32.7171 | 31.631 | 30.811
|  | HOOK | ST |  |  | 35.0186 | 35.0186 | 35.0186 | 35.0186 | 35.0174 | 35.0152 | 35.0117 | 35.0067 | 34.9953 | 34.9899 | 34.9606 | 34.9222 | 34.7874 | 34.7384 | 33.5864 | 33.5864 | 33.5864 | 33.5864 | 33.5853 | 33.583 | 33.5796 | 33.5745 | 33.5632 | 33.5577 | 33.5284 | 33.49 | 32.9098 | 32.3315 | 33.906 | 33.9 | 33.8929 | 33.8807 | 33.8646 | 33.8443 | 33.8336 | 33.8214 | 33.8034 | 33.7909 | 33.7408 | 33.6683 | 33.4995 | 33.0011
|  | HOOK | SP |  |  | 35.0186 | 35.0186 | 35.0186 | 35.0186 | 35.0185 | 35.0185 | 35.0183 | 35.0181 | 35.0176 | 35.0158 | 35.0052 | 34.9968 | 34.9566 | 34.9174 | 33.5864 | 33.5864 | 33.5864 | 33.5864 | 33.5864 | 33.5863 | 33.5862 | 33.586 | 33.5855 | 33.5837 | 33.5731 | 33.5647 | 33.5245 | 33.4853 | 33.9129 | 33.912 | 33.9111 | 33.9103 | 33.9065 | 33.9019 | 33.8992 | 33.8964 | 33.8926 | 33.888 | 33.8694 | 33.8481 | 33.7954 | 33.7445
LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR | MINIMUM HEADROOM | TQ 12710 72057 | YES | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.1676 | 13.0472 | 12.9214 | 12.791 | 12.5929 | 12.5655 | 12.4715 | 12.0459 | 10.4481 | 9.1573 | 12.5 | 12.5 | 12.5 | 12.5 | 12.3833 | 12.2628 | 12.137 | 12.0066 | 11.8086 | 11.7811 | 11.6871 | 11.0864 | 9.2601 | 7.7359 | 12.4851 | 12.4725 | 12.4561 | 12.4344 | 12.2925 | 12.1422 | 11.9631 | 11.7759 | 11.5181 | 11.4309 | 11.0885 | 9.8928 | 8.0711 | 6.5514
|  | HOPE AND ANCHOR | CT |  |  | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.0322 | 11.7889 | 10.5187 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.0761 | 10.6044 | 9.1008 | 12.4851 | 12.4725 | 12.4561 | 12.4344 | 12.4092 | 12.3794 | 12.3482 | 12.2913 | 12.2316 | 12.1718 | 11.9234 | 10.8825 | 9.4152 | 7.9162
|  | HOPE AND ANCHOR | LW |  |  | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.1676 | 13.0472 | 12.9214 | 12.791 | 12.5929 | 12.5655 | 12.4715 | 12.0459 | 10.4481 | 9.1573 | 12.5 | 12.5 | 12.5 | 12.5 | 12.3833 | 12.2628 | 12.137 | 12.0066 | 11.8086 | 11.7811 | 11.6871 | 11.0864 | 9.2601 | 7.7359 | 12.4851 | 12.4725 | 12.4561 | 12.4344 | 12.2925 | 12.1422 | 11.9631 | 11.7759 | 11.5181 | 11.4309 | 11.0885 | 9.8928 | 8.0711 | 6.5514
|  | HOPE AND ANCHOR | ST |  |  | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 12.6096 | 11.8125 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 11.5759 | 10.6323 | 12.4872 | 12.4779 | 12.4667 | 12.4531 | 12.4367 | 12.4168 | 12.3932 | 12.367 | 12.3268 | 12.2858 | 12.1098 | 11.3651 | 10.3837 | 9.4431
|  | HOPE AND ANCHOR | SP |  |  | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.2844 | 13.0969 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.1517 | 12.4892 | 12.483 | 12.4762 | 12.469 | 12.4609 | 12.4518 | 12.442 | 12.4316 | 12.4204 | 12.4042 | 12.3346 | 12.0122 | 11.5115 | 10.9588
LOVEDEAN GSP | HAVANT | HORNDEAN | MINIMUM HEADROOM | SU 70271 12802 | YES | 36.8393 | 36.8393 | 36.8393 | 36.8393 | 36.7966 | 36.7518 | 36.7043 | 36.6545 | 36.5773 | 36.5665 | 36.5047 | 35.865 | 33.629 | 31.4824 | 22.9454 | 22.8988 | 22.8325 | 22.7233 | 22.5739 | 22.419 | 22.2248 | 22.0235 | 21.7915 | 21.6152 | 21.0445 | 20.0948 | 18.1463 | 15.6582 | 26.7564 | 26.6493 | 26.4971 | 26.2462 | 25.9586 | 25.6607 | 25.2762 | 24.8786 | 24.4458 | 24.0549 | 22.6593 | 20.2178 | 17.5329 | 15.0013
|  | HORNDEAN | CT |  |  | 36.8393 | 36.8393 | 36.8393 | 36.8393 | 36.8178 | 36.7956 | 36.773 | 36.7491 | 36.7118 | 36.707 | 36.6909 | 36.2132 | 34.0672 | 31.9064 | 22.9522 | 22.9106 | 22.8508 | 22.7553 | 22.6403 | 22.5211 | 22.3988 | 22.2236 | 22.0316 | 21.8613 | 21.3135 | 20.3461 | 18.6228 | 16.1206 | 26.7721 | 26.6764 | 26.539 | 26.3196 | 26.0835 | 25.8384 | 25.587 | 25.2155 | 24.8227 | 24.4378 | 23.1058 | 20.6465 | 18.0143 | 15.4686
|  | HORNDEAN | LW |  |  | 36.8393 | 36.8393 | 36.8393 | 36.8393 | 36.7966 | 36.7518 | 36.7043 | 36.6545 | 36.5773 | 36.5665 | 36.5276 | 35.865 | 33.629 | 31.4824 | 22.9454 | 22.8988 | 22.8325 | 22.7233 | 22.5739 | 22.419 | 22.2248 | 22.0235 | 21.7915 | 21.6152 | 21.0445 | 20.0948 | 18.1463 | 15.6582 | 26.7564 | 26.6493 | 26.4971 | 26.2462 | 25.9586 | 25.6607 | 25.2762 | 24.8786 | 24.4458 | 24.0549 | 22.6593 | 20.2178 | 17.5329 | 15.0013
|  | HORNDEAN | ST |  |  | 36.8393 | 36.8393 | 36.8393 | 36.8393 | 36.8392 | 36.839 | 36.8386 | 36.838 | 36.8367 | 36.836 | 36.8327 | 36.8283 | 36.6856 | 35.4541 | 22.9656 | 22.9371 | 22.8995 | 22.8508 | 22.7936 | 22.7241 | 22.6262 | 22.5252 | 22.4186 | 22.3048 | 21.9351 | 21.3243 | 20.689 | 20.079 | 26.8028 | 26.7374 | 26.651 | 26.5391 | 26.4078 | 26.2486 | 26.0242 | 25.793 | 25.5499 | 25.2893 | 24.4446 | 22.9037 | 21.2263 | 19.5999
|  | HORNDEAN | SP |  |  | 36.8393 | 36.8393 | 36.8393 | 36.8393 | 36.8252 | 36.8114 | 36.7975 | 36.7834 | 36.7614 | 36.7 | 36.5047 | 36.4113 | 36.1157 | 35.8678 | 22.9848 | 22.9737 | 22.9597 | 22.9491 | 22.9137 | 22.875 | 22.828 | 22.7799 | 22.7158 | 22.6101 | 22.2714 | 21.9368 | 21.3825 | 20.8737 | 26.8469 | 26.8214 | 26.7891 | 26.7649 | 26.7018 | 26.6309 | 26.5409 | 26.4487 | 26.33 | 26.1669 | 25.6422 | 24.9949 | 24.1051 | 23.2579
NURSLING GSP | WINCHESTER | HOUGHTON | MINIMUM HEADROOM | SU 33784 31741 | YES | 17.5748 | 17.5698 | 17.5633 | 17.5494 | 17.4915 | 17.4202 | 17.3433 | 17.2268 | 17.0292 | 16.9755 | 16.7703 | 16.3274 | 15.5377 | 15.2145 | 15.8501 | 15.8473 | 15.8438 | 15.8362 | 15.8115 | 15.763 | 15.6901 | 15.5906 | 15.4135 | 15.3816 | 15.2411 | 14.9349 | 14.224 | 13.8501 | 15.7758 | 15.7309 | 15.6719 | 15.5471 | 15.4089 | 15.266 | 15.1182 | 15.0202 | 14.8342 | 14.742 | 14.4234 | 13.8256 | 12.962 | 12.6127
|  | HOUGHTON | CT |  |  | 17.5748 | 17.5698 | 17.5633 | 17.5494 | 17.4915 | 17.4202 | 17.3433 | 17.2812 | 17.1883 | 17.1519 | 17.0169 | 16.4821 | 15.8217 | 15.4296 | 15.8501 | 15.8473 | 15.8438 | 15.8362 | 15.8115 | 15.7811 | 15.7447 | 15.7031 | 15.6304 | 15.616 | 15.5574 | 15.1971 | 14.4804 | 14.038 | 15.7758 | 15.7309 | 15.6719 | 15.5471 | 15.4089 | 15.266 | 15.1182 | 15.0202 | 14.8916 | 14.8168 | 14.5802 | 13.9282 | 13.2317 | 12.814
|  | HOUGHTON | LW |  |  | 17.5762 | 17.5723 | 17.5671 | 17.5562 | 17.5223 | 17.4403 | 17.3467 | 17.2268 | 17.0292 | 16.9755 | 16.7703 | 16.3274 | 15.5377 | 15.2145 | 15.8509 | 15.8487 | 15.8459 | 15.8399 | 15.8128 | 15.763 | 15.6901 | 15.5906 | 15.4135 | 15.3816 | 15.2411 | 14.9349 | 14.224 | 13.8501 | 15.7887 | 15.7533 | 15.7068 | 15.6084 | 15.4916 | 15.353 | 15.2231 | 15.0673 | 14.8342 | 14.742 | 14.4234 | 13.8256 | 12.962 | 12.6127
|  | HOUGHTON | ST |  |  | 17.577 | 17.5738 | 17.57 | 17.5635 | 17.5292 | 17.487 | 17.4346 | 17.3753 | 17.2837 | 17.2368 | 17.064 | 16.8484 | 16.3117 | 16.0536 | 15.8513 | 15.8495 | 15.8474 | 15.8439 | 15.8132 | 15.777 | 15.7384 | 15.6926 | 15.6149 | 15.583 | 15.4537 | 15.3086 | 14.8545 | 14.6939 | 15.7959 | 15.7667 | 15.7324 | 15.6736 | 15.5752 | 15.4571 | 15.3805 | 15.2973 | 15.1814 | 15.1083 | 14.8592 | 14.5202 | 13.8728 | 13.52
|  | HOUGHTON | SP |  |  | 17.5808 | 17.5804 | 17.58 | 17.5796 | 17.5777 | 17.5752 | 17.573 | 17.5704 | 17.5663 | 17.5559 | 17.5018 | 17.4546 | 17.2615 | 17.0533 | 15.8533 | 15.8531 | 15.8529 | 15.8527 | 15.8516 | 15.8501 | 15.8485 | 15.8467 | 15.8434 | 15.8339 | 15.7823 | 15.7389 | 15.5496 | 15.3651 | 15.8297 | 15.8261 | 15.8226 | 15.8192 | 15.8033 | 15.7841 | 15.7693 | 15.7542 | 15.7341 | 15.7086 | 15.6107 | 15.4941 | 15.2353 | 14.9851
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS | MINIMUM HEADROOM | SU 62187 52886 | YES | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.0096 | 46.2062 | 45.6175 | 45.0845 | 46.6079 | 46.5994 | 46.5932 | 46.5812 | 46.5656 | 46.5524 | 46.5353 | 46.5155 | 46.4926 | 46.1263 | 44.702 | 43.7511 | 43.0542 | 42.4233 | 46.7042 | 46.6957 | 46.6894 | 46.6774 | 46.6617 | 46.6485 | 46.6313 | 46.6114 | 46.5885 | 46.3227 | 44.9547 | 44.0413 | 43.3719 | 42.7659
|  | HOUNDMILLS | CT |  |  | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.0721 | 46.2685 | 45.6798 | 45.147 | 46.608 | 46.5996 | 46.5935 | 46.5817 | 46.5663 | 46.5534 | 46.5394 | 46.5196 | 46.4967 | 46.2003 | 44.7761 | 43.8249 | 43.128 | 42.4973 | 46.7043 | 46.6958 | 46.6897 | 46.6779 | 46.6624 | 46.6494 | 46.6355 | 46.6156 | 46.5926 | 46.3938 | 45.0258 | 44.1121 | 43.4427 | 42.837
|  | HOUNDMILLS | LW |  |  | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.0096 | 46.2062 | 45.6175 | 45.0845 | 46.6079 | 46.5994 | 46.5932 | 46.5812 | 46.5656 | 46.5524 | 46.5353 | 46.5155 | 46.4926 | 46.1263 | 44.702 | 43.7511 | 43.0542 | 42.4233 | 46.7042 | 46.6957 | 46.6894 | 46.6774 | 46.6617 | 46.6485 | 46.6313 | 46.6114 | 46.5885 | 46.3227 | 44.9547 | 44.0413 | 43.3719 | 42.7659
|  | HOUNDMILLS | ST |  |  | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.4897 | 47.1085 | 46.7629 | 46.6083 | 46.6068 | 46.596 | 46.5884 | 46.5778 | 46.5684 | 46.5579 | 46.5456 | 46.5302 | 46.5131 | 45.9267 | 45.2704 | 44.8192 | 44.41 | 46.7046 | 46.703 | 46.6922 | 46.6846 | 46.674 | 46.6645 | 46.654 | 46.6416 | 46.6262 | 46.609 | 46.131 | 45.5006 | 45.0672 | 44.6742
|  | HOUNDMILLS | SP |  |  | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 47.8133 | 46.6094 | 46.6089 | 46.6002 | 46.5967 | 46.5918 | 46.588 | 46.5837 | 46.5788 | 46.573 | 46.5663 | 46.5438 | 46.5291 | 46.5194 | 46.5112 | 46.7057 | 46.7051 | 46.6964 | 46.6929 | 46.688 | 46.6842 | 46.6799 | 46.675 | 46.6692 | 46.6624 | 46.6398 | 46.6251 | 46.6154 | 46.6072
BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD | MINIMUM HEADROOM | SU 34066 68957 | YES | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1232 | 16.1174 | 16.1115 | 16.1056 | 16.0963 | 16.0704 | 15.9883 | 15.9492 | 15.8261 | 15.7231 | 11.7784 | 11.7768 | 11.7751 | 11.7714 | 11.7678 | 11.7641 | 11.7601 | 11.7533 | 11.7428 | 11.7158 | 11.6305 | 11.3976 | 10.9185 | 10.4467 | 12.0985 | 12.0965 | 12.0942 | 12.0893 | 12.0846 | 12.0798 | 12.0751 | 12.0438 | 11.9755 | 11.9019 | 11.6843 | 11.3238 | 10.9534 | 10.5887
|  | HUNGERFORD | CT |  |  | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 11.7784 | 11.7768 | 11.7751 | 11.7714 | 11.7678 | 11.7641 | 11.7605 | 11.7565 | 11.7526 | 11.7483 | 11.7357 | 11.3976 | 10.9185 | 10.4467 | 12.0985 | 12.0965 | 12.0942 | 12.0893 | 12.0846 | 12.0798 | 12.0751 | 12.0438 | 11.9755 | 11.9019 | 11.6843 | 11.3238 | 10.9534 | 10.5887
|  | HUNGERFORD | LW |  |  | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 11.7786 | 11.7772 | 11.7756 | 11.7723 | 11.7691 | 11.7659 | 11.7618 | 11.7578 | 11.7539 | 11.7496 | 11.737 | 11.4265 | 10.9473 | 10.4756 | 12.0988 | 12.0969 | 12.0949 | 12.0906 | 12.0864 | 12.0821 | 12.0768 | 12.066 | 11.9977 | 11.9241 | 11.7064 | 11.3461 | 10.9756 | 10.611
|  | HUNGERFORD | ST |  |  | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 11.7799 | 11.7794 | 11.779 | 11.7784 | 11.7777 | 11.7767 | 11.7741 | 11.7715 | 11.7688 | 11.7659 | 11.7574 | 11.7435 | 11.7297 | 11.4236 | 12.1004 | 12.0998 | 12.0993 | 12.0985 | 12.0975 | 12.0963 | 12.0929 | 12.0895 | 12.086 | 12.0822 | 12.0593 | 11.8193 | 11.5808 | 11.3439
|  | HUNGERFORD | SP |  |  | 16.1292 | 16.1292 | 16.1292 | 16.1292 | 16.1232 | 16.1174 | 16.1115 | 16.1056 | 16.0963 | 16.0704 | 15.9883 | 15.9492 | 15.8261 | 15.7231 | 11.7801 | 11.7799 | 11.7798 | 11.7797 | 11.7733 | 11.7669 | 11.7601 | 11.7533 | 11.7428 | 11.7158 | 11.6305 | 11.5861 | 11.458 | 11.3503 | 12.1008 | 12.1005 | 12.1003 | 12.1002 | 12.0937 | 12.0871 | 12.0801 | 12.0729 | 12.0621 | 12.0348 | 11.9484 | 11.9024 | 11.7727 | 11.6343
LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON | MINIMUM HEADROOM | SU 86949 02632 | YES | 35.9373 | 35.9037 | 35.8667 | 35.8071 | 35.7446 | 35.6765 | 35.5713 | 35.461 | 35.3281 | 35.1825 | 34.678 | 34.1195 | 33.6807 | 33.2547 | 34.4714 | 34.4268 | 34.3776 | 34.2985 | 34.2155 | 34.1253 | 33.9855 | 33.8392 | 33.6628 | 33.4696 | 32.8 | 32.0589 | 31.4765 | 30.9112 | 32.4064 | 32.3698 | 32.3295 | 32.2646 | 32.1965 | 32.1225 | 32.0078 | 31.8877 | 31.743 | 31.5845 | 31.0352 | 30.4271 | 29.9493 | 29.4856
|  | HUNSTON | CT |  |  | 35.9388 | 35.9062 | 35.8706 | 35.8139 | 35.7543 | 35.6891 | 35.6213 | 35.511 | 35.3781 | 35.2325 | 34.728 | 34.1696 | 33.7308 | 33.3052 | 34.4733 | 34.4301 | 34.3828 | 34.3076 | 34.2284 | 34.1419 | 34.0519 | 33.9055 | 33.7292 | 33.536 | 32.8664 | 32.1253 | 31.5429 | 30.9781 | 32.408 | 32.3725 | 32.3338 | 32.272 | 32.2071 | 32.1361 | 32.0622 | 31.9422 | 31.7975 | 31.639 | 31.0897 | 30.4816 | 30.0038 | 29.5405
|  | HUNSTON | LW |  |  | 35.9373 | 35.9037 | 35.8667 | 35.8071 | 35.7446 | 35.6765 | 35.5713 | 35.461 | 35.3281 | 35.1825 | 34.678 | 34.1195 | 33.6807 | 33.2547 | 34.4714 | 34.4268 | 34.3776 | 34.2985 | 34.2155 | 34.1253 | 33.9855 | 33.8392 | 33.6628 | 33.4696 | 32.8 | 32.0589 | 31.4765 | 30.9112 | 32.4064 | 32.3698 | 32.3295 | 32.2646 | 32.1965 | 32.1225 | 32.0078 | 31.8877 | 31.743 | 31.5845 | 31.0352 | 30.4271 | 29.9493 | 29.4856
|  | HUNSTON | ST |  |  | 35.9449 | 35.92 | 35.8951 | 35.8614 | 35.8197 | 35.7684 | 35.7041 | 35.6366 | 35.5468 | 35.4472 | 35.0942 | 34.7112 | 34.4277 | 34.1514 | 34.4814 | 34.4484 | 34.4154 | 34.3706 | 34.3153 | 34.2472 | 34.1618 | 34.0722 | 33.9531 | 33.8209 | 33.3525 | 32.8441 | 32.4679 | 32.1012 | 32.4146 | 32.3876 | 32.3605 | 32.3237 | 32.2784 | 32.2225 | 32.1525 | 32.0789 | 31.9812 | 31.8727 | 31.4884 | 31.0713 | 30.7627 | 30.4619
|  | HUNSTON | SP |  |  | 35.9594 | 35.9479 | 35.9387 | 35.9306 | 35.9166 | 35.9001 | 35.8765 | 35.8519 | 35.8175 | 35.7785 | 35.6397 | 35.4899 | 35.384 | 35.2844 | 34.5006 | 34.4853 | 34.4732 | 34.4625 | 34.4439 | 34.4219 | 34.3906 | 34.3579 | 34.3124 | 34.2606 | 34.0764 | 33.8775 | 33.737 | 33.6049 | 32.4304 | 32.4179 | 32.4079 | 32.3991 | 32.3838 | 32.3658 | 32.3401 | 32.3133 | 32.276 | 32.2335 | 32.0823 | 31.9192 | 31.8039 | 31.6955
BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT | MINIMUM HEADROOM | SU 39384 52476 | YES | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 7.8653 | 7.6682 | 7.4624 | 7.249 | 6.925 | 6.8801 | 6.7262 | 6.4961 | 6.1095 | 6.0024 | 6.107 | 6.107 | 6.107 | 6.107 | 5.916 | 5.719 | 5.5131 | 5.2998 | 4.9757 | 4.9309 | 4.777 | 4.4369 | 3.8482 | 3.627 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.1086 | 5.9115 | 5.7057 | 5.4923 | 5.1683 | 5.1234 | 4.9695 | 4.7394 | 4.3528 | 4.3304
|  | HURSTBOURNE TARRANT | CT |  |  | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 7.9848 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.0145 | 5.8126 | 5.6141 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995
|  | HURSTBOURNE TARRANT | LW |  |  | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 7.8653 | 7.6682 | 7.4624 | 7.249 | 6.925 | 6.8801 | 6.7262 | 6.4961 | 6.1095 | 6.0024 | 6.107 | 6.107 | 6.107 | 6.107 | 5.916 | 5.719 | 5.5131 | 5.2998 | 4.9757 | 4.9309 | 4.777 | 4.4369 | 3.8482 | 3.627 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.1086 | 5.9115 | 5.7057 | 5.4923 | 5.1683 | 5.1234 | 4.9695 | 4.7394 | 4.3528 | 4.3304
|  | HURSTBOURNE TARRANT | ST |  |  | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.107 | 6.031 | 5.9014 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2995
|  | HURSTBOURNE TARRANT | SP |  |  | 8.0562 | 8.0562 | 8.0562 | 8.0562 | 8.0472 | 8.0383 | 8.0294 | 8.0203 | 8.0062 | 7.9669 | 7.8422 | 7.7828 | 7.5958 | 7.4394 | 6.107 | 6.107 | 6.107 | 6.107 | 6.098 | 6.0891 | 6.0802 | 6.0711 | 6.057 | 6.0177 | 5.893 | 5.8336 | 5.6466 | 5.4902 | 6.2995 | 6.2995 | 6.2995 | 6.2995 | 6.2905 | 6.2816 | 6.2727 | 6.2636 | 6.2495 | 6.2102 | 6.0855 | 6.0261 | 5.8391 | 5.6827
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE | MINIMUM HEADROOM | SU 63055 50105 | YES | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 46.5721 | 46.5628 | 46.5607 | 46.5561 | 46.5517 | 46.5474 | 46.5394 | 46.5316 | 46.5238 | 46.5154 | 46.4857 | 46.3698 | 46.2291 | 46.0905 | 45.6466 | 45.49 | 45.4536 | 45.3771 | 45.3027 | 45.2286 | 45.0949 | 44.9624 | 44.8309 | 44.6893 | 44.2687 | 43.5548 | 42.804 | 42.0638
|  | JAYS CLOSE | CT |  |  | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 46.5726 | 46.5636 | 46.5619 | 46.5583 | 46.5548 | 46.5513 | 46.5478 | 46.54 | 46.5322 | 46.5238 | 46.4989 | 46.3963 | 46.2557 | 46.1171 | 45.6545 | 45.5035 | 45.4745 | 45.4135 | 45.3543 | 45.2952 | 45.2366 | 45.104 | 44.9725 | 44.8308 | 44.4102 | 43.6965 | 42.9457 | 42.2061
|  | JAYS CLOSE | LW |  |  | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 46.5721 | 46.5628 | 46.5607 | 46.5561 | 46.5517 | 46.5474 | 46.5394 | 46.5316 | 46.5238 | 46.5154 | 46.4857 | 46.3698 | 46.2291 | 46.0905 | 45.6466 | 45.49 | 45.4536 | 45.3771 | 45.3027 | 45.2286 | 45.0949 | 44.9624 | 44.8309 | 44.6893 | 44.2687 | 43.5548 | 42.804 | 42.0638
|  | JAYS CLOSE | ST |  |  | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 46.5952 | 46.571 | 46.5617 | 46.559 | 46.5556 | 46.5514 | 46.5459 | 46.5403 | 46.535 | 46.5293 | 46.5125 | 46.4747 | 46.3929 | 46.3029 | 46.0376 | 45.6281 | 45.4716 | 45.4247 | 45.3672 | 45.2977 | 45.2033 | 45.11 | 45.0202 | 44.9235 | 44.6398 | 44.163 | 43.6784 | 43.1977
|  | JAYS CLOSE | SP |  |  | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 48.6251 | 46.5968 | 46.5738 | 46.566 | 46.5658 | 46.5651 | 46.5642 | 46.5623 | 46.5605 | 46.5581 | 46.5559 | 46.5494 | 46.5386 | 46.5279 | 46.5177 | 46.0645 | 45.6753 | 45.5434 | 45.5405 | 45.528 | 45.5133 | 45.4818 | 45.4505 | 45.4103 | 45.3728 | 45.2631 | 45.081 | 44.9007 | 44.7272
COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON | MINIMUM HEADROOM | SP 52881 01094 | NO | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.1083 | 12.8298 | 12.5388 | 12.2373 | 11.7793 | 11.7158 | 11.4984 | 11.1732 | 10.5948 | 10.5536 | 9.993 | 9.9879 | 9.9812 | 9.9671 | 9.6834 | 9.3913 | 9.0959 | 8.7899 | 8.3275 | 8.2593 | 8.0279 | 7.6798 | 7.0779 | 7.0135 | 10.3492 | 10.3441 | 10.3375 | 10.3234 | 10.0398 | 9.7477 | 9.4523 | 9.1463 | 8.6839 | 8.6158 | 8.3844 | 8.0363 | 7.4345 | 7.3701
|  | KENNINGTON | CT |  |  | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.2963 | 13.213 | 13.1283 | 13.0398 | 12.9034 | 12.8862 | 12.8307 | 12.5582 | 12.2281 | 12.1522 | 9.994 | 9.9897 | 9.984 | 9.9719 | 9.8783 | 9.7833 | 9.6871 | 9.5942 | 9.4535 | 9.4314 | 9.362 | 9.0666 | 8.7129 | 8.6139 | 10.3503 | 10.346 | 10.3403 | 10.3282 | 10.2346 | 10.1397 | 10.0435 | 9.9506 | 9.8099 | 9.7879 | 9.7184 | 9.4232 | 9.0695 | 8.9706
|  | KENNINGTON | LW |  |  | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.1083 | 12.8298 | 12.5388 | 12.2373 | 11.7793 | 11.7158 | 11.4984 | 11.1732 | 10.5948 | 10.5536 | 9.993 | 9.9879 | 9.9812 | 9.9671 | 9.6834 | 9.3913 | 9.0959 | 8.7899 | 8.3275 | 8.2593 | 8.0279 | 7.6798 | 7.0779 | 7.0135 | 10.3492 | 10.3441 | 10.3375 | 10.3234 | 10.0398 | 9.7477 | 9.4523 | 9.1463 | 8.6839 | 8.6158 | 8.3844 | 8.0363 | 7.4345 | 7.3701
|  | KENNINGTON | ST |  |  | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 9.994 | 9.9898 | 9.9849 | 9.9765 | 9.9662 | 9.9538 | 9.9502 | 9.9465 | 9.9435 | 9.9403 | 9.9309 | 9.9157 | 9.9006 | 9.8855 | 10.3502 | 10.346 | 10.3412 | 10.3328 | 10.3225 | 10.3102 | 10.3065 | 10.3029 | 10.2999 | 10.2967 | 10.2874 | 10.2722 | 10.2571 | 10.2421
|  | KENNINGTON | SP |  |  | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 13.3782 | 9.9988 | 9.9983 | 9.9978 | 9.9973 | 9.995 | 9.9924 | 9.9911 | 9.9899 | 9.9884 | 9.9871 | 9.9836 | 9.9779 | 9.9726 | 9.9675 | 10.355 | 10.3545 | 10.354 | 10.3535 | 10.3512 | 10.3486 | 10.3474 | 10.3461 | 10.3446 | 10.3434 | 10.3398 | 10.3342 | 10.3289 | 10.3238
BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL | MINIMUM HEADROOM | SU 67102 74048 | YES | 16.1527 | 16.1527 | 16.1527 | 16.1527 | 16.1358 | 16.1185 | 16.1006 | 16.0819 | 16.0526 | 16.0424 | 16.0084 | 15.979 | 15.8203 | 15.4981 | 15.8015 | 15.7999 | 15.7979 | 15.7952 | 15.782 | 15.7643 | 15.7443 | 15.7234 | 15.6918 | 15.6794 | 15.6387 | 15.5593 | 15.2429 | 14.8773 | 14.9509 | 14.9152 | 14.8698 | 14.8075 | 14.7674 | 14.7308 | 14.6797 | 14.603 | 14.5237 | 14.4471 | 14.2209 | 13.8245 | 13.4103 | 13.0304
|  | KENTWOOD HILL | CT |  |  | 16.1527 | 16.1527 | 16.1527 | 16.1527 | 16.1525 | 16.1521 | 16.1515 | 16.1506 | 16.1486 | 16.1483 | 16.1464 | 16.1308 | 15.8512 | 15.5255 | 15.8015 | 15.7999 | 15.7979 | 15.7952 | 15.7932 | 15.7912 | 15.7889 | 15.7847 | 15.7795 | 15.7758 | 15.7642 | 15.5793 | 15.2729 | 14.906 | 14.9509 | 14.9152 | 14.8698 | 14.8075 | 14.7674 | 14.7308 | 14.6921 | 14.6178 | 14.543 | 14.4673 | 14.245 | 13.8467 | 13.4426 | 13.0592
|  | KENTWOOD HILL | LW |  |  | 16.1527 | 16.1527 | 16.1527 | 16.1527 | 16.152 | 16.1505 | 16.1482 | 16.1449 | 16.1384 | 16.1373 | 16.1315 | 16.1175 | 15.8203 | 15.4981 | 15.8017 | 15.8002 | 15.7983 | 15.7958 | 15.7935 | 15.7907 | 15.7852 | 15.7787 | 15.7689 | 15.7644 | 15.7489 | 15.5593 | 15.2429 | 14.8773 | 14.9538 | 14.9202 | 14.8776 | 14.8211 | 14.7861 | 14.7539 | 14.6797 | 14.603 | 14.5237 | 14.4471 | 14.2209 | 13.8245 | 13.4103 | 13.0304
|  | KENTWOOD HILL | ST |  |  | 16.1527 | 16.1527 | 16.1527 | 16.1527 | 16.1358 | 16.1185 | 16.1006 | 16.0819 | 16.0526 | 16.0424 | 16.0084 | 15.979 | 15.885 | 15.8452 | 15.8023 | 15.8014 | 15.8004 | 15.7994 | 15.782 | 15.7643 | 15.7443 | 15.7234 | 15.6918 | 15.6794 | 15.6387 | 15.5979 | 15.4515 | 15.2369 | 14.9679 | 14.9483 | 14.9255 | 14.9024 | 14.876 | 14.8507 | 14.7833 | 14.7141 | 14.6352 | 14.5735 | 14.3897 | 14.1031 | 13.7588 | 13.4823
|  | KENTWOOD HILL | SP |  |  | 16.1527 | 16.1527 | 16.1527 | 16.1527 | 16.1527 | 16.1527 | 16.1527 | 16.1527 | 16.1526 | 16.1524 | 16.151 | 16.1498 | 16.1444 | 16.1392 | 15.8025 | 15.8019 | 15.8012 | 15.8007 | 15.8005 | 15.8004 | 15.7996 | 15.7988 | 15.7977 | 15.7966 | 15.7926 | 15.787 | 15.7774 | 15.7681 | 14.9719 | 14.9584 | 14.9443 | 14.932 | 14.9279 | 14.925 | 14.9075 | 14.8895 | 14.8673 | 14.847 | 14.7874 | 14.6861 | 14.5849 | 14.4881
COWLEY GSP | YARNTON BSP | KIDDINGTON | MINIMUM HEADROOM | SP 43362 24301 | NO | 42.011 | 42.011 | 42.011 | 42.011 | 41.9814 | 41.9513 | 41.9208 | 41.8888 | 41.8396 | 41.8333 | 41.8133 | 41.7207 | 40.3426 | 38.0477 | 32.4419 | 32.4388 | 32.435 | 32.4289 | 32.3933 | 32.357 | 32.3201 | 32.2687 | 32.2002 | 32.1733 | 32.0897 | 31.0064 | 28.4747 | 25.9827 | 32.6277 | 32.6244 | 32.6203 | 32.6137 | 32.5777 | 32.541 | 32.5037 | 32.4509 | 32.381 | 32.3527 | 32.2645 | 31.6026 | 28.9575 | 26.3444
|  | KIDDINGTON | CT |  |  | 42.011 | 42.011 | 42.011 | 42.011 | 41.9814 | 41.9513 | 41.9208 | 41.8888 | 41.8396 | 41.8333 | 41.8133 | 41.7207 | 40.3426 | 38.0477 | 32.4419 | 32.4388 | 32.435 | 32.4289 | 32.3933 | 32.357 | 32.3201 | 32.2687 | 32.2002 | 32.1733 | 32.0897 | 31.0879 | 28.4902 | 25.9827 | 32.6277 | 32.6244 | 32.6203 | 32.6137 | 32.5777 | 32.541 | 32.5037 | 32.4509 | 32.381 | 32.3527 | 32.2645 | 31.6926 | 28.9815 | 26.347
|  | KIDDINGTON | LW |  |  | 42.011 | 42.011 | 42.011 | 42.011 | 41.9883 | 41.9649 | 41.9404 | 41.9151 | 41.8766 | 41.8712 | 41.853 | 41.8256 | 40.3431 | 38.0722 | 32.4421 | 32.4392 | 32.4356 | 32.4299 | 32.4016 | 32.3724 | 32.3285 | 32.2837 | 32.2259 | 32.2 | 32.118 | 31.0064 | 28.4747 | 25.9912 | 32.6279 | 32.6248 | 32.6209 | 32.6148 | 32.5862 | 32.5565 | 32.5113 | 32.4651 | 32.4059 | 32.3785 | 32.2921 | 31.6026 | 28.9575 | 26.3444
|  | KIDDINGTON | ST |  |  | 42.011 | 42.011 | 42.011 | 42.011 | 42.0025 | 41.9939 | 41.9851 | 41.976 | 41.962 | 41.9572 | 41.942 | 41.9291 | 41.8853 | 41.2923 | 32.4433 | 32.4414 | 32.4393 | 32.4367 | 32.4252 | 32.4128 | 32.3921 | 32.371 | 32.3438 | 32.3249 | 32.2664 | 32.1645 | 31.1082 | 29.5041 | 32.6291 | 32.6271 | 32.6249 | 32.6221 | 32.6104 | 32.5977 | 32.5761 | 32.5543 | 32.5261 | 32.5062 | 32.4447 | 32.3365 | 31.7063 | 30.0296
|  | KIDDINGTON | SP |  |  | 42.011 | 42.011 | 42.011 | 42.011 | 42.0081 | 42.0053 | 42.0024 | 41.9995 | 41.995 | 41.9824 | 41.9425 | 41.9235 | 41.8636 | 41.8135 | 32.4444 | 32.4436 | 32.4428 | 32.4422 | 32.4382 | 32.4341 | 32.4274 | 32.4206 | 32.4113 | 32.3932 | 32.3364 | 32.2819 | 32.1804 | 32.0878 | 32.6303 | 32.6295 | 32.6286 | 32.628 | 32.624 | 32.6197 | 32.6127 | 32.6057 | 32.596 | 32.5776 | 32.5196 | 32.4626 | 32.3582 | 32.2626
BRAMLEY (FLEE) | READING BSP | KIDMORE END | MINIMUM HEADROOM | SU 69953 78205 | YES | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.2611 | 26.134 | 26.0012 | 25.8635 | 25.6545 | 25.6255 | 25.5262 | 25.3778 | 25.1284 | 25.1139 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.2799 | 26.1528 | 26.0199 | 25.8748 | 25.6584 | 25.6215 | 25.4987 | 25.3114 | 24.8585 | 24.5682 | 26.454 | 26.3204 | 26.3087 | 26.2838 | 26.1907 | 26.0553 | 25.8781 | 25.6964 | 25.4437 | 25.3677 | 25.1031 | 24.6607 | 24.1064 | 23.792
|  | KIDMORE END | CT |  |  | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4028 | 26.3987 | 26.3947 | 26.3873 | 26.3799 | 26.372 | 26.3485 | 26.3004 | 26.0665 | 25.7778 | 26.454 | 26.3204 | 26.3087 | 26.2838 | 26.2597 | 26.2358 | 26.2121 | 26.1681 | 26.1244 | 26.0757 | 25.8986 | 25.6047 | 25.2999 | 25.0002
|  | KIDMORE END | LW |  |  | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.2611 | 26.134 | 26.0012 | 25.8635 | 25.6545 | 25.6255 | 25.5262 | 25.3778 | 25.1284 | 25.1139 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.2799 | 26.1528 | 26.0199 | 25.8748 | 25.6584 | 25.6215 | 25.4987 | 25.3114 | 24.8585 | 24.5682 | 26.4622 | 26.3346 | 26.3306 | 26.3221 | 26.1907 | 26.0553 | 25.8781 | 25.6964 | 25.4437 | 25.3677 | 25.1031 | 24.6607 | 24.1064 | 23.792
|  | KIDMORE END | ST |  |  | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.3988 | 26.3934 | 26.3776 | 26.3516 | 26.3256 | 26.2434 | 26.4637 | 26.4619 | 26.3352 | 26.3316 | 26.3271 | 26.3216 | 26.2936 | 26.2661 | 26.2363 | 26.2042 | 26.1104 | 25.9222 | 25.7256 | 25.5304
|  | KIDMORE END | SP |  |  | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.3843 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4032 | 26.4021 | 26.3922 | 26.3827 | 26.3737 | 26.4656 | 26.4653 | 26.3404 | 26.3401 | 26.3388 | 26.3373 | 26.3271 | 26.3172 | 26.3043 | 26.2919 | 26.2555 | 26.1971 | 26.1409 | 26.0876
BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE | MINIMUM HEADROOM | SU 87551 61530 | YES | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7419 | 26.0471 | 25.2119 | 24.3738 | 25.1284 | 25.1089 | 25.0834 | 25.0304 | 24.9787 | 24.8352 | 24.594 | 24.4812 | 24.368 | 24.2476 | 23.8657 | 22.999 | 21.9571 | 20.9116 | 25.7161 | 25.704 | 25.6882 | 25.6553 | 25.4984 | 25.3361 | 25.1749 | 25.0995 | 25.0239 | 24.9434 | 24.6883 | 24.1092 | 23.3381 | 22.2802
|  | KINGS RIDE | CT |  |  | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7419 | 26.0471 | 25.2119 | 24.3738 | 25.1284 | 25.1089 | 25.0834 | 25.0304 | 24.9787 | 24.8352 | 24.594 | 24.4812 | 24.368 | 24.2476 | 23.8657 | 22.999 | 21.9571 | 20.9116 | 25.7161 | 25.704 | 25.6882 | 25.6553 | 25.4984 | 25.3361 | 25.1749 | 25.0995 | 25.0239 | 24.9434 | 24.6883 | 24.1092 | 23.3381 | 22.2802
|  | KINGS RIDE | LW |  |  | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.3985 | 25.5631 | 24.7247 | 25.1361 | 25.1222 | 25.1039 | 25.0664 | 25.0296 | 24.9929 | 24.969 | 24.9194 | 24.8062 | 24.6859 | 24.3038 | 23.4373 | 22.3951 | 21.3493 | 25.7209 | 25.7123 | 25.7009 | 25.6776 | 25.6548 | 25.5429 | 25.4677 | 25.3923 | 25.3167 | 25.2363 | 24.981 | 24.4021 | 23.7058 | 22.7232
|  | KINGS RIDE | ST |  |  | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.5998 | 26.0648 | 25.1457 | 25.139 | 25.1312 | 25.1181 | 25.1022 | 25.0829 | 25.0638 | 25.0448 | 25.0284 | 25.011 | 24.9556 | 24.3734 | 23.6885 | 23.021 | 25.7269 | 25.7227 | 25.7178 | 25.7097 | 25.6998 | 25.6879 | 25.676 | 25.6642 | 25.654 | 25.5999 | 25.4256 | 25.0275 | 24.5699 | 24.1239
|  | KINGS RIDE | SP |  |  | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 26.7435 | 25.1516 | 25.1498 | 25.148 | 25.1462 | 25.1401 | 25.1329 | 25.126 | 25.1191 | 25.1104 | 25.1036 | 25.0821 | 25.0309 | 24.9665 | 24.7048 | 25.7305 | 25.7294 | 25.7283 | 25.7272 | 25.7234 | 25.7189 | 25.7146 | 25.7104 | 25.705 | 25.7007 | 25.6873 | 25.6556 | 25.4601 | 25.2489
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE | MINIMUM HEADROOM | SU 51982 59358 | YES | 34.3928 | 34.3928 | 34.3928 | 34.3928 | 34.2585 | 34.1218 | 33.9827 | 33.8372 | 33.6124 | 33.5838 | 33.4914 | 33.0158 | 32.5121 | 31.8578 | 33.3554 | 33.3554 | 33.3554 | 33.3554 | 33.2212 | 33.0845 | 32.9454 | 32.7999 | 32.3837 | 32.1728 | 31.5075 | 30.2494 | 29.0034 | 28.117 | 33.5757 | 33.5757 | 33.5757 | 33.5757 | 33.4415 | 33.3048 | 33.1657 | 33.0202 | 32.7954 | 32.7668 | 32.6744 | 32.2416 | 31.6279 | 30.7902
|  | KINGSCLERE | CT |  |  | 34.3928 | 34.3928 | 34.3928 | 34.3928 | 34.2585 | 34.1218 | 33.9827 | 33.8372 | 33.6124 | 33.5838 | 33.4914 | 33.0158 | 32.5121 | 31.8578 | 33.3554 | 33.3554 | 33.3554 | 33.3554 | 33.2212 | 33.0845 | 32.9454 | 32.7999 | 32.3837 | 32.1728 | 31.5075 | 30.2494 | 29.0034 | 28.117 | 33.5757 | 33.5757 | 33.5757 | 33.5757 | 33.4415 | 33.3048 | 33.1657 | 33.0202 | 32.7954 | 32.7668 | 32.6744 | 32.2416 | 31.6279 | 30.7902
|  | KINGSCLERE | LW |  |  | 34.3928 | 34.3928 | 34.3928 | 34.3928 | 34.3922 | 34.3909 | 34.3888 | 34.386 | 34.3803 | 34.3794 | 34.3744 | 34.3272 | 34.247 | 33.7808 | 33.3554 | 33.3554 | 33.3554 | 33.3554 | 33.3548 | 33.3535 | 33.3515 | 33.3486 | 33.2611 | 33.0777 | 32.4998 | 31.6625 | 30.84 | 30.0556 | 33.5757 | 33.5757 | 33.5757 | 33.5757 | 33.5751 | 33.5738 | 33.5718 | 33.569 | 33.5633 | 33.5623 | 33.5573 | 33.5452 | 33.4577 | 32.722
|  | KINGSCLERE | ST |  |  | 34.3928 | 34.3928 | 34.3928 | 34.3928 | 34.3927 | 34.3924 | 34.392 | 34.3914 | 34.3901 | 34.3895 | 34.386 | 34.3816 | 34.3659 | 34.3441 | 33.3554 | 33.3554 | 33.3554 | 33.3554 | 33.3553 | 33.355 | 33.3546 | 33.354 | 33.3527 | 33.3521 | 33.3487 | 32.9733 | 32.4387 | 31.928 | 33.5757 | 33.5757 | 33.5757 | 33.5757 | 33.5756 | 33.5753 | 33.5749 | 33.5744 | 33.573 | 33.5724 | 33.569 | 33.5645 | 33.5489 | 33.5432
|  | KINGSCLERE | SP |  |  | 34.3928 | 34.3928 | 34.3928 | 34.3928 | 34.3928 | 34.3928 | 34.3928 | 34.3927 | 34.3927 | 34.3925 | 34.3912 | 34.3903 | 34.3856 | 34.381 | 33.3554 | 33.3554 | 33.3554 | 33.3554 | 33.3554 | 33.3554 | 33.3554 | 33.3554 | 33.3553 | 33.3551 | 33.3539 | 33.3529 | 33.3482 | 33.3437 | 33.5757 | 33.5757 | 33.5757 | 33.5757 | 33.5757 | 33.5757 | 33.5757 | 33.5757 | 33.5756 | 33.5754 | 33.5742 | 33.5732 | 33.5685 | 33.564
BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY | MINIMUM HEADROOM | SU 37657 67143 | YES | 12.1787 | 12.1353 | 12.0785 | 11.958 | 11.8408 | 11.7242 | 11.608 | 11.5463 | 11.4821 | 11.4178 | 11.2257 | 10.875 | 10.5067 | 10.1842 | 9.0723 | 9.0723 | 9.0723 | 9.0723 | 9.0703 | 8.9407 | 8.8062 | 8.735 | 8.6613 | 8.5868 | 8.3647 | 7.9647 | 7.549 | 7.1732 | 9.1525 | 9.1525 | 9.1525 | 9.1525 | 9.1505 | 9.1463 | 9.1397 | 9.0818 | 9.013 | 8.9436 | 8.7306 | 8.3396 | 7.933 | 7.5664
|  | KINTBURY | CT |  |  | 12.1787 | 12.1353 | 12.0785 | 11.958 | 11.8408 | 11.7242 | 11.608 | 11.5463 | 11.4821 | 11.4178 | 11.2257 | 10.875 | 10.51 | 10.1842 | 9.0723 | 9.0723 | 9.0723 | 9.0723 | 9.0717 | 8.9407 | 8.8062 | 8.735 | 8.6613 | 8.5868 | 8.3647 | 7.9647 | 7.549 | 7.1732 | 9.1525 | 9.1525 | 9.1525 | 9.1525 | 9.1519 | 9.1507 | 9.1482 | 9.0818 | 9.013 | 8.9436 | 8.7306 | 8.3396 | 7.933 | 7.5664
|  | KINTBURY | LW |  |  | 12.1796 | 12.1369 | 12.0809 | 11.9623 | 11.8453 | 11.7272 | 11.6608 | 11.5926 | 11.5154 | 11.4489 | 11.2458 | 10.8998 | 10.5067 | 10.1905 | 9.0723 | 9.0723 | 9.0723 | 9.0723 | 9.0703 | 8.945 | 8.869 | 8.7912 | 8.7046 | 8.628 | 8.3948 | 7.9995 | 7.5556 | 7.1895 | 9.1525 | 9.1525 | 9.1525 | 9.1525 | 9.1505 | 9.1463 | 9.1397 | 9.1305 | 9.0512 | 8.9797 | 8.759 | 8.3725 | 7.9379 | 7.5808
|  | KINTBURY | ST |  |  | 12.1915 | 12.1587 | 12.12 | 12.0535 | 11.9716 | 11.8725 | 11.824 | 11.7753 | 11.731 | 11.6857 | 11.5488 | 11.3305 | 11.0761 | 10.8553 | 9.0723 | 9.0723 | 9.0723 | 9.0723 | 9.0719 | 9.071 | 9.0566 | 9.0005 | 8.9497 | 8.8975 | 8.7404 | 8.4894 | 8.2022 | 7.9489 | 9.1525 | 9.1525 | 9.1525 | 9.1525 | 9.1521 | 9.1512 | 9.1499 | 9.148 | 9.1437 | 9.1417 | 9.0857 | 8.8513 | 8.5705 | 8.3231
|  | KINTBURY | SP |  |  | 12.229 | 12.2246 | 12.2204 | 12.2163 | 12.1972 | 12.1742 | 12.158 | 12.1418 | 12.1208 | 12.1035 | 12.0509 | 11.9708 | 11.8822 | 11.7981 | 9.0723 | 9.0723 | 9.0723 | 9.0723 | 9.0723 | 9.0722 | 9.0722 | 9.0721 | 9.0719 | 9.0712 | 9.0672 | 9.0641 | 9.0489 | 9.0324 | 9.1525 | 9.1525 | 9.1525 | 9.1525 | 9.1525 | 9.1525 | 9.1524 | 9.1523 | 9.1522 | 9.1515 | 9.1475 | 9.1443 | 9.1291 | 9.1143
BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL | MINIMUM HEADROOM | SU 82849 79105 | YES | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2296 | 12.2128 | 12.1956 | 12.1779 | 12.1505 | 12.1412 | 12.008 | 11.7637 | 11.5053 | 11.2786 | 8.5087 | 8.4994 | 8.4983 | 8.4959 | 8.4838 | 8.4667 | 8.4481 | 8.429 | 8.4001 | 8.3893 | 8.355 | 8.2823 | 8.0135 | 7.7468 | 8.6797 | 8.6675 | 8.666 | 8.663 | 8.6509 | 8.635 | 8.616 | 8.5964 | 8.5671 | 8.5558 | 8.4565 | 8.1803 | 7.8888 | 7.6287
|  | KNOWL HILL | CT |  |  | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.237 | 12.2278 | 12.2183 | 12.2085 | 12.1889 | 12.1432 | 12.008 | 11.7637 | 11.5053 | 11.2786 | 8.5087 | 8.4994 | 8.4983 | 8.4959 | 8.4846 | 8.4731 | 8.4614 | 8.4495 | 8.4322 | 8.428 | 8.4151 | 8.2823 | 8.0135 | 7.7468 | 8.6797 | 8.6675 | 8.666 | 8.663 | 8.6509 | 8.6387 | 8.6264 | 8.6138 | 8.5959 | 8.591 | 8.4565 | 8.1803 | 7.8888 | 7.6287
|  | KNOWL HILL | LW |  |  | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.1196 | 11.9057 | 11.6838 | 11.4654 | 8.509 | 8.4999 | 8.4991 | 8.4973 | 8.4957 | 8.494 | 8.4919 | 8.4897 | 8.4876 | 8.4853 | 8.4786 | 8.4183 | 8.2013 | 7.9428 | 8.6801 | 8.6681 | 8.6671 | 8.6648 | 8.6627 | 8.6605 | 8.6577 | 8.6549 | 8.6521 | 8.6491 | 8.5757 | 8.3298 | 8.0749 | 7.8238
|  | KNOWL HILL | ST |  |  | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2296 | 12.2128 | 12.1956 | 12.1779 | 12.1505 | 12.1412 | 12.1116 | 12.0292 | 11.8091 | 11.6422 | 8.5097 | 8.5095 | 8.5009 | 8.5007 | 8.4838 | 8.4667 | 8.4481 | 8.429 | 8.4001 | 8.3893 | 8.355 | 8.3237 | 8.2392 | 8.1552 | 8.681 | 8.6808 | 8.6695 | 8.6692 | 8.6523 | 8.635 | 8.616 | 8.5964 | 8.5671 | 8.5558 | 8.5201 | 8.4865 | 8.254 | 8.0659
|  | KNOWL HILL | SP |  |  | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 12.2461 | 8.5097 | 8.5096 | 8.5011 | 8.501 | 8.5008 | 8.5004 | 8.4999 | 8.4994 | 8.4988 | 8.4982 | 8.4965 | 8.4936 | 8.4909 | 8.4883 | 8.681 | 8.6809 | 8.6697 | 8.6696 | 8.6693 | 8.6689 | 8.6682 | 8.6676 | 8.6668 | 8.666 | 8.6637 | 8.66 | 8.6564 | 8.653
BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD | MINIMUM HEADROOM | SU 86017 50475 | YES | 7.3685 | 7.3586 | 7.3454 | 7.3176 | 7.1008 | 6.8807 | 6.6574 | 6.4246 | 6.0795 | 6.01 | 5.7933 | 5.035 | 4.2351 | 3.9189 | 5.673 | 5.6725 | 5.6717 | 5.6701 | 5.4788 | 5.2839 | 5.0857 | 4.8783 | 4.5585 | 4.5164 | 4.3804 | 3.7572 | 2.9476 | 2.6013 | 4.9943 | 4.9902 | 4.9847 | 4.9733 | 4.7724 | 4.568 | 4.3604 | 4.1434 | 3.8141 | 3.7617 | 3.5954 | 2.9213 | 2.2091 | 1.9794
|  | LABURNAM ROAD | CT |  |  | 7.3685 | 7.3586 | 7.3454 | 7.3176 | 7.1008 | 6.8807 | 6.6574 | 6.4246 | 6.0795 | 6.01 | 5.7933 | 5.035 | 4.2351 | 3.9189 | 5.673 | 5.6725 | 5.6717 | 5.6701 | 5.4788 | 5.2839 | 5.0857 | 4.8783 | 4.5585 | 4.5164 | 4.3804 | 3.7572 | 2.9476 | 2.6013 | 4.9943 | 4.9902 | 4.9847 | 4.9733 | 4.7724 | 4.568 | 4.3604 | 4.1434 | 3.8141 | 3.7617 | 3.5954 | 2.9213 | 2.2091 | 1.9794
|  | LABURNAM ROAD | LW |  |  | 7.3768 | 7.3727 | 7.3674 | 7.356 | 7.3439 | 7.3308 | 7.3001 | 7.2684 | 7.2322 | 7.2016 | 7.1076 | 6.9442 | 6.7557 | 6.6059 | 5.6735 | 5.6733 | 5.673 | 5.6723 | 5.6706 | 5.6679 | 5.6629 | 5.6567 | 5.6458 | 5.6425 | 5.6293 | 5.601 | 5.4824 | 5.3025 | 4.9977 | 4.996 | 4.9938 | 4.9891 | 4.9835 | 4.9769 | 4.9622 | 4.9464 | 4.926 | 4.9124 | 4.8688 | 4.7897 | 4.689 | 4.6257
|  | LABURNAM ROAD | ST |  |  | 7.3792 | 7.3769 | 7.3742 | 7.3696 | 7.2995 | 7.227 | 7.1406 | 7.0518 | 6.9248 | 6.8679 | 6.6891 | 6.4899 | 6.0352 | 5.834 | 5.6737 | 5.6735 | 5.6734 | 5.6731 | 5.6083 | 5.5422 | 5.4737 | 5.4028 | 5.2931 | 5.2547 | 5.1304 | 5.0212 | 4.6573 | 4.5462 | 4.9987 | 4.9977 | 4.9966 | 4.9947 | 4.9279 | 4.8594 | 4.7842 | 4.7066 | 4.5903 | 4.545 | 4.4002 | 4.2571 | 3.8591 | 3.714
|  | LABURNAM ROAD | SP |  |  | 7.3816 | 7.3812 | 7.3808 | 7.3805 | 7.3789 | 7.377 | 7.3703 | 7.3635 | 7.3545 | 7.3465 | 7.3223 | 7.2845 | 7.2416 | 7.2005 | 5.6738 | 5.6738 | 5.6737 | 5.6737 | 5.6736 | 5.6735 | 5.6731 | 5.6727 | 5.6721 | 5.6713 | 5.668 | 5.6643 | 5.6545 | 5.645 | 4.9997 | 4.9995 | 4.9994 | 4.9992 | 4.9986 | 4.9978 | 4.995 | 4.9922 | 4.9884 | 4.9849 | 4.9737 | 4.9572 | 4.935 | 4.9136
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN | MINIMUM HEADROOM | SU 33280 78217 | YES | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2825 | 57.2803 | 57.2781 | 57.2759 | 57.2724 | 57.2626 | 57.2318 | 57.2171 | 57.1708 | 57.1321 | 32.5111 | 32.5086 | 32.5051 | 32.4957 | 32.4852 | 32.4809 | 32.4714 | 32.4616 | 32.4513 | 32.4403 | 32.396 | 31.7227 | 30.2829 | 28.8701 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2245 | 33.2223 | 33.2201 | 33.2179 | 33.2144 | 33.2046 | 33.1738 | 33.1161 | 31.7285 | 30.3584
|  | LAMBOURN | CT |  |  | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 32.5113 | 32.5089 | 32.5055 | 32.4964 | 32.4862 | 32.4822 | 32.4782 | 32.4684 | 32.4581 | 32.4471 | 32.4074 | 31.8649 | 30.4255 | 29.0127 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.1675 | 31.8659 | 30.4972
|  | LAMBOURN | LW |  |  | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 32.5111 | 32.5086 | 32.5051 | 32.4957 | 32.4852 | 32.4809 | 32.4714 | 32.4616 | 32.4513 | 32.4403 | 32.396 | 31.7227 | 30.2829 | 28.8701 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.1161 | 31.7285 | 30.3584
|  | LAMBOURN | ST |  |  | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 32.5118 | 32.51 | 32.5076 | 32.5018 | 32.4948 | 32.4915 | 32.4855 | 32.4793 | 32.4723 | 32.4647 | 32.4429 | 32.3831 | 31.9256 | 31.0178 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2241 | 33.171 | 32.4368
|  | LAMBOURN | SP |  |  | 57.2847 | 57.2847 | 57.2847 | 57.2847 | 57.2825 | 57.2803 | 57.2781 | 57.2759 | 57.2724 | 57.2626 | 57.2318 | 57.2171 | 57.1708 | 57.1321 | 32.5131 | 32.5123 | 32.5113 | 32.5089 | 32.5036 | 32.5005 | 32.4965 | 32.4923 | 32.4863 | 32.4736 | 32.4343 | 32.4028 | 32.3379 | 32.2807 | 33.2268 | 33.2268 | 33.2268 | 33.2268 | 33.2245 | 33.2223 | 33.2201 | 33.2179 | 33.2144 | 33.2046 | 33.1738 | 33.1591 | 33.1128 | 33.0741
FAWLEY GSP | LANGLEY BSP | LANGLEY | MINIMUM HEADROOM | SU 45158 01418 | NO | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2224 | 12.1988 | 12.1748 | 12.1499 | 12.1114 | 12.0984 | 12.0567 | 12.0233 | 11.907 | 11.7071 | 9.0083 | 9.0076 | 9.0068 | 9.0049 | 8.9838 | 8.9594 | 8.9328 | 8.9055 | 8.8644 | 8.8486 | 8.7989 | 8.454 | 7.9721 | 7.537 | 9.1183 | 9.1175 | 9.1165 | 9.1142 | 9.0936 | 9.0691 | 9.042 | 9.0141 | 8.9726 | 8.9563 | 8.9051 | 8.8561 | 8.7242 | 8.4028
|  | LANGLEY | CT |  |  | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2297 | 12.2135 | 12.197 | 12.1798 | 12.1533 | 12.15 | 12.1392 | 12.0893 | 12.038 | 11.7071 | 9.0084 | 9.0077 | 9.0069 | 9.0051 | 8.9874 | 8.9695 | 8.9513 | 8.9303 | 8.9001 | 8.8927 | 8.8699 | 8.454 | 7.9721 | 7.537 | 9.1184 | 9.1176 | 9.1166 | 9.1145 | 9.0965 | 9.0783 | 9.0598 | 9.0381 | 9.0071 | 8.999 | 8.974 | 8.9007 | 8.7731 | 8.4028
|  | LANGLEY | LW |  |  | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2191 | 11.8844 | 9.0083 | 9.0076 | 9.0068 | 9.0049 | 9.003 | 9.0012 | 8.9974 | 8.9936 | 8.9899 | 8.9858 | 8.9734 | 8.5574 | 8.1268 | 7.7031 | 9.1183 | 9.1175 | 9.1165 | 9.1142 | 9.1121 | 9.1099 | 9.1054 | 9.1009 | 9.0965 | 9.0917 | 9.0775 | 9.0541 | 8.936 | 8.5771
|  | LANGLEY | ST |  |  | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2224 | 12.1988 | 12.1748 | 12.1499 | 12.1114 | 12.0984 | 12.0567 | 12.0233 | 11.907 | 11.8722 | 9.0089 | 9.0086 | 9.0083 | 9.0077 | 8.9838 | 8.9594 | 8.9328 | 8.9055 | 8.8644 | 8.8486 | 8.7989 | 8.7523 | 8.3745 | 8.0641 | 9.119 | 9.1186 | 9.1183 | 9.1176 | 9.0936 | 9.0691 | 9.042 | 9.0141 | 8.9726 | 8.9563 | 8.9051 | 8.8561 | 8.7242 | 8.6739
|  | LANGLEY | SP |  |  | 12.2456 | 12.2456 | 12.2456 | 12.2456 | 12.2445 | 12.2434 | 12.2423 | 12.2411 | 12.2394 | 12.2345 | 12.2189 | 12.2114 | 12.1881 | 12.1685 | 9.0092 | 9.0091 | 9.0091 | 9.009 | 9.0077 | 9.0064 | 9.0044 | 9.0025 | 8.9996 | 8.9936 | 8.9749 | 8.9625 | 8.9344 | 8.9103 | 9.1193 | 9.1192 | 9.1192 | 9.1191 | 9.1178 | 9.1164 | 9.1143 | 9.1122 | 9.1092 | 9.103 | 9.0837 | 9.0704 | 9.0413 | 9.0164
BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT | MINIMUM HEADROOM | SU 80847 29056 | YES | 10.0409 | 10.0297 | 10.0149 | 9.9837 | 9.9337 | 9.8579 | 9.6892 | 9.5117 | 9.3082 | 9.0727 | 8.2385 | 7.1833 | 6.539 | 5.9135 | 5.936 | 5.9229 | 5.9056 | 5.8691 | 5.8107 | 5.722 | 5.5247 | 5.3172 | 5.0791 | 4.8037 | 3.8282 | 2.5943 | 1.8408 | 1.1093 | 7.521 | 7.5089 | 7.493 | 7.4593 | 7.4054 | 7.3235 | 7.1414 | 6.9499 | 6.7302 | 6.4761 | 5.5759 | 4.3619 | 3.6155 | 2.891
|  | LANGLEY COURT | CT |  |  | 10.0409 | 10.0297 | 10.0149 | 9.9837 | 9.9337 | 9.8579 | 9.7789 | 9.6015 | 9.398 | 9.1624 | 8.3283 | 7.273 | 6.6288 | 6.0036 | 5.936 | 5.9229 | 5.9056 | 5.8691 | 5.8107 | 5.722 | 5.6296 | 5.4222 | 5.1842 | 4.9086 | 3.9333 | 2.6992 | 1.9458 | 1.2148 | 7.521 | 7.5089 | 7.493 | 7.4593 | 7.4054 | 7.3235 | 7.2383 | 7.0468 | 6.8272 | 6.5729 | 5.6728 | 4.4658 | 3.7195 | 2.9954
|  | LANGLEY COURT | LW |  |  | 10.0409 | 10.0297 | 10.0149 | 9.9837 | 9.9337 | 9.8579 | 9.6892 | 9.5117 | 9.3082 | 9.0727 | 8.2385 | 7.1833 | 6.539 | 5.9135 | 5.936 | 5.9229 | 5.9056 | 5.8691 | 5.8107 | 5.722 | 5.5247 | 5.3172 | 5.0791 | 4.8037 | 3.8282 | 2.5943 | 1.8408 | 1.1093 | 7.521 | 7.5089 | 7.493 | 7.4593 | 7.4054 | 7.3235 | 7.1414 | 6.9499 | 6.7302 | 6.4761 | 5.5759 | 4.3619 | 3.6155 | 2.891
|  | LANGLEY COURT | ST |  |  | 10.0463 | 10.0393 | 10.0311 | 10.017 | 9.9866 | 9.9352 | 9.8436 | 9.7462 | 9.6084 | 9.4472 | 8.8624 | 8.1276 | 7.7123 | 7.3055 | 5.9424 | 5.9342 | 5.9246 | 5.908 | 5.8725 | 5.8124 | 5.7053 | 5.5914 | 5.4303 | 5.2417 | 4.5579 | 3.6986 | 3.213 | 2.7371 | 7.5268 | 7.5193 | 7.5104 | 7.4952 | 7.4624 | 7.4069 | 7.308 | 7.2029 | 7.0543 | 6.8802 | 6.2492 | 5.4557 | 4.9747 | 4.5034
|  | LANGLEY COURT | SP |  |  | 10.0538 | 10.0527 | 10.0516 | 10.0506 | 10.0389 | 10.0185 | 9.9881 | 9.9561 | 9.9129 | 9.8496 | 9.6192 | 9.3298 | 9.1788 | 9.039 | 5.9512 | 5.9498 | 5.9486 | 5.9473 | 5.9337 | 5.9098 | 5.8743 | 5.8368 | 5.7864 | 5.7123 | 5.4429 | 5.1044 | 4.9279 | 4.7644 | 7.535 | 7.5337 | 7.5326 | 7.5314 | 7.5188 | 7.4968 | 7.464 | 7.4295 | 7.3829 | 7.3145 | 7.0659 | 6.7536 | 6.5906 | 6.4398
AXMINSTER | YEOVIL BSP | LARKHILL | MINIMUM HEADROOM | ST 53677 16914 | YES | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.0721 | 26.9842 | 26.8948 | 26.8014 | 26.6574 | 26.6392 | 26.5806 | 26.3101 | 26.0313 | 25.7628 | 12.4758 | 12.4712 | 12.4653 | 12.4545 | 12.3584 | 12.2608 | 12.1617 | 12.0601 | 11.9079 | 11.8809 | 11.7966 | 11.1166 | 10.2885 | 9.6853 | 12.5979 | 12.5946 | 12.5904 | 12.5827 | 12.4894 | 12.3946 | 12.2984 | 12.1991 | 12.0493 | 12.0249 | 11.948 | 11.2541 | 10.4661 | 9.9022
|  | LARKHILL | CT |  |  | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.0721 | 26.9842 | 26.8948 | 26.8014 | 26.6574 | 26.6392 | 26.5806 | 26.3101 | 26.0313 | 25.7628 | 12.4758 | 12.4712 | 12.4653 | 12.4545 | 12.3584 | 12.2608 | 12.1617 | 12.0601 | 11.9079 | 11.8809 | 11.7966 | 11.1166 | 10.2885 | 9.6853 | 12.5979 | 12.5946 | 12.5904 | 12.5827 | 12.4894 | 12.3946 | 12.2984 | 12.1991 | 12.0493 | 12.0249 | 11.948 | 11.2541 | 10.4661 | 9.9022
|  | LARKHILL | LW |  |  | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 26.9706 | 12.4758 | 12.4713 | 12.4654 | 12.4546 | 12.4451 | 12.4355 | 12.4272 | 12.4188 | 12.4106 | 12.4019 | 12.3761 | 11.985 | 11.4354 | 10.896 | 12.5979 | 12.5947 | 12.5905 | 12.5828 | 12.576 | 12.5692 | 12.5633 | 12.5574 | 12.5516 | 12.5454 | 12.5271 | 12.121 | 11.6115 | 11.1115
|  | LARKHILL | ST |  |  | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 12.479 | 12.477 | 12.4747 | 12.4715 | 12.4684 | 12.4646 | 12.4586 | 12.4525 | 12.4469 | 12.4409 | 12.4236 | 12.395 | 12.3669 | 12.0561 | 12.6002 | 12.5987 | 12.5971 | 12.5948 | 12.5926 | 12.5899 | 12.5856 | 12.5813 | 12.5773 | 12.5731 | 12.5608 | 12.5405 | 12.5119 | 12.187
|  | LARKHILL | SP |  |  | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 27.1586 | 12.4802 | 12.4793 | 12.4784 | 12.4777 | 12.4763 | 12.4746 | 12.4725 | 12.4704 | 12.4678 | 12.4654 | 12.4587 | 12.4479 | 12.4376 | 12.4278 | 12.601 | 12.6003 | 12.5997 | 12.5992 | 12.5982 | 12.597 | 12.5955 | 12.594 | 12.5921 | 12.5905 | 12.5857 | 12.578 | 12.5707 | 12.5638
COWLEY GSP | WITNEY BSP | LEAFIELD | MINIMUM HEADROOM | SP 30282 15270 | NO | 33.5336 | 33.5184 | 33.5169 | 33.514 | 33.5111 | 33.508 | 33.4973 | 33.4865 | 33.4757 | 33.4643 | 33.4283 | 33.3508 | 33.2594 | 32.521 | 29.827 | 29.609 | 29.5869 | 29.5454 | 29.5035 | 29.4598 | 29.3054 | 29.1508 | 28.9962 | 28.8314 | 28.3155 | 27.2032 | 25.8914 | 24.5782 | 32.6856 | 32.6733 | 32.6721 | 32.6698 | 32.6674 | 32.6649 | 32.6562 | 32.6475 | 32.6388 | 32.6296 | 32.3319 | 31.3822 | 30.1876 | 28.8784
|  | LEAFIELD | CT |  |  | 33.5338 | 33.5187 | 33.5173 | 33.5147 | 33.5121 | 33.5093 | 33.5065 | 33.4958 | 33.485 | 33.4735 | 33.4376 | 33.36 | 33.2687 | 32.634 | 29.8291 | 29.6128 | 29.5926 | 29.5556 | 29.5178 | 29.4783 | 29.4384 | 29.2837 | 29.1291 | 28.9642 | 28.4484 | 27.3359 | 26.0244 | 24.7114 | 32.6857 | 32.6736 | 32.6724 | 32.6703 | 32.6682 | 32.666 | 32.6637 | 32.655 | 32.6463 | 32.637 | 32.4454 | 31.4955 | 30.3202 | 29.0112
|  | LEAFIELD | LW |  |  | 33.5336 | 33.5184 | 33.5169 | 33.514 | 33.5111 | 33.508 | 33.4973 | 33.4865 | 33.4757 | 33.4643 | 33.4283 | 33.3508 | 33.2594 | 32.521 | 29.827 | 29.609 | 29.5869 | 29.5454 | 29.5035 | 29.4598 | 29.3054 | 29.1508 | 28.9962 | 28.8314 | 28.3155 | 27.2032 | 25.8914 | 24.5782 | 32.6856 | 32.6733 | 32.6721 | 32.6698 | 32.6674 | 32.6649 | 32.6562 | 32.6475 | 32.6388 | 32.6296 | 32.3319 | 31.3822 | 30.1876 | 28.8784
|  | LEAFIELD | ST |  |  | 33.5444 | 33.5329 | 33.5178 | 33.5161 | 33.514 | 33.5115 | 33.5064 | 33.5013 | 33.494 | 33.4861 | 33.4616 | 33.4085 | 33.3486 | 33.2901 | 29.9812 | 29.8172 | 29.6004 | 29.5758 | 29.5457 | 29.5093 | 29.4365 | 29.3634 | 29.2579 | 29.1453 | 28.7937 | 28.0317 | 27.172 | 26.3322 | 32.6943 | 32.6851 | 32.6729 | 32.6715 | 32.6698 | 32.6677 | 32.6636 | 32.6595 | 32.6536 | 32.6472 | 32.6274 | 32.0896 | 31.3555 | 30.627
|  | LEAFIELD | SP |  |  | 33.5452 | 33.5449 | 33.5341 | 33.5338 | 33.5332 | 33.5325 | 33.5311 | 33.5297 | 33.528 | 33.5249 | 33.5154 | 33.494 | 33.4681 | 33.4413 | 29.9929 | 29.989 | 29.8342 | 29.8301 | 29.8215 | 29.8116 | 29.7913 | 29.771 | 29.7456 | 29.7017 | 29.5651 | 29.2589 | 28.8863 | 28.5015 | 32.695 | 32.6947 | 32.686 | 32.6858 | 32.6853 | 32.6847 | 32.6836 | 32.6825 | 32.681 | 32.6786 | 32.6709 | 32.6536 | 32.6326 | 32.4908
WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK | MINIMUM HEADROOM | TQ 20539 81536 | YES | 8.0567 | 8.0072 | 8.0046 | 7.9991 | 7.9055 | 7.7981 | 7.6864 | 7.571 | 7.3941 | 7.332 | 7.1303 | 6.833 | 6.2538 | 5.9848 | 5.4958 | 5.0193 | 4.9847 | 4.9113 | 4.8398 | 4.7679 | 4.6972 | 4.5534 | 4.343 | 4.2449 | 3.9427 | 3.6067 | 2.9891 | 2.682 | 5.4953 | 5.1353 | 5.1008 | 5.0277 | 4.9563 | 4.8846 | 4.8142 | 4.6695 | 4.4592 | 4.3613 | 4.0594 | 3.7239 | 3.1069 | 2.8003
|  | LEAMINGTON PARK | CT |  |  | 8.0567 | 8.0072 | 8.0046 | 7.9991 | 7.9937 | 7.9619 | 7.9061 | 7.8637 | 7.822 | 7.777 | 7.6442 | 7.4253 | 7.2017 | 6.9816 | 5.4958 | 5.0193 | 4.9847 | 4.9113 | 4.8398 | 4.7679 | 4.6972 | 4.6435 | 4.5907 | 4.5337 | 4.3656 | 4.0885 | 3.8053 | 3.5267 | 5.4953 | 5.1353 | 5.1008 | 5.0277 | 4.9563 | 4.8846 | 4.8142 | 4.7607 | 4.708 | 4.6512 | 4.4836 | 4.2073 | 3.925 | 3.6472
|  | LEAMINGTON PARK | LW |  |  | 8.0572 | 8.0079 | 8.0057 | 8.001 | 7.9965 | 7.9919 | 7.9561 | 7.9136 | 7.8719 | 7.8269 | 7.694 | 7.4752 | 7.2515 | 7.0315 | 5.497 | 5.0289 | 4.9994 | 4.9371 | 4.8762 | 4.8148 | 4.7605 | 4.7067 | 4.6538 | 4.5969 | 4.4286 | 4.1516 | 3.8683 | 3.5898 | 5.4957 | 5.1449 | 5.1155 | 5.0533 | 4.9926 | 4.9314 | 4.8773 | 4.8237 | 4.771 | 4.7142 | 4.5465 | 4.2703 | 3.9879 | 3.7101
|  | LEAMINGTON PARK | ST |  |  | 8.0594 | 8.059 | 8.0114 | 8.0111 | 7.9055 | 7.7981 | 7.6864 | 7.571 | 7.3941 | 7.332 | 7.1303 | 6.833 | 6.2538 | 5.9848 | 5.5031 | 5.5023 | 5.0766 | 5.0722 | 4.9614 | 4.8471 | 4.7018 | 4.5534 | 4.343 | 4.2449 | 3.9427 | 3.6067 | 2.9891 | 2.682 | 5.498 | 5.4977 | 5.1924 | 5.188 | 5.0772 | 4.963 | 4.8178 | 4.6695 | 4.4592 | 4.3613 | 4.0594 | 3.7239 | 3.1069 | 2.8003
|  | LEAMINGTON PARK | SP |  |  | 8.0595 | 8.0593 | 8.0118 | 8.0117 | 8.0113 | 8.0108 | 8.0099 | 8.009 | 8.0078 | 8.0067 | 8.0034 | 7.9982 | 7.9932 | 7.964 | 5.5034 | 5.5029 | 5.0808 | 5.0797 | 5.0743 | 5.0676 | 5.0555 | 5.0436 | 5.0284 | 5.0133 | 4.9694 | 4.8993 | 4.833 | 4.7705 | 5.4981 | 5.4979 | 5.1966 | 5.1955 | 5.1901 | 5.1835 | 5.1714 | 5.1596 | 5.1444 | 5.1293 | 5.0856 | 5.0156 | 4.9496 | 4.8873
MINETY GSP | STRATTON (2 X 60) | LECHLADE | MINIMUM HEADROOM | SP 22074 00496 | NO | 17.0493 | 17.0456 | 27.3209 | 27.312 | 27.3029 | 27.2936 | 27.2824 | 27.2509 | 27.2137 | 27.1748 | 27.04 | 26.6111 | 25.7853 | 24.9482 | 12.6495 | 12.637 | 24.7006 | 24.6698 | 24.6387 | 24.6065 | 24.5678 | 24.5283 | 24.4811 | 24.4163 | 24.1917 | 23.4904 | 22.549 | 21.5949 | 16.2392 | 16.234 | 26.5071 | 26.4942 | 26.4811 | 26.4676 | 26.4513 | 26.4347 | 26.4139 | 26.3657 | 26.1987 | 25.4729 | 24.4448 | 23.4026
|  | LECHLADE | CT |  |  | 17.0497 | 17.0465 | 27.3222 | 27.3143 | 27.3062 | 27.2978 | 27.2893 | 27.2729 | 27.2357 | 27.1968 | 27.062 | 26.6462 | 25.8202 | 24.9832 | 12.6512 | 12.6399 | 24.7051 | 24.6777 | 24.6499 | 24.6209 | 24.5916 | 24.552 | 24.5118 | 24.4529 | 24.2283 | 23.5303 | 22.5889 | 21.6348 | 16.24 | 16.2352 | 26.509 | 26.4975 | 26.4858 | 26.4736 | 26.4613 | 26.4447 | 26.4278 | 26.3929 | 26.2259 | 25.5165 | 24.4883 | 23.4462
|  | LECHLADE | LW |  |  | 17.0493 | 17.0456 | 27.3209 | 27.312 | 27.3029 | 27.2936 | 27.2824 | 27.2509 | 27.2137 | 27.1748 | 27.04 | 26.6111 | 25.7853 | 24.9482 | 12.6495 | 12.637 | 24.7006 | 24.6698 | 24.6387 | 24.6065 | 24.5678 | 24.5283 | 24.4811 | 24.4163 | 24.1917 | 23.4904 | 22.549 | 21.5949 | 16.2392 | 16.234 | 26.5071 | 26.4942 | 26.4811 | 26.4676 | 26.4513 | 26.4347 | 26.4139 | 26.3657 | 26.1987 | 25.4729 | 24.4448 | 23.4026
|  | LECHLADE | ST |  |  | 17.0503 | 17.0476 | 27.3245 | 27.3195 | 27.3135 | 27.3063 | 27.2976 | 27.2888 | 27.2809 | 27.2562 | 27.1631 | 26.8844 | 26.448 | 25.9188 | 12.653 | 12.6439 | 24.713 | 24.696 | 24.6753 | 24.6502 | 24.6203 | 24.5899 | 24.5627 | 24.5339 | 24.3968 | 23.9287 | 23.3044 | 22.7013 | 16.2407 | 16.2369 | 26.5123 | 26.5052 | 26.4965 | 26.4859 | 26.4734 | 26.4606 | 26.4492 | 26.4371 | 26.3512 | 25.9517 | 25.2698 | 24.611
|  | LECHLADE | SP |  |  | 17.0525 | 17.0517 | 27.3309 | 27.33 | 27.3282 | 27.3261 | 27.3229 | 27.3196 | 27.3156 | 27.3124 | 27.301 | 27.2305 | 27.0657 | 26.8878 | 12.6608 | 12.658 | 24.7351 | 24.7322 | 24.7259 | 24.7186 | 24.7075 | 24.6963 | 24.6825 | 24.6714 | 24.6322 | 24.5062 | 24.2345 | 23.9349 | 16.244 | 16.2428 | 26.5216 | 26.5204 | 26.5177 | 26.5147 | 26.51 | 26.5053 | 26.4995 | 26.4948 | 26.4784 | 26.4255 | 26.2306 | 25.9584
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD | MINIMUM HEADROOM | SU 43962 77635 | YES | 12.042 | 12.0196 | 11.9902 | 16.678 | 16.6114 | 16.5388 | 16.4757 | 16.4052 | 16.3067 | 16.2517 | 16.068 | 15.7242 | 15.2566 | 15.0125 | 8.4082 | 8.4064 | 8.404 | 14.67 | 14.5837 | 14.4914 | 14.4144 | 14.33 | 14.2178 | 14.1445 | 13.9039 | 13.4655 | 12.8995 | 12.5585 | 11.3673 | 11.3429 | 11.3108 | 15.2431 | 15.1652 | 15.0733 | 14.9966 | 14.9125 | 14.8005 | 14.731 | 14.5043 | 14.0891 | 13.5471 | 13.2299
|  | LECKHAMPSTEAD | CT |  |  | 12.0469 | 12.0281 | 12.0033 | 16.7008 | 16.648 | 16.594 | 16.5388 | 16.4888 | 16.4297 | 16.3815 | 16.2312 | 15.8738 | 15.4919 | 15.2178 | 8.4086 | 8.4071 | 8.4051 | 14.7002 | 14.6308 | 14.5603 | 14.4888 | 14.4249 | 14.3521 | 14.2889 | 14.0818 | 13.6297 | 13.1494 | 12.7785 | 11.3726 | 11.3521 | 11.3251 | 15.2679 | 15.2106 | 15.1419 | 15.0707 | 15.0071 | 14.9346 | 14.8718 | 14.6787 | 14.2496 | 13.7934 | 13.4462
|  | LECKHAMPSTEAD | LW |  |  | 12.042 | 12.0196 | 11.9902 | 16.678 | 16.6114 | 16.5388 | 16.4757 | 16.4052 | 16.3067 | 16.2517 | 16.068 | 15.7242 | 15.2566 | 15.0125 | 8.4082 | 8.4064 | 8.404 | 14.67 | 14.5837 | 14.4914 | 14.4144 | 14.33 | 14.2178 | 14.1445 | 13.9039 | 13.4655 | 12.8995 | 12.5585 | 11.3673 | 11.3429 | 11.3108 | 15.2431 | 15.1652 | 15.0733 | 14.9966 | 14.9125 | 14.8005 | 14.731 | 14.5043 | 14.0891 | 13.5471 | 13.2299
|  | LECKHAMPSTEAD | ST |  |  | 12.0458 | 12.0266 | 12.0041 | 16.7157 | 16.66 | 16.5933 | 16.556 | 16.517 | 16.4633 | 16.4221 | 16.285 | 16.0814 | 15.7391 | 15.5236 | 8.4085 | 8.407 | 8.4052 | 14.7021 | 14.6489 | 14.5636 | 14.5178 | 14.4704 | 14.4074 | 14.3561 | 14.1883 | 13.9217 | 13.5161 | 13.2377 | 11.3713 | 11.3505 | 11.326 | 15.2842 | 15.2243 | 15.1451 | 15.0995 | 15.0523 | 14.9894 | 14.9384 | 14.7722 | 14.521 | 14.1309 | 13.8679
|  | LECKHAMPSTEAD | SP |  |  | 12.068 | 12.0656 | 12.0633 | 16.8112 | 16.7988 | 16.7847 | 16.7733 | 16.7619 | 16.7465 | 16.7229 | 16.6454 | 16.5646 | 16.4176 | 16.2821 | 8.4103 | 8.4101 | 8.4099 | 14.7097 | 14.7067 | 14.7035 | 14.7004 | 14.6972 | 14.6923 | 14.6796 | 14.6342 | 14.5495 | 14.3846 | 14.2321 | 11.3956 | 11.393 | 11.3905 | 15.3881 | 15.3749 | 15.3596 | 15.3475 | 15.3353 | 15.3189 | 15.2942 | 15.2136 | 15.1278 | 14.9663 | 14.8141
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT | MINIMUM HEADROOM | SU 56858 00293 | YES | 9.278 | 9.2682 | 9.2553 | 9.2281 | 9.1152 | 8.9539 | 8.791 | 8.623 | 8.3689 | 8.277 | 7.972 | 7.6337 | 6.8551 | 6.5272 | 7.2669 | 7.2587 | 7.2479 | 7.2252 | 7.1064 | 6.9468 | 6.7853 | 6.6188 | 6.366 | 6.2755 | 5.9884 | 5.6994 | 4.8878 | 4.5272 | 7.3565 | 7.3204 | 7.2729 | 7.1725 | 7.0752 | 6.9668 | 6.7801 | 6.5887 | 6.3138 | 6.1995 | 5.843 | 5.4837 | 4.6841 | 4.3353
|  | LEE-ON-SOLENT | CT |  |  | 9.278 | 9.2682 | 9.2553 | 9.2281 | 9.2009 | 9.1185 | 9.0369 | 9.001 | 8.9652 | 8.9267 | 8.813 | 8.6264 | 8.4265 | 8.2245 | 7.2669 | 7.2587 | 7.2479 | 7.2252 | 7.2032 | 7.1814 | 7.0971 | 7.0515 | 7.0062 | 6.9574 | 6.8136 | 6.5773 | 6.3337 | 6.0946 | 7.3565 | 7.3204 | 7.2729 | 7.1725 | 7.0752 | 6.9788 | 6.8834 | 6.8413 | 6.7995 | 6.7544 | 6.6215 | 6.4031 | 6.1782 | 5.9572
|  | LEE-ON-SOLENT | LW |  |  | 9.2853 | 9.2807 | 9.2746 | 9.2619 | 9.2495 | 9.2373 | 9.2257 | 9.2142 | 9.2029 | 9.1662 | 9.0526 | 8.866 | 8.6737 | 8.4805 | 7.2729 | 7.2691 | 7.2641 | 7.2534 | 7.2431 | 7.2329 | 7.2232 | 7.2137 | 7.2042 | 7.194 | 7.1169 | 6.8807 | 6.6371 | 6.3977 | 7.3832 | 7.3663 | 7.3441 | 7.297 | 7.2515 | 7.2063 | 7.1637 | 7.1215 | 7.0797 | 7.0347 | 6.9017 | 6.6835 | 6.4584 | 6.2372
|  | LEE-ON-SOLENT | ST |  |  | 9.2867 | 9.2833 | 9.2792 | 9.2723 | 9.1152 | 8.9539 | 8.791 | 8.623 | 8.3689 | 8.277 | 7.972 | 7.6337 | 6.8551 | 6.5272 | 7.2741 | 7.2713 | 7.2679 | 7.2621 | 7.1064 | 6.9468 | 6.7853 | 6.6188 | 6.366 | 6.2755 | 5.9884 | 5.6994 | 4.8878 | 4.5272 | 7.3885 | 7.3759 | 7.361 | 7.3355 | 7.1556 | 6.9668 | 6.7801 | 6.5887 | 6.3138 | 6.1995 | 5.843 | 5.4837 | 4.6841 | 4.3353
|  | LEE-ON-SOLENT | SP |  |  | 9.2907 | 9.2902 | 9.2898 | 9.2894 | 9.2789 | 9.2683 | 9.2567 | 9.2451 | 9.2277 | 9.1872 | 9.0596 | 8.9884 | 8.7969 | 8.6353 | 7.2774 | 7.2771 | 7.2767 | 7.2764 | 7.2662 | 7.2559 | 7.2449 | 7.2338 | 7.217 | 7.1771 | 7.051 | 6.9823 | 6.7932 | 6.6337 | 7.4031 | 7.4015 | 7.3999 | 7.3985 | 7.3829 | 7.3663 | 7.3463 | 7.3264 | 7.2983 | 7.2492 | 7.0964 | 6.9851 | 6.7556 | 6.5579
LOVEDEAN GSP | HAVANT | LEIGH PARK | MINIMUM HEADROOM | SU 72144 07875 | YES | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.3921 | 25.9789 | 24.5652 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 23.8215 | 22.1537 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 25.7678 | 24.1427 | 22.5181
|  | LEIGH PARK | CT |  |  | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.5157 | 26.1052 | 24.6921 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 23.9705 | 22.3034 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 25.9129 | 24.2878 | 22.6639
|  | LEIGH PARK | LW |  |  | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.3921 | 25.9789 | 24.5652 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 23.8215 | 22.1537 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 25.7678 | 24.1427 | 22.5181
|  | LEIGH PARK | ST |  |  | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.6199 | 26.7224 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 24.6986 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.0352 | 24.997
|  | LEIGH PARK | SP |  |  | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 27.9147 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 25.2835 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777 | 26.9777
BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD | MINIMUM HEADROOM | SU 75372 72019 | YES | 37.2999 | 37.2985 | 37.2948 | 37.2893 | 37.2614 | 37.2327 | 37.1967 | 37.1595 | 37.1082 | 37.0919 | 37.0391 | 36.9316 | 36.7693 | 36.2162 | 36.624 | 36.624 | 36.624 | 36.624 | 36.5997 | 36.5746 | 36.5439 | 36.4878 | 36.4174 | 36.3812 | 36.2659 | 35.9973 | 34.8283 | 33.604 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5666 | 36.5415 | 36.5153 | 36.4882 | 36.4469 | 36.4412 | 36.4216 | 36.3353 | 36.0001 | 34.8114
|  | LITTLE HUNGERFORD | CT |  |  | 37.3001 | 37.2987 | 37.2951 | 37.2898 | 37.2865 | 37.283 | 37.2795 | 37.2694 | 37.2593 | 37.2488 | 37.2156 | 37.1413 | 37.0529 | 36.5796 | 36.624 | 36.624 | 36.624 | 36.624 | 36.624 | 36.624 | 36.624 | 36.6111 | 36.582 | 36.5515 | 36.4558 | 36.2414 | 35.2026 | 33.9826 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5438 | 36.3714 | 35.1871
|  | LITTLE HUNGERFORD | LW |  |  | 37.2999 | 37.2985 | 37.2948 | 37.2893 | 37.2614 | 37.2327 | 37.1967 | 37.1595 | 37.1082 | 37.0919 | 37.0391 | 36.9316 | 36.7693 | 36.2162 | 36.624 | 36.624 | 36.624 | 36.624 | 36.5997 | 36.5746 | 36.5439 | 36.4878 | 36.4174 | 36.3812 | 36.2659 | 35.9973 | 34.8283 | 33.604 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5666 | 36.5415 | 36.5153 | 36.4882 | 36.4469 | 36.4412 | 36.4216 | 36.3353 | 36.0001 | 34.8114
|  | LITTLE HUNGERFORD | ST |  |  | 37.3009 | 37.3003 | 37.2982 | 37.2957 | 37.2818 | 37.2674 | 37.2511 | 37.234 | 37.2064 | 37.1922 | 37.1471 | 37.078 | 36.9682 | 36.8968 | 36.624 | 36.624 | 36.624 | 36.624 | 36.6115 | 36.5988 | 36.5858 | 36.5724 | 36.5517 | 36.5377 | 36.4499 | 36.2845 | 36.0654 | 35.4353 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5784 | 36.5658 | 36.5528 | 36.5394 | 36.5187 | 36.5117 | 36.4892 | 36.4709 | 36.3711 | 36.3093
|  | LITTLE HUNGERFORD | SP |  |  | 37.3012 | 37.3009 | 37.2998 | 37.2986 | 37.2948 | 37.291 | 37.2867 | 37.2824 | 37.276 | 37.2597 | 37.2082 | 37.1672 | 37.0776 | 36.9975 | 36.624 | 36.624 | 36.624 | 36.624 | 36.6209 | 36.6179 | 36.6148 | 36.6117 | 36.6069 | 36.5934 | 36.5507 | 36.4926 | 36.3547 | 36.2245 | 36.5909 | 36.5909 | 36.5909 | 36.5909 | 36.5878 | 36.5848 | 36.5818 | 36.5787 | 36.5738 | 36.5604 | 36.5177 | 36.4973 | 36.4333 | 36.3798
COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW | MINIMUM HEADROOM | SU 86037 87794 | YES | 64.714 | 64.714 | 64.7069 | 64.6495 | 64.5934 | 64.5055 | 64.415 | 64.3221 | 64.1916 | 64.1354 | 63.9579 | 63.4264 | 61.7486 | 60.1095 | 50.8989 | 50.8855 | 50.8683 | 50.8319 | 50.7837 | 50.6903 | 50.3673 | 50.0327 | 49.6975 | 49.3392 | 48.271 | 46.4028 | 44.4213 | 42.4824 | 50.8562 | 50.8562 | 50.8562 | 50.8562 | 50.7881 | 50.7188 | 50.6477 | 50.5717 | 50.2841 | 49.9399 | 48.9138 | 47.1185 | 45.2142 | 43.3516
|  | LITTLE MARLOW | CT |  |  | 64.714 | 64.714 | 64.7069 | 64.6495 | 64.5934 | 64.5375 | 64.4819 | 64.4572 | 64.4313 | 64.4058 | 64.3289 | 63.4264 | 61.7486 | 60.1095 | 50.8989 | 50.8855 | 50.8683 | 50.8319 | 50.7963 | 50.7606 | 50.3673 | 50.0327 | 49.6975 | 49.3392 | 48.271 | 46.4028 | 44.4213 | 42.4824 | 50.8562 | 50.8562 | 50.8562 | 50.8562 | 50.845 | 50.7997 | 50.7546 | 50.6061 | 50.2841 | 49.9399 | 48.9138 | 47.1185 | 45.2142 | 43.3516
|  | LITTLE MARLOW | LW |  |  | 64.714 | 64.714 | 64.7092 | 64.6535 | 64.5985 | 64.5427 | 64.5158 | 64.4878 | 64.4554 | 64.4289 | 64.3465 | 63.8752 | 62.1831 | 60.5481 | 50.8995 | 50.8865 | 50.8698 | 50.8345 | 50.7992 | 50.7631 | 50.7448 | 50.5714 | 50.2363 | 49.8771 | 48.8031 | 46.9375 | 44.9416 | 43.0067 | 50.8562 | 50.8562 | 50.8562 | 50.8562 | 50.849 | 50.8035 | 50.7811 | 50.7576 | 50.7296 | 50.456 | 49.4241 | 47.6313 | 45.7127 | 43.854
|  | LITTLE MARLOW | ST |  |  | 64.714 | 64.714 | 64.714 | 64.7123 | 64.6128 | 64.5055 | 64.415 | 64.3221 | 64.1916 | 64.1354 | 63.9579 | 63.7666 | 63.3722 | 63.0017 | 50.9203 | 50.8974 | 50.8879 | 50.8717 | 50.7837 | 50.6903 | 50.607 | 50.5211 | 50.3965 | 50.3465 | 50.1874 | 49.0036 | 47.432 | 46.0901 | 50.8562 | 50.8562 | 50.8562 | 50.8562 | 50.7881 | 50.7188 | 50.6477 | 50.5717 | 50.4443 | 50.3913 | 50.2234 | 49.5915 | 48.0698 | 46.7773
|  | LITTLE MARLOW | SP |  |  | 64.714 | 64.714 | 64.714 | 64.714 | 64.714 | 64.714 | 64.714 | 64.7139 | 64.7138 | 64.7135 | 64.7023 | 64.6675 | 64.6264 | 64.5865 | 50.9203 | 50.9177 | 50.9116 | 50.9103 | 50.9045 | 50.8976 | 50.8933 | 50.8889 | 50.8833 | 50.8788 | 50.8645 | 50.8418 | 50.813 | 50.785 | 50.8562 | 50.8562 | 50.8562 | 50.8562 | 50.8562 | 50.8561 | 50.8561 | 50.8561 | 50.856 | 50.8556 | 50.8536 | 50.8521 | 50.8445 | 50.8358
NURSLING GSP | ROWNHAMS | LORDSHILL | MINIMUM HEADROOM | SU 38746 16055 | YES | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.2784 | 35.2632 | 35.3001 | 35.2891 | 35.2746 | 35.244 | 35.2143 | 35.1849 | 35.1557 | 35.1399 | 35.1242 | 35.1072 | 34.8883 | 33.7963 | 32.6218 | 31.4604 | 35.5616 | 35.5538 | 35.5435 | 35.5218 | 35.5007 | 35.4798 | 35.4591 | 35.4479 | 35.4367 | 35.4247 | 35.3887 | 34.9786 | 33.7849 | 32.6032
|  | LORDSHILL | CT |  |  | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.2784 | 35.2632 | 35.3001 | 35.2891 | 35.2746 | 35.244 | 35.2143 | 35.1849 | 35.1557 | 35.1399 | 35.1242 | 35.1072 | 34.8883 | 33.7963 | 32.6218 | 31.4604 | 35.5616 | 35.5538 | 35.5435 | 35.5218 | 35.5007 | 35.4798 | 35.4591 | 35.4479 | 35.4367 | 35.4247 | 35.3887 | 34.9786 | 33.7849 | 32.6032
|  | LORDSHILL | LW |  |  | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 35.6579 | 35.3029 | 35.2939 | 35.2821 | 35.2571 | 35.2328 | 35.2088 | 35.1928 | 35.177 | 35.1613 | 35.1443 | 35.0937 | 34.2485 | 33.0738 | 31.912 | 35.5636 | 35.5572 | 35.5488 | 35.5311 | 35.5138 | 35.4968 | 35.4854 | 35.4742 | 35.463 | 35.451 | 35.4151 | 35.3514 | 34.2448 | 33.0626
|  | LORDSHILL | ST |  |  | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 35.3106 | 35.3073 | 35.3033 | 35.2966 | 35.2884 | 35.2784 | 35.2661 | 35.2539 | 35.2431 | 35.2316 | 35.1974 | 35.1373 | 35.0749 | 34.359 | 35.5691 | 35.5667 | 35.5639 | 35.5591 | 35.5533 | 35.5462 | 35.5374 | 35.5288 | 35.5211 | 35.5129 | 35.4887 | 35.446 | 35.4017 | 35.3579
|  | LORDSHILL | SP |  |  | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 36.4997 | 35.3137 | 35.3129 | 35.3121 | 35.3113 | 35.3079 | 35.304 | 35.2996 | 35.2953 | 35.2897 | 35.2853 | 35.2721 | 35.2489 | 35.2248 | 35.2014 | 35.5712 | 35.5707 | 35.5701 | 35.5695 | 35.5672 | 35.5643 | 35.5612 | 35.5582 | 35.5542 | 35.5511 | 35.5417 | 35.5252 | 35.5082 | 35.4915
BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE | MINIMUM HEADROOM | SU 47334 68495 | YES | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.2363 | 34.1251 | 34.0088 | 33.8884 | 33.7055 | 33.6802 | 33.5933 | 32.79 | 31.2447 | 29.9995 | 32.9154 | 32.9139 | 32.912 | 32.9083 | 32.7974 | 32.6824 | 32.5597 | 32.4327 | 32.2432 | 32.2109 | 32.1015 | 31.0584 | 29.4332 | 27.9741 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.8048 | 32.6935 | 32.5773 | 32.4569 | 32.274 | 32.2486 | 32.1618 | 31.0442 | 29.3748 | 27.9087
|  | LOVE LANE | CT |  |  | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 33.7058 | 32.4879 | 31.2621 | 32.9154 | 32.9139 | 32.912 | 32.9083 | 32.9046 | 32.9008 | 32.897 | 32.8904 | 32.8838 | 32.8769 | 32.8543 | 31.9766 | 30.6787 | 29.243 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 31.963 | 30.6244 | 29.1777
|  | LOVE LANE | LW |  |  | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.2363 | 34.1251 | 34.0088 | 33.8884 | 33.7055 | 33.6802 | 33.5933 | 32.79 | 31.2447 | 29.9995 | 32.9155 | 32.9141 | 32.9122 | 32.9087 | 32.7974 | 32.6824 | 32.5597 | 32.4327 | 32.2432 | 32.2109 | 32.1015 | 31.0584 | 29.4332 | 27.9741 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.8048 | 32.6935 | 32.5773 | 32.4569 | 32.274 | 32.2486 | 32.1618 | 31.0442 | 29.3748 | 27.9087
|  | LOVE LANE | ST |  |  | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3155 | 33.5124 | 32.7321 | 32.9154 | 32.914 | 32.9124 | 32.9098 | 32.9066 | 32.9026 | 32.8995 | 32.8963 | 32.8918 | 32.887 | 32.8715 | 32.6263 | 31.7705 | 30.939 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.6242 | 31.7533 | 30.9072
|  | LOVE LANE | SP |  |  | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 34.3441 | 32.9168 | 32.9165 | 32.9161 | 32.9158 | 32.9149 | 32.9138 | 32.9128 | 32.9117 | 32.9104 | 32.9086 | 32.9025 | 32.8868 | 32.8662 | 32.841 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.8427
COWLEY GSP | YARNTON BSP | LOVELACE ROAD | MINIMUM HEADROOM | SP 50395 10376 | NO | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8221 | 36.8094 | 36.7974 | 36.7871 | 36.7765 | 36.7452 | 36.3037 | 35.3052 | 34.3357 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.21 | 37.1609 | 36.5071 | 35.4486 | 34.4753 | 33.5312
|  | LOVELACE ROAD | CT |  |  | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8234 | 36.8094 | 36.7974 | 36.7871 | 36.7765 | 36.7452 | 36.3037 | 35.3052 | 34.3357 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.21 | 37.1609 | 36.5071 | 35.4486 | 34.4753 | 33.5312
|  | LOVELACE ROAD | LW |  |  | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8221 | 36.8111 | 36.799 | 36.7887 | 36.7781 | 36.7468 | 36.337 | 35.3402 | 34.3701 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2121 | 37.1951 | 36.5412 | 35.4828 | 34.5093 | 33.5647
|  | LOVELACE ROAD | ST |  |  | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8295 | 36.8225 | 36.8153 | 36.794 | 36.7599 | 36.7299 | 36.4251 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2188 | 36.8144 | 36.1866 | 35.5732
|  | LOVELACE ROAD | SP |  |  | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 48.8439 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8347 | 36.8281 | 36.8178 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197 | 37.2197
MANNINGTON GSP | ARNEWOOD | LYMINGTON | MINIMUM HEADROOM | SZ 31720 96856 | YES | 24.7588 | 24.7528 | 24.7445 | 24.7275 | 24.7088 | 24.6914 | 24.5986 | 24.5359 | 24.4664 | 24.38 | 24.0626 | 23.5475 | 22.9692 | 22.3978 | 24.1682 | 24.1634 | 24.1566 | 24.143 | 23.9971 | 23.7512 | 23.531 | 23.452 | 23.371 | 23.2702 | 22.9 | 22.2993 | 21.6248 | 20.9584 | 24.2549 | 24.2498 | 24.2425 | 24.2279 | 24.2117 | 24.0668 | 23.8603 | 23.7862 | 23.7103 | 23.6158 | 23.2686 | 22.7053 | 22.0276 | 21.3533
|  | LYMINGTON | CT |  |  | 24.7588 | 24.7528 | 24.7445 | 24.7275 | 24.7088 | 24.6914 | 24.5986 | 24.5359 | 24.4664 | 24.38 | 24.0626 | 23.5475 | 22.9692 | 22.3978 | 24.1682 | 24.1634 | 24.1566 | 24.143 | 23.9971 | 23.7512 | 23.531 | 23.452 | 23.371 | 23.2702 | 22.9 | 22.2993 | 21.6248 | 20.9584 | 24.2549 | 24.2498 | 24.2425 | 24.2279 | 24.2117 | 24.0668 | 23.8603 | 23.7862 | 23.7103 | 23.6158 | 23.2686 | 22.7053 | 22.0276 | 21.3533
|  | LYMINGTON | LW |  |  | 24.7618 | 24.758 | 24.7525 | 24.7415 | 24.7286 | 24.717 | 24.7112 | 24.7057 | 24.6999 | 24.6928 | 24.4925 | 23.9774 | 23.3991 | 22.8273 | 24.1706 | 24.1675 | 24.1631 | 24.1542 | 24.1438 | 24.113 | 24.0324 | 23.9535 | 23.8724 | 23.7718 | 23.4014 | 22.8007 | 22.1261 | 21.4594 | 24.2575 | 24.2542 | 24.2495 | 24.24 | 24.2288 | 24.2188 | 24.2139 | 24.2091 | 24.1805 | 24.0861 | 23.7388 | 23.1755 | 22.5349 | 21.8602
|  | LYMINGTON | ST |  |  | 24.7645 | 24.7628 | 24.7603 | 24.7563 | 24.7502 | 24.7441 | 24.7393 | 24.7346 | 24.7307 | 24.7259 | 24.7077 | 24.6243 | 24.2546 | 23.8894 | 24.1728 | 24.1714 | 24.1694 | 24.1662 | 24.1612 | 24.1563 | 24.1525 | 24.1487 | 24.1456 | 24.1416 | 23.9817 | 23.5672 | 23.1239 | 22.698 | 24.2598 | 24.2583 | 24.2562 | 24.2528 | 24.2475 | 24.2422 | 24.2381 | 24.2341 | 24.2307 | 24.2265 | 24.2108 | 23.8942 | 23.4786 | 23.0792
|  | LYMINGTON | SP |  |  | 24.7662 | 24.7657 | 24.765 | 24.7642 | 24.7608 | 24.7578 | 24.755 | 24.7521 | 24.7483 | 24.7422 | 24.7219 | 24.7038 | 24.6703 | 24.6398 | 24.1741 | 24.1737 | 24.1732 | 24.1725 | 24.1696 | 24.167 | 24.1645 | 24.1621 | 24.1587 | 24.153 | 24.1341 | 24.1183 | 24.0875 | 23.876 | 24.2613 | 24.2609 | 24.2603 | 24.2595 | 24.2565 | 24.2538 | 24.2512 | 24.2486 | 24.2451 | 24.2393 | 24.22 | 24.2035 | 24.1719 | 24.1433
MELKSHAM GSP | CHIPPENHAM | LYNEHAM | MINIMUM HEADROOM | ST 99348 80481 | YES | 37.4551 | 37.4146 | 37.3659 | 36.3752 | 36.2149 | 36.0495 | 35.7721 | 35.468 | 35.1943 | 34.9541 | 34.2053 | 32.9875 | 31.8008 | 30.5622 | 29.7935 | 29.7525 | 29.7033 | 28.7112 | 28.5494 | 28.3823 | 28.1014 | 27.8164 | 27.5593 | 27.3373 | 26.6921 | 25.6423 | 24.628 | 23.5583 | 34.7519 | 34.7091 | 34.6575 | 33.6599 | 33.481 | 33.2865 | 32.9442 | 32.5966 | 32.2853 | 32.0061 | 31.1955 | 29.8777 | 28.5881 | 27.249
|  | LYNEHAM | CT |  |  | 37.521 | 37.482 | 37.4336 | 36.7963 | 36.6541 | 36.5068 | 36.3497 | 36.08 | 35.8362 | 35.6085 | 34.899 | 33.175 | 31.847 | 30.6089 | 29.8593 | 29.8198 | 29.7707 | 29.1318 | 28.9879 | 28.8388 | 28.6797 | 28.4248 | 28.1977 | 27.9875 | 27.3785 | 25.8225 | 24.667 | 23.5977 | 34.8173 | 34.7756 | 34.7237 | 34.0785 | 33.9072 | 33.7271 | 33.5341 | 33.2166 | 32.9352 | 32.6679 | 31.8936 | 30.0695 | 28.6387 | 27.3
|  | LYNEHAM | LW |  |  | 37.4551 | 37.4146 | 37.3659 | 36.3752 | 36.2149 | 36.0495 | 35.7721 | 35.468 | 35.1943 | 34.9541 | 34.2053 | 32.9875 | 31.8008 | 30.5622 | 29.7935 | 29.7525 | 29.7033 | 28.7112 | 28.5494 | 28.3823 | 28.1014 | 27.8164 | 27.5593 | 27.3373 | 26.6921 | 25.6423 | 24.628 | 23.5583 | 34.7519 | 34.7091 | 34.6575 | 33.6599 | 33.481 | 33.2865 | 32.9442 | 32.5966 | 32.2853 | 32.0061 | 31.1955 | 29.8777 | 28.5881 | 27.249
|  | LYNEHAM | ST |  |  | 37.572 | 37.5477 | 37.52 | 37.1136 | 37.0272 | 36.9276 | 36.7689 | 36.6079 | 36.4485 | 36.2935 | 35.8488 | 35.0782 | 34.3361 | 33.572 | 29.9106 | 29.8859 | 29.8578 | 29.4507 | 29.3633 | 29.2625 | 29.1015 | 28.9382 | 28.7838 | 28.6408 | 28.2302 | 27.571 | 26.94 | 26.2857 | 34.8697 | 34.8437 | 34.814 | 34.404 | 34.3126 | 34.2011 | 34.0011 | 33.7981 | 33.6067 | 33.4247 | 32.9025 | 32.0649 | 31.2566 | 30.427
|  | LYNEHAM | SP |  |  | 37.6286 | 37.623 | 37.6175 | 37.4301 | 37.3982 | 37.363 | 37.3025 | 37.2417 | 37.1773 | 37.1214 | 36.9614 | 36.7019 | 36.4485 | 36.1949 | 29.9675 | 29.9618 | 29.9563 | 29.7688 | 29.7367 | 29.7011 | 29.6398 | 29.5781 | 29.5129 | 29.4561 | 29.2936 | 29.0366 | 28.8029 | 28.5678 | 34.928 | 34.9222 | 34.9164 | 34.7286 | 34.6953 | 34.6583 | 34.5937 | 34.5288 | 34.4601 | 34.3917 | 34.1862 | 33.8616 | 33.5636 | 33.2683
BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E | MINIMUM HEADROOM | SU 98120 65945 | YES | 18.165 | 18.1397 | 25.2866 | 25.2164 | 25.1428 | 25.0649 | 24.9826 | 24.8507 | 24.6229 | 24.5154 | 24.1571 | 23.5027 | 22.6117 | 22.173 | 13.2909 | 13.2635 | 23.8048 | 23.7221 | 23.6362 | 23.5462 | 23.4519 | 23.3264 | 23.0848 | 22.9622 | 22.5598 | 21.833 | 20.8673 | 20.3552 | 16.3593 | 16.3409 | 22.2968 | 22.2457 | 22.1906 | 22.131 | 22.0648 | 21.9252 | 21.7185 | 21.6336 | 21.3422 | 20.7974 | 20.0194 | 19.6918
|  | M V E E | CT |  |  | 18.165 | 18.1397 | 25.2866 | 25.2164 | 25.1428 | 25.0649 | 24.9826 | 24.882 | 24.7605 | 24.67 | 24.3896 | 23.7201 | 23.0129 | 22.5235 | 13.2909 | 13.2635 | 23.8048 | 23.7221 | 23.6362 | 23.5462 | 23.4519 | 23.3373 | 23.2019 | 23.0965 | 22.7718 | 22.0299 | 21.2481 | 20.6854 | 16.3593 | 16.3409 | 22.2968 | 22.2457 | 22.1906 | 22.131 | 22.0668 | 21.9874 | 21.8869 | 21.8191 | 21.6055 | 21.0457 | 20.4515 | 20.0731
|  | M V E E | LW |  |  | 18.1797 | 18.1651 | 25.3259 | 25.2852 | 25.2273 | 25.15 | 25.0115 | 24.8507 | 24.6229 | 24.5154 | 24.1571 | 23.5027 | 22.6117 | 22.173 | 13.2919 | 13.2909 | 23.8507 | 23.8032 | 23.7382 | 23.6539 | 23.5012 | 23.3264 | 23.0848 | 22.9622 | 22.5598 | 21.833 | 20.8673 | 20.3552 | 16.37 | 16.3593 | 22.3254 | 22.2958 | 22.2486 | 22.1819 | 22.0648 | 21.9252 | 21.7185 | 21.6336 | 21.3422 | 20.7974 | 20.0194 | 19.6918
|  | M V E E | ST |  |  | 18.1937 | 18.1894 | 25.3643 | 25.3556 | 25.3409 | 25.3202 | 25.2668 | 25.2083 | 25.1215 | 25.0499 | 24.8122 | 24.4556 | 23.889 | 23.5225 | 13.2928 | 13.2925 | 23.8722 | 23.8716 | 23.867 | 23.8459 | 23.7857 | 23.7198 | 23.6235 | 23.5417 | 23.2742 | 22.8696 | 22.2549 | 21.8406 | 16.3802 | 16.377 | 22.3533 | 22.347 | 22.3352 | 22.318 | 22.276 | 22.2287 | 22.1562 | 22.1 | 21.9074 | 21.6237 | 21.1298 | 20.8357
|  | M V E E | SP |  |  | 18.1981 | 18.1973 | 25.3765 | 25.3757 | 25.359 | 25.3417 | 25.3141 | 25.286 | 25.2455 | 25.1595 | 24.8731 | 24.6522 | 24.1238 | 23.6491 | 13.2931 | 13.2931 | 23.873 | 23.8729 | 23.8595 | 23.8461 | 23.8317 | 23.8131 | 23.7696 | 23.6799 | 23.3822 | 23.143 | 22.5973 | 22.1063 | 16.3834 | 16.3828 | 22.3622 | 22.3616 | 22.3458 | 22.3297 | 22.3059 | 22.2817 | 22.2462 | 22.1661 | 21.8971 | 21.7038 | 21.2017 | 20.7517
CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON | MINIMUM HEADROOM | SY 59138 97747 | YES | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 29.8904 | 29.7649 | 29.6374 | 29.5043 | 29.2989 | 29.2729 | 29.1894 | 28.8013 | 28.3777 | 28.2682 | 29.9394 | 29.8942 | 29.8559 | 29.7955 | 29.6041 | 29.404 | 29.1994 | 28.9888 | 28.7112 | 28.6405 | 28.4465 | 27.8998 | 27.3415 | 27.1091 | 29.9349 | 29.8864 | 29.8452 | 29.7804 | 29.584 | 29.3784 | 29.1681 | 28.9517 | 28.6688 | 28.5949 | 28.3927 | 27.8343 | 27.266 | 27.0246
|  | MAIDEN NEWTON | CT |  |  | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 29.8904 | 29.7649 | 29.6374 | 29.5043 | 29.2989 | 29.2729 | 29.1894 | 28.8013 | 28.3777 | 28.2682 | 29.9394 | 29.8942 | 29.8559 | 29.7955 | 29.6041 | 29.404 | 29.1994 | 28.9888 | 28.7112 | 28.6405 | 28.4465 | 27.8998 | 27.3415 | 27.1091 | 29.9349 | 29.8864 | 29.8452 | 29.7804 | 29.584 | 29.3784 | 29.1681 | 28.9517 | 28.6688 | 28.5949 | 28.3927 | 27.8343 | 27.266 | 27.0246
|  | MAIDEN NEWTON | LW |  |  | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 29.9429 | 29.8698 | 29.7934 | 29.7143 | 29.5941 | 29.5774 | 29.5204 | 29.435 | 29.2916 | 29.2833 | 29.9487 | 29.9104 | 29.8809 | 29.8393 | 29.7186 | 29.5889 | 29.4439 | 29.2872 | 29.0948 | 29.0335 | 28.8659 | 28.622 | 28.3437 | 28.2126 | 29.945 | 29.9038 | 29.8722 | 29.8275 | 29.703 | 29.5692 | 29.4191 | 29.2567 | 29.0589 | 28.9944 | 28.8186 | 28.563 | 28.2748 | 28.1346
|  | MAIDEN NEWTON | ST |  |  | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 29.9576 | 29.9306 | 29.9122 | 29.8892 | 29.86 | 29.8257 | 29.7785 | 29.7255 | 29.677 | 29.6465 | 29.5697 | 29.4606 | 29.3728 | 29.2934 | 29.9545 | 29.9255 | 29.9057 | 29.881 | 29.8496 | 29.8128 | 29.7622 | 29.7052 | 29.6532 | 29.6204 | 29.5379 | 29.4208 | 29.3265 | 29.2412
|  | MAIDEN NEWTON | SP |  |  | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 30.0138 | 29.9625 | 29.9431 | 29.9314 | 29.9185 | 29.9027 | 29.8857 | 29.8659 | 29.8446 | 29.8241 | 29.8121 | 29.782 | 29.7382 | 29.703 | 29.672 | 29.9597 | 29.9389 | 29.9263 | 29.9125 | 29.8955 | 29.8772 | 29.856 | 29.8332 | 29.8111 | 29.7982 | 29.7659 | 29.7189 | 29.6811 | 29.6478
BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD | MINIMUM HEADROOM | SU 86485 79800 | YES | 11.0713 | 11.0561 | 11.0362 | 10.994 | 10.9531 | 10.9126 | 10.8602 | 10.8084 | 10.757 | 10.7016 | 10.5383 | 10.2711 | 9.9961 | 9.7259 | 7.2837 | 7.2646 | 7.2394 | 7.1862 | 7.1346 | 7.0835 | 7.0175 | 6.9521 | 6.8873 | 6.8174 | 6.6114 | 6.2744 | 5.9277 | 5.5869 | 7.5389 | 7.5303 | 7.5191 | 7.4952 | 7.472 | 7.4491 | 7.4195 | 7.3901 | 7.3611 | 7.3297 | 7.2373 | 7.086 | 6.9304 | 6.7775
|  | MAIDENHEAD | CT |  |  | 11.0739 | 11.0607 | 11.0432 | 11.0064 | 10.9707 | 10.9354 | 10.9003 | 10.8485 | 10.7971 | 10.7417 | 10.5784 | 10.3112 | 10.0363 | 9.7663 | 7.287 | 7.2703 | 7.2483 | 7.2018 | 7.1568 | 7.1122 | 7.068 | 7.0026 | 6.9379 | 6.8681 | 6.662 | 6.325 | 5.9784 | 5.6379 | 7.5404 | 7.5329 | 7.523 | 7.5022 | 7.482 | 7.462 | 7.4421 | 7.4128 | 7.3838 | 7.3524 | 7.26 | 7.1088 | 6.9532 | 6.8004
|  | MAIDENHEAD | LW |  |  | 11.0713 | 11.0561 | 11.0362 | 10.994 | 10.9531 | 10.9126 | 10.8602 | 10.8084 | 10.757 | 10.7016 | 10.5383 | 10.2711 | 9.9961 | 9.7259 | 7.2837 | 7.2646 | 7.2394 | 7.1862 | 7.1346 | 7.0835 | 7.0175 | 6.9521 | 6.8873 | 6.8174 | 6.6114 | 6.2744 | 5.9277 | 5.5869 | 7.5389 | 7.5303 | 7.5191 | 7.4952 | 7.472 | 7.4491 | 7.4195 | 7.3901 | 7.3611 | 7.3297 | 7.2373 | 7.086 | 6.9304 | 6.7775
|  | MAIDENHEAD | ST |  |  | 11.0745 | 11.0621 | 11.0475 | 11.0224 | 10.9916 | 10.9544 | 10.9253 | 10.8965 | 10.8614 | 10.8237 | 10.7136 | 10.5363 | 10.3594 | 10.1834 | 7.2878 | 7.2721 | 7.2537 | 7.222 | 7.1831 | 7.1363 | 7.0996 | 7.0632 | 7.019 | 6.9714 | 6.8325 | 6.6089 | 6.3858 | 6.1638 | 7.5407 | 7.5337 | 7.5254 | 7.5112 | 7.4938 | 7.4728 | 7.4563 | 7.44 | 7.4201 | 7.3988 | 7.3365 | 7.2361 | 7.136 | 7.0364
|  | MAIDENHEAD | SP |  |  | 11.0889 | 11.0873 | 11.0858 | 11.0844 | 11.0777 | 11.0697 | 11.0606 | 11.0516 | 11.0401 | 11.0254 | 10.9829 | 10.9157 | 10.8521 | 10.7922 | 7.3059 | 7.3039 | 7.302 | 7.3002 | 7.2917 | 7.2817 | 7.2702 | 7.2589 | 7.2443 | 7.2259 | 7.1723 | 7.0875 | 7.0072 | 6.9317 | 7.5489 | 7.548 | 7.5472 | 7.5463 | 7.5425 | 7.538 | 7.5329 | 7.5278 | 7.5213 | 7.513 | 7.4889 | 7.4509 | 7.4148 | 7.381
MELKSHAM GSP | CHIPPENHAM | MALMESBURY | MINIMUM HEADROOM | ST 92288 87493 | YES | 58.3233 | 58.3233 | 58.3233 | 58.3233 | 58.3213 | 58.3173 | 58.311 | 58.3022 | 58.2845 | 58.2815 | 58.266 | 58.2282 | 58.1545 | 57.6773 | 43.6064 | 43.596 | 43.5823 | 43.554 | 43.5243 | 43.4905 | 43.4673 | 43.4313 | 43.2963 | 43.1166 | 42.6595 | 41.3113 | 39.9613 | 38.7107 | 43.4003 | 43.4003 | 43.4003 | 43.4003 | 43.3983 | 43.3943 | 43.3879 | 43.3792 | 43.3615 | 43.3585 | 43.343 | 42.5094 | 41.2141 | 40.0085
|  | MALMESBURY | CT |  |  | 58.3233 | 58.3233 | 58.3233 | 58.3233 | 58.3227 | 58.3216 | 58.3199 | 58.3175 | 58.3122 | 58.3112 | 58.3061 | 58.2642 | 58.2173 | 57.739 | 43.6077 | 43.5983 | 43.5859 | 43.5602 | 43.5345 | 43.5061 | 43.4768 | 43.4473 | 43.3279 | 43.1504 | 42.7038 | 41.3565 | 40.0335 | 38.7739 | 43.4003 | 43.4003 | 43.4003 | 43.4003 | 43.3997 | 43.3986 | 43.3969 | 43.3945 | 43.3892 | 43.3882 | 43.3831 | 42.5539 | 41.2859 | 40.0714
|  | MALMESBURY | LW |  |  | 58.3233 | 58.3233 | 58.3233 | 58.3233 | 58.3213 | 58.3173 | 58.311 | 58.3022 | 58.2845 | 58.2815 | 58.266 | 58.2282 | 58.1545 | 57.6773 | 43.6064 | 43.596 | 43.5823 | 43.554 | 43.5243 | 43.4905 | 43.4673 | 43.4313 | 43.2963 | 43.1166 | 42.6595 | 41.3113 | 39.9613 | 38.7107 | 43.4003 | 43.4003 | 43.4003 | 43.4003 | 43.3983 | 43.3943 | 43.3879 | 43.3792 | 43.3615 | 43.3585 | 43.343 | 42.5094 | 41.2141 | 40.0085
|  | MALMESBURY | ST |  |  | 58.3233 | 58.3233 | 58.3233 | 58.3233 | 58.3229 | 58.322 | 58.3208 | 58.319 | 58.3149 | 58.3129 | 58.3023 | 58.2884 | 58.2396 | 58.2219 | 43.6132 | 43.6079 | 43.6017 | 43.5912 | 43.578 | 43.5602 | 43.5458 | 43.5289 | 43.5099 | 43.492 | 43.4345 | 43.1073 | 42.708 | 41.9847 | 43.4003 | 43.4003 | 43.4003 | 43.4003 | 43.3999 | 43.399 | 43.3978 | 43.3959 | 43.3918 | 43.3899 | 43.3793 | 43.3654 | 43.3166 | 43.1279
|  | MALMESBURY | SP |  |  | 58.3233 | 58.3233 | 58.3233 | 58.3233 | 58.3233 | 58.3232 | 58.3232 | 58.3231 | 58.3229 | 58.3223 | 58.3184 | 58.3154 | 58.3009 | 58.2867 | 43.6183 | 43.6171 | 43.6159 | 43.6148 | 43.6104 | 43.6045 | 43.5996 | 43.5939 | 43.5866 | 43.5796 | 43.5601 | 43.538 | 43.5062 | 43.4759 | 43.4003 | 43.4003 | 43.4003 | 43.4003 | 43.4002 | 43.4002 | 43.4002 | 43.4001 | 43.3999 | 43.3993 | 43.3954 | 43.3924 | 43.3778 | 43.3637
MINETY GSP | SWINDON BSP | MANCHESTER ROAD | MINIMUM HEADROOM | SU 15254 85130 | NO | 18.3349 | 18.3265 | 18.3156 | 18.2949 | 18.2571 | 18.2181 | 18.1781 | 18.1469 | 18.1008 | 18.0866 | 17.8473 | 17.1884 | 16.5009 | 15.9328 | 14.0208 | 14.0155 | 14.0086 | 13.9955 | 13.9649 | 13.8978 | 13.6006 | 13.4572 | 13.3009 | 13.1688 | 12.7753 | 12.0286 | 11.2518 | 10.5961 | 14.2849 | 14.2849 | 14.2849 | 14.2849 | 14.2215 | 13.9419 | 13.662 | 13.5261 | 13.3772 | 13.253 | 12.8827 | 12.1743 | 11.4185 | 10.7719
|  | MANCHESTER ROAD | CT |  |  | 18.3349 | 18.3265 | 18.3156 | 18.2949 | 18.2571 | 18.2181 | 18.1781 | 18.1469 | 18.1008 | 18.0866 | 17.8473 | 17.1884 | 16.5009 | 15.9328 | 14.0208 | 14.0155 | 14.0086 | 13.9955 | 13.9649 | 13.8978 | 13.6006 | 13.4572 | 13.3009 | 13.1688 | 12.7753 | 12.0286 | 11.2518 | 10.5961 | 14.2849 | 14.2849 | 14.2849 | 14.2849 | 14.2215 | 13.9419 | 13.662 | 13.5261 | 13.3772 | 13.253 | 12.8827 | 12.1743 | 11.4185 | 10.7719
|  | MANCHESTER ROAD | LW |  |  | 18.3353 | 18.3272 | 18.3166 | 18.2967 | 18.2744 | 18.2485 | 18.2289 | 18.205 | 18.1658 | 18.1515 | 18.0654 | 17.4713 | 16.8056 | 16.2697 | 14.021 | 14.0159 | 14.0092 | 13.9966 | 13.9812 | 13.9622 | 13.8402 | 13.7041 | 13.5547 | 13.4226 | 13.0224 | 12.3405 | 11.5854 | 10.9618 | 14.2849 | 14.2849 | 14.2849 | 14.2849 | 14.271 | 14.0136 | 13.8889 | 13.7603 | 13.6183 | 13.4941 | 13.1171 | 12.4735 | 11.7492 | 11.1346
|  | MANCHESTER ROAD | ST |  |  | 18.3374 | 18.3313 | 18.324 | 18.313 | 18.299 | 18.2815 | 18.2726 | 18.2627 | 18.2498 | 18.2403 | 18.204 | 18.1507 | 17.837 | 17.4631 | 14.0224 | 14.0185 | 14.0139 | 14.0069 | 13.9978 | 13.9862 | 13.9797 | 13.9723 | 13.9615 | 13.9542 | 13.6871 | 13.2523 | 12.7636 | 12.3327 | 14.2849 | 14.2849 | 14.2849 | 14.2849 | 14.2842 | 14.2828 | 14.2579 | 14.1666 | 14.0835 | 13.999 | 13.7443 | 13.3352 | 12.8716 | 12.4655
|  | MANCHESTER ROAD | SP |  |  | 18.3436 | 18.3423 | 18.341 | 18.3401 | 18.337 | 18.3331 | 18.3306 | 18.328 | 18.3247 | 18.3211 | 18.3076 | 18.2912 | 18.2555 | 18.221 | 14.0231 | 14.0231 | 14.0231 | 14.0231 | 14.0221 | 14.0196 | 14.018 | 14.0163 | 14.0141 | 14.0114 | 14.0004 | 13.9881 | 13.9562 | 13.9252 | 14.2849 | 14.2849 | 14.2849 | 14.2849 | 14.2849 | 14.2848 | 14.2847 | 14.2846 | 14.2843 | 14.2831 | 14.2765 | 14.2712 | 14.2458 | 14.221
MANNINGTON GSP | MANNINGTON BSP | MANNINGTON | MINIMUM HEADROOM | SU 07592 05256 | YES | 67.964 | 67.9291 | 67.8915 | 66.3183 | 66.1737 | 66.0287 | 65.8768 | 65.7243 | 65.5722 | 65.4921 | 65.2534 | 64.8519 | 64.5389 | 62.9313 | 67.1383 | 67.0962 | 67.0492 | 65.4609 | 65.3028 | 65.1442 | 64.9733 | 64.8013 | 64.6302 | 64.5274 | 63.8837 | 62.7702 | 61.5605 | 59.2858 | 67.6541 | 67.6211 | 67.5859 | 66.0168 | 65.8756 | 65.7342 | 65.5873 | 65.4398 | 65.2928 | 65.2185 | 64.9972 | 64.2545 | 61.899 | 59.4363
|  | MANNINGTON | CT |  |  | 68.0867 | 68.0624 | 68.0355 | 67.0847 | 66.992 | 66.8989 | 66.8053 | 66.7037 | 66.6026 | 66.5428 | 66.3653 | 65.104 | 64.5505 | 63.0667 | 67.2615 | 67.2302 | 67.1942 | 66.2291 | 66.1237 | 66.0177 | 65.9108 | 65.7897 | 65.6695 | 65.5872 | 65.052 | 63.0786 | 61.6463 | 59.446 | 67.7767 | 67.7542 | 67.7296 | 66.7827 | 66.6932 | 66.6035 | 66.5134 | 66.4169 | 66.3208 | 66.2669 | 66.1067 | 64.6546 | 62.0586 | 59.596
|  | MANNINGTON | LW |  |  | 67.964 | 67.9291 | 67.8915 | 66.3183 | 66.1737 | 66.0287 | 65.8768 | 65.7243 | 65.5722 | 65.4921 | 65.2534 | 64.8519 | 64.5389 | 62.9313 | 67.1383 | 67.0962 | 67.0492 | 65.4609 | 65.3028 | 65.1442 | 64.9733 | 64.8013 | 64.6302 | 64.5274 | 63.8837 | 62.7702 | 61.5605 | 59.2858 | 67.6541 | 67.6211 | 67.5859 | 66.0168 | 65.8756 | 65.7342 | 65.5873 | 65.4398 | 65.2928 | 65.2185 | 64.9972 | 64.2545 | 61.899 | 59.4363
|  | MANNINGTON | ST |  |  | 68.1498 | 68.133 | 68.1149 | 67.483 | 67.4211 | 67.3571 | 67.2931 | 67.2287 | 67.161 | 67.1207 | 67.0008 | 66.7989 | 66.6332 | 66.4193 | 67.3261 | 67.3041 | 67.28 | 66.6399 | 66.5696 | 66.4955 | 66.4214 | 66.3465 | 66.2658 | 66.2101 | 66.0447 | 65.4146 | 64.742 | 64.0339 | 67.8394 | 67.8239 | 67.8075 | 67.1777 | 67.118 | 67.0566 | 66.9953 | 66.9336 | 66.8693 | 66.833 | 66.725 | 66.5433 | 66.3988 | 65.0238
|  | MANNINGTON | SP |  |  | 68.2152 | 68.2073 | 68.1993 | 67.8862 | 67.8557 | 67.8247 | 67.7931 | 67.7614 | 67.7279 | 67.7027 | 67.6263 | 67.5248 | 67.4164 | 67.2879 | 67.3948 | 67.3847 | 67.3745 | 67.0595 | 67.0264 | 66.9925 | 66.9574 | 66.922 | 66.8843 | 66.8531 | 66.7591 | 66.627 | 66.4851 | 66.3228 | 67.9039 | 67.8966 | 67.8892 | 67.5766 | 67.5467 | 67.5166 | 67.4859 | 67.455 | 67.4226 | 67.399 | 67.3273 | 67.2338 | 67.1342 | 67.0145
LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET | MINIMUM HEADROOM | SU 86479 04732 | NO | 16.6015 | 16.6015 | 16.6015 | 16.6015 | 16.5924 | 16.5835 | 16.5746 | 16.5654 | 16.5511 | 16.5112 | 16.3829 | 16.3207 | 16.1202 | 15.9507 | 16.1884 | 16.1884 | 16.1884 | 16.1884 | 16.1793 | 16.1704 | 16.1615 | 16.1523 | 16.138 | 16.0981 | 15.9698 | 15.9076 | 15.7071 | 15.5376 | 16.5041 | 16.5041 | 16.5041 | 16.5041 | 16.495 | 16.4861 | 16.4772 | 16.468 | 16.4537 | 16.4138 | 16.2855 | 16.2233 | 16.0228 | 15.8533
|  | MARKET | CT |  |  | 16.6015 | 16.6015 | 16.6015 | 16.6015 | 16.601 | 16.5999 | 16.5984 | 16.5962 | 16.5913 | 16.5905 | 16.5858 | 16.5472 | 16.5042 | 16.491 | 16.1884 | 16.1884 | 16.1884 | 16.1884 | 16.1879 | 16.1869 | 16.1853 | 16.1831 | 16.1782 | 16.1774 | 16.1727 | 16.1341 | 16.0734 | 15.9475 | 16.5041 | 16.5041 | 16.5041 | 16.5041 | 16.5036 | 16.5026 | 16.501 | 16.4988 | 16.4939 | 16.4931 | 16.4884 | 16.4498 | 16.4068 | 16.3936
|  | MARKET | LW |  |  | 16.6015 | 16.6015 | 16.6015 | 16.6015 | 16.5997 | 16.596 | 16.5902 | 16.5821 | 16.566 | 16.5632 | 16.5489 | 16.5142 | 16.4466 | 16.442 | 16.1884 | 16.1884 | 16.1884 | 16.1884 | 16.1866 | 16.1829 | 16.1771 | 16.1691 | 16.1529 | 16.1501 | 16.1358 | 16.1011 | 16.0042 | 15.8869 | 16.5041 | 16.5041 | 16.5041 | 16.5041 | 16.5023 | 16.4986 | 16.4928 | 16.4848 | 16.4686 | 16.4658 | 16.4515 | 16.4168 | 16.3492 | 16.3446
|  | MARKET | ST |  |  | 16.6015 | 16.6015 | 16.6015 | 16.6015 | 16.6011 | 16.6004 | 16.5992 | 16.5976 | 16.5938 | 16.592 | 16.5822 | 16.5695 | 16.5247 | 16.5084 | 16.1884 | 16.1884 | 16.1884 | 16.1884 | 16.188 | 16.1873 | 16.1862 | 16.1845 | 16.1807 | 16.1789 | 16.1692 | 16.1564 | 16.1116 | 16.0954 | 16.5041 | 16.5041 | 16.5041 | 16.5041 | 16.5037 | 16.503 | 16.5019 | 16.5002 | 16.4964 | 16.4946 | 16.4849 | 16.4721 | 16.4273 | 16.4111
|  | MARKET | SP |  |  | 16.6015 | 16.6015 | 16.6015 | 16.6015 | 16.5924 | 16.5835 | 16.5746 | 16.5654 | 16.5511 | 16.5112 | 16.3829 | 16.3207 | 16.1202 | 15.9507 | 16.1884 | 16.1884 | 16.1884 | 16.1884 | 16.1793 | 16.1704 | 16.1615 | 16.1523 | 16.138 | 16.0981 | 15.9698 | 15.9076 | 15.7071 | 15.5376 | 16.5041 | 16.5041 | 16.5041 | 16.5041 | 16.495 | 16.4861 | 16.4772 | 16.468 | 16.4537 | 16.4138 | 16.2855 | 16.2233 | 16.0228 | 15.8533
MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH | MINIMUM HEADROOM | SU 19293 68264 | YES | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 23.0937 | 23.0734 | 23.047 | 22.9929 | 22.9409 | 22.8899 | 22.8524 | 22.8137 | 22.7725 | 22.6918 | 22.3763 | 21.1346 | 19.7077 | 18.2837 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3274 | 22.1253 | 21.4588 | 20.2661 | 18.8955 | 17.5277
|  | MARLBOROUGH SOUTH | CT |  |  | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 23.0979 | 23.0808 | 23.0584 | 23.0127 | 22.969 | 22.9261 | 22.8829 | 22.8442 | 22.803 | 22.7536 | 22.4592 | 21.2804 | 19.8536 | 18.4299 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.2653 | 21.5988 | 20.4061 | 19.0357 | 17.6681
|  | MARLBOROUGH SOUTH | LW |  |  | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 23.0937 | 23.0734 | 23.047 | 22.9929 | 22.9409 | 22.8899 | 22.8524 | 22.8137 | 22.7725 | 22.6918 | 22.3763 | 21.1346 | 19.7077 | 18.2837 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3274 | 22.1253 | 21.4588 | 20.2661 | 18.8955 | 17.5277
|  | MARLBOROUGH SOUTH | ST |  |  | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 23.1002 | 23.0857 | 23.0687 | 23.0396 | 23.0057 | 22.9661 | 22.9321 | 22.8974 | 22.8695 | 22.8394 | 22.7136 | 22.2677 | 21.3315 | 20.4224 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.1748 | 21.3545 | 20.4552 | 19.582
|  | MARLBOROUGH SOUTH | SP |  |  | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 30.6728 | 23.1138 | 23.1101 | 23.1064 | 23.1016 | 23.0917 | 23.0807 | 23.0686 | 23.0564 | 23.0407 | 23.0291 | 22.99 | 22.9181 | 22.8325 | 22.7232 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.3869 | 22.1965
NURSLING GSP | ROWNHAMS | MAYBUSH | MINIMUM HEADROOM | SU 38426 14930 | YES | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 20.9525 | 20.4056 | 14.9176 | 14.8635 | 14.7943 | 14.6478 | 14.5053 | 14.3636 | 14.2235 | 14.1161 | 14.0095 | 13.8946 | 13.5558 | 13.0004 | 12.4303 | 11.87 | 19.6951 | 19.6914 | 19.6866 | 19.6765 | 19.6666 | 19.5862 | 19.4374 | 19.3232 | 19.21 | 19.0879 | 18.7279 | 18.1378 | 17.5321 | 16.9368
|  | MAYBUSH | CT |  |  | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 20.9525 | 20.4056 | 14.9176 | 14.8635 | 14.7943 | 14.6478 | 14.5053 | 14.3636 | 14.2235 | 14.1161 | 14.0095 | 13.8946 | 13.5558 | 13.0004 | 12.4303 | 11.87 | 19.6951 | 19.6914 | 19.6866 | 19.6765 | 19.6666 | 19.5862 | 19.4374 | 19.3232 | 19.21 | 19.0879 | 18.7279 | 18.1378 | 17.5321 | 16.9368
|  | MAYBUSH | LW |  |  | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 20.996 | 20.4487 | 14.9192 | 14.8663 | 14.7985 | 14.655 | 14.5156 | 14.3768 | 14.2682 | 14.1606 | 14.0541 | 13.9393 | 13.6003 | 13.0451 | 12.4749 | 11.9142 | 19.6952 | 19.6916 | 19.6869 | 19.677 | 19.6674 | 19.6003 | 19.4848 | 19.3705 | 19.2574 | 19.1354 | 18.7752 | 18.1853 | 17.5794 | 16.9837
|  | MAYBUSH | ST |  |  | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 14.9398 | 14.9028 | 14.8604 | 14.7877 | 14.6982 | 14.59 | 14.515 | 14.4411 | 14.3684 | 14.2902 | 14.0621 | 13.6931 | 13.3262 | 12.9615 | 19.6967 | 19.6941 | 19.6912 | 19.6862 | 19.68 | 19.6725 | 19.6673 | 19.6622 | 19.5913 | 19.5082 | 19.2658 | 18.8738 | 18.484 | 18.0965
|  | MAYBUSH | SP |  |  | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 21.1127 | 14.9806 | 14.9746 | 14.9696 | 14.9648 | 14.9419 | 14.9146 | 14.8883 | 14.8623 | 14.829 | 14.7987 | 14.7111 | 14.5718 | 14.4398 | 14.3157 | 19.6995 | 19.6991 | 19.6987 | 19.6984 | 19.6968 | 19.6949 | 19.6931 | 19.6913 | 19.689 | 19.6869 | 19.6809 | 19.6712 | 19.6621 | 19.5353
MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN | MINIMUM HEADROOM | ST 90170 64096 | NO | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6185 | 30.5415 | 30.4633 | 30.3816 | 30.2557 | 30.2397 | 30.1884 | 29.9517 | 29.6468 | 28.426 | 23.7958 | 23.795 | 23.7938 | 23.7917 | 23.7138 | 23.634 | 23.5526 | 23.4628 | 23.3287 | 23.3042 | 23.226 | 22.3686 | 20.4538 | 18.7722 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.1587 | 24.0817 | 24.0035 | 23.9218 | 23.7959 | 23.7799 | 23.7287 | 23.4892 | 21.7095 | 20.1631
|  | MELKSHAM TOWN | CT |  |  | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6185 | 30.5415 | 30.4633 | 30.3816 | 30.2557 | 30.2397 | 30.1884 | 29.9517 | 29.6468 | 28.426 | 23.7959 | 23.7951 | 23.794 | 23.7921 | 23.7138 | 23.634 | 23.5526 | 23.4628 | 23.3287 | 23.3042 | 23.226 | 22.3686 | 20.4538 | 18.7722 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.1587 | 24.0817 | 24.0035 | 23.9218 | 23.7959 | 23.7799 | 23.7287 | 23.4892 | 21.7095 | 20.1631
|  | MELKSHAM TOWN | LW |  |  | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 29.421 | 23.7958 | 23.795 | 23.7938 | 23.7917 | 23.789 | 23.7861 | 23.7772 | 23.769 | 23.7609 | 23.7523 | 23.7254 | 22.9672 | 21.3569 | 19.7454 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.0999 | 22.6247 | 21.1484
|  | MELKSHAM TOWN | ST |  |  | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 23.7988 | 23.7954 | 23.7947 | 23.7935 | 23.7917 | 23.7896 | 23.7869 | 23.7847 | 23.7792 | 23.7734 | 23.755 | 23.7141 | 23.0027 | 21.9734 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.1324 | 23.1894
|  | MELKSHAM TOWN | SP |  |  | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 30.6942 | 23.7993 | 23.7963 | 23.7961 | 23.7959 | 23.7952 | 23.7945 | 23.7935 | 23.7928 | 23.792 | 23.7897 | 23.7825 | 23.766 | 23.7455 | 23.7242 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344 | 24.2344
LOVEDEAN GSP | HAVANT | MEYRICK ROAD | MINIMUM HEADROOM | SU 70849 06469 | YES | 32.6986 | 32.6772 | 32.6557 | 31.347 | 31.2242 | 31.0849 | 30.9274 | 30.7505 | 30.5163 | 30.4528 | 30.2287 | 29.8002 | 29.2671 | 29.0055 | 27.9943 | 27.812 | 27.6416 | 26.0752 | 25.7132 | 25.3335 | 24.881 | 24.4105 | 23.8874 | 23.5148 | 22.3804 | 20.4525 | 18.3945 | 16.6359 | 29.8389 | 29.8175 | 29.796 | 28.4873 | 28.3576 | 28.2037 | 28.0282 | 27.8319 | 27.3607 | 26.9988 | 25.8688 | 23.9279 | 21.8004 | 19.9735
|  | MEYRICK ROAD | CT |  |  | 32.8016 | 32.7887 | 32.7759 | 31.9906 | 31.9215 | 31.8483 | 31.7709 | 31.6874 | 31.5857 | 31.5538 | 31.4471 | 30.281 | 29.7012 | 29.3968 | 28.1143 | 27.953 | 27.8073 | 26.7985 | 26.5232 | 26.2424 | 25.9571 | 25.5801 | 25.1894 | 24.8483 | 23.8314 | 21.166 | 19.0616 | 17.2612 | 29.9419 | 29.9291 | 29.9162 | 29.131 | 29.0617 | 28.9759 | 28.8858 | 28.7846 | 28.6209 | 28.3311 | 27.3186 | 24.652 | 22.4781 | 20.6095
|  | MEYRICK ROAD | LW |  |  | 32.6986 | 32.6772 | 32.6557 | 31.347 | 31.2242 | 31.0849 | 30.9274 | 30.7505 | 30.5163 | 30.4528 | 30.2287 | 29.8002 | 29.2671 | 29.0055 | 27.9943 | 27.812 | 27.6416 | 26.0752 | 25.7132 | 25.3335 | 24.881 | 24.4105 | 23.8874 | 23.5148 | 22.3804 | 20.4525 | 18.3945 | 16.6359 | 29.8389 | 29.8175 | 29.796 | 28.4873 | 28.3576 | 28.2037 | 28.0282 | 27.8319 | 27.3607 | 26.9988 | 25.8688 | 23.9279 | 21.8004 | 19.9735
|  | MEYRICK ROAD | ST |  |  | 32.8531 | 32.8445 | 32.8359 | 32.3124 | 32.2663 | 32.2168 | 32.1641 | 32.1066 | 32.0349 | 32.0051 | 31.8923 | 31.7308 | 31.4248 | 31.2458 | 28.2789 | 28.0772 | 27.9222 | 27.2518 | 27.0349 | 26.778 | 26.5527 | 26.3239 | 26.0549 | 25.8142 | 25.0873 | 23.9267 | 22.6388 | 21.486 | 29.9934 | 29.9848 | 29.9763 | 29.4528 | 29.4066 | 29.3546 | 29.2913 | 29.2234 | 29.1398 | 29.0972 | 28.5707 | 27.4149 | 26.1317 | 24.9426
|  | MEYRICK ROAD | SP |  |  | 32.9046 | 32.9003 | 32.896 | 32.6343 | 32.6127 | 32.5909 | 32.569 | 32.5468 | 32.5237 | 32.5087 | 32.4462 | 32.3742 | 32.2089 | 32.0256 | 28.4151 | 28.3862 | 28.257 | 27.9824 | 27.9268 | 27.8641 | 27.7884 | 27.7129 | 27.622 | 27.5252 | 27.2257 | 26.7743 | 26.2533 | 25.735 | 30.0449 | 30.0406 | 30.0363 | 29.7746 | 29.753 | 29.7313 | 29.7093 | 29.6871 | 29.664 | 29.649 | 29.5866 | 29.5021 | 29.3153 | 29.1117
BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP | MINIMUM HEADROOM | SU 30984 40155 | YES | 29.8982 | 29.884 | 29.8789 | 29.8699 | 29.7272 | 29.5733 | 29.3994 | 29.2207 | 28.9622 | 28.8989 | 28.693 | 27.9302 | 25.6124 | 23.5803 | 28.4011 | 28.3749 | 28.3656 | 28.3489 | 28.1996 | 28.0333 | 27.8352 | 27.6327 | 27.3492 | 27.2591 | 26.6916 | 24.329 | 21.6574 | 19.2751 | 28.4551 | 28.4428 | 28.4385 | 28.4307 | 28.2891 | 28.1372 | 27.9672 | 27.7924 | 27.538 | 27.479 | 26.7744 | 24.3912 | 21.7188 | 19.3358
|  | MIDDLE WALLOP | CT |  |  | 29.8982 | 29.884 | 29.8789 | 29.8699 | 29.8573 | 29.8411 | 29.8252 | 29.7971 | 29.7674 | 29.7358 | 29.6385 | 29.1097 | 27.0764 | 25.0653 | 28.4011 | 28.3749 | 28.3656 | 28.3489 | 28.3255 | 28.2957 | 28.2664 | 28.2145 | 28.1598 | 28.1014 | 27.7213 | 25.5222 | 23.1349 | 20.7738 | 28.4551 | 28.4428 | 28.4385 | 28.4307 | 28.4198 | 28.4058 | 28.3921 | 28.3679 | 28.3423 | 28.315 | 27.8051 | 25.5844 | 23.1963 | 20.8345
|  | MIDDLE WALLOP | LW |  |  | 29.8989 | 29.8853 | 29.8809 | 29.8733 | 29.7272 | 29.5733 | 29.3994 | 29.2207 | 28.9622 | 28.8989 | 28.693 | 27.9302 | 25.6124 | 23.5803 | 28.4025 | 28.3773 | 28.3692 | 28.3552 | 28.1996 | 28.0333 | 27.8352 | 27.6327 | 27.3492 | 27.2591 | 26.6916 | 24.329 | 21.6574 | 19.2751 | 28.4557 | 28.4439 | 28.4402 | 28.4336 | 28.2891 | 28.1372 | 27.9672 | 27.7924 | 27.538 | 27.479 | 26.7744 | 24.3912 | 21.7188 | 19.3358
|  | MIDDLE WALLOP | ST |  |  | 29.9003 | 29.8981 | 29.8856 | 29.882 | 29.8757 | 29.8666 | 29.8492 | 29.8321 | 29.8121 | 29.7904 | 29.7229 | 29.6158 | 29.3903 | 28.1038 | 28.405 | 28.4009 | 28.3779 | 28.3713 | 28.3596 | 28.3429 | 28.3108 | 28.2792 | 28.2421 | 28.2021 | 28.0776 | 27.4003 | 25.8516 | 24.3412 | 28.4569 | 28.455 | 28.4442 | 28.4411 | 28.4357 | 28.4279 | 28.4128 | 28.3981 | 28.3808 | 28.3621 | 28.3039 | 27.4803 | 25.9139 | 24.403
|  | MIDDLE WALLOP | SP |  |  | 29.9011 | 29.8997 | 29.8884 | 29.8868 | 29.8836 | 29.8794 | 29.873 | 29.867 | 29.8597 | 29.8512 | 29.8247 | 29.7814 | 29.7339 | 29.6855 | 28.4064 | 28.4039 | 28.383 | 28.3801 | 28.3742 | 28.3664 | 28.3546 | 28.3435 | 28.33 | 28.3143 | 28.2654 | 28.1856 | 28.0979 | 28.0085 | 28.4575 | 28.4564 | 28.4466 | 28.4453 | 28.4425 | 28.4388 | 28.4333 | 28.4281 | 28.4218 | 28.4145 | 28.3917 | 28.3544 | 28.3134 | 28.2716
BRAMLEY (FLEE) | FERNHURST | MIDHURST | MINIMUM HEADROOM | SU 88127 19555 | YES | 8.6859 | 8.6703 | 8.65 | 8.6068 | 8.5108 | 8.3949 | 8.2756 | 8.1499 | 7.9685 | 7.9124 | 7.7283 | 7.4082 | 6.9019 | 6.7117 | 5.5541 | 5.5372 | 5.515 | 5.468 | 5.3701 | 5.2511 | 5.1289 | 5.0005 | 4.8168 | 4.7584 | 4.5677 | 4.2278 | 3.694 | 3.4766 | 5.851 | 5.8335 | 5.8108 | 5.7626 | 5.6641 | 5.544 | 5.421 | 5.2916 | 5.1071 | 5.0477 | 4.8541 | 4.5183 | 3.9959 | 3.7897
|  | MIDHURST | CT |  |  | 8.6859 | 8.6703 | 8.65 | 8.6068 | 8.5641 | 8.5208 | 8.4772 | 8.4412 | 8.4009 | 8.3649 | 8.2551 | 8.0221 | 7.7762 | 7.584 | 5.5541 | 5.5372 | 5.515 | 5.468 | 5.4216 | 5.3747 | 5.3274 | 5.2892 | 5.2468 | 5.2085 | 5.0921 | 4.8359 | 4.5624 | 4.3432 | 5.851 | 5.8335 | 5.8108 | 5.7626 | 5.7149 | 5.6668 | 5.6184 | 5.5793 | 5.536 | 5.4967 | 5.3774 | 5.1288 | 4.8667 | 4.6586
|  | MIDHURST | LW |  |  | 8.6891 | 8.6758 | 8.6584 | 8.6215 | 8.5108 | 8.3949 | 8.2756 | 8.1499 | 7.9685 | 7.9124 | 7.7283 | 7.4082 | 6.9019 | 6.7117 | 5.5576 | 5.5431 | 5.5242 | 5.484 | 5.3701 | 5.2511 | 5.1289 | 5.0005 | 4.8168 | 4.7584 | 4.5677 | 4.2278 | 3.694 | 3.4766 | 5.8545 | 5.8397 | 5.8202 | 5.779 | 5.6641 | 5.544 | 5.421 | 5.2916 | 5.1071 | 5.0477 | 4.8541 | 4.5183 | 3.9959 | 3.7897
|  | MIDHURST | ST |  |  | 8.692 | 8.6812 | 8.6685 | 8.6467 | 8.6194 | 8.5859 | 8.565 | 8.5434 | 8.5156 | 8.4895 | 8.4049 | 8.272 | 8.0844 | 7.9462 | 5.5608 | 5.549 | 5.5352 | 5.5115 | 5.4818 | 5.4455 | 5.4229 | 5.3996 | 5.3699 | 5.3418 | 5.2521 | 5.1119 | 4.9143 | 4.7585 | 5.8578 | 5.8457 | 5.8315 | 5.8072 | 5.7767 | 5.7395 | 5.7164 | 5.6925 | 5.6622 | 5.6334 | 5.5419 | 5.3985 | 5.2005 | 5.052
|  | MIDHURST | SP |  |  | 8.7045 | 8.7031 | 8.7018 | 8.7005 | 8.6946 | 8.6875 | 8.6806 | 8.6736 | 8.6646 | 8.6546 | 8.6227 | 8.5767 | 8.5147 | 8.4554 | 5.5744 | 5.5729 | 5.5714 | 5.57 | 5.5636 | 5.5559 | 5.5483 | 5.5408 | 5.531 | 5.5202 | 5.486 | 5.4363 | 5.3709 | 5.3082 | 5.8717 | 5.8702 | 5.8687 | 5.8673 | 5.8607 | 5.8528 | 5.845 | 5.8373 | 5.8272 | 5.8162 | 5.7812 | 5.7304 | 5.6638 | 5.6001
AXMINSTER | YEOVIL BSP | MILBORNE PORT | MINIMUM HEADROOM | ST 67929 19741 | YES | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 26.579 | 26.5682 | 26.566 | 26.5614 | 26.557 | 26.5526 | 26.5404 | 26.5284 | 26.5164 | 26.5036 | 26.4656 | 26.4034 | 25.7821 | 24.9887 | 26.6163 | 26.6084 | 26.6069 | 26.6035 | 26.6003 | 26.597 | 26.5882 | 26.5794 | 26.5707 | 26.5613 | 26.5336 | 26.4883 | 25.7087 | 24.9178
|  | MILBORNE PORT | CT |  |  | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 26.5791 | 26.5683 | 26.5663 | 26.5619 | 26.5576 | 26.5534 | 26.5492 | 26.5371 | 26.5252 | 26.5123 | 26.4744 | 26.4122 | 25.8931 | 25.1002 | 26.6164 | 26.6086 | 26.6071 | 26.6039 | 26.6007 | 26.5977 | 26.5946 | 26.5858 | 26.5771 | 26.5677 | 26.54 | 26.4947 | 25.8194 | 25.0289
|  | MILBORNE PORT | LW |  |  | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 26.579 | 26.5682 | 26.566 | 26.5614 | 26.557 | 26.5526 | 26.5404 | 26.5284 | 26.5164 | 26.5036 | 26.4656 | 26.4034 | 25.7821 | 24.9887 | 26.6163 | 26.6084 | 26.6069 | 26.6035 | 26.6003 | 26.597 | 26.5882 | 26.5794 | 26.5707 | 26.5613 | 26.5336 | 26.4883 | 25.7087 | 24.9178
|  | MILBORNE PORT | ST |  |  | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 26.5802 | 26.5794 | 26.5693 | 26.5678 | 26.5659 | 26.5636 | 26.5569 | 26.5504 | 26.5422 | 26.5335 | 26.5079 | 26.4666 | 26.4254 | 26.3495 | 26.6172 | 26.6166 | 26.6093 | 26.6082 | 26.6068 | 26.6051 | 26.6003 | 26.5955 | 26.5895 | 26.5831 | 26.5645 | 26.5343 | 26.5043 | 26.2744
|  | MILBORNE PORT | SP |  |  | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 30.0918 | 26.5809 | 26.5808 | 26.5715 | 26.5714 | 26.5708 | 26.5701 | 26.568 | 26.5658 | 26.563 | 26.5596 | 26.5498 | 26.5342 | 26.5194 | 26.5054 | 26.6178 | 26.6177 | 26.6109 | 26.6108 | 26.6104 | 26.6099 | 26.6083 | 26.6067 | 26.6047 | 26.6022 | 26.595 | 26.5836 | 26.5728 | 26.5627
BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD | MINIMUM HEADROOM | SU 94719 43018 | YES | 3.1077 | 3.1061 | 3.104 | 3.0997 | 2.9359 | 2.767 | 2.559 | 2.345 | 2.0389 | 1.9633 | 1.7217 | 1.3389 | 0.77751 | 0.55501 | 3.2028 | 3.2009 | 3.1985 | 3.1935 | 3.029 | 2.8595 | 2.6457 | 2.426 | 2.1143 | 2.0325 | 1.7728 | 1.3575 | 0.75946 | 0.50085 | 3.3389 | 3.337 | 3.3346 | 3.3294 | 3.1649 | 2.9953 | 2.7807 | 2.5604 | 2.2479 | 2.1654 | 1.9034 | 1.4863 | 0.88895 | 0.63104
|  | MILFORD | CT |  |  | 3.1077 | 3.1061 | 3.104 | 3.0997 | 3.0954 | 3.0911 | 3.0869 | 3.0512 | 3.0157 | 2.9775 | 2.8644 | 2.6739 | 2.4744 | 2.278 | 3.2028 | 3.2009 | 3.1985 | 3.1935 | 3.1886 | 3.1836 | 3.1787 | 3.1372 | 3.0961 | 3.0518 | 2.9207 | 2.6983 | 2.4622 | 2.2297 | 3.3389 | 3.337 | 3.3346 | 3.3294 | 3.3244 | 3.3194 | 3.3144 | 3.2722 | 3.2304 | 3.1853 | 3.0519 | 2.827 | 2.5915 | 2.3598
|  | MILFORD | LW |  |  | 3.1077 | 3.1061 | 3.104 | 3.0997 | 2.9359 | 2.767 | 2.559 | 2.345 | 2.0389 | 1.9633 | 1.7217 | 1.3389 | 0.77751 | 0.55501 | 3.2028 | 3.2009 | 3.1985 | 3.1935 | 3.029 | 2.8595 | 2.6457 | 2.426 | 2.1143 | 2.0325 | 1.7728 | 1.3575 | 0.75946 | 0.50085 | 3.3389 | 3.337 | 3.3346 | 3.3294 | 3.1649 | 2.9953 | 2.7807 | 2.5604 | 2.2479 | 2.1654 | 1.9034 | 1.4863 | 0.88895 | 0.63104
|  | MILFORD | ST |  |  | 3.1084 | 3.1074 | 3.1062 | 3.1043 | 3.1018 | 3.0989 | 3.0783 | 3.0579 | 3.0336 | 3.0076 | 2.9312 | 2.804 | 2.6753 | 2.5476 | 3.2037 | 3.2025 | 3.2011 | 3.1988 | 3.196 | 3.1926 | 3.1687 | 3.145 | 3.1169 | 3.0867 | 2.9981 | 2.8506 | 2.7 | 2.5489 | 3.3398 | 3.3386 | 3.3372 | 3.3349 | 3.332 | 3.3285 | 3.3042 | 3.2801 | 3.2515 | 3.2208 | 3.1307 | 2.9806 | 2.8286 | 2.678
|  | MILFORD | SP |  |  | 3.1094 | 3.1092 | 3.109 | 3.1088 | 3.1081 | 3.1073 | 3.1009 | 3.0946 | 3.0865 | 3.0764 | 3.0467 | 2.9981 | 2.9504 | 2.9047 | 3.2048 | 3.2046 | 3.2043 | 3.2041 | 3.2033 | 3.2023 | 3.195 | 3.1876 | 3.1783 | 3.1665 | 3.1321 | 3.0757 | 3.0204 | 2.9674 | 3.341 | 3.3407 | 3.3405 | 3.3403 | 3.3394 | 3.3385 | 3.3309 | 3.3235 | 3.314 | 3.302 | 3.267 | 3.2096 | 3.1533 | 3.0994
MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA | MINIMUM HEADROOM | SZ 28252 93347 | YES | 29.2028 | 29.1957 | 29.1861 | 29.1683 | 29.1528 | 29.1382 | 29.1236 | 29.112 | 29.0823 | 29.0669 | 29.0201 | 28.8879 | 28.1931 | 27.5144 | 27.7839 | 27.7708 | 27.7532 | 27.7203 | 27.6917 | 27.6648 | 27.6377 | 27.6175 | 27.5973 | 27.5759 | 27.2863 | 26.4796 | 25.6611 | 24.8616 | 28.3953 | 28.3892 | 28.3809 | 28.3656 | 28.3522 | 28.3396 | 28.327 | 28.2909 | 28.1456 | 27.9922 | 27.545 | 26.7996 | 26.0434 | 25.3047
|  | MILFORD-ON-SEA | CT |  |  | 29.2028 | 29.1957 | 29.1861 | 29.1683 | 29.1528 | 29.1382 | 29.1236 | 29.1126 | 29.1016 | 29.0901 | 29.0563 | 28.8879 | 28.1931 | 27.5144 | 27.7839 | 27.7708 | 27.7532 | 27.7203 | 27.6917 | 27.6648 | 27.6377 | 27.6175 | 27.5973 | 27.5759 | 27.2863 | 26.4796 | 25.6611 | 24.8616 | 28.3953 | 28.3892 | 28.3809 | 28.3656 | 28.3522 | 28.3396 | 28.327 | 28.2909 | 28.1456 | 27.9922 | 27.545 | 26.7996 | 26.0434 | 25.3047
|  | MILFORD-ON-SEA | LW |  |  | 29.2056 | 29.2005 | 29.1937 | 29.1816 | 29.1716 | 29.1625 | 29.1516 | 29.1406 | 29.1297 | 29.1181 | 29.0844 | 29.0282 | 28.5349 | 27.8558 | 27.7892 | 27.7798 | 27.7672 | 27.7448 | 27.7264 | 27.7096 | 27.6895 | 27.6693 | 27.6491 | 27.6277 | 27.5654 | 26.8824 | 26.0638 | 25.2637 | 28.3977 | 28.3934 | 28.3875 | 28.377 | 28.3684 | 28.3605 | 28.3512 | 28.3417 | 28.3323 | 28.3223 | 27.917 | 27.1718 | 26.4154 | 25.6762
|  | MILFORD-ON-SEA | ST |  |  | 29.2074 | 29.204 | 29.1998 | 29.1938 | 29.1746 | 29.1547 | 29.1336 | 29.112 | 29.0823 | 29.0669 | 29.0201 | 28.9625 | 28.8565 | 28.8003 | 27.7924 | 27.7862 | 27.7785 | 27.7674 | 27.7433 | 27.718 | 27.6908 | 27.6631 | 27.6271 | 27.605 | 27.5389 | 27.4496 | 27.0648 | 26.5253 | 28.3993 | 28.3964 | 28.3928 | 28.3875 | 28.3692 | 28.3501 | 28.33 | 28.3094 | 28.2808 | 28.2664 | 28.2227 | 27.8821 | 27.3252 | 26.8252
|  | MILFORD-ON-SEA | SP |  |  | 29.2097 | 29.2084 | 29.2069 | 29.2054 | 29.2036 | 29.2017 | 29.1991 | 29.1965 | 29.1932 | 29.1902 | 29.1813 | 29.167 | 29.1535 | 29.1407 | 27.7967 | 27.7943 | 27.7915 | 27.7888 | 27.7854 | 27.782 | 27.7773 | 27.7724 | 27.7663 | 27.7606 | 27.7444 | 27.7179 | 27.6929 | 27.6694 | 28.4012 | 28.4001 | 28.3988 | 28.3976 | 28.396 | 28.3944 | 28.3922 | 28.3899 | 28.3871 | 28.3844 | 28.3768 | 28.3644 | 28.3528 | 28.3418
MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood | MINIMUM HEADROOM | SU 14691 05633 | YES | 16.1767 | 16.1767 | 16.1767 | 26.4567 | 26.4405 | 26.4237 | 26.4063 | 26.3881 | 26.3606 | 26.3568 | 26.3438 | 26.3223 | 25.8558 | 25.0621 | 11.9894 | 11.9894 | 11.9894 | 24.0694 | 24.0532 | 24.0365 | 24.019 | 23.9963 | 23.9593 | 23.9463 | 23.4762 | 22.5303 | 21.5311 | 20.6059 | 15.1338 | 15.1338 | 15.1338 | 24.2138 | 24.1976 | 24.1809 | 24.1634 | 24.1453 | 24.1178 | 24.114 | 24.1009 | 23.9156 | 22.9153 | 21.9792
|  | Mill Lane, Ringwood | CT |  |  | 16.1767 | 16.1767 | 16.1767 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.1397 | 25.3492 | 11.9894 | 11.9894 | 11.9894 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0606 | 24.0513 | 23.7059 | 22.7815 | 21.8316 | 20.9097 | 15.1338 | 15.1338 | 15.1338 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.1665 | 23.2172 | 22.2843
|  | Mill Lane, Ringwood | LW |  |  | 16.1767 | 16.1767 | 16.1767 | 26.4567 | 26.4405 | 26.4237 | 26.4063 | 26.3881 | 26.3606 | 26.3568 | 26.3438 | 26.3223 | 25.8558 | 25.0621 | 11.9894 | 11.9894 | 11.9894 | 24.0694 | 24.0532 | 24.0365 | 24.019 | 23.9963 | 23.9593 | 23.9463 | 23.4762 | 22.5303 | 21.5311 | 20.6059 | 15.1338 | 15.1338 | 15.1338 | 24.2138 | 24.1976 | 24.1809 | 24.1634 | 24.1453 | 24.1178 | 24.114 | 24.1009 | 23.9156 | 22.9153 | 21.9792
|  | Mill Lane, Ringwood | ST |  |  | 16.1767 | 16.1767 | 16.1767 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 11.9894 | 11.9894 | 11.9894 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0633 | 24.0459 | 23.5421 | 22.9293 | 22.3303 | 15.1338 | 15.1338 | 15.1338 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 23.7162
|  | Mill Lane, Ringwood | SP |  |  | 16.1767 | 16.1767 | 16.1767 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 26.4567 | 11.9894 | 11.9894 | 11.9894 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0694 | 24.0615 | 24.0521 | 15.1338 | 15.1338 | 15.1338 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138 | 24.2138
COWLEY GSP | DRAYTON BSP | MILTON | MINIMUM HEADROOM | SU 49992 92060 | NO | 36.6669 | 45.4533 | 45.4397 | 44.6099 | 44.2835 | 43.9466 | 43.5953 | 43.231 | 42.7081 | 42.6172 | 42.3113 | 41.823 | 41.0422 | 40.8416 | 34.7327 | 41.5171 | 41.5008 | 40.6653 | 40.3334 | 39.9889 | 39.6228 | 39.2431 | 38.7053 | 38.5972 | 38.2388 | 36.912 | 35.098 | 33.8854 | 34.9869 | 41.7733 | 41.7597 | 40.9299 | 40.6035 | 40.2666 | 39.9153 | 39.551 | 39.0281 | 38.9372 | 38.6313 | 38.143 | 36.7006 | 35.4911
|  | MILTON | CT |  |  | 36.7322 | 45.5241 | 45.5159 | 45.018 | 44.9765 | 44.9344 | 44.8917 | 44.8481 | 44.8011 | 44.7836 | 44.7288 | 44.0848 | 43.8204 | 43.6541 | 34.7965 | 41.5852 | 41.573 | 41.0664 | 41.0164 | 40.9638 | 40.9086 | 40.8495 | 40.7876 | 40.7529 | 40.6457 | 38.9839 | 37.6868 | 36.5086 | 35.0522 | 41.8441 | 41.8359 | 41.338 | 41.2965 | 41.2544 | 41.2117 | 41.1681 | 41.1211 | 41.1036 | 41.0488 | 40.4048 | 39.29 | 38.1149
|  | MILTON | LW |  |  | 36.6669 | 45.4533 | 45.4397 | 44.6099 | 44.2835 | 43.9466 | 43.5953 | 43.231 | 42.7081 | 42.6172 | 42.3113 | 41.823 | 41.0422 | 40.8416 | 34.7327 | 41.5171 | 41.5008 | 40.6653 | 40.3334 | 39.9889 | 39.6228 | 39.2431 | 38.7053 | 38.5972 | 38.2388 | 36.912 | 35.098 | 33.8854 | 34.9869 | 41.7733 | 41.7597 | 40.9299 | 40.6035 | 40.2666 | 39.9153 | 39.551 | 39.0281 | 38.9372 | 38.6313 | 38.143 | 36.7006 | 35.4911
|  | MILTON | ST |  |  | 36.7649 | 45.5594 | 45.554 | 45.222 | 45.1944 | 45.1662 | 45.1376 | 45.1082 | 45.0762 | 45.0631 | 45.0182 | 44.9476 | 44.8585 | 44.7781 | 34.8313 | 41.6243 | 41.617 | 41.2819 | 41.2503 | 41.2161 | 41.1763 | 41.1354 | 41.0933 | 41.0684 | 40.9872 | 40.8745 | 40.3845 | 39.6471 | 35.0849 | 41.8794 | 41.874 | 41.542 | 41.5144 | 41.4862 | 41.4576 | 41.4282 | 41.3962 | 41.3831 | 41.3382 | 41.2676 | 41.1785 | 41.0981
|  | MILTON | SP |  |  | 36.7975 | 45.5948 | 45.5921 | 45.4261 | 45.4125 | 45.3988 | 45.3852 | 45.3715 | 45.3577 | 45.3515 | 45.3307 | 45.3 | 45.2668 | 45.2204 | 34.8692 | 41.6627 | 41.6598 | 41.4937 | 41.4791 | 41.4638 | 41.4461 | 41.4283 | 41.4098 | 41.399 | 41.3641 | 41.3172 | 41.2703 | 41.211 | 35.1175 | 41.9148 | 41.9121 | 41.7461 | 41.7325 | 41.7188 | 41.7052 | 41.6915 | 41.6777 | 41.6715 | 41.6507 | 41.62 | 41.5868 | 41.5404
MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON | MINIMUM HEADROOM | ST 96164 14520 | YES | 72.1253 | 72.1253 | 72.1253 | 72.1253 | 72.1244 | 72.1225 | 72.1045 | 72.0482 | 71.6786 | 70.9744 | 69.6259 | 68.2411 | 67.0547 | 65.977 | 70.2653 | 70.2331 | 70.2183 | 70.1883 | 70.0798 | 69.9418 | 69.7886 | 69.0738 | 68.2811 | 67.5306 | 66.0938 | 64.6202 | 63.2532 | 62.0035 | 64.5564 | 64.5564 | 64.5564 | 64.5564 | 64.5555 | 64.5536 | 64.5507 | 64.5466 | 64.5384 | 64.537 | 64.5297 | 64.5121 | 64.4778 | 64.4755
|  | MINCHINGTON | CT |  |  | 72.1253 | 72.1253 | 72.1253 | 72.1253 | 72.125 | 72.1245 | 72.1045 | 72.0482 | 71.6786 | 70.9744 | 69.6259 | 68.2411 | 67.0547 | 65.977 | 70.2653 | 70.2331 | 70.2183 | 70.1883 | 70.0798 | 69.9418 | 69.7886 | 69.0738 | 68.2811 | 67.5306 | 66.0938 | 64.6202 | 63.2532 | 62.0035 | 64.5564 | 64.5564 | 64.5564 | 64.5564 | 64.5562 | 64.5556 | 64.5549 | 64.5537 | 64.5513 | 64.5508 | 64.5485 | 64.5289 | 64.5071 | 64.5003
|  | MINCHINGTON | LW |  |  | 72.1253 | 72.1253 | 72.1253 | 72.1253 | 72.1244 | 72.1225 | 72.1182 | 72.0589 | 71.8819 | 71.1767 | 69.8233 | 68.4417 | 67.2428 | 66.1695 | 70.2668 | 70.2356 | 70.2222 | 70.1982 | 70.1154 | 69.9866 | 69.8391 | 69.2972 | 68.4986 | 67.7472 | 66.3054 | 64.8342 | 63.4763 | 62.2309 | 64.5564 | 64.5564 | 64.5564 | 64.5564 | 64.5555 | 64.5536 | 64.5507 | 64.5466 | 64.5384 | 64.537 | 64.5297 | 64.5121 | 64.4778 | 64.4755
|  | MINCHINGTON | ST |  |  | 72.1253 | 72.1253 | 72.1253 | 72.1253 | 72.1251 | 72.1247 | 72.1241 | 72.1233 | 72.1077 | 72.067 | 71.7295 | 70.7897 | 70.0151 | 69.3162 | 70.269 | 70.2623 | 70.232 | 70.2183 | 70.2014 | 70.1391 | 70.0412 | 69.9291 | 69.804 | 69.3425 | 68.3356 | 67.3345 | 66.5105 | 65.7664 | 64.5564 | 64.5564 | 64.5564 | 64.5564 | 64.5562 | 64.5559 | 64.5553 | 64.5544 | 64.5525 | 64.5516 | 64.5467 | 64.5402 | 64.5175 | 64.5092
|  | MINCHINGTON | SP |  |  | 72.1253 | 72.1253 | 72.1253 | 72.1253 | 72.1253 | 72.1253 | 72.1252 | 72.1252 | 72.1251 | 72.1248 | 72.123 | 72.1216 | 72.1148 | 72.0922 | 70.2723 | 70.269 | 70.2434 | 70.2381 | 70.231 | 70.2214 | 70.2106 | 70.1987 | 70.1659 | 70.1182 | 70.0246 | 69.9318 | 69.8531 | 69.7836 | 64.5564 | 64.5564 | 64.5564 | 64.5564 | 64.5564 | 64.5564 | 64.5564 | 64.5564 | 64.5563 | 64.556 | 64.5542 | 64.5528 | 64.546 | 64.5394
MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE | MINIMUM HEADROOM | SU 01647 91932 | NO | 6.114 | 6.114 | 6.114 | 6.114 | 6.0194 | 5.9231 | 5.8253 | 5.7231 | 5.5655 | 5.5456 | 5.4359 | 5.0162 | 4.5775 | 4.3721 | 5 | 5 | 5 | 5 | 4.9053 | 4.8091 | 4.7112 | 4.609 | 4.4515 | 4.4315 | 4.3674 | 4.0713 | 3.7607 | 3.681 | 5.5309 | 5.5289 | 5.5262 | 5.5205 | 5.4204 | 5.3186 | 5.2153 | 5.0902 | 4.91 | 4.8657 | 4.7166 | 4.2685 | 3.8005 | 3.5663
|  | MINETY VILLAGE | CT |  |  | 6.114 | 6.114 | 6.114 | 6.114 | 6.0194 | 5.9231 | 5.8253 | 5.7231 | 5.5655 | 5.5456 | 5.4359 | 5.0162 | 4.5775 | 4.3721 | 5 | 5 | 5 | 5 | 4.9053 | 4.8091 | 4.7112 | 4.609 | 4.4515 | 4.4315 | 4.3674 | 4.0713 | 3.7607 | 3.681 | 5.5309 | 5.5289 | 5.5262 | 5.5205 | 5.4204 | 5.3186 | 5.2153 | 5.0902 | 4.91 | 4.8657 | 4.7166 | 4.2685 | 3.8005 | 3.5663
|  | MINETY VILLAGE | LW |  |  | 6.114 | 6.114 | 6.114 | 6.114 | 6.0534 | 5.9908 | 5.9255 | 5.8578 | 5.7549 | 5.7406 | 5.628 | 5.4313 | 5.1192 | 4.9825 | 5 | 5 | 5 | 5 | 4.9394 | 4.8768 | 4.8114 | 4.7437 | 4.6408 | 4.6266 | 4.5777 | 4.5047 | 4.3206 | 4.3099 | 5.5309 | 5.5289 | 5.5262 | 5.5205 | 5.4544 | 5.3863 | 5.2979 | 5.2073 | 5.0818 | 5.0432 | 4.9045 | 4.6795 | 4.338 | 4.1725
|  | MINETY VILLAGE | ST |  |  | 6.114 | 6.114 | 6.114 | 6.114 | 6.0547 | 5.9944 | 5.9328 | 5.8692 | 5.7708 | 5.7374 | 5.6309 | 5.4761 | 5.0867 | 4.9159 | 5 | 5 | 5 | 5 | 4.9406 | 4.8803 | 4.8188 | 4.7552 | 4.6568 | 4.6234 | 4.5168 | 4.4312 | 4.1242 | 4.0354 | 5.5319 | 5.5306 | 5.5291 | 5.5266 | 5.4641 | 5.4 | 5.3282 | 5.2545 | 5.1406 | 5.0906 | 4.9354 | 4.7514 | 4.3431 | 4.1535
|  | MINETY VILLAGE | SP |  |  | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 6.114 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5.5332 | 5.533 | 5.5328 | 5.5326 | 5.5318 | 5.5307 | 5.5267 | 5.5229 | 5.5178 | 5.5113 | 5.4926 | 5.4624 | 5.4336 | 5.4054
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER | MINIMUM HEADROOM | SU 62236 64103 | YES | 16.9802 | 16.9736 | -38.3304 | -38.3506 | -38.5633 | -38.8922 | -39.1233 | -39.4083 | -39.8023 | -40.0689 | -40.9769 | -41.8705 | -42.6638 | -42.9586 | 16.1157 | 16.1084 | -39.1965 | -39.2185 | -39.3756 | -39.7536 | -40.0123 | -40.3299 | -40.7624 | -41.0715 | -42.1188 | -43.1237 | -43.9684 | -44.3097 | 16.2262 | 16.1715 | -39.2507 | -39.5274 | -39.8561 | -40.2331 | -40.4913 | -40.8082 | -41.24 | -41.5482 | -42.5927 | -43.5953 | -44.439 | -44.7794
|  | MORTIMER | CT |  |  | 16.9817 | 16.9761 | 16.9682 | 16.9511 | 16.872 | 16.6185 | 16.348 | 16.1406 | 15.8788 | 15.6329 | 14.8149 | 13.9232 | 13.3429 | 12.9999 | 16.1173 | 16.1112 | 16.1026 | 16.0838 | 16.0575 | 15.7833 | 15.4675 | 15.2274 | 14.9272 | 14.6388 | 13.6814 | 12.6785 | 12.0469 | 11.6573 | 16.2278 | 16.2063 | 16.098 | 15.862 | 15.599 | 15.3033 | 14.9884 | 14.749 | 14.4495 | 14.162 | 13.2074 | 12.2067 | 11.5761 | 11.1874
|  | MORTIMER | LW |  |  | 16.9802 | 16.9736 | -38.3304 | -38.3506 | -38.5633 | -38.8922 | -39.1233 | -39.4083 | -39.8023 | -40.0689 | -40.9769 | -41.8705 | -42.6638 | -42.9586 | 16.1157 | 16.1084 | -39.1965 | -39.2185 | -39.3756 | -39.7536 | -40.0123 | -40.3299 | -40.7624 | -41.0715 | -42.1188 | -43.1237 | -43.9684 | -44.3097 | 16.2262 | 16.1715 | -39.2507 | -39.5274 | -39.8561 | -40.2331 | -40.4913 | -40.8082 | -41.24 | -41.5482 | -42.5927 | -43.5953 | -44.439 | -44.7794
|  | MORTIMER | ST |  |  | 16.982 | 16.9769 | 16.9705 | 16.959 | 16.9399 | 16.7831 | 16.6575 | 16.5067 | 16.3267 | 16.1478 | 15.517 | 14.9861 | 14.5004 | 14.2297 | 16.1176 | 16.1121 | 16.1051 | 16.0924 | 16.072 | 15.9763 | 15.8306 | 15.6562 | 15.4504 | 15.2424 | 14.5122 | 13.9027 | 13.3837 | 13.0827 | 16.2282 | 16.2176 | 16.1298 | 15.9704 | 15.7607 | 15.4957 | 15.3503 | 15.1764 | 14.9712 | 14.7637 | 14.0356 | 13.4276 | 12.9093 | 12.6089
|  | MORTIMER | SP |  |  | 16.9872 | 16.9862 | 16.9849 | 16.9828 | 16.978 | 16.972 | 16.9674 | 16.962 | 16.9546 | 16.9413 | 16.8425 | 16.6295 | 16.3905 | 16.1669 | 16.1233 | 16.1222 | 16.1208 | 16.1186 | 16.1133 | 16.1067 | 16.1018 | 16.096 | 16.0881 | 16.0742 | 16.009 | 15.8096 | 15.5581 | 15.324 | 16.2339 | 16.2328 | 16.2313 | 16.2291 | 16.2238 | 16.1558 | 16.1009 | 16.0384 | 15.962 | 15.8779 | 15.5732 | 15.3292 | 15.078 | 14.8441
MANNINGTON GSP | SALISBURY | NETHERHAMPTON | MINIMUM HEADROOM | SU 12478 29102 | YES | 17.936 | 17.936 | 17.936 | 17.936 | 17.8843 | 17.8307 | 17.7751 | 17.7157 | 17.6206 | 17.608 | 17.5633 | 17.3109 | 17.0107 | 16.8836 | 13.6809 | 13.6809 | 13.6809 | 13.6809 | 13.6292 | 13.5755 | 13.5093 | 13.3397 | 13.1364 | 13.0076 | 12.6186 | 11.7823 | 10.8759 | 10.2026 | 13.878 | 13.878 | 13.878 | 13.878 | 13.8263 | 13.7727 | 13.7171 | 13.6577 | 13.5626 | 13.5501 | 13.341 | 12.5133 | 11.6157 | 10.9513
|  | NETHERHAMPTON | CT |  |  | 17.936 | 17.936 | 17.936 | 17.936 | 17.8843 | 17.8307 | 17.7751 | 17.7157 | 17.6206 | 17.608 | 17.5633 | 17.3109 | 17.0107 | 16.8836 | 13.6809 | 13.6809 | 13.6809 | 13.6809 | 13.6292 | 13.5755 | 13.5093 | 13.3397 | 13.1364 | 13.0076 | 12.6186 | 11.7823 | 10.8759 | 10.2026 | 13.878 | 13.878 | 13.878 | 13.878 | 13.8263 | 13.7727 | 13.7171 | 13.6577 | 13.5626 | 13.5501 | 13.341 | 12.5133 | 11.6157 | 10.9513
|  | NETHERHAMPTON | LW |  |  | 17.936 | 17.936 | 17.936 | 17.936 | 17.932 | 17.9236 | 17.9106 | 17.8924 | 17.856 | 17.8497 | 17.8177 | 17.7397 | 17.5875 | 17.5772 | 13.6809 | 13.6809 | 13.6809 | 13.6809 | 13.6768 | 13.6685 | 13.6554 | 13.6373 | 13.5664 | 13.4439 | 13.0674 | 12.4058 | 11.6473 | 11.0397 | 13.878 | 13.878 | 13.878 | 13.878 | 13.874 | 13.8657 | 13.8526 | 13.8345 | 13.798 | 13.7917 | 13.7597 | 13.1339 | 12.3843 | 11.7856
|  | NETHERHAMPTON | ST |  |  | 17.936 | 17.936 | 17.936 | 17.936 | 17.9352 | 17.9335 | 17.9309 | 17.9271 | 17.9186 | 17.9146 | 17.8927 | 17.864 | 17.7633 | 17.7267 | 13.6809 | 13.6809 | 13.6809 | 13.6809 | 13.68 | 13.6783 | 13.6757 | 13.672 | 13.6635 | 13.6594 | 13.6169 | 13.1984 | 12.7063 | 12.2819 | 13.878 | 13.878 | 13.878 | 13.878 | 13.8772 | 13.8755 | 13.8729 | 13.8691 | 13.8606 | 13.8566 | 13.8347 | 13.806 | 13.4303 | 13.0117
|  | NETHERHAMPTON | SP |  |  | 17.936 | 17.936 | 17.936 | 17.936 | 17.936 | 17.9359 | 17.9358 | 17.9357 | 17.9353 | 17.9339 | 17.926 | 17.9197 | 17.8897 | 17.8604 | 13.6809 | 13.6809 | 13.6809 | 13.6809 | 13.6808 | 13.6808 | 13.6807 | 13.6805 | 13.6801 | 13.6788 | 13.6709 | 13.6646 | 13.6346 | 13.6053 | 13.878 | 13.878 | 13.878 | 13.878 | 13.878 | 13.8779 | 13.8778 | 13.8777 | 13.8773 | 13.8759 | 13.868 | 13.8618 | 13.8317 | 13.8024
BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV | MINIMUM HEADROOM | SU 47615 12025 | YES | 14.2514 | 14.2514 | 14.2514 | 14.2514 | 14.2496 | 14.2478 | 14.2451 | 14.2406 | 14.2316 | 14.2301 | 14.2067 | 14.1934 | 13.9215 | 13.6147 | 10.2382 | 10.2365 | 10.2338 | 10.2281 | 10.2211 | 10.2122 | 10.2036 | 10.1923 | 10.1752 | 10.1662 | 10.1233 | 9.8 | 9.3941 | 9.0387 | 10.2727 | 10.2727 | 10.2727 | 10.2727 | 10.2709 | 10.2692 | 10.2664 | 10.262 | 10.2529 | 10.2514 | 10.1611 | 9.7512 | 9.3388 | 8.9773
|  | NETLEY COMMON 11kV | CT |  |  | 14.2514 | 14.2514 | 14.2514 | 14.2514 | 14.2511 | 14.2505 | 14.2497 | 14.2485 | 14.2457 | 14.2453 | 14.2427 | 14.2212 | 13.9882 | 13.6766 | 10.2386 | 10.2371 | 10.2347 | 10.2297 | 10.2241 | 10.2174 | 10.21 | 10.2019 | 10.1911 | 10.1832 | 10.1566 | 9.8585 | 9.4662 | 9.1061 | 10.2727 | 10.2727 | 10.2727 | 10.2727 | 10.2724 | 10.2719 | 10.271 | 10.2698 | 10.2671 | 10.2666 | 10.2224 | 9.8104 | 9.4117 | 9.0453
|  | NETLEY COMMON 11kV | LW |  |  | 14.2514 | 14.2514 | 14.2514 | 14.2514 | 14.2504 | 14.2484 | 14.2451 | 14.2406 | 14.2316 | 14.2301 | 14.2221 | 14.2028 | 13.9215 | 13.6147 | 10.2382 | 10.2365 | 10.2338 | 10.2281 | 10.2211 | 10.2122 | 10.2036 | 10.1923 | 10.1752 | 10.1662 | 10.1233 | 9.8 | 9.3941 | 9.0387 | 10.2727 | 10.2727 | 10.2727 | 10.2727 | 10.2717 | 10.2697 | 10.2664 | 10.262 | 10.2529 | 10.2514 | 10.1611 | 9.7512 | 9.3388 | 8.9773
|  | NETLEY COMMON 11kV | ST |  |  | 14.2514 | 14.2514 | 14.2514 | 14.2514 | 14.2512 | 14.2508 | 14.2501 | 14.2492 | 14.2471 | 14.2461 | 14.2407 | 14.2336 | 14.2087 | 14.1996 | 10.2392 | 10.2383 | 10.2368 | 10.2343 | 10.2308 | 10.2259 | 10.2217 | 10.2161 | 10.2085 | 10.2025 | 10.1875 | 10.1687 | 10.1241 | 9.9966 | 10.2727 | 10.2727 | 10.2727 | 10.2727 | 10.2725 | 10.2721 | 10.2715 | 10.2705 | 10.2684 | 10.2674 | 10.262 | 10.2549 | 10.193 | 9.9513
|  | NETLEY COMMON 11kV | SP |  |  | 14.2514 | 14.2514 | 14.2514 | 14.2514 | 14.2496 | 14.2478 | 14.2461 | 14.2442 | 14.2414 | 14.2333 | 14.2067 | 14.1934 | 14.149 | 14.1109 | 10.2403 | 10.2402 | 10.2398 | 10.2394 | 10.2364 | 10.2332 | 10.23 | 10.2264 | 10.2213 | 10.2112 | 10.1808 | 10.163 | 10.1145 | 10.0726 | 10.2727 | 10.2727 | 10.2727 | 10.2727 | 10.2709 | 10.2692 | 10.2674 | 10.2656 | 10.2627 | 10.2546 | 10.228 | 10.2147 | 10.1704 | 10.1322
MANNINGTON GSP | ARNEWOOD | NEW MILTON | MINIMUM HEADROOM | SZ 23049 94942 | YES | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.5728 | 40.39 | 40.2042 | 40.0102 | 39.711 | 39.6731 | 39.5514 | 38.9892 | 37.5978 | 35.1374 | 30.6314 | 30.6262 | 30.6204 | 30.6102 | 30.4247 | 30.2325 | 30.0372 | 29.8274 | 29.5125 | 29.4581 | 29.2853 | 27.9487 | 24.6872 | 21.8965 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.5352 | 30.3524 | 30.1666 | 29.9726 | 29.6734 | 29.6355 | 29.449 | 28.753 | 25.5057 | 22.7032
|  | NEW MILTON | CT |  |  | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.5728 | 40.39 | 40.2042 | 40.0102 | 39.711 | 39.6731 | 39.5514 | 38.9892 | 37.5978 | 35.1374 | 30.632 | 30.6274 | 30.6222 | 30.6134 | 30.4247 | 30.2325 | 30.0372 | 29.8274 | 29.5125 | 29.4581 | 29.2853 | 27.9487 | 24.6872 | 21.8965 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.5352 | 30.3524 | 30.1666 | 29.9726 | 29.6734 | 29.6355 | 29.449 | 28.753 | 25.5057 | 22.7032
|  | NEW MILTON | LW |  |  | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.713 | 40.6722 | 40.6295 | 40.5853 | 40.5182 | 40.5089 | 40.4771 | 40.4294 | 39.3004 | 36.9988 | 30.6314 | 30.6262 | 30.6204 | 30.6102 | 30.5604 | 30.5089 | 30.4497 | 30.3897 | 30.3069 | 30.2811 | 30.1982 | 29.1084 | 26.3544 | 23.7225 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.6754 | 30.6346 | 30.5919 | 30.5477 | 30.4806 | 30.4553 | 30.3583 | 29.9375 | 27.1716 | 24.5279
|  | NEW MILTON | ST |  |  | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.6716 | 30.6322 | 30.6281 | 30.6238 | 30.6176 | 30.61 | 30.6006 | 30.5904 | 30.5808 | 30.5701 | 30.5588 | 30.5241 | 30.4525 | 29.5414 | 27.8592 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.6981 | 30.6068 | 30.371 | 28.6812
|  | NEW MILTON | SP |  |  | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 40.7525 | 30.6356 | 30.6343 | 30.6332 | 30.6325 | 30.6307 | 30.6285 | 30.6253 | 30.6223 | 30.6186 | 30.6142 | 30.6007 | 30.5721 | 30.5387 | 30.5046 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.7149 | 30.6733
FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT | MINIMUM HEADROOM | SZ 50076 89544 | NO | 39.776 | 39.7653 | 39.7545 | 39.096 | 39.0039 | 38.8954 | 38.6598 | 38.421 | 38.177 | 37.9471 | 37.2369 | 35.9467 | 34.5808 | 33.1937 | 34.9729 | 34.9608 | 34.9483 | 34.2863 | 34.2283 | 34.1688 | 34.0985 | 34.0273 | 33.9531 | 33.9156 | 33.2967 | 31.8906 | 30.3982 | 28.8856 | 35.7459 | 35.7351 | 35.7243 | 35.0659 | 35.0113 | 34.9561 | 34.9002 | 34.8436 | 34.7843 | 34.7618 | 34.6923 | 34.5729 | 33.2591 | 31.6438
|  | NEWPORT | CT |  |  | 39.8279 | 39.8214 | 39.8149 | 39.4198 | 39.3545 | 39.2699 | 39.1784 | 38.9632 | 38.7445 | 38.5378 | 37.8691 | 36.2133 | 34.7538 | 33.3645 | 35.0248 | 35.0171 | 35.0089 | 34.6104 | 34.5745 | 34.5376 | 34.5 | 34.4523 | 34.4035 | 34.3753 | 33.9442 | 32.1724 | 30.5863 | 29.0717 | 35.7977 | 35.7912 | 35.7847 | 35.3897 | 35.3571 | 35.3244 | 35.2915 | 35.2584 | 35.2244 | 35.2112 | 35.1708 | 34.6857 | 33.4598 | 31.8425
|  | NEWPORT | LW |  |  | 39.776 | 39.7653 | 39.7545 | 39.096 | 39.0039 | 38.8954 | 38.6598 | 38.421 | 38.177 | 37.9471 | 37.2369 | 35.9467 | 34.5808 | 33.1937 | 34.9729 | 34.9608 | 34.9483 | 34.2863 | 34.2283 | 34.1688 | 34.0985 | 34.0273 | 33.9531 | 33.9156 | 33.2967 | 31.8906 | 30.3982 | 28.8856 | 35.7459 | 35.7351 | 35.7243 | 35.0659 | 35.0113 | 34.9561 | 34.9002 | 34.8436 | 34.7843 | 34.7618 | 34.6923 | 34.5729 | 33.2591 | 31.6438
|  | NEWPORT | ST |  |  | 39.8538 | 39.8494 | 39.8451 | 39.5818 | 39.5427 | 39.4681 | 39.3246 | 39.1801 | 39.0314 | 38.8945 | 38.4673 | 37.6304 | 36.7591 | 35.8887 | 35.0506 | 35.045 | 35.0392 | 34.7733 | 34.7485 | 34.7224 | 34.6907 | 34.6588 | 34.6258 | 34.6063 | 34.5479 | 33.6636 | 32.71 | 31.7587 | 35.8236 | 35.8193 | 35.815 | 35.5516 | 35.5299 | 35.508 | 35.4861 | 35.4639 | 35.4411 | 35.4319 | 35.4027 | 35.3554 | 35.3147 | 34.6451
|  | NEWPORT | SP |  |  | 39.8797 | 39.8775 | 39.8754 | 39.7437 | 39.7329 | 39.7221 | 39.7113 | 39.7004 | 39.6681 | 39.6139 | 39.4581 | 39.1812 | 38.8803 | 38.5451 | 35.078 | 35.0756 | 35.0732 | 34.9414 | 34.93 | 34.9182 | 34.905 | 34.8917 | 34.8777 | 34.8692 | 34.8437 | 34.8008 | 34.7616 | 34.6473 | 35.8495 | 35.8473 | 35.8452 | 35.7135 | 35.7027 | 35.6919 | 35.6811 | 35.6703 | 35.6594 | 35.6549 | 35.6408 | 35.6183 | 35.6009 | 35.5729
BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY | MINIMUM HEADROOM | SU 93221 52894 | YES | 39.525 | 39.5077 | 39.4905 | 38.4375 | 38.0729 | 37.6979 | 37.3084 | 36.9063 | 36.3372 | 36.2354 | 35.8973 | 35.3633 | 34.083 | 32.6378 | 35.9571 | 35.9382 | 35.9174 | 34.8579 | 34.4862 | 34.1039 | 33.6977 | 33.2799 | 32.6952 | 32.5769 | 32.1893 | 30.8703 | 28.5326 | 26.7517 | 37.6147 | 37.5975 | 37.5802 | 36.5273 | 36.1626 | 35.7876 | 35.3982 | 34.9961 | 34.427 | 34.3252 | 33.9871 | 33.4531 | 31.3078 | 29.6012
|  | NORMANDY | CT |  |  | 39.6078 | 39.5975 | 39.5871 | 38.9553 | 38.9031 | 38.8505 | 38.7975 | 38.744 | 38.6883 | 38.6669 | 38.601 | 37.8147 | 37.1433 | 35.7361 | 36.0399 | 36.028 | 36.0141 | 35.3757 | 35.3164 | 35.2566 | 35.1965 | 35.1273 | 35.056 | 35.0181 | 34.9027 | 33.5261 | 31.638 | 29.8926 | 37.6976 | 37.6872 | 37.6769 | 37.0451 | 36.9929 | 36.9403 | 36.8873 | 36.8337 | 36.778 | 36.7566 | 36.6907 | 35.9045 | 34.3983 | 32.7346
|  | NORMANDY | LW |  |  | 39.525 | 39.5077 | 39.4905 | 38.4375 | 38.0729 | 37.6979 | 37.3084 | 36.9063 | 36.3372 | 36.2354 | 35.8973 | 35.3633 | 34.083 | 32.6378 | 35.9571 | 35.9382 | 35.9174 | 34.8579 | 34.4862 | 34.1039 | 33.6977 | 33.2799 | 32.6952 | 32.5769 | 32.1893 | 30.8703 | 28.5326 | 26.7517 | 37.6147 | 37.5975 | 37.5802 | 36.5273 | 36.1626 | 35.7876 | 35.3982 | 34.9961 | 34.427 | 34.3252 | 33.9871 | 33.4531 | 31.3078 | 29.6012
|  | NORMANDY | ST |  |  | 39.6493 | 39.6424 | 39.6354 | 39.2143 | 39.1794 | 39.1443 | 39.1089 | 39.073 | 39.0355 | 39.0202 | 38.971 | 38.8917 | 38.8144 | 38.7255 | 36.0806 | 36.0716 | 36.0612 | 35.6344 | 35.5926 | 35.5493 | 35.5046 | 35.4604 | 35.4122 | 35.3856 | 35.3028 | 35.1733 | 34.6572 | 33.5642 | 37.739 | 37.7321 | 37.7252 | 37.304 | 37.2692 | 37.2341 | 37.1986 | 37.1628 | 37.1252 | 37.11 | 37.0607 | 36.9815 | 36.9042 | 36.2724
|  | NORMANDY | SP |  |  | 39.6907 | 39.6872 | 39.6838 | 39.4732 | 39.4559 | 39.4386 | 39.4213 | 39.404 | 39.3866 | 39.3792 | 39.3557 | 39.3189 | 39.2875 | 39.2391 | 36.1244 | 36.1207 | 36.1163 | 35.9046 | 35.8852 | 35.8656 | 35.8454 | 35.8256 | 35.8051 | 35.7933 | 35.7568 | 35.7009 | 35.6518 | 35.5868 | 37.7804 | 37.777 | 37.7735 | 37.5629 | 37.5457 | 37.5284 | 37.5111 | 37.4938 | 37.4764 | 37.469 | 37.4455 | 37.4087 | 37.3773 | 37.3289
NURSLING GSP | ROWNHAMS | NORTH BADDESLEY | MINIMUM HEADROOM | SU 38080 20568 | YES | 7.0816 | 7.0816 | 7.0816 | 7.0816 | 7.0387 | 6.9949 | 6.9501 | 6.9029 | 6.8294 | 6.7771 | 6.4881 | 6.1441 | 5.8012 | 5.6173 | 4.9796 | 4.9648 | 4.9328 | 4.8715 | 4.7675 | 4.6567 | 4.5422 | 4.4347 | 4.2926 | 4.2089 | 3.9504 | 3.6288 | 3.3033 | 3.1357 | 5.3048 | 5.3048 | 5.3048 | 5.3048 | 5.2523 | 5.1201 | 4.9833 | 4.8565 | 4.6925 | 4.585 | 4.2538 | 3.8787 | 3.5114 | 3.305
|  | NORTH BADDESLEY | CT |  |  | 7.0816 | 7.0816 | 7.0816 | 7.0816 | 7.0387 | 6.9949 | 6.9501 | 6.9029 | 6.8294 | 6.7771 | 6.4881 | 6.1441 | 5.8012 | 5.6173 | 4.98 | 4.9655 | 4.9339 | 4.8736 | 4.7675 | 4.6567 | 4.5422 | 4.4347 | 4.2926 | 4.2089 | 3.9504 | 3.6288 | 3.3033 | 3.1357 | 5.3048 | 5.3048 | 5.3048 | 5.3048 | 5.2523 | 5.1201 | 4.9833 | 4.8565 | 4.6925 | 4.585 | 4.2538 | 3.8787 | 3.5114 | 3.305
|  | NORTH BADDESLEY | LW |  |  | 7.0816 | 7.0816 | 7.0816 | 7.0816 | 7.0806 | 7.0786 | 7.0755 | 7.0711 | 7.0623 | 7.0327 | 6.7673 | 6.5586 | 6.3738 | 6.2339 | 4.9796 | 4.9648 | 4.9328 | 4.8715 | 4.8064 | 4.7366 | 4.6806 | 4.6159 | 4.5386 | 4.4627 | 4.2278 | 4.0415 | 3.8742 | 3.7506 | 5.3048 | 5.3048 | 5.3048 | 5.3048 | 5.2903 | 5.1988 | 5.1259 | 5.0418 | 4.9426 | 4.843 | 4.5354 | 4.2955 | 4.0864 | 3.924
|  | NORTH BADDESLEY | ST |  |  | 7.0816 | 7.0816 | 7.0816 | 7.0816 | 7.0814 | 7.081 | 7.0804 | 7.0794 | 7.0774 | 7.0764 | 7.022 | 6.8843 | 6.764 | 6.6662 | 4.9818 | 4.9691 | 4.9452 | 4.906 | 4.8581 | 4.8008 | 4.7631 | 4.7202 | 4.6721 | 4.6202 | 4.4545 | 4.3323 | 4.2234 | 4.136 | 5.3048 | 5.3048 | 5.3048 | 5.3048 | 5.3046 | 5.2827 | 5.2332 | 5.1768 | 5.1141 | 5.0458 | 4.8289 | 4.6698 | 4.5338 | 4.4213
|  | NORTH BADDESLEY | SP |  |  | 7.0816 | 7.0816 | 7.0816 | 7.0816 | 7.0736 | 7.0659 | 7.058 | 7.0501 | 7.0376 | 7.0029 | 6.8918 | 6.8383 | 6.6673 | 6.5233 | 4.9967 | 4.9951 | 4.9878 | 4.9782 | 4.9549 | 4.93 | 4.9073 | 4.883 | 4.8511 | 4.7962 | 4.6216 | 4.5225 | 4.3191 | 4.1463 | 5.3048 | 5.3048 | 5.3048 | 5.3048 | 5.2969 | 5.2891 | 5.2813 | 5.2733 | 5.2609 | 5.2261 | 5.1067 | 4.9931 | 4.7793 | 4.5973
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM | MINIMUM HEADROOM | SU 56427 07430 | YES | 25.1698 | 25.1698 | 25.1698 | 25.1698 | 25.0951 | 25.0187 | 24.9403 | 24.8586 | 24.7309 | 24.6869 | 24.5416 | 24.4188 | 24.0415 | 23.9204 | 19.4145 | 19.4093 | 19.4037 | 19.3949 | 19.3309 | 19.2504 | 19.167 | 19.0805 | 18.9481 | 18.8992 | 18.7394 | 18.0031 | 17.0865 | 16.2819 | 19.5681 | 19.5681 | 19.5681 | 19.5681 | 19.4934 | 19.417 | 19.3386 | 19.257 | 19.1293 | 19.0739 | 18.5786 | 17.7407 | 16.842 | 16.0582
|  | NORTH FAREHAM | CT |  |  | 25.1698 | 25.1698 | 25.1698 | 25.1698 | 25.16 | 25.1495 | 25.1382 | 25.1256 | 25.1044 | 25.1015 | 25.0895 | 25.0135 | 24.9307 | 24.9059 | 19.4155 | 19.411 | 19.4064 | 19.3997 | 19.3834 | 19.3661 | 19.348 | 19.3284 | 19.3004 | 19.2902 | 19.0778 | 18.2195 | 17.3347 | 16.5128 | 19.5681 | 19.5681 | 19.5681 | 19.5681 | 19.5584 | 19.5478 | 19.5366 | 19.524 | 19.4654 | 19.3026 | 18.8198 | 17.958 | 17.085 | 16.2838
|  | NORTH FAREHAM | LW |  |  | 25.1698 | 25.1698 | 25.1698 | 25.1698 | 25.1595 | 25.1465 | 25.1306 | 25.1116 | 25.0779 | 25.0725 | 25.0484 | 24.9958 | 24.8878 | 24.8791 | 19.4145 | 19.4093 | 19.4037 | 19.3949 | 19.376 | 19.3544 | 19.3313 | 19.3053 | 19.2648 | 19.2522 | 18.8376 | 18.0031 | 17.0865 | 16.2819 | 19.5681 | 19.5681 | 19.5681 | 19.5681 | 19.5578 | 19.5449 | 19.529 | 19.4225 | 19.2389 | 19.0739 | 18.5786 | 17.7407 | 16.842 | 16.0582
|  | NORTH FAREHAM | ST |  |  | 25.1698 | 25.1698 | 25.1698 | 25.1698 | 25.0951 | 25.0187 | 24.9403 | 24.8586 | 24.7309 | 24.6869 | 24.5416 | 24.4188 | 24.0415 | 23.9204 | 19.4172 | 19.4143 | 19.4117 | 19.409 | 19.3309 | 19.2504 | 19.167 | 19.0805 | 18.9481 | 18.8992 | 18.7394 | 18.5513 | 17.6664 | 17.0427 | 19.5681 | 19.5681 | 19.5681 | 19.5681 | 19.4934 | 19.417 | 19.3386 | 19.257 | 19.1293 | 19.0853 | 18.94 | 18.2939 | 17.4068 | 16.7808
|  | NORTH FAREHAM | SP |  |  | 25.1698 | 25.1698 | 25.1698 | 25.1698 | 25.1698 | 25.1697 | 25.1697 | 25.1696 | 25.1694 | 25.1686 | 25.1643 | 25.1608 | 25.1444 | 25.1283 | 19.4186 | 19.4172 | 19.4163 | 19.416 | 19.4148 | 19.4132 | 19.4115 | 19.4097 | 19.4075 | 19.4048 | 19.3948 | 19.3823 | 19.3573 | 19.3332 | 19.5681 | 19.5681 | 19.5681 | 19.5681 | 19.5681 | 19.5681 | 19.568 | 19.5679 | 19.5677 | 19.567 | 19.5627 | 19.5592 | 19.5427 | 19.5267
LALEHAM | EAST BEDFONT A | NORTH FELTHAM | MINIMUM HEADROOM | TQ 10987 74875 | YES | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.3755 | 17.3353 | 17.2942 | 17.2518 | 17.1862 | 17.1639 | 17.0928 | 17.0343 | 16.7772 | 15.8388 | 15.5111 | 15.5041 | 15.5023 | 15.4987 | 15.459 | 15.4156 | 15.3675 | 15.3182 | 15.2458 | 15.2162 | 15.1079 | 14.0648 | 12.9018 | 11.8143 | 16.6237 | 16.6167 | 16.6149 | 16.6113 | 16.5716 | 16.5282 | 16.4801 | 16.4307 | 16.3583 | 16.3287 | 16.2359 | 15.4178 | 14.2509 | 13.1596
|  | NORTH FELTHAM | CT |  |  | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.1317 | 16.1988 | 15.5111 | 15.5041 | 15.5023 | 15.4987 | 15.4951 | 15.4915 | 15.4879 | 15.4779 | 15.468 | 15.4573 | 15.3628 | 14.3551 | 13.2626 | 12.1806 | 16.6237 | 16.6167 | 16.6149 | 16.6113 | 16.6077 | 16.6041 | 16.6005 | 16.5905 | 16.5805 | 16.5698 | 16.5376 | 15.7078 | 14.6119 | 13.526
|  | NORTH FELTHAM | LW |  |  | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.3851 | 17.3541 | 17.3218 | 17.2883 | 17.2374 | 17.2304 | 17.2062 | 17.1701 | 16.7772 | 15.8388 | 15.5115 | 15.5049 | 15.5035 | 15.5008 | 15.4681 | 15.4344 | 15.392 | 15.3485 | 15.2877 | 15.27 | 15.1079 | 14.0648 | 12.9018 | 11.8143 | 16.6242 | 16.6175 | 16.6161 | 16.6134 | 16.5807 | 16.547 | 16.5046 | 16.461 | 16.4002 | 16.3824 | 16.3261 | 15.4178 | 14.2509 | 13.1596
|  | NORTH FELTHAM | ST |  |  | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.3755 | 17.3353 | 17.2942 | 17.2518 | 17.1862 | 17.1639 | 17.0928 | 17.0343 | 16.8296 | 16.7703 | 15.5114 | 15.5103 | 15.5034 | 15.5012 | 15.459 | 15.4156 | 15.3675 | 15.3182 | 15.2458 | 15.2162 | 15.1174 | 14.6625 | 13.7495 | 12.9909 | 16.624 | 16.6229 | 16.616 | 16.6139 | 16.5716 | 16.5282 | 16.4801 | 16.4307 | 16.3583 | 16.3287 | 16.2359 | 16.0088 | 15.1023 | 14.3415
|  | NORTH FELTHAM | SP |  |  | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 17.4151 | 15.5126 | 15.5125 | 15.5123 | 15.5122 | 15.5117 | 15.5112 | 15.509 | 15.5067 | 15.5039 | 15.5011 | 15.4927 | 15.4777 | 15.4618 | 15.441 | 16.6253 | 16.6251 | 16.625 | 16.6249 | 16.6244 | 16.6238 | 16.6216 | 16.6194 | 16.6165 | 16.6137 | 16.6053 | 16.5902 | 16.5743 | 16.5587
COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY | MINIMUM HEADROOM | SP 48645 04403 | YES | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.4688 | 37.3795 | 37.2884 | 37.1943 | 37.0488 | 36.9994 | 36.8417 | 36.715 | 36.31 | 36.1845 | 27.7888 | 27.7863 | 27.7819 | 27.7749 | 27.6895 | 27.5951 | 27.4966 | 27.3931 | 27.2341 | 27.1706 | 26.9665 | 26.7675 | 26.2878 | 26.0897 | 25.2364 | 25.2172 | 25.1846 | 25.1325 | 25.0629 | 24.9351 | 24.7882 | 24.6248 | 24.3789 | 24.2237 | 23.7194 | 23.0421 | 22.0585 | 21.3492
|  | NORTH HINKSEY | CT |  |  | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.1769 | 27.7888 | 27.7863 | 27.7819 | 27.7749 | 27.7678 | 27.7603 | 27.7524 | 27.7324 | 27.7126 | 27.6919 | 27.6247 | 27.5191 | 27.1987 | 26.4371 | 25.2364 | 25.2172 | 25.1846 | 25.1325 | 25.0797 | 25.023 | 24.9641 | 24.815 | 24.6669 | 24.5121 | 24.0046 | 23.186 | 22.3006 | 21.422
|  | NORTH HINKSEY | LW |  |  | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.1192 | 27.7888 | 27.7863 | 27.7819 | 27.7749 | 27.7678 | 27.7603 | 27.743 | 27.723 | 27.7032 | 27.6825 | 27.6153 | 27.5097 | 27.1384 | 26.3655 | 25.2364 | 25.2172 | 25.1846 | 25.1325 | 25.0797 | 25.023 | 24.8941 | 24.745 | 24.5969 | 24.4422 | 23.9319 | 23.1134 | 22.2279 | 21.3492
|  | NORTH HINKSEY | ST |  |  | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.4688 | 37.3795 | 37.2884 | 37.1943 | 37.0488 | 36.9994 | 36.8417 | 36.715 | 36.31 | 36.1845 | 27.7898 | 27.788 | 27.7853 | 27.7816 | 27.6895 | 27.5951 | 27.4966 | 27.3931 | 27.2341 | 27.1706 | 26.9665 | 26.7675 | 26.2878 | 26.0897 | 25.2433 | 25.2305 | 25.21 | 25.1827 | 25.0629 | 24.9351 | 24.7882 | 24.6248 | 24.3789 | 24.2237 | 23.7194 | 23.0421 | 22.0585 | 21.3699
|  | NORTH HINKSEY | SP |  |  | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 37.5566 | 27.7909 | 27.7903 | 27.7891 | 27.788 | 27.7863 | 27.7845 | 27.782 | 27.7787 | 27.7752 | 27.7697 | 27.7515 | 27.7227 | 27.6913 | 27.6594 | 25.2521 | 25.2471 | 25.2383 | 25.23 | 25.2179 | 25.2041 | 25.1852 | 25.1611 | 25.1345 | 25.0932 | 24.9578 | 24.7428 | 24.5079 | 24.2697
MINETY GSP | CIRENCESTER BSP | NORTHLEACH | MINIMUM HEADROOM | SP 10557 14251 | NO | 11.982 | 11.982 | 11.982 | 1.4556 | 1.4054 | 1.3538 | 1.3009 | 1.2451 | 1.1576 | 1.1463 | 1.1081 | 0.85426 | 0.23926 | -0.21719 | 9.001 | 8.9958 | 8.989 | -1.5517 | -1.6159 | -1.9029 | -2.1942 | -2.3352 | -2.5071 | -2.6095 | -2.9172 | -3.565 | -4.2437 | -4.7628 | 9.0883 | 9.0883 | 9.0883 | -1.438 | -1.4882 | -1.7131 | -2.0085 | -2.1511 | -2.3244 | -2.4284 | -2.7408 | -3.3966 | -4.0837 | -4.6111
|  | NORTHLEACH | CT |  |  | 11.982 | 11.982 | 11.982 | 1.4556 | 1.4054 | 1.3538 | 1.3009 | 1.2451 | 1.1576 | 1.1463 | 1.1081 | 0.85426 | 0.23926 | -0.21719 | 9.001 | 8.9958 | 8.989 | -1.5517 | -1.6159 | -1.9029 | -2.1942 | -2.3352 | -2.5071 | -2.6095 | -2.9172 | -3.565 | -4.2437 | -4.7628 | 9.0883 | 9.0883 | 9.0883 | -1.438 | -1.4882 | -1.7131 | -2.0085 | -2.1511 | -2.3244 | -2.4284 | -2.7408 | -3.3966 | -4.0837 | -4.6111
|  | NORTHLEACH | LW |  |  | 11.982 | 11.982 | 11.982 | 1.4556 | 1.4539 | 1.4503 | 1.4447 | 1.4369 | 1.4213 | 1.4186 | 1.4048 | 1.3714 | 1.1356 | 0.7241 | 9.0023 | 8.9981 | 8.9925 | -1.5455 | -1.5586 | -1.6082 | -1.6998 | -1.7927 | -1.8927 | -1.9864 | -2.2698 | -2.7582 | -3.3005 | -3.7747 | 9.0883 | 9.0883 | 9.0883 | -1.438 | -1.4397 | -1.4433 | -1.508 | -1.6024 | -1.7039 | -1.7992 | -2.0873 | -2.5837 | -3.1343 | -3.6168
|  | NORTHLEACH | ST |  |  | 11.982 | 11.982 | 11.982 | 11.982 | 11.9727 | 1.4365 | 1.4262 | 1.415 | 1.3966 | 1.3898 | 1.3644 | 1.3387 | 1.2493 | 1.2202 | 9.0044 | 9.0019 | 8.9988 | 8.9937 | 8.978 | -1.5658 | -1.58 | -1.5951 | -1.6168 | -1.6271 | -1.7577 | -2.0875 | -2.4845 | -2.8182 | 9.0883 | 9.0883 | 9.0883 | 9.0883 | 9.079 | -1.4571 | -1.4674 | -1.4786 | -1.4971 | -1.5038 | -1.5656 | -1.9007 | -2.3031 | -2.6421
|  | NORTHLEACH | SP |  |  | 11.982 | 11.982 | 11.982 | 11.982 | 11.9819 | 11.9819 | 11.9819 | 11.9818 | 1.4553 | 1.4547 | 1.4514 | 1.4487 | 1.4358 | 1.4232 | 9.0072 | 9.0068 | 9.0064 | 9.006 | 9.0042 | 9.002 | 9.0006 | 8.9991 | -1.5292 | -1.5312 | -1.5386 | -1.5479 | -1.5674 | -1.5862 | 9.0883 | 9.0883 | 9.0883 | 9.0883 | 9.0883 | 9.0883 | 9.0882 | 9.0882 | -1.4383 | -1.4389 | -1.4423 | -1.445 | -1.4579 | -1.4704
BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE | MINIMUM HEADROOM | SU 72207 71092 | YES | 15.4655 | 15.4617 | 15.4568 | 15.4462 | 15.3111 | 15.1609 | 14.9892 | 14.8129 | 14.5442 | 14.4253 | 14.0571 | 13.6681 | 12.817 | 12.4224 | 11.6622 | 11.6575 | 11.6514 | 11.6385 | 11.5047 | 11.353 | 11.1756 | 10.9936 | 10.718 | 10.5934 | 10.2086 | 9.7929 | 8.9152 | 8.4942 | 11.9029 | 11.8983 | 11.8922 | 11.8793 | 11.7455 | 11.5939 | 11.4166 | 11.2349 | 10.9595 | 10.8352 | 10.4512 | 10.0367 | 9.1604 | 8.7406
|  | NORTHUMBERLAND AVENUE | CT |  |  | 15.4655 | 15.4618 | 15.4568 | 15.4463 | 15.436 | 15.4258 | 15.4156 | 15.3646 | 15.3109 | 15.2528 | 15.082 | 14.8026 | 14.5154 | 14.2332 | 11.6622 | 11.6576 | 11.6515 | 11.6386 | 11.626 | 11.6135 | 11.6011 | 11.5392 | 11.4777 | 11.4113 | 11.2159 | 10.8962 | 10.5678 | 10.2449 | 11.9029 | 11.8983 | 11.8923 | 11.8794 | 11.867 | 11.8545 | 11.8422 | 11.7806 | 11.7195 | 11.6536 | 11.4594 | 11.1416 | 10.8151 | 10.4942
|  | NORTHUMBERLAND AVENUE | LW |  |  | 15.4655 | 15.4617 | 15.4568 | 15.4462 | 15.4197 | 15.3927 | 15.324 | 15.2519 | 15.1707 | 15.1089 | 14.925 | 14.6262 | 14.303 | 14.0179 | 11.6622 | 11.6575 | 11.6514 | 11.6385 | 11.6097 | 11.5804 | 11.5003 | 11.4201 | 11.3312 | 11.2611 | 11.0525 | 10.7135 | 10.349 | 10.0232 | 11.9029 | 11.8983 | 11.8922 | 11.8793 | 11.8506 | 11.8214 | 11.7417 | 11.6619 | 11.5733 | 11.5036 | 11.2963 | 10.9592 | 10.5966 | 10.2729
|  | NORTHUMBERLAND AVENUE | ST |  |  | 15.4675 | 15.4652 | 15.4625 | 15.4578 | 15.3111 | 15.1609 | 14.9892 | 14.8129 | 14.5442 | 14.4253 | 14.0571 | 13.6681 | 12.817 | 12.4224 | 11.6646 | 11.6618 | 11.6584 | 11.6527 | 11.5047 | 11.353 | 11.1756 | 10.9936 | 10.718 | 10.5934 | 10.2086 | 9.7929 | 8.9152 | 8.4942 | 11.9052 | 11.9024 | 11.8991 | 11.8935 | 11.7455 | 11.5939 | 11.4166 | 11.2349 | 10.9595 | 10.8352 | 10.4512 | 10.0367 | 9.1604 | 8.7406
|  | NORTHUMBERLAND AVENUE | SP |  |  | 15.47 | 15.4696 | 15.4692 | 15.4689 | 15.4673 | 15.4655 | 15.4567 | 15.4481 | 15.4369 | 15.4225 | 15.3811 | 15.3116 | 15.2448 | 15.1823 | 11.6676 | 11.6671 | 11.6667 | 11.6663 | 11.6644 | 11.6621 | 11.6514 | 11.6409 | 11.6272 | 11.6096 | 11.5588 | 11.4785 | 11.4021 | 11.3306 | 11.9083 | 11.9078 | 11.9074 | 11.907 | 11.9051 | 11.9028 | 11.8922 | 11.8817 | 11.8681 | 11.8506 | 11.8002 | 11.7203 | 11.6444 | 11.5733
COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD | MINIMUM HEADROOM | SU 68329 86784 | YES | 33.0569 | 33.0511 | 33.0436 | 33.0317 | 33.0061 | 32.9751 | 32.934 | 32.8778 | 32.8104 | 32.7443 | 32.3276 | 31.1554 | 29.979 | 28.808 | 19.8056 | 19.7984 | 19.789 | 19.7743 | 19.7438 | 19.7066 | 19.6526 | 19.5827 | 19.5068 | 19.4248 | 19.1156 | 17.968 | 16.8161 | 15.6696 | 20.3087 | 20.2916 | 20.2696 | 20.2347 | 20.1704 | 20.0901 | 19.9469 | 19.7815 | 19.6041 | 19.4131 | 18.7411 | 17.6536 | 16.3779 | 15.1081
|  | NUFFIELD | CT |  |  | 33.0569 | 33.0511 | 33.0436 | 33.0317 | 33.0061 | 32.9751 | 32.9425 | 32.8801 | 32.8104 | 32.7443 | 32.3765 | 31.1866 | 29.9873 | 28.8114 | 19.8056 | 19.7984 | 19.789 | 19.7743 | 19.7438 | 19.7066 | 19.6674 | 19.5913 | 19.5068 | 19.4248 | 19.1368 | 17.9973 | 16.8226 | 15.6711 | 20.3087 | 20.2916 | 20.2696 | 20.2347 | 20.1704 | 20.0901 | 20.0056 | 19.834 | 19.6472 | 19.4548 | 18.7791 | 17.6921 | 16.3936 | 15.1188
|  | NUFFIELD | LW |  |  | 33.0569 | 33.0511 | 33.0436 | 33.0317 | 33.0118 | 32.9865 | 32.934 | 32.8778 | 32.8176 | 32.7527 | 32.3276 | 31.1554 | 29.979 | 28.808 | 19.8056 | 19.7984 | 19.789 | 19.7743 | 19.7495 | 19.718 | 19.6526 | 19.5827 | 19.5077 | 19.4269 | 19.1156 | 17.968 | 16.8161 | 15.6696 | 20.3087 | 20.2916 | 20.2696 | 20.2347 | 20.1761 | 20.1016 | 19.9469 | 19.7815 | 19.6041 | 19.4131 | 18.7411 | 17.6536 | 16.3779 | 15.1081
|  | NUFFIELD | ST |  |  | 33.0584 | 33.0544 | 33.0496 | 33.0432 | 33.0234 | 32.9991 | 32.9687 | 32.9356 | 32.8831 | 32.8346 | 32.6617 | 32.0981 | 31.2932 | 30.5359 | 19.8075 | 19.8025 | 19.7965 | 19.7885 | 19.7657 | 19.7372 | 19.7012 | 19.6618 | 19.5993 | 19.54 | 19.3278 | 18.8895 | 18.1008 | 17.3591 | 20.3132 | 20.3013 | 20.2872 | 20.2683 | 20.224 | 20.1666 | 20.0916 | 20.0089 | 19.8772 | 19.7423 | 19.2581 | 18.5319 | 17.8114 | 16.991
|  | NUFFIELD | SP |  |  | 33.0603 | 33.0582 | 33.056 | 33.0537 | 33.0425 | 33.03 | 33.0153 | 32.9999 | 32.9797 | 32.9389 | 32.8016 | 32.6672 | 32.4534 | 32.254 | 19.8099 | 19.8072 | 19.8045 | 19.8016 | 19.7891 | 19.7747 | 19.7578 | 19.7399 | 19.7169 | 19.6717 | 19.5189 | 19.3603 | 19.1214 | 18.8959 | 20.3188 | 20.3126 | 20.306 | 20.2994 | 20.277 | 20.2502 | 20.2174 | 20.1825 | 20.1395 | 20.0646 | 19.8045 | 19.4777 | 19.0644 | 18.6582
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE | MINIMUM HEADROOM | SU 63496 53664 | YES | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 14.9741 | 14.9553 | 14.9306 | 14.8784 | 14.8278 | 14.7776 | 14.728 | 14.692 | 14.6563 | 14.6177 | 14.5038 | 14.3155 | 14.1206 | 13.9292 | 15.8809 | 15.8799 | 15.8785 | 15.8756 | 15.8727 | 15.8699 | 15.8671 | 15.865 | 15.863 | 15.8609 | 15.8544 | 15.8438 | 15.7267 | 15.5356
|  | OAKRIDGE | CT |  |  | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 14.9741 | 14.9553 | 14.9306 | 14.8784 | 14.8278 | 14.7776 | 14.728 | 14.692 | 14.6563 | 14.6177 | 14.5038 | 14.3155 | 14.1206 | 13.9292 | 15.8809 | 15.8799 | 15.8785 | 15.8756 | 15.8727 | 15.8699 | 15.8671 | 15.865 | 15.863 | 15.8609 | 15.8544 | 15.8438 | 15.7267 | 15.5356
|  | OAKRIDGE | LW |  |  | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 14.9945 | 14.9904 | 14.9851 | 14.9739 | 14.963 | 14.9521 | 14.9157 | 14.8796 | 14.8439 | 14.8053 | 14.6914 | 14.5031 | 14.3082 | 14.1165 | 15.8821 | 15.8819 | 15.8816 | 15.8809 | 15.8803 | 15.8797 | 15.8777 | 15.8756 | 15.8736 | 15.8714 | 15.865 | 15.8544 | 15.8434 | 15.7225
|  | OAKRIDGE | ST |  |  | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 14.9967 | 14.9944 | 14.9917 | 14.9871 | 14.9813 | 14.9744 | 14.9477 | 14.9213 | 14.8969 | 14.8707 | 14.7939 | 14.6688 | 14.5432 | 14.4183 | 15.8822 | 15.8821 | 15.8819 | 15.8817 | 15.8814 | 15.881 | 15.8795 | 15.878 | 15.8766 | 15.8751 | 15.8708 | 15.8637 | 15.8567 | 15.8496
|  | OAKRIDGE | SP |  |  | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 16.9092 | 14.9991 | 14.9987 | 14.9983 | 14.9979 | 14.9962 | 14.9941 | 14.9847 | 14.9753 | 14.9632 | 14.953 | 14.9233 | 14.8761 | 14.8306 | 14.7874 | 15.8824 | 15.8823 | 15.8823 | 15.8823 | 15.8822 | 15.8821 | 15.8815 | 15.881 | 15.8803 | 15.8798 | 15.8781 | 15.8754 | 15.8729 | 15.8704
COWLEY GSP | HEADINGTON BSP | OLD ROAD | MINIMUM HEADROOM | SP 55274 06426 | NO | 33.3692 | 33.3692 | 33.3692 | 33.3692 | 33.3476 | 33.3253 | 33.3022 | 33.2774 | 33.2379 | 33.2327 | 33.2142 | 33.1132 | 32.9691 | 32.2091 | 32.762 | 32.7594 | 32.7561 | 32.7501 | 32.7224 | 32.6943 | 32.6653 | 32.6308 | 32.5816 | 32.5661 | 32.5177 | 32.2972 | 31.4763 | 30.5983 | 32.8277 | 32.8277 | 32.8277 | 32.8277 | 32.8062 | 32.7838 | 32.7607 | 32.7359 | 32.6964 | 32.6912 | 32.6727 | 31.9984 | 30.9762 | 30.0554
|  | OLD ROAD | CT |  |  | 33.3692 | 33.3692 | 33.3692 | 33.3692 | 33.3476 | 33.3253 | 33.3022 | 33.2774 | 33.2379 | 33.2327 | 33.2142 | 33.1132 | 32.9691 | 32.2091 | 32.762 | 32.7594 | 32.7561 | 32.7501 | 32.7224 | 32.6943 | 32.6653 | 32.6308 | 32.5816 | 32.5661 | 32.5177 | 32.2972 | 31.4763 | 30.5983 | 32.8277 | 32.8277 | 32.8277 | 32.8277 | 32.8062 | 32.7838 | 32.7607 | 32.7359 | 32.6964 | 32.6912 | 32.6727 | 31.9984 | 30.9762 | 30.0554
|  | OLD ROAD | LW |  |  | 33.3692 | 33.3692 | 33.3692 | 33.3692 | 33.3676 | 33.3642 | 33.3589 | 33.3516 | 33.3368 | 33.3343 | 33.3213 | 33.2897 | 33.1976 | 32.4923 | 32.7628 | 32.7608 | 32.7582 | 32.7539 | 32.7477 | 32.7401 | 32.7241 | 32.7069 | 32.6825 | 32.6697 | 32.6268 | 32.4811 | 31.7358 | 30.8849 | 32.8277 | 32.8277 | 32.8277 | 32.8277 | 32.8261 | 32.8227 | 32.8174 | 32.8101 | 32.7953 | 32.7928 | 32.7798 | 32.2102 | 31.2374 | 30.3437
|  | OLD ROAD | ST |  |  | 33.3692 | 33.3692 | 33.3692 | 33.3692 | 33.3688 | 33.3682 | 33.3671 | 33.3656 | 33.3622 | 33.3605 | 33.3516 | 33.34 | 33.2993 | 33.2844 | 32.7639 | 32.7627 | 32.7614 | 32.7596 | 32.7571 | 32.7543 | 32.7483 | 32.7424 | 32.7324 | 32.7237 | 32.6946 | 32.6495 | 32.5688 | 32.392 | 32.8277 | 32.8277 | 32.8277 | 32.8277 | 32.8274 | 32.8267 | 32.8256 | 32.8241 | 32.8207 | 32.819 | 32.8102 | 32.7986 | 32.589 | 31.9999
|  | OLD ROAD | SP |  |  | 33.3692 | 33.3692 | 33.3692 | 33.3692 | 33.3639 | 33.3587 | 33.3534 | 33.3481 | 33.3397 | 33.3162 | 33.2402 | 33.2029 | 33.0816 | 32.9784 | 32.7644 | 32.7638 | 32.7632 | 32.7625 | 32.7563 | 32.7503 | 32.7434 | 32.7368 | 32.7267 | 32.7005 | 32.6166 | 32.5666 | 32.4328 | 32.318 | 32.8277 | 32.8277 | 32.8277 | 32.8277 | 32.8224 | 32.8172 | 32.812 | 32.8066 | 32.7982 | 32.7747 | 32.6987 | 32.6615 | 32.5401 | 32.4369
COWLEY GSP | OXFORD (OSNEY) BSP | OSNEY | MINIMUM HEADROOM | SP 50148 05901 | YES | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9507 | 36.9392 | 36.9276 | 36.9159 | 36.8976 | 36.8467 | 36.6851 | 36.6082 | 36.3659 | 36.1633 | 35.828 | 35.828 | 35.828 | 35.828 | 35.8163 | 35.8048 | 35.7932 | 35.7815 | 35.7632 | 35.7123 | 35.5507 | 34.9593 | 33.5984 | 32.2362 | 36.6444 | 36.6393 | 36.6321 | 36.6193 | 36.6062 | 36.5949 | 36.5869 | 36.5792 | 36.5675 | 36.5143 | 36.3303 | 35.2247 | 33.8633 | 32.5007
|  | OSNEY | CT |  |  | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 34.9593 | 33.5984 | 32.2362 | 36.6446 | 36.6397 | 36.6328 | 36.6205 | 36.6079 | 36.5971 | 36.5869 | 36.5792 | 36.5712 | 36.5628 | 36.3303 | 35.2247 | 33.8633 | 32.5007
|  | OSNEY | LW |  |  | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 34.9675 | 33.6066 | 32.2442 | 36.6444 | 36.6393 | 36.6321 | 36.6193 | 36.6062 | 36.5949 | 36.5874 | 36.5797 | 36.5717 | 36.5633 | 36.3385 | 35.2329 | 33.8716 | 32.5087
|  | OSNEY | ST |  |  | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.828 | 35.0582 | 34.1932 | 36.6462 | 36.6428 | 36.6385 | 36.6321 | 36.6242 | 36.6164 | 36.611 | 36.6055 | 36.6001 | 36.5943 | 36.576 | 36.2223 | 35.3236 | 34.4583
|  | OSNEY | SP |  |  | 36.9624 | 36.9624 | 36.9624 | 36.9624 | 36.9507 | 36.9392 | 36.9276 | 36.9159 | 36.8976 | 36.8467 | 36.6851 | 36.6082 | 36.3659 | 36.1633 | 35.828 | 35.828 | 35.828 | 35.828 | 35.8163 | 35.8048 | 35.7932 | 35.7815 | 35.7632 | 35.7123 | 35.5507 | 35.4738 | 35.2315 | 35.0289 | 36.6486 | 36.6474 | 36.6459 | 36.6444 | 36.6297 | 36.6158 | 36.6022 | 36.5884 | 36.5675 | 36.5143 | 36.3456 | 36.2495 | 35.9822 | 35.7533
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON | MINIMUM HEADROOM | SU 52061 50913 | YES | 29.6933 | 29.5942 | 29.4688 | 28.3085 | 27.9721 | 27.6012 | 27.3376 | 27.0537 | 26.7599 | 26.5625 | 26.0413 | 25.1113 | 24.1059 | 23.0841 | 34.6445 | 34.6292 | 34.614 | 33.6835 | 33.6017 | 33.5198 | 33.4377 | 33.3553 | 33.2698 | 33.238 | 33.1421 | 32.983 | 32.8788 | 32.71 | 35.6725 | 35.6573 | 35.642 | 34.7115 | 34.6298 | 34.5479 | 34.2808 | 33.9641 | 33.6339 | 33.4077 | 32.8123 | 31.7478 | 30.5752 | 29.4044
|  | OVERTON | CT |  |  | 29.7686 | 29.677 | 29.5595 | 28.7752 | 28.4786 | 28.1476 | 27.8095 | 27.5622 | 27.3081 | 27.1242 | 26.6441 | 25.2055 | 24.1059 | 23.0841 | 34.7177 | 34.7085 | 34.6994 | 34.1411 | 34.0953 | 34.0496 | 34.0038 | 33.958 | 33.9123 | 33.894 | 33.8391 | 33.1715 | 32.936 | 32.7682 | 35.7458 | 35.7366 | 35.7274 | 35.1691 | 35.1234 | 35.0776 | 34.7378 | 34.4561 | 34.1657 | 33.9529 | 33.3986 | 31.8255 | 30.5752 | 29.4044
|  | OVERTON | LW |  |  | 29.6933 | 29.5942 | 29.4688 | 28.3085 | 27.9721 | 27.6012 | 27.3376 | 27.0537 | 26.7599 | 26.5625 | 26.0413 | 25.1113 | 24.1429 | 23.12 | 34.6445 | 34.6292 | 34.614 | 33.6835 | 33.6017 | 33.5198 | 33.4377 | 33.3553 | 33.2698 | 33.238 | 33.1421 | 32.983 | 32.8788 | 32.71 | 35.6725 | 35.6573 | 35.642 | 34.7115 | 34.6298 | 34.5479 | 34.2808 | 33.9641 | 33.6339 | 33.4077 | 32.8123 | 31.7478 | 30.6287 | 29.4568
|  | OVERTON | ST |  |  | 29.8608 | 29.8123 | 29.756 | 29.2993 | 29.1053 | 28.8659 | 28.6636 | 28.447 | 28.2115 | 28.0642 | 27.6664 | 27.0218 | 26.2586 | 25.5976 | 34.7543 | 34.7482 | 34.7421 | 34.3699 | 34.3004 | 34.2302 | 34.1593 | 34.087 | 33.9918 | 33.9577 | 33.851 | 33.7337 | 33.5358 | 33.4219 | 35.7824 | 35.7763 | 35.7702 | 35.398 | 35.3284 | 35.2583 | 35.1873 | 35.115 | 35.0199 | 34.9857 | 34.5962 | 33.8606 | 32.9988 | 32.2424
|  | OVERTON | SP |  |  | 29.9418 | 29.9298 | 29.9179 | 29.7233 | 29.662 | 29.5843 | 29.514 | 29.4396 | 29.3558 | 29.3004 | 29.1529 | 28.9048 | 28.6222 | 28.3252 | 34.7909 | 34.7879 | 34.7848 | 34.5987 | 34.5823 | 34.5658 | 34.5494 | 34.533 | 34.5159 | 34.5046 | 34.4699 | 34.4315 | 34.3886 | 34.3344 | 35.819 | 35.8159 | 35.8129 | 35.6268 | 35.6103 | 35.5939 | 35.5775 | 35.561 | 35.5439 | 35.5326 | 35.4979 | 35.4596 | 35.4167 | 35.2828
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH | MINIMUM HEADROOM | SU 62243 66052 | YES | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.2832 | 30.2586 | 30.2337 | 30.2076 | 30.1674 | 30.1623 | 30.1301 | 30.0658 | 29.9714 | 29.9497 | 30.3001 | 30.2981 | 30.2956 | 30.2902 | 30.2608 | 30.231 | 30.2009 | 30.1717 | 30.1284 | 30.12 | 29.9672 | 29.5402 | 29.0878 | 28.7139 | 30.3404 | 30.3378 | 30.3343 | 30.3269 | 30.2956 | 30.264 | 30.232 | 30.2017 | 30.1573 | 30.1477 | 30.0179 | 29.5866 | 29.1299 | 28.7517
|  | PADWORTH | CT |  |  | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.2832 | 30.2586 | 30.2337 | 30.2076 | 30.1674 | 30.1623 | 30.1459 | 30.0658 | 29.9714 | 29.9497 | 30.3001 | 30.2981 | 30.2956 | 30.2902 | 30.2608 | 30.231 | 30.2009 | 30.1717 | 30.1284 | 30.12 | 29.9672 | 29.5402 | 29.0878 | 28.7139 | 30.3404 | 30.3378 | 30.3343 | 30.3269 | 30.2956 | 30.264 | 30.232 | 30.2017 | 30.1573 | 30.1477 | 30.0179 | 29.5866 | 29.1299 | 28.7517
|  | PADWORTH | LW |  |  | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3005 | 30.2988 | 30.2967 | 30.2921 | 30.2876 | 30.2832 | 30.2801 | 30.277 | 30.2739 | 30.2706 | 30.2457 | 29.8992 | 29.5411 | 29.189 | 30.341 | 30.3387 | 30.3358 | 30.3295 | 30.3234 | 30.3174 | 30.3132 | 30.3089 | 30.3047 | 30.3002 | 30.2869 | 29.947 | 29.5846 | 29.2282
|  | PADWORTH | ST |  |  | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.2856 | 30.2635 | 30.2409 | 30.2175 | 30.1814 | 30.1692 | 30.1301 | 30.0987 | 29.986 | 29.9534 | 30.3012 | 30.3001 | 30.2988 | 30.2966 | 30.2721 | 30.2467 | 30.2217 | 30.196 | 30.1578 | 30.1433 | 30.0976 | 30.0555 | 29.7673 | 29.5057 | 30.3419 | 30.3404 | 30.3387 | 30.3357 | 30.3102 | 30.2836 | 30.2577 | 30.2312 | 30.1923 | 30.1769 | 30.1288 | 30.0828 | 29.8175 | 29.5531
|  | PADWORTH | SP |  |  | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3074 | 30.3024 | 30.3023 | 30.3021 | 30.3019 | 30.3012 | 30.3003 | 30.2995 | 30.2987 | 30.2976 | 30.2968 | 30.2942 | 30.2902 | 30.2863 | 30.2826 | 30.3436 | 30.3433 | 30.3431 | 30.3429 | 30.3419 | 30.3407 | 30.3396 | 30.3385 | 30.3371 | 30.3359 | 30.3324 | 30.3269 | 30.3216 | 30.3166
BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE | MINIMUM HEADROOM | SU 62960 76144 | YES | 8.4584 | 8.4584 | 8.4584 | 8.4584 | 8.4466 | 8.4342 | 8.4212 | 8.4071 | 8.3842 | 8.3811 | 8.3696 | 8.2384 | 8.05 | 7.9225 | 8.005 | 8.0037 | 8.0019 | 7.9983 | 7.9847 | 7.9693 | 7.9533 | 7.9375 | 7.9128 | 7.9077 | 7.8905 | 7.8081 | 7.7172 | 7.6658 | 7.9945 | 7.9935 | 7.9923 | 7.9898 | 7.9767 | 7.9621 | 7.947 | 7.9317 | 7.9075 | 7.903 | 7.8874 | 7.7273 | 7.5247 | 7.3833
|  | PANGBOURNE | CT |  |  | 8.4584 | 8.4584 | 8.4584 | 8.4584 | 8.4466 | 8.4342 | 8.4212 | 8.4071 | 8.3842 | 8.3811 | 8.3696 | 8.2384 | 8.05 | 7.9225 | 8.0052 | 8.0041 | 8.0026 | 7.9995 | 7.9847 | 7.9693 | 7.9533 | 7.9375 | 7.9128 | 7.9077 | 7.8905 | 7.8081 | 7.7172 | 7.6658 | 7.9946 | 7.9939 | 7.9928 | 7.9906 | 7.9767 | 7.9621 | 7.947 | 7.9317 | 7.9075 | 7.903 | 7.8874 | 7.7273 | 7.5247 | 7.3833
|  | PANGBOURNE | LW |  |  | 8.4584 | 8.4584 | 8.4584 | 8.4584 | 8.457 | 8.454 | 8.4492 | 8.4427 | 8.4295 | 8.4272 | 8.4156 | 8.3181 | 8.1554 | 8.0455 | 8.005 | 8.0037 | 8.0019 | 7.9983 | 7.9934 | 7.9869 | 7.9803 | 7.972 | 7.957 | 7.9528 | 7.9355 | 7.8977 | 7.8326 | 7.7881 | 7.9945 | 7.9935 | 7.9923 | 7.9898 | 7.9858 | 7.9803 | 7.9743 | 7.9665 | 7.952 | 7.9484 | 7.9328 | 7.8055 | 7.6287 | 7.5048
|  | PANGBOURNE | ST |  |  | 8.4584 | 8.4584 | 8.4584 | 8.4584 | 8.4581 | 8.4575 | 8.4566 | 8.4552 | 8.4521 | 8.4507 | 8.4428 | 8.4324 | 8.3843 | 8.3022 | 8.0054 | 8.0045 | 8.0034 | 8.0015 | 7.9989 | 7.9955 | 7.9931 | 7.9901 | 7.9859 | 7.9831 | 7.9713 | 7.9545 | 7.9116 | 7.892 | 7.9948 | 7.9941 | 7.9934 | 7.992 | 7.9901 | 7.9875 | 7.9855 | 7.983 | 7.9791 | 7.9767 | 7.966 | 7.9511 | 7.8793 | 7.7881
|  | PANGBOURNE | SP |  |  | 8.4584 | 8.4584 | 8.4584 | 8.4584 | 8.4584 | 8.4584 | 8.4584 | 8.4583 | 8.4582 | 8.4577 | 8.4548 | 8.4525 | 8.4417 | 8.4311 | 8.0065 | 8.0063 | 8.0062 | 8.0061 | 8.0055 | 8.0048 | 8.0042 | 8.0036 | 8.0028 | 8.0018 | 7.9975 | 7.9928 | 7.9795 | 7.9666 | 7.9955 | 7.9954 | 7.9953 | 7.9952 | 7.9948 | 7.9943 | 7.9939 | 7.9935 | 7.9929 | 7.992 | 7.9881 | 7.9841 | 7.9715 | 7.9593
BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE | MINIMUM HEADROOM | SU 51369 08259 | NO | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2059 | 33.1875 | 33.169 | 33.1501 | 33.1208 | 33.039 | 32.7797 | 32.6562 | 32.2674 | 31.9421 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9305 | 31.912 | 31.8411 | 31.7544 | 31.6683 | 31.5756 | 31.3006 | 30.837 | 30.3522 | 29.8745 | 32.1241 | 32.1199 | 32.1144 | 32.1028 | 32.0916 | 32.0805 | 32.0674 | 32.047 | 32.0157 | 31.9325 | 31.6692 | 31.5391 | 31.1437 | 30.6954
|  | PARK GATE | CT |  |  | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.1697 | 32.7642 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.8411 | 31.7544 | 31.6683 | 31.5756 | 31.3006 | 30.837 | 30.3522 | 29.8745 | 32.1241 | 32.1199 | 32.1144 | 32.1028 | 32.0916 | 32.0805 | 32.0695 | 32.0646 | 32.0598 | 32.0546 | 32.0391 | 31.6418 | 31.1651 | 30.6954
|  | PARK GATE | LW |  |  | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 32.993 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9382 | 31.8454 | 31.5703 | 31.107 | 30.622 | 30.144 | 32.1251 | 32.1217 | 32.1173 | 32.1078 | 32.0987 | 32.0896 | 32.0847 | 32.0798 | 32.075 | 32.0698 | 32.0543 | 31.9072 | 31.4304 | 30.9604
|  | PARK GATE | ST |  |  | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.7593 | 31.4467 | 31.1365 | 32.127 | 32.125 | 32.1227 | 32.1187 | 32.1138 | 32.1078 | 32.1037 | 32.0996 | 32.0963 | 32.0927 | 32.0823 | 32.0649 | 32.0473 | 31.9362
|  | PARK GATE | SP |  |  | 33.2248 | 33.2248 | 33.2248 | 33.2248 | 33.2059 | 33.1875 | 33.169 | 33.1501 | 33.1208 | 33.039 | 32.7797 | 32.6562 | 32.2674 | 31.9421 | 31.9493 | 31.9493 | 31.9493 | 31.9493 | 31.9305 | 31.912 | 31.8935 | 31.8747 | 31.8453 | 31.7635 | 31.5042 | 31.3807 | 30.9919 | 30.6666 | 32.1291 | 32.1287 | 32.1284 | 32.128 | 32.1077 | 32.0874 | 32.0674 | 32.047 | 32.0157 | 31.9325 | 31.6692 | 31.5391 | 31.1437 | 30.8123
MELKSHAM GSP | AMESBURY | PARK HOUSE | MINIMUM HEADROOM | SU 23138 43780 | YES | 35.3919 | 35.3812 | 35.3719 | 35.3526 | 35.2022 | 35.0313 | 34.8612 | 34.6855 | 34.4221 | 34.3248 | 34.0134 | 33.7359 | 33.0101 | 32.6546 | 33.8266 | 33.8149 | 33.8048 | 33.778 | 33.6315 | 33.4304 | 33.2378 | 33.0334 | 32.7347 | 32.5991 | 32.1629 | 31.5167 | 30.4392 | 29.8292 | 33.7447 | 33.7353 | 33.7271 | 33.7101 | 33.5595 | 33.3904 | 33.2218 | 33.0475 | 32.7855 | 32.6895 | 32.3827 | 32.112 | 31.3929 | 30.8967
|  | PARK HOUSE | CT |  |  | 35.3937 | 35.3843 | 35.3768 | 35.3611 | 35.3344 | 35.3075 | 35.279 | 35.2514 | 35.2167 | 35.1974 | 35.135 | 35.0147 | 34.6867 | 34.3857 | 33.8286 | 33.8183 | 33.8101 | 33.7929 | 33.747 | 33.6912 | 33.6248 | 33.5465 | 33.4598 | 33.3845 | 33.007 | 32.345 | 31.6805 | 31.0493 | 33.7463 | 33.738 | 33.7314 | 33.7176 | 33.6927 | 33.6677 | 33.6411 | 33.6154 | 33.5826 | 33.5653 | 33.5095 | 33.3863 | 32.7791 | 31.902
|  | PARK HOUSE | LW |  |  | 35.3919 | 35.3812 | 35.3719 | 35.3526 | 35.3337 | 35.3149 | 35.3003 | 35.2849 | 35.2692 | 35.2523 | 35.1976 | 35.0832 | 34.7901 | 34.4995 | 33.8266 | 33.8149 | 33.8048 | 33.778 | 33.7236 | 33.6646 | 33.6017 | 33.5357 | 33.468 | 33.3881 | 32.9838 | 32.3575 | 31.7312 | 31.1101 | 33.7447 | 33.7353 | 33.7271 | 33.7101 | 33.6935 | 33.6769 | 33.664 | 33.6506 | 33.6367 | 33.6218 | 33.5737 | 33.4079 | 32.8389 | 31.8773
|  | PARK HOUSE | ST |  |  | 35.394 | 35.3885 | 35.3787 | 35.3679 | 35.2022 | 35.0313 | 34.8612 | 34.6855 | 34.4221 | 34.3248 | 34.0134 | 33.7359 | 33.0101 | 32.6546 | 33.829 | 33.8229 | 33.8122 | 33.8004 | 33.6315 | 33.4304 | 33.2378 | 33.0334 | 32.7347 | 32.5991 | 32.1629 | 31.5167 | 30.4392 | 29.8292 | 33.7466 | 33.7417 | 33.7331 | 33.7236 | 33.5595 | 33.3904 | 33.2218 | 33.0475 | 32.7855 | 32.6895 | 32.3827 | 32.112 | 31.3929 | 30.8967
|  | PARK HOUSE | SP |  |  | 35.4003 | 35.3994 | 35.3952 | 35.3945 | 35.3916 | 35.3881 | 35.384 | 35.3797 | 35.3744 | 35.3699 | 35.3552 | 35.3326 | 35.3107 | 35.2889 | 33.8358 | 33.8348 | 33.8302 | 33.8295 | 33.8263 | 33.8224 | 33.8179 | 33.8133 | 33.8075 | 33.8026 | 33.7856 | 33.7203 | 33.6465 | 33.5527 | 33.7521 | 33.7513 | 33.7476 | 33.747 | 33.7444 | 33.7413 | 33.7377 | 33.734 | 33.7293 | 33.7253 | 33.7124 | 33.6925 | 33.6732 | 33.654
MINETY GSP | STRATTON (2 X 90) | PARK NORTH | MINIMUM HEADROOM | SU 18052 84542 | YES | 4.738 | 4.738 | 4.738 | 4.738 | 4.7176 | 4.6816 | 4.6496 | 4.613 | 4.5595 | 4.5326 | 4.4404 | 4.2622 | 4.0095 | 3.8908 | 3.9992 | 3.9987 | 3.998 | 3.9964 | 3.9912 | 3.9819 | 3.9687 | 3.9508 | 3.9157 | 3.9088 | 3.8756 | 3.7973 | 3.6495 | 3.619 | 4.2236 | 4.2229 | 4.222 | 4.2201 | 4.2144 | 4.2048 | 4.1912 | 4.173 | 4.1377 | 4.1305 | 4.0964 | 4.0166 | 3.7647 | 3.627
|  | PARK NORTH | CT |  |  | 4.738 | 4.738 | 4.738 | 4.738 | 4.7362 | 4.7106 | 4.6841 | 4.6599 | 4.6301 | 4.6073 | 4.5352 | 4.3488 | 4.1478 | 4.011 | 3.9994 | 3.9989 | 3.9983 | 3.997 | 3.9946 | 3.9913 | 3.9869 | 3.9812 | 3.9699 | 3.967 | 3.954 | 3.8675 | 3.7714 | 3.7379 | 4.2238 | 4.2232 | 4.2224 | 4.2208 | 4.2181 | 4.2144 | 4.2097 | 4.2037 | 4.1922 | 4.1889 | 4.175 | 4.0871 | 3.9061 | 3.7502
|  | PARK NORTH | LW |  |  | 4.738 | 4.738 | 4.738 | 4.738 | 4.7176 | 4.6816 | 4.6496 | 4.613 | 4.5595 | 4.5326 | 4.4404 | 4.2622 | 4.0095 | 3.8908 | 3.9992 | 3.9987 | 3.998 | 3.9964 | 3.9912 | 3.9819 | 3.9687 | 3.9508 | 3.9157 | 3.9088 | 3.8756 | 3.7973 | 3.6495 | 3.6342 | 4.2236 | 4.2229 | 4.222 | 4.2201 | 4.2144 | 4.2048 | 4.1912 | 4.173 | 4.1377 | 4.1305 | 4.0964 | 4.0166 | 3.7647 | 3.627
|  | PARK NORTH | ST |  |  | 4.738 | 4.738 | 4.738 | 4.738 | 4.7372 | 4.7356 | 4.7332 | 4.7297 | 4.7218 | 4.718 | 4.6766 | 4.5793 | 4.4138 | 4.3088 | 3.9999 | 3.9999 | 3.9999 | 3.9998 | 3.9989 | 3.9972 | 3.9942 | 3.99 | 3.9814 | 3.9769 | 3.9543 | 3.9238 | 3.8261 | 3.7882 | 4.2245 | 4.2245 | 4.2244 | 4.2243 | 4.2234 | 4.2217 | 4.2185 | 4.2142 | 4.2054 | 4.2007 | 4.1774 | 4.146 | 4.0472 | 4.0083
|  | PARK NORTH | SP |  |  | 4.738 | 4.738 | 4.738 | 4.738 | 4.7335 | 4.7291 | 4.7246 | 4.72 | 4.7127 | 4.6921 | 4.6233 | 4.5882 | 4.4455 | 4.3156 | 3.9999 | 3.9998 | 3.9998 | 3.9997 | 3.995 | 3.9902 | 3.9856 | 3.9808 | 3.9733 | 3.9523 | 3.8827 | 3.8462 | 3.7247 | 3.619 | 4.2245 | 4.2244 | 4.2243 | 4.2242 | 4.2194 | 4.2146 | 4.2099 | 4.2051 | 4.1975 | 4.1765 | 4.1066 | 4.0697 | 3.9478 | 3.8418
WILLESDEN GSP | ACTON LANE | PARK ROYAL | MINIMUM HEADROOM | TQ 20137 82215 | YES | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.249 | 35.7417 | 34.2395 | 29.9937 | 29.9915 | 29.9893 | 29.9851 | 29.9808 | 29.976 | 29.9643 | 29.9526 | 29.9411 | 29.9288 | 29.8909 | 29.8157 | 29.7309 | 29.6464 | 36.6393 | 36.6365 | 36.6338 | 36.6284 | 36.6229 | 36.617 | 36.6021 | 36.5874 | 36.5728 | 36.5572 | 36.5093 | 35.8884 | 34.1563 | 32.4302
|  | PARK ROYAL | CT |  |  | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 35.9183 | 34.4169 | 29.994 | 29.9919 | 29.99 | 29.9863 | 29.9825 | 29.9783 | 29.9742 | 29.9626 | 29.951 | 29.9387 | 29.9008 | 29.8256 | 29.7408 | 29.6564 | 36.6396 | 36.637 | 36.6347 | 36.63 | 36.6251 | 36.6198 | 36.6147 | 36.5999 | 36.5853 | 36.5697 | 36.5219 | 36.0911 | 34.3592 | 32.634
|  | PARK ROYAL | LW |  |  | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.249 | 35.7417 | 34.2395 | 29.9937 | 29.9915 | 29.9893 | 29.9851 | 29.9808 | 29.976 | 29.9643 | 29.9526 | 29.9411 | 29.9288 | 29.8909 | 29.8157 | 29.7309 | 29.6464 | 36.6393 | 36.6365 | 36.6338 | 36.6284 | 36.6229 | 36.617 | 36.6021 | 36.5874 | 36.5728 | 36.5572 | 36.5093 | 35.8884 | 34.1563 | 32.4302
|  | PARK ROYAL | ST |  |  | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 36.4948 | 29.9949 | 29.9934 | 29.9922 | 29.9903 | 29.9878 | 29.9846 | 29.9804 | 29.9761 | 29.9683 | 29.9598 | 29.9341 | 29.8829 | 29.8275 | 29.7733 | 36.6408 | 36.6389 | 36.6374 | 36.635 | 36.6318 | 36.6278 | 36.6225 | 36.6171 | 36.6071 | 36.5965 | 36.5639 | 36.4992 | 36.1273 | 35.0218
|  | PARK ROYAL | SP |  |  | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 37.2609 | 29.9961 | 29.9955 | 29.9952 | 29.9949 | 29.9941 | 29.993 | 29.9919 | 29.9907 | 29.9893 | 29.986 | 29.976 | 29.9557 | 29.9326 | 29.9092 | 36.6423 | 36.6416 | 36.6412 | 36.6409 | 36.6398 | 36.6385 | 36.637 | 36.6355 | 36.6337 | 36.6296 | 36.6169 | 36.5912 | 36.5621 | 36.5325
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH | MINIMUM HEADROOM | SZ 03222 92233 | YES | 17.447 | 17.447 | 17.447 | 17.447 | 17.4425 | 17.438 | 17.4334 | 17.4286 | 17.4212 | 17.4187 | 17.4107 | 17.4042 | 17.3811 | 17.3745 | 14.8167 | 14.8119 | 14.8107 | 14.8084 | 14.805 | 14.7989 | 14.7923 | 14.7856 | 14.7761 | 14.7714 | 14.7563 | 14.55 | 14.2206 | 13.8462 | 14.742 | 14.7384 | 14.7375 | 14.7358 | 14.7322 | 14.7264 | 14.7203 | 14.7141 | 14.7051 | 14.7009 | 14.6875 | 14.6684 | 14.4136 | 14.0403
|  | PARKSTONE NORTH | CT |  |  | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 14.8167 | 14.8119 | 14.8107 | 14.8084 | 14.8061 | 14.8037 | 14.8014 | 14.7984 | 14.7953 | 14.792 | 14.7816 | 14.5569 | 14.229 | 13.8545 | 14.742 | 14.7384 | 14.7375 | 14.7358 | 14.734 | 14.7322 | 14.7305 | 14.7282 | 14.7259 | 14.7234 | 14.7155 | 14.6971 | 14.4219 | 14.0486
|  | PARKSTONE NORTH | LW |  |  | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 17.447 | 14.8167 | 14.8119 | 14.8107 | 14.8084 | 14.8061 | 14.8037 | 14.8007 | 14.7977 | 14.7946 | 14.7914 | 14.781 | 14.55 | 14.2206 | 13.8462 | 14.742 | 14.7384 | 14.7375 | 14.7358 | 14.734 | 14.7322 | 14.73 | 14.7277 | 14.7253 | 14.7229 | 14.715 | 14.6966 | 14.4136 | 14.0403
|  | PARKSTONE NORTH | ST |  |  | 17.447 | 17.447 | 17.447 | 17.447 | 17.4425 | 17.438 | 17.4334 | 17.4286 | 17.4212 | 17.4187 | 17.4107 | 17.4042 | 17.3811 | 17.3745 | 14.8171 | 14.8165 | 14.8119 | 14.8108 | 14.805 | 14.7989 | 14.7923 | 14.7856 | 14.7761 | 14.7714 | 14.7563 | 14.7081 | 14.4826 | 14.2787 | 14.7423 | 14.7419 | 14.7385 | 14.7376 | 14.7322 | 14.7264 | 14.7203 | 14.7141 | 14.7051 | 14.7009 | 14.6875 | 14.6684 | 14.6306 | 14.4726
|  | PARKSTONE NORTH | SP |  |  | 17.447 | 17.447 | 17.447 | 17.447 | 17.446 | 17.4451 | 17.4442 | 17.4432 | 17.4417 | 17.4376 | 17.4244 | 17.4182 | 17.3985 | 17.382 | 14.8176 | 14.8174 | 14.8134 | 14.8132 | 14.8119 | 14.8105 | 14.8089 | 14.8072 | 14.8049 | 14.7999 | 14.7841 | 14.7711 | 14.7428 | 14.7172 | 14.7427 | 14.7426 | 14.7396 | 14.7395 | 14.7382 | 14.7369 | 14.7354 | 14.734 | 14.7318 | 14.7271 | 14.7119 | 14.7005 | 14.6743 | 14.651
MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH | MINIMUM HEADROOM | SZ 04762 89848 | YES | 29.6247 | 29.5337 | 29.4215 | 28.217 | 27.9465 | 27.6604 | 27.2581 | 26.8378 | 26.3993 | 25.9844 | 24.8774 | 23.0957 | 21.2338 | 19.3026 | 35.5043 | 35.4824 | 35.4592 | 34.3618 | 34.2622 | 34.1618 | 34.0549 | 33.9469 | 33.8379 | 33.781 | 33.2431 | 31.2395 | 29.1126 | 26.9027 | 35.6057 | 35.5878 | 35.5699 | 34.4788 | 34.3894 | 34.3 | 34.2106 | 34.1211 | 34.0317 | 33.9959 | 33.8886 | 32.0746 | 29.9608 | 27.7805
|  | PARKSTONE SOUTH | CT |  |  | 29.7133 | 29.6313 | 29.5289 | 28.7663 | 28.5368 | 28.2917 | 28.037 | 27.6524 | 27.2497 | 26.849 | 25.7849 | 23.3995 | 21.3689 | 19.4379 | 35.5903 | 35.5756 | 35.5598 | 34.8991 | 34.8356 | 34.7712 | 34.7063 | 34.6341 | 34.5609 | 34.5182 | 34.1693 | 31.562 | 29.2694 | 27.0597 | 35.6915 | 35.6808 | 35.67 | 35.0154 | 34.9618 | 34.9081 | 34.8544 | 34.8008 | 34.7471 | 34.7257 | 34.6613 | 32.3978 | 30.1152 | 27.9352
|  | PARKSTONE SOUTH | LW |  |  | 29.6247 | 29.5337 | 29.4215 | 28.217 | 27.9465 | 27.6604 | 27.2581 | 26.8378 | 26.3993 | 25.9844 | 24.8774 | 23.0957 | 21.2338 | 19.3026 | 35.5043 | 35.4824 | 35.4592 | 34.3618 | 34.2622 | 34.1618 | 34.0549 | 33.9469 | 33.8379 | 33.781 | 33.2431 | 31.2395 | 29.1126 | 26.9027 | 35.6057 | 35.5878 | 35.5699 | 34.4788 | 34.3894 | 34.3 | 34.2106 | 34.1211 | 34.0317 | 33.9959 | 33.8886 | 32.0746 | 29.9608 | 27.7805
|  | PARKSTONE SOUTH | ST |  |  | 29.8767 | 29.7159 | 29.6494 | 29.1591 | 29.0114 | 28.8406 | 28.5399 | 28.2288 | 27.9572 | 27.6833 | 26.9523 | 25.7835 | 24.5933 | 23.4035 | 35.64 | 35.6243 | 35.6138 | 35.1744 | 35.1323 | 35.089 | 35.0384 | 34.9872 | 34.9382 | 34.9094 | 34.8279 | 34.124 | 32.775 | 31.4297 | 35.7344 | 35.7273 | 35.7201 | 35.2837 | 35.2479 | 35.2122 | 35.1764 | 35.1406 | 35.1049 | 35.0905 | 35.0476 | 34.9217 | 33.6115 | 32.2621
|  | PARKSTONE SOUTH | SP |  |  | 29.9471 | 29.9202 | 29.7893 | 29.5642 | 29.502 | 29.4339 | 29.3298 | 29.2227 | 29.0964 | 28.9877 | 28.6978 | 28.2243 | 27.7171 | 27.187 | 35.6845 | 35.6796 | 35.6689 | 35.4503 | 35.4299 | 35.4092 | 35.3865 | 35.3636 | 35.3397 | 35.3269 | 35.2904 | 35.2301 | 35.1814 | 35.1146 | 35.7774 | 35.7738 | 35.7702 | 35.552 | 35.5341 | 35.5162 | 35.4983 | 35.4805 | 35.4626 | 35.4554 | 35.4339 | 35.3982 | 35.3767 | 35.3374
BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM | MINIMUM HEADROOM | SU 84770 68709 | YES | 33.9647 | 33.9545 | 33.941 | 33.9127 | 33.8839 | 33.8551 | 33.8268 | 33.6851 | 33.5158 | 33.3452 | 32.857 | 31.954 | 30.9516 | 30.0276 | 32.5717 | 32.5634 | 32.5525 | 32.5297 | 32.5065 | 32.4793 | 32.454 | 32.3327 | 32.1418 | 31.9479 | 31.3935 | 30.3656 | 29.203 | 28.1205 | 32.7473 | 32.7385 | 32.7269 | 32.7024 | 32.6776 | 32.6499 | 32.5569 | 32.3729 | 32.1764 | 31.9765 | 31.4049 | 30.3577 | 29.1971 | 28.1166
|  | PEACOCK FARM | CT |  |  | 33.9647 | 33.9545 | 33.941 | 33.9127 | 33.8839 | 33.8552 | 33.8268 | 33.6851 | 33.5158 | 33.3452 | 32.857 | 31.954 | 30.9516 | 30.0276 | 32.5717 | 32.5634 | 32.5525 | 32.5297 | 32.5065 | 32.4835 | 32.4605 | 32.3327 | 32.1418 | 31.9479 | 31.3935 | 30.3656 | 29.203 | 28.1205 | 32.7473 | 32.7385 | 32.7269 | 32.7024 | 32.6776 | 32.6529 | 32.5569 | 32.3729 | 32.1764 | 31.9765 | 31.4049 | 30.3577 | 29.1971 | 28.1166
|  | PEACOCK FARM | LW |  |  | 33.9672 | 33.9587 | 33.9475 | 33.9241 | 33.8897 | 33.8551 | 33.8275 | 33.7942 | 33.7449 | 33.7212 | 33.2171 | 32.3379 | 31.3279 | 30.4224 | 32.5736 | 32.5668 | 32.5578 | 32.539 | 32.5093 | 32.4793 | 32.454 | 32.4232 | 32.3764 | 32.3594 | 31.8164 | 30.8228 | 29.6594 | 28.5953 | 32.7494 | 32.7421 | 32.7325 | 32.7123 | 32.6813 | 32.6499 | 32.624 | 32.5924 | 32.5449 | 32.4316 | 31.8441 | 30.8207 | 29.6525 | 28.5904
|  | PEACOCK FARM | ST |  |  | 33.9734 | 33.9696 | 33.9651 | 33.9574 | 33.9307 | 33.9017 | 33.8697 | 33.8358 | 33.7933 | 33.7719 | 33.7038 | 33.5249 | 32.8113 | 32.1939 | 32.5787 | 32.5756 | 32.5719 | 32.5658 | 32.541 | 32.5144 | 32.4851 | 32.4539 | 32.4131 | 32.3935 | 32.3306 | 32.1766 | 31.3813 | 30.6838 | 32.7548 | 32.7515 | 32.7476 | 32.741 | 32.7157 | 32.6884 | 32.6583 | 32.6263 | 32.585 | 32.5649 | 32.5005 | 32.2179 | 31.4013 | 30.6831
|  | PEACOCK FARM | SP |  |  | 33.9769 | 33.9759 | 33.975 | 33.9741 | 33.9698 | 33.9648 | 33.96 | 33.9552 | 33.9488 | 33.9441 | 33.9283 | 33.9067 | 33.874 | 33.8431 | 32.5814 | 32.5807 | 32.5799 | 32.5792 | 32.5757 | 32.5717 | 32.5679 | 32.5639 | 32.5587 | 32.5547 | 32.541 | 32.5228 | 32.4939 | 32.4668 | 32.7578 | 32.757 | 32.7562 | 32.7554 | 32.7517 | 32.7474 | 32.7433 | 32.7391 | 32.7335 | 32.7293 | 32.715 | 32.6958 | 32.6658 | 32.6376
BRAMLEY (FLEE) | FERNHURST | PETERSFIELD | MINIMUM HEADROOM | SU 74173 23420 | YES | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.3085 | 16.3017 | 16.301 | 16.2997 | 16.2983 | 16.2967 | 16.2953 | 16.2941 | 16.2929 | 16.2917 | 16.2878 | 16.2793 | 16.123 | 15.909 | 16.3212 | 16.3124 | 16.3116 | 16.31 | 16.3081 | 16.3062 | 16.3043 | 16.3028 | 16.3013 | 16.2997 | 16.2948 | 16.2745 | 16.0612 | 15.8482
|  | PETERSFIELD | CT |  |  | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.3086 | 16.3018 | 16.3013 | 16.3001 | 16.2988 | 16.2975 | 16.2961 | 16.2949 | 16.2937 | 16.2925 | 16.2886 | 16.2801 | 16.1394 | 15.9253 | 16.3213 | 16.3126 | 16.3119 | 16.3105 | 16.3088 | 16.3071 | 16.3053 | 16.3038 | 16.3023 | 16.3007 | 16.2958 | 16.2849 | 16.0775 | 15.8645
|  | PETERSFIELD | LW |  |  | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.3085 | 16.3017 | 16.301 | 16.2997 | 16.2983 | 16.2967 | 16.2953 | 16.2941 | 16.2929 | 16.2917 | 16.2878 | 16.2793 | 16.123 | 15.909 | 16.3212 | 16.3124 | 16.3116 | 16.31 | 16.3081 | 16.3062 | 16.3043 | 16.3028 | 16.3013 | 16.2997 | 16.2948 | 16.2745 | 16.0612 | 15.8482
|  | PETERSFIELD | ST |  |  | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.3091 | 16.309 | 16.3026 | 16.3025 | 16.3022 | 16.3019 | 16.3009 | 16.3001 | 16.2993 | 16.2984 | 16.2958 | 16.2899 | 16.2833 | 16.2768 | 16.3219 | 16.3218 | 16.3136 | 16.3135 | 16.3132 | 16.3128 | 16.3115 | 16.3104 | 16.3094 | 16.3083 | 16.305 | 16.2975 | 16.289 | 16.2216
|  | PETERSFIELD | SP |  |  | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.4504 | 16.309 | 16.309 | 16.3025 | 16.3025 | 16.3022 | 16.3018 | 16.3014 | 16.3012 | 16.3008 | 16.3005 | 16.2995 | 16.2971 | 16.2941 | 16.2911 | 16.3218 | 16.3217 | 16.3135 | 16.3135 | 16.3131 | 16.3126 | 16.3122 | 16.3118 | 16.3113 | 16.3109 | 16.3096 | 16.3066 | 16.3028 | 16.2989
IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE | MINIMUM HEADROOM | SU 98108 80286 | YES | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.6977 | 37.6886 | 37.6793 | 37.6698 | 37.655 | 37.6499 | 37.6339 | 37.6201 | 37.1693 | 36.108 | 28.6118 | 28.6005 | 28.5856 | 28.5541 | 28.5236 | 28.4933 | 28.4633 | 28.4444 | 28.4256 | 28.4053 | 27.9696 | 26.755 | 25.5026 | 24.2718 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1052 | 29.0961 | 29.0868 | 29.0773 | 29.0625 | 29.0575 | 29.0414 | 28.3225 | 27.0817 | 25.8621
|  | PETERSFIELD AVENUE | CT |  |  | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.1693 | 36.108 | 28.6118 | 28.6005 | 28.5856 | 28.5541 | 28.5236 | 28.4933 | 28.4633 | 28.4444 | 28.4256 | 28.4053 | 27.9696 | 26.755 | 25.5026 | 24.2718 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 28.3225 | 27.0817 | 25.8621
|  | PETERSFIELD AVENUE | LW |  |  | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.4815 | 36.4195 | 28.614 | 28.6043 | 28.5914 | 28.5643 | 28.5379 | 28.5118 | 28.4927 | 28.4737 | 28.4549 | 28.4346 | 28.3319 | 27.1173 | 25.8648 | 24.6331 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 28.6815 | 27.4405 | 26.2202
|  | PETERSFIELD AVENUE | ST |  |  | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.6977 | 37.6886 | 37.6793 | 37.6698 | 37.655 | 37.6499 | 37.6339 | 37.6201 | 37.574 | 37.5606 | 28.6193 | 28.6136 | 28.6068 | 28.5952 | 28.572 | 28.5458 | 28.5212 | 28.4966 | 28.4689 | 28.4501 | 28.3937 | 28.3145 | 27.718 | 26.9034 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1052 | 29.0961 | 29.0868 | 29.0773 | 29.0625 | 29.0575 | 29.0414 | 29.0276 | 28.9815 | 28.4683
|  | PETERSFIELD AVENUE | SP |  |  | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 37.7066 | 28.6256 | 28.6246 | 28.6237 | 28.6229 | 28.6189 | 28.6142 | 28.609 | 28.6038 | 28.5972 | 28.5918 | 28.5763 | 28.5516 | 28.528 | 28.5058 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141 | 29.1141
MANNINGTON GSP | SALISBURY | PETERSFINGER | MINIMUM HEADROOM | SU 15608 29334 | YES | 59.5834 | 59.5834 | 59.5834 | 59.5834 | 59.5644 | 59.5449 | 59.5249 | 59.504 | 59.4715 | 59.4603 | 59.4233 | 58.915 | 57.3426 | 55.8425 | 58.1685 | 58.1595 | 58.1511 | 58.1392 | 58.1199 | 58.0896 | 58.0566 | 58.0217 | 57.8527 | 57.7106 | 57.4051 | 55.9552 | 54.2889 | 52.5299 | 58.4352 | 58.4087 | 58.3841 | 58.349 | 58.3061 | 58.2588 | 58.193 | 58.0684 | 57.734 | 57.3404 | 56.4099 | 54.7599 | 52.9418 | 51.2043
|  | PETERSFINGER | CT |  |  | 59.5834 | 59.5834 | 59.5834 | 59.5834 | 59.5833 | 59.5829 | 59.5825 | 59.5818 | 59.5803 | 59.58 | 59.5786 | 59.0422 | 57.4776 | 55.9751 | 58.1686 | 58.1598 | 58.1516 | 58.1401 | 58.1258 | 58.1102 | 58.0925 | 58.0683 | 57.9036 | 57.7621 | 57.4596 | 56.0895 | 54.431 | 52.6832 | 58.4357 | 58.4096 | 58.3856 | 58.3516 | 58.3101 | 58.2647 | 58.2135 | 58.14 | 57.8267 | 57.4813 | 56.554 | 54.9057 | 53.0954 | 51.3555
|  | PETERSFINGER | LW |  |  | 59.5834 | 59.5834 | 59.5834 | 59.5834 | 59.5829 | 59.5817 | 59.58 | 59.5775 | 59.5725 | 59.5717 | 59.5673 | 58.915 | 57.3426 | 55.8425 | 58.1685 | 58.1595 | 58.1511 | 58.1392 | 58.1242 | 58.1074 | 58.0838 | 58.0294 | 57.8527 | 57.7106 | 57.4051 | 55.9552 | 54.2889 | 52.5299 | 58.4352 | 58.4087 | 58.3841 | 58.349 | 58.3061 | 58.2588 | 58.193 | 58.0684 | 57.734 | 57.3404 | 56.4099 | 54.7599 | 52.9418 | 51.2043
|  | PETERSFINGER | ST |  |  | 59.5834 | 59.5834 | 59.5834 | 59.5834 | 59.5644 | 59.5449 | 59.5249 | 59.504 | 59.4715 | 59.4603 | 59.4233 | 59.3911 | 59.2824 | 58.312 | 58.1692 | 58.1662 | 58.1557 | 58.1484 | 58.1199 | 58.0896 | 58.0566 | 58.0217 | 57.9728 | 57.9479 | 57.7177 | 57.3227 | 56.3815 | 55.3343 | 58.4373 | 58.4284 | 58.3976 | 58.3763 | 58.3294 | 58.2782 | 58.22 | 58.1576 | 58.077 | 58.0255 | 57.6127 | 56.5222 | 55.2508 | 54.11
|  | PETERSFINGER | SP |  |  | 59.5834 | 59.5834 | 59.5834 | 59.5834 | 59.5805 | 59.5777 | 59.5748 | 59.5718 | 59.5673 | 59.5544 | 59.5133 | 59.4934 | 59.4292 | 59.375 | 58.1704 | 58.1687 | 58.1632 | 58.16 | 58.1527 | 58.1452 | 58.137 | 58.1285 | 58.118 | 58.0998 | 58.0471 | 58.0063 | 57.9188 | 57.7274 | 58.4409 | 58.436 | 58.4198 | 58.4102 | 58.3944 | 58.3781 | 58.3595 | 58.3401 | 58.3181 | 58.2894 | 58.2143 | 58.133 | 58.0002 | 57.6787
MELKSHAM GSP | AMESBURY | PEWSEY | MINIMUM HEADROOM | SU 14710 59252 | YES | 28.2717 | 28.2717 | 28.2717 | 28.2717 | 28.2621 | 28.2518 | 28.2407 | 28.2284 | 28.2074 | 28.1995 | 28.1675 | 28.129 | 28.0185 | 27.7345 | 26.5118 | 26.5069 | 26.504 | 26.4979 | 26.4883 | 26.4728 | 26.4574 | 26.4403 | 26.4068 | 26.3942 | 26.3486 | 26.1996 | 25.3385 | 24.5932 | 26.5269 | 26.5269 | 26.5269 | 26.5269 | 26.5174 | 26.5071 | 26.4959 | 26.4836 | 26.4627 | 26.4547 | 26.4228 | 26.3843 | 26.2358 | 25.5091
|  | PEWSEY | CT |  |  | 28.2717 | 28.2717 | 28.2717 | 28.2717 | 28.2708 | 28.2691 | 28.2666 | 28.263 | 28.255 | 28.2536 | 28.246 | 28.183 | 28.1126 | 27.8042 | 26.5118 | 26.5069 | 26.504 | 26.4979 | 26.4911 | 26.4836 | 26.4753 | 26.464 | 26.4476 | 26.4381 | 26.4083 | 26.2407 | 25.42 | 24.6612 | 26.5269 | 26.5269 | 26.5269 | 26.5269 | 26.526 | 26.5243 | 26.5219 | 26.5182 | 26.5103 | 26.5088 | 26.5012 | 26.4382 | 26.3176 | 25.5773
|  | PEWSEY | LW |  |  | 28.2717 | 28.2717 | 28.2717 | 28.2717 | 28.2687 | 28.2627 | 28.2532 | 28.24 | 28.2135 | 28.209 | 28.1857 | 28.129 | 28.0185 | 27.7345 | 26.512 | 26.5072 | 26.5045 | 26.4988 | 26.4904 | 26.4789 | 26.4625 | 26.4416 | 26.4068 | 26.3942 | 26.3486 | 26.1996 | 25.3385 | 24.5932 | 26.5269 | 26.5269 | 26.5269 | 26.5269 | 26.524 | 26.5179 | 26.5084 | 26.4952 | 26.4688 | 26.4642 | 26.4409 | 26.3843 | 26.2358 | 25.5091
|  | PEWSEY | ST |  |  | 28.2717 | 28.2717 | 28.2717 | 28.2717 | 28.2621 | 28.2518 | 28.2407 | 28.2284 | 28.2074 | 28.1995 | 28.1675 | 28.1338 | 28.0197 | 27.9798 | 26.5123 | 26.5106 | 26.5058 | 26.5022 | 26.4883 | 26.4728 | 26.4574 | 26.4403 | 26.4136 | 26.4002 | 26.3532 | 26.2959 | 26.1585 | 25.8039 | 26.5269 | 26.5269 | 26.5269 | 26.5269 | 26.5174 | 26.5071 | 26.4959 | 26.4836 | 26.4627 | 26.4547 | 26.4228 | 26.3891 | 26.275 | 26.235
|  | PEWSEY | SP |  |  | 28.2717 | 28.2717 | 28.2717 | 28.2717 | 28.2716 | 28.2716 | 28.2715 | 28.2714 | 28.2711 | 28.2701 | 28.2644 | 28.2598 | 28.238 | 28.2167 | 26.5144 | 26.5142 | 26.5112 | 26.511 | 26.5101 | 26.509 | 26.5075 | 26.5057 | 26.5032 | 26.5001 | 26.4885 | 26.475 | 26.4447 | 26.4155 | 26.5269 | 26.5269 | 26.5269 | 26.5269 | 26.5269 | 26.5268 | 26.5268 | 26.5266 | 26.5264 | 26.5254 | 26.5196 | 26.5151 | 26.4933 | 26.472
CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE | MINIMUM HEADROOM | SY 70169 99809 | YES | 19.8473 | 19.809 | 19.7587 | 19.6523 | 19.548 | 19.4418 | 19.3542 | 19.2666 | 19.1772 | 19.0856 | 18.8134 | 18.3634 | 17.8892 | 17.4435 | 17.8133 | 17.7671 | 17.7065 | 17.5782 | 17.4533 | 17.3288 | 17.2263 | 17.1239 | 17.0199 | 16.9125 | 16.5938 | 16.0674 | 15.5145 | 14.9915 | 18.2548 | 18.2548 | 18.2548 | 18.2548 | 18.2412 | 18.2279 | 18.2145 | 18.2009 | 18.1797 | 18.1206 | 17.9326 | 17.6899 | 17.1369 | 16.6136
|  | PIDDLETRENTHIDE | CT |  |  | 19.8555 | 19.823 | 19.7805 | 19.6905 | 19.6031 | 19.5149 | 19.4265 | 19.3409 | 19.2553 | 19.1643 | 18.8954 | 18.444 | 17.978 | 17.5297 | 17.8231 | 17.784 | 17.7327 | 17.6243 | 17.519 | 17.4144 | 17.3107 | 17.2104 | 17.1101 | 17.0033 | 16.6879 | 16.1602 | 15.6156 | 15.09 | 18.2548 | 18.2548 | 18.2548 | 18.2548 | 18.2546 | 18.2542 | 18.2537 | 18.253 | 18.2514 | 18.2511 | 18.2496 | 17.7827 | 17.2379 | 16.7121
|  | PIDDLETRENTHIDE | LW |  |  | 19.8473 | 19.809 | 19.7587 | 19.6523 | 19.548 | 19.4418 | 19.3542 | 19.2666 | 19.1772 | 19.0856 | 18.8134 | 18.3634 | 17.8892 | 17.4435 | 17.8133 | 17.7671 | 17.7065 | 17.5782 | 17.4533 | 17.3288 | 17.2263 | 17.1239 | 17.0199 | 16.9125 | 16.5938 | 16.0674 | 15.5145 | 14.9915 | 18.2548 | 18.2548 | 18.2548 | 18.2548 | 18.2542 | 18.2529 | 18.251 | 18.2484 | 18.243 | 18.2421 | 18.2164 | 17.6899 | 17.1369 | 16.6136
|  | PIDDLETRENTHIDE | ST |  |  | 19.8541 | 19.8219 | 19.7839 | 19.7185 | 19.6383 | 19.5409 | 19.4906 | 19.4407 | 19.3819 | 19.3195 | 19.136 | 18.8402 | 18.5345 | 18.2401 | 17.8215 | 17.7826 | 17.7368 | 17.6581 | 17.5614 | 17.4448 | 17.3859 | 17.3274 | 17.2586 | 17.1854 | 16.9705 | 16.624 | 16.2677 | 15.9229 | 18.2548 | 18.2548 | 18.2548 | 18.2548 | 18.2546 | 18.2544 | 18.254 | 18.2535 | 18.2522 | 18.2516 | 18.2484 | 18.2442 | 17.8902 | 17.5454
|  | PIDDLETRENTHIDE | SP |  |  | 19.8918 | 19.8877 | 19.8839 | 19.8802 | 19.8494 | 19.8158 | 19.7863 | 19.7567 | 19.7148 | 19.6324 | 19.3766 | 19.1791 | 18.7901 | 18.4524 | 17.8668 | 17.862 | 17.8574 | 17.8529 | 17.8186 | 17.7808 | 17.748 | 17.7151 | 17.669 | 17.5818 | 17.3121 | 17.0925 | 16.6846 | 16.3297 | 18.2548 | 18.2548 | 18.2548 | 18.2548 | 18.2412 | 18.2279 | 18.2145 | 18.2009 | 18.1797 | 18.1206 | 17.9326 | 17.8427 | 17.5581 | 17.3195
BRAMLEY (FLEE) | FERNHURST | PLAISTOW | MINIMUM HEADROOM | TQ 02071 29626 | YES | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5.007 | 5.0041 | 5.0003 | 4.9923 | 4.9845 | 4.9766 | 4.9452 | 4.9141 | 4.8832 | 4.8499 | 4.7514 | 4.5872 | 4.4162 | 4.2478 | 5.0183 | 5.0156 | 5.012 | 5.0044 | 4.997 | 4.9896 | 4.96 | 4.9306 | 4.9015 | 4.8701 | 4.7772 | 4.6223 | 4.4611 | 4.3023
|  | PLAISTOW | CT |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5.007 | 5.0041 | 5.0003 | 4.9923 | 4.9845 | 4.9766 | 4.9689 | 4.9377 | 4.9069 | 4.8735 | 4.775 | 4.6108 | 4.4398 | 4.2717 | 5.0183 | 5.0156 | 5.012 | 5.0044 | 4.997 | 4.9896 | 4.9823 | 4.9529 | 4.9238 | 4.8924 | 4.7995 | 4.6446 | 4.4834 | 4.3248
|  | PLAISTOW | LW |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5.007 | 5.0041 | 5.0003 | 4.9923 | 4.9845 | 4.9766 | 4.9452 | 4.9141 | 4.8832 | 4.8499 | 4.7514 | 4.5872 | 4.4162 | 4.2478 | 5.0183 | 5.0156 | 5.012 | 5.0044 | 4.997 | 4.9896 | 4.96 | 4.9306 | 4.9015 | 4.8701 | 4.7772 | 4.6223 | 4.4611 | 4.3023
|  | PLAISTOW | ST |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5.0085 | 5.0067 | 5.0045 | 5.0009 | 4.9964 | 4.9911 | 4.9721 | 4.9535 | 4.9324 | 4.9097 | 4.8433 | 4.7338 | 4.6236 | 4.5141 | 5.0196 | 5.0179 | 5.0159 | 5.0125 | 5.0083 | 5.0032 | 4.9854 | 4.9678 | 4.9479 | 4.9265 | 4.8639 | 4.7606 | 4.6567 | 4.5535
|  | PLAISTOW | SP |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5.0104 | 5.0101 | 5.0098 | 5.0095 | 5.0082 | 5.0068 | 5.0004 | 4.9942 | 4.9862 | 4.9774 | 4.9517 | 4.9102 | 4.8699 | 4.8315 | 5.0214 | 5.0211 | 5.0208 | 5.0206 | 5.0194 | 5.018 | 5.012 | 5.0062 | 4.9986 | 4.9903 | 4.9661 | 4.927 | 4.889 | 4.8527
MINETY GSP | STRATTON (2 X 90) | PLESSEY Swindon | MINIMUM HEADROOM | SU 16381 86720 | YES | 12.9523 | 14.4188 | 14.3735 | 14.2778 | 14.1827 | 14.086 | 14.0043 | 13.9576 | 13.9078 | 13.8597 | 13.7076 | 13.4287 | 13.0964 | 12.8486 | 10.8014 | 14.6014 | 14.6014 | 14.6014 | 14.5991 | 14.5944 | 14.5869 | 14.5659 | 14.5083 | 14.4519 | 14.282 | 13.9561 | 13.5856 | 13.2947 | 12.944 | 14.3959 | 14.3427 | 14.2303 | 14.1191 | 14.0063 | 13.9098 | 13.8554 | 13.798 | 13.7418 | 13.5723 | 13.2473 | 12.8775 | 12.5875
|  | PLESSEY Swindon | CT |  |  | 12.953 | 14.4199 | 14.3752 | 14.2807 | 14.1883 | 14.0962 | 14.0043 | 13.9576 | 13.9078 | 13.8597 | 13.7145 | 13.4304 | 13.13 | 12.8712 | 10.8014 | 14.6014 | 14.6014 | 14.6014 | 14.6007 | 14.5994 | 14.5974 | 14.5659 | 14.5083 | 14.4519 | 14.282 | 13.9561 | 13.6119 | 13.3101 | 12.9448 | 14.3973 | 14.3447 | 14.2337 | 14.1253 | 14.0174 | 13.9098 | 13.8554 | 13.798 | 13.7418 | 13.5723 | 13.2473 | 12.904 | 12.603
|  | PLESSEY Swindon | LW |  |  | 12.9523 | 14.4188 | 14.3735 | 14.2778 | 14.1827 | 14.086 | 14.0343 | 13.9799 | 13.9156 | 13.8651 | 13.7076 | 13.4287 | 13.0964 | 12.8486 | 10.8014 | 14.6014 | 14.6014 | 14.6014 | 14.5991 | 14.5944 | 14.5869 | 14.5766 | 14.5234 | 14.4645 | 14.2822 | 13.9615 | 13.5856 | 13.2947 | 12.944 | 14.3959 | 14.3427 | 14.2303 | 14.1191 | 14.0063 | 13.9469 | 13.8848 | 13.8129 | 13.7542 | 13.5724 | 13.2526 | 12.8775 | 12.5875
|  | PLESSEY Swindon | ST |  |  | 12.9572 | 14.4772 | 14.3929 | 14.3326 | 14.258 | 14.1676 | 14.1254 | 14.0832 | 14.0486 | 14.0143 | 13.9079 | 13.7353 | 13.5196 | 13.3415 | 10.8014 | 14.6014 | 14.6014 | 14.6014 | 14.6009 | 14.6 | 14.5985 | 14.5963 | 14.5915 | 14.5892 | 14.5106 | 14.3102 | 14.0663 | 13.8602 | 12.9497 | 14.4645 | 14.3655 | 14.2946 | 14.2071 | 14.1012 | 14.0519 | 14.0026 | 13.9629 | 13.923 | 13.8003 | 13.6004 | 13.357 | 13.1515
|  | PLESSEY Swindon | SP |  |  | 12.9923 | 14.5386 | 14.4861 | 14.4828 | 14.4667 | 14.4477 | 14.4333 | 14.4189 | 14.4002 | 14.3844 | 14.3355 | 14.2687 | 14.1807 | 14.0977 | 10.8014 | 14.6014 | 14.6014 | 14.6014 | 14.6008 | 14.6002 | 14.5995 | 14.5988 | 14.5977 | 14.5943 | 14.5816 | 14.5741 | 14.5447 | 14.5177 | 12.9909 | 14.5366 | 14.475 | 14.4711 | 14.4523 | 14.4301 | 14.4133 | 14.3965 | 14.3747 | 14.3568 | 14.3015 | 14.2244 | 14.1262 | 14.0334
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSY TITCHFIELD | MINIMUM HEADROOM | SU 53390 06922 | YES | 22.9161 | 22.8966 | 22.8766 | 21.7842 | 21.6909 | 21.5974 | 21.4981 | 21.3987 | 21.2994 | 21.2528 | 21.1117 | 20.8589 | 20.0293 | 18.7555 | 14.7844 | 14.7655 | 14.7462 | 13.6551 | 13.5631 | 13.471 | 13.3748 | 13.2787 | 13.1826 | 13.1395 | 13.0092 | 12.7801 | 12.6128 | 12.2683 | 18.1724 | 18.1531 | 18.1333 | 17.0412 | 16.9482 | 16.8551 | 16.7566 | 16.6581 | 16.5596 | 16.514 | 16.3757 | 16.1292 | 15.8186 | 14.3569
|  | PLESSY TITCHFIELD | CT |  |  | 23.0018 | 22.9896 | 22.9769 | 22.3201 | 22.2628 | 22.2053 | 22.1478 | 22.0841 | 22.0204 | 21.9882 | 21.8899 | 21.0347 | 20.1196 | 18.846 | 14.8702 | 14.8584 | 14.8464 | 14.1908 | 14.1346 | 14.0784 | 14.0222 | 13.9617 | 13.9013 | 13.8725 | 13.785 | 12.9535 | 12.6179 | 12.3613 | 18.2582 | 18.2461 | 18.2335 | 17.577 | 17.52 | 17.4629 | 17.4057 | 17.3429 | 17.28 | 17.2487 | 17.1533 | 16.3044 | 15.9248 | 14.4631
|  | PLESSY TITCHFIELD | LW |  |  | 22.9161 | 22.8966 | 22.8766 | 21.7842 | 21.6909 | 21.5974 | 21.4981 | 21.3987 | 21.2994 | 21.2528 | 21.1117 | 20.8589 | 20.0293 | 18.7555 | 14.7844 | 14.7655 | 14.7462 | 13.6551 | 13.5631 | 13.471 | 13.3748 | 13.2787 | 13.1826 | 13.1395 | 13.0092 | 12.7801 | 12.6128 | 12.2683 | 18.1724 | 18.1531 | 18.1333 | 17.0412 | 16.9482 | 16.8551 | 16.7566 | 16.6581 | 16.5596 | 16.514 | 16.3757 | 16.1292 | 15.8186 | 14.3569
|  | PLESSY TITCHFIELD | ST |  |  | 23.045 | 23.0367 | 23.0281 | 22.5906 | 22.5521 | 22.5131 | 22.4733 | 22.4334 | 22.3908 | 22.3691 | 22.3031 | 22.1807 | 22.08 | 21.674 | 14.9132 | 14.9053 | 14.8972 | 14.4603 | 14.4228 | 14.3848 | 14.3463 | 14.3078 | 14.2673 | 14.248 | 14.1894 | 14.0832 | 14.0009 | 13.8839 | 18.3013 | 18.2931 | 18.2846 | 17.8472 | 17.809 | 17.7703 | 17.7308 | 17.6913 | 17.6493 | 17.6282 | 17.5642 | 17.446 | 17.3502 | 17.2199
|  | PLESSY TITCHFIELD | SP |  |  | 23.0889 | 23.085 | 23.0811 | 22.8632 | 22.8445 | 22.8258 | 22.8066 | 22.7874 | 22.7679 | 22.7579 | 22.7275 | 22.6713 | 22.6247 | 22.5594 | 14.9568 | 14.953 | 14.9492 | 14.7313 | 14.713 | 14.6945 | 14.6757 | 14.657 | 14.638 | 14.6289 | 14.6014 | 14.5517 | 14.5131 | 14.4561 | 18.3451 | 18.3412 | 18.3374 | 18.1194 | 18.1009 | 18.0822 | 18.0631 | 18.0441 | 18.0247 | 18.0149 | 17.9853 | 17.9308 | 17.8863 | 17.8232
LOVEDEAN GSP | WYMERING BSP | PORTCHESTER | MINIMUM HEADROOM | SU 62043 05575 | NO | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4367 | 35.4292 | 35.4217 | 35.4139 | 35.4017 | 35.4002 | 35.0257 | 34.156 | 33.1319 | 32.1264 | 34.1355 | 34.12 | 34.1108 | 34.0928 | 34.0738 | 33.7803 | 33.6436 | 33.5058 | 33.3682 | 33.2237 | 32.7715 | 31.7736 | 30.5889 | 29.4229 | 34.3092 | 34.2932 | 34.2838 | 34.157 | 33.9003 | 33.6459 | 33.5275 | 33.4081 | 33.2888 | 33.1636 | 32.7389 | 31.7299 | 30.5315 | 29.3518
|  | PORTCHESTER | CT |  |  | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4367 | 35.4292 | 35.4217 | 35.4139 | 35.4017 | 35.4002 | 35.0328 | 34.156 | 33.1319 | 32.1264 | 34.1367 | 34.122 | 34.114 | 34.0984 | 34.0766 | 33.9457 | 33.6861 | 33.5404 | 33.3907 | 33.2447 | 32.7876 | 31.7736 | 30.5889 | 29.4229 | 34.3104 | 34.2953 | 34.2871 | 34.2426 | 34.0141 | 33.7874 | 33.5614 | 33.4341 | 33.3027 | 33.1759 | 32.7557 | 31.7299 | 30.5315 | 29.3518
|  | PORTCHESTER | LW |  |  | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4152 | 35.0257 | 34.1717 | 33.1725 | 32.1734 | 34.1355 | 34.12 | 34.1108 | 34.0928 | 34.0738 | 33.7803 | 33.6436 | 33.5058 | 33.3682 | 33.2237 | 32.7715 | 31.7803 | 30.6206 | 29.461 | 34.3092 | 34.2932 | 34.2838 | 34.157 | 33.9003 | 33.6459 | 33.5275 | 33.4081 | 33.2888 | 33.1636 | 32.7389 | 31.7359 | 30.5624 | 29.389
|  | PORTCHESTER | ST |  |  | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 34.9068 | 34.2509 | 33.6125 | 34.1493 | 34.1303 | 34.1152 | 34.1039 | 34.0905 | 34.0498 | 33.933 | 33.8159 | 33.7221 | 33.6233 | 33.3146 | 32.6335 | 31.8723 | 31.1313 | 34.3235 | 34.3039 | 34.2883 | 34.2766 | 34.1222 | 33.8795 | 33.7783 | 33.6768 | 33.5955 | 33.5099 | 33.2424 | 32.5992 | 31.8289 | 31.0792
|  | PORTCHESTER | SP |  |  | 35.4439 | 35.4439 | 35.4439 | 35.4439 | 35.4417 | 35.4396 | 35.4374 | 35.4352 | 35.4317 | 35.4222 | 35.3918 | 35.3773 | 35.3318 | 35.2937 | 34.1555 | 34.1541 | 34.132 | 34.1309 | 34.1256 | 34.12 | 34.1155 | 34.1109 | 34.1046 | 34.0928 | 34.0556 | 34.0255 | 33.9119 | 33.5291 | 34.3299 | 34.3284 | 34.3057 | 34.3045 | 34.2991 | 34.2934 | 34.2888 | 34.2842 | 34.2777 | 34.2659 | 34.2285 | 34.0792 | 33.7451 | 33.4082
CHICKERELL GSP | CHICKERELL BSP | PORTLAND | MINIMUM HEADROOM | SY 68307 73941 | YES | 24.6777 | 24.6777 | 24.6777 | 24.6777 | 24.6409 | 24.603 | 24.5642 | 24.5232 | 24.4588 | 24.4505 | 24.4222 | 24.2579 | 22.3628 | 20.5757 | 19.5388 | 19.5388 | 19.5388 | 19.5388 | 19.5019 | 19.4635 | 19.4149 | 19.3544 | 19.2706 | 19.2418 | 19.111 | 17.3992 | 15.2057 | 13.1053 | 19.2744 | 19.2744 | 19.2744 | 19.2744 | 19.2375 | 19.1997 | 19.1609 | 19.1199 | 19.0555 | 19.0471 | 19.0188 | 18.8751 | 16.9354 | 14.985
|  | PORTLAND | CT |  |  | 24.6777 | 24.6777 | 24.6777 | 24.6777 | 24.6409 | 24.603 | 24.5642 | 24.5232 | 24.4588 | 24.4505 | 24.4222 | 24.2579 | 22.3628 | 20.5757 | 19.5388 | 19.5388 | 19.5388 | 19.5388 | 19.5019 | 19.4635 | 19.4149 | 19.3544 | 19.2706 | 19.2418 | 19.111 | 17.4138 | 15.2057 | 13.1053 | 19.2744 | 19.2744 | 19.2744 | 19.2744 | 19.2375 | 19.1997 | 19.1609 | 19.1199 | 19.0555 | 19.0471 | 19.0188 | 18.8751 | 16.9354 | 14.985
|  | PORTLAND | LW |  |  | 24.6777 | 24.6777 | 24.6777 | 24.6777 | 24.6731 | 24.6669 | 24.6589 | 24.6491 | 24.6311 | 24.6282 | 24.6146 | 24.2921 | 22.4914 | 20.7435 | 19.5388 | 19.5388 | 19.5388 | 19.5388 | 19.5312 | 19.5118 | 19.4842 | 19.4548 | 19.4175 | 19.3941 | 19.1873 | 17.3992 | 15.2855 | 13.2242 | 19.2744 | 19.2744 | 19.2744 | 19.2744 | 19.2698 | 19.2636 | 19.2556 | 19.2458 | 19.2278 | 19.2248 | 19.2112 | 19.0025 | 17.0387 | 15.1273
|  | PORTLAND | ST |  |  | 24.6777 | 24.6777 | 24.6777 | 24.6777 | 24.6744 | 24.6708 | 24.6668 | 24.6623 | 24.6544 | 24.6513 | 24.6384 | 24.6242 | 24.4162 | 23.2842 | 19.5388 | 19.5388 | 19.5388 | 19.5388 | 19.5355 | 19.5318 | 19.5276 | 19.5107 | 19.4896 | 19.4725 | 19.4157 | 18.9436 | 17.5472 | 16.2148 | 19.2744 | 19.2744 | 19.2744 | 19.2744 | 19.2711 | 19.2674 | 19.2634 | 19.2589 | 19.251 | 19.2479 | 19.235 | 19.2208 | 19.1391 | 17.9026
|  | PORTLAND | SP |  |  | 24.6777 | 24.6777 | 24.6777 | 24.6777 | 24.6777 | 24.6777 | 24.6776 | 24.6776 | 24.6775 | 24.677 | 24.6743 | 24.6721 | 24.6618 | 24.6517 | 19.5388 | 19.5388 | 19.5388 | 19.5388 | 19.5387 | 19.5387 | 19.5387 | 19.5386 | 19.5385 | 19.538 | 19.5339 | 19.4931 | 19.4361 | 19.3365 | 19.2744 | 19.2744 | 19.2744 | 19.2744 | 19.2744 | 19.2743 | 19.2743 | 19.2742 | 19.2741 | 19.2736 | 19.2709 | 19.2688 | 19.2584 | 19.2483
LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH | MINIMUM HEADROOM | SZ 63405 99685 | YES | 27.7963 | 27.7806 | 27.7648 | 26.8044 | 26.7257 | 26.647 | 26.5682 | 26.4895 | 26.4108 | 26.3793 | 26.2848 | 26.1274 | 25.8944 | 24.7445 | 23.7565 | 23.6006 | 23.5287 | 22.4984 | 22.3557 | 22.2084 | 21.9297 | 21.6524 | 21.3784 | 21.1387 | 20.4219 | 19.1629 | 17.9041 | 16.5804 | 27.023 | 26.9988 | 26.9797 | 26.015 | 25.9325 | 25.8496 | 25.7589 | 25.6682 | 25.5778 | 25.5338 | 25.4019 | 24.6984 | 23.4737 | 22.1836
|  | PORTSMOUTH | CT |  |  | 27.8719 | 27.8625 | 27.853 | 27.2768 | 27.2295 | 27.1823 | 27.1351 | 27.0878 | 27.0406 | 27.0217 | 26.965 | 26.276 | 26.004 | 24.8544 | 23.8321 | 23.6825 | 23.6169 | 22.9707 | 22.8595 | 22.7437 | 22.6256 | 22.3797 | 22.1372 | 21.91 | 21.2311 | 19.4405 | 18.0332 | 16.7099 | 27.0985 | 27.0807 | 27.0678 | 26.4874 | 26.4363 | 26.3849 | 26.3334 | 26.2743 | 26.2153 | 26.1839 | 26.0898 | 24.9723 | 23.599 | 22.3093
|  | PORTSMOUTH | LW |  |  | 27.7963 | 27.7806 | 27.7648 | 26.8044 | 26.7257 | 26.647 | 26.5682 | 26.4895 | 26.4108 | 26.3793 | 26.2848 | 26.1274 | 25.8944 | 24.7445 | 23.7565 | 23.6006 | 23.5287 | 22.4984 | 22.3557 | 22.2084 | 21.9297 | 21.6524 | 21.3784 | 21.1387 | 20.4219 | 19.1629 | 17.9041 | 16.5804 | 27.023 | 26.9988 | 26.9797 | 26.015 | 25.9325 | 25.8496 | 25.7589 | 25.6682 | 25.5778 | 25.5338 | 25.4019 | 24.6984 | 23.4737 | 22.1836
|  | PORTSMOUTH | ST |  |  | 27.9097 | 27.9034 | 27.8971 | 27.5129 | 27.4814 | 27.45 | 27.4185 | 27.387 | 27.3555 | 27.3429 | 27.3051 | 27.2421 | 27.2043 | 27.1351 | 23.8847 | 23.8378 | 23.7142 | 23.2968 | 23.2286 | 23.15 | 23.0246 | 22.9 | 22.7354 | 22.5807 | 22.1224 | 21.319 | 20.5276 | 19.715 | 27.1372 | 27.1285 | 27.1151 | 26.729 | 26.6953 | 26.6609 | 26.6238 | 26.5867 | 26.5472 | 26.5261 | 26.463 | 26.3556 | 26.0548 | 25.2638
|  | PORTSMOUTH | SP |  |  | 27.9475 | 27.9443 | 27.9412 | 27.7491 | 27.7334 | 27.7176 | 27.7019 | 27.6861 | 27.6704 | 27.6641 | 27.6452 | 27.6137 | 27.5948 | 27.5602 | 23.9404 | 23.9153 | 23.8976 | 23.7002 | 23.6737 | 23.6439 | 23.6028 | 23.5621 | 23.5156 | 23.4544 | 23.2733 | 22.9565 | 22.6476 | 22.3299 | 27.1761 | 27.1716 | 27.1676 | 26.9752 | 26.9588 | 26.9422 | 26.9249 | 26.9077 | 26.8901 | 26.8805 | 26.8519 | 26.8032 | 26.7669 | 26.7152
BRAMLEY (ANDO-THAT) | ANDOVER BSP | PORTWAY | MINIMUM HEADROOM | SU 34402 46001 | YES | 44.8694 | 44.8619 | 44.8557 | 44.8452 | 44.8285 | 44.8086 | 44.7933 | 44.775 | 44.7467 | 44.5084 | 43.0568 | 40.5557 | 39.597 | 38.8035 | 43.2613 | 43.2389 | 43.2202 | 43.1887 | 43.1384 | 43.0789 | 42.8734 | 42.6252 | 42.2393 | 41.8112 | 40.1768 | 37.2606 | 36.1313 | 35.1964 | 43.7926 | 43.7861 | 43.7807 | 43.7717 | 43.7572 | 43.7331 | 43.5213 | 43.27 | 42.8794 | 42.4462 | 40.8037 | 37.9737 | 36.8889 | 35.9909
|  | PORTWAY | CT |  |  | 44.8694 | 44.8619 | 44.8557 | 44.8452 | 44.8285 | 44.8086 | 44.7933 | 44.775 | 44.7467 | 44.5084 | 43.0568 | 40.5557 | 39.597 | 38.8035 | 43.2613 | 43.2389 | 43.2202 | 43.1887 | 43.1384 | 43.0789 | 42.8734 | 42.6252 | 42.2393 | 41.8112 | 40.1768 | 37.2606 | 36.1313 | 35.1964 | 43.7926 | 43.7861 | 43.7807 | 43.7717 | 43.7572 | 43.7331 | 43.5213 | 43.27 | 42.8794 | 42.4462 | 40.8037 | 37.9737 | 36.8889 | 35.9909
|  | PORTWAY | LW |  |  | 44.8698 | 44.8626 | 44.8568 | 44.8472 | 44.8312 | 44.8122 | 44.796 | 44.7778 | 44.7494 | 44.5416 | 43.09 | 40.5888 | 39.6301 | 38.8363 | 43.2626 | 43.241 | 43.2235 | 43.1946 | 43.1467 | 43.0896 | 42.9104 | 42.6621 | 42.2763 | 41.8484 | 40.2151 | 37.2996 | 36.1702 | 35.2351 | 43.7929 | 43.7867 | 43.7817 | 43.7734 | 43.7596 | 43.7432 | 43.5587 | 43.3075 | 42.9169 | 42.4837 | 40.8413 | 38.0111 | 36.9263 | 36.0281
|  | PORTWAY | ST |  |  | 44.8703 | 44.865 | 44.8611 | 44.8551 | 44.8446 | 44.8319 | 44.8201 | 44.807 | 44.7881 | 44.7665 | 44.0906 | 42.2828 | 41.6425 | 41.1405 | 43.264 | 43.2481 | 43.2363 | 43.2183 | 43.1869 | 43.1487 | 43.1134 | 43.061 | 42.803 | 42.5092 | 41.3442 | 39.2834 | 38.5409 | 37.9494 | 43.7933 | 43.7888 | 43.7854 | 43.7802 | 43.7712 | 43.7602 | 43.7501 | 43.7112 | 43.4501 | 43.1526 | 41.9734 | 39.9279 | 39.2034 | 38.6353
|  | PORTWAY | SP |  |  | 44.8708 | 44.8671 | 44.8648 | 44.8616 | 44.8536 | 44.845 | 44.8375 | 44.8297 | 44.8176 | 44.798 | 44.7291 | 44.5576 | 44.1978 | 43.8869 | 43.2655 | 43.2545 | 43.2474 | 43.2379 | 43.2189 | 43.1981 | 43.1807 | 43.1622 | 43.1338 | 43.097 | 42.7543 | 41.8753 | 41.4793 | 41.1368 | 43.7938 | 43.7906 | 43.7886 | 43.7858 | 43.7786 | 43.7708 | 43.764 | 43.7569 | 43.746 | 43.7276 | 43.4015 | 42.5119 | 42.1117 | 41.7656
IVER 132KV | LONGFORD | POYLE | MINIMUM HEADROOM | TQ 03425 75555 | YES | 30.1856 | 30.1373 | 30.0792 | 28.961 | 28.7914 | 28.6215 | 28.4486 | 28.2756 | 28.0998 | 27.9737 | 27.5956 | 26.9513 | 26.3366 | 25.6698 | 30.1577 | 30.1125 | 30.0585 | 28.949 | 28.7877 | 28.6125 | 28.4217 | 28.2308 | 28.0374 | 27.8922 | 27.4574 | 26.7166 | 26.0003 | 25.2333 | 30.2396 | 30.1906 | 30.1315 | 29.0113 | 28.8396 | 28.6677 | 28.4928 | 28.3177 | 28.1399 | 28.0116 | 27.6269 | 26.9715 | 26.3452 | 25.6622
|  | POYLE | CT |  |  | 30.2778 | 30.2444 | 30.2036 | 29.5204 | 29.4068 | 29.2933 | 29.1802 | 29.0432 | 28.9059 | 28.7941 | 28.4605 | 27.2439 | 26.4798 | 25.8096 | 30.2489 | 30.2177 | 30.18 | 29.5032 | 29.3958 | 29.2885 | 29.1782 | 29.0234 | 28.8684 | 28.7375 | 28.3473 | 27.0342 | 26.1685 | 25.3982 | 30.3322 | 30.2981 | 30.2566 | 29.5719 | 29.4568 | 29.3418 | 29.2271 | 29.0882 | 28.9488 | 28.8348 | 28.4947 | 27.267 | 26.4912 | 25.8095
|  | POYLE | LW |  |  | 30.1856 | 30.1373 | 30.0792 | 28.961 | 28.7914 | 28.6215 | 28.4486 | 28.2756 | 28.0998 | 27.9737 | 27.5956 | 26.9513 | 26.3366 | 25.6698 | 30.1577 | 30.1125 | 30.0585 | 28.949 | 28.7877 | 28.6125 | 28.4217 | 28.2308 | 28.0374 | 27.8922 | 27.4574 | 26.7166 | 26.0003 | 25.2333 | 30.2396 | 30.1906 | 30.1315 | 29.0113 | 28.8396 | 28.6677 | 28.4928 | 28.3177 | 28.1399 | 28.0116 | 27.6269 | 26.9715 | 26.3452 | 25.6622
|  | POYLE | ST |  |  | 30.3153 | 30.2839 | 30.2481 | 29.7859 | 29.6909 | 29.5832 | 29.4801 | 29.3776 | 29.2845 | 29.2081 | 28.981 | 28.6003 | 28.2279 | 27.8364 | 30.2867 | 30.2577 | 30.2247 | 29.7675 | 29.6785 | 29.5781 | 29.4772 | 29.3604 | 29.2552 | 29.1659 | 28.9006 | 28.4555 | 28.0175 | 27.561 | 30.3696 | 30.3376 | 30.301 | 29.8376 | 29.7412 | 29.6317 | 29.527 | 29.4228 | 29.3283 | 29.2504 | 29.019 | 28.6309 | 28.2509 | 27.8519
|  | POYLE | SP |  |  | 30.3839 | 30.3772 | 30.3705 | 30.1611 | 30.1287 | 30.0938 | 30.0539 | 30.0141 | 29.9671 | 29.9309 | 29.8223 | 29.6621 | 29.4949 | 29.3194 | 30.3525 | 30.3461 | 30.3397 | 30.1306 | 30.0997 | 30.0664 | 30.0287 | 29.991 | 29.9469 | 29.913 | 29.8114 | 29.6614 | 29.4697 | 29.2707 | 30.4389 | 30.432 | 30.4253 | 30.2158 | 30.1831 | 30.1477 | 30.1073 | 30.067 | 30.0194 | 29.9826 | 29.8723 | 29.7093 | 29.5392 | 29.361
MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON SE | MINIMUM HEADROOM | SU 16963 86368 | YES | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.204 | 37.1713 | 37.1371 | 37.1017 | 37.0479 | 37.0405 | 37.0149 | 36.9749 | 36.8955 | 36.3912 | 35.6427 | 35.6269 | 35.6224 | 35.613 | 35.5721 | 35.5302 | 35.481 | 35.4307 | 35.362 | 35.3386 | 35.2505 | 34.6855 | 33.8262 | 33.0456 | 35.1739 | 35.1462 | 35.1383 | 35.0856 | 34.9854 | 34.884 | 34.7378 | 34.5908 | 34.4259 | 34.2991 | 33.8067 | 33.0762 | 32.228 | 31.4578
|  | PRESSED STEEL SWINDON SE | CT |  |  | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 36.7941 | 35.643 | 35.6274 | 35.6231 | 35.6143 | 35.6056 | 35.597 | 35.5883 | 35.5734 | 35.5585 | 35.5425 | 35.48 | 35.0135 | 34.2336 | 33.4589 | 35.1744 | 35.1471 | 35.1396 | 35.0951 | 35.0305 | 34.9658 | 34.9012 | 34.7897 | 34.6786 | 34.5593 | 34.0925 | 33.4018 | 32.6345 | 31.8701
|  | PRESSED STEEL SWINDON SE | LW |  |  | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.204 | 37.1713 | 37.1371 | 37.1017 | 37.0479 | 37.0405 | 37.0149 | 36.9749 | 36.8955 | 36.3912 | 35.6427 | 35.6269 | 35.6224 | 35.613 | 35.5721 | 35.5302 | 35.481 | 35.4307 | 35.362 | 35.3386 | 35.2505 | 34.6855 | 33.8262 | 33.0456 | 35.1739 | 35.1462 | 35.1383 | 35.0856 | 34.9854 | 34.884 | 34.7378 | 34.5908 | 34.4259 | 34.2991 | 33.8067 | 33.0762 | 32.228 | 31.4578
|  | PRESSED STEEL SWINDON SE | ST |  |  | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 35.645 | 35.6434 | 35.629 | 35.6257 | 35.6217 | 35.6168 | 35.6055 | 35.5943 | 35.5842 | 35.5733 | 35.5302 | 35.4678 | 35.1281 | 34.6287 | 35.178 | 35.1751 | 35.1499 | 35.1442 | 35.1371 | 35.1138 | 35.0297 | 34.9462 | 34.8706 | 34.7892 | 34.4672 | 34.0008 | 33.5123 | 33.0243
|  | PRESSED STEEL SWINDON SE | SP |  |  | 37.2357 | 37.2357 | 37.2357 | 37.2357 | 37.2346 | 37.2334 | 37.2322 | 37.231 | 37.2292 | 37.224 | 37.2076 | 37.1998 | 37.1751 | 37.1546 | 35.6465 | 35.6461 | 35.6333 | 35.6329 | 35.6301 | 35.6272 | 35.6227 | 35.6183 | 35.6122 | 35.6028 | 35.5697 | 35.5375 | 35.4867 | 35.4401 | 35.1806 | 35.1798 | 35.1574 | 35.1567 | 35.1528 | 35.1485 | 35.1416 | 35.1347 | 35.1221 | 35.0856 | 34.9441 | 34.7546 | 34.5347 | 34.3192
BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER | MINIMUM HEADROOM | SU 60879 41131 | YES | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.6958 | 15.4109 | 14.5035 | 10.0174 | 10.0167 | 10.0158 | 10.0141 | 10.0123 | 10.0105 | 10.0048 | 9.9991 | 9.9933 | 9.9872 | 9.968 | 9.9253 | 9.8744 | 9.5213 | 12.1797 | 12.1785 | 12.1769 | 12.174 | 12.1711 | 12.168 | 12.1585 | 12.1489 | 12.1394 | 12.1292 | 12.097 | 11.8082 | 10.8183 | 9.7953
|  | PRESTON CANDOVER | CT |  |  | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7033 | 15.4919 | 14.5882 | 10.0175 | 10.0169 | 10.016 | 10.0145 | 10.0129 | 10.0112 | 10.0095 | 10.0038 | 9.9981 | 9.992 | 9.9728 | 9.9301 | 9.8792 | 9.6196 | 12.1798 | 12.1788 | 12.1773 | 12.1747 | 12.1721 | 12.1693 | 12.1665 | 12.1569 | 12.1473 | 12.1371 | 12.105 | 11.9005 | 10.9107 | 9.8926
|  | PRESTON CANDOVER | LW |  |  | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.6958 | 15.4109 | 14.5035 | 10.0174 | 10.0167 | 10.0158 | 10.0141 | 10.0123 | 10.0105 | 10.0048 | 9.9991 | 9.9933 | 9.9872 | 9.968 | 9.9253 | 9.8744 | 9.5213 | 12.1797 | 12.1785 | 12.1769 | 12.174 | 12.1711 | 12.168 | 12.1585 | 12.1489 | 12.1394 | 12.1292 | 12.097 | 11.8082 | 10.8183 | 9.7953
|  | PRESTON CANDOVER | ST |  |  | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.6896 | 15.6383 | 10.0176 | 10.017 | 10.0164 | 10.0154 | 10.0142 | 10.0127 | 10.009 | 10.0053 | 10.0014 | 9.9972 | 9.9841 | 9.9548 | 9.9214 | 9.8888 | 12.18 | 12.1791 | 12.178 | 12.1763 | 12.1742 | 12.1717 | 12.1656 | 12.1594 | 12.1529 | 12.1459 | 12.1239 | 12.0749 | 11.7314 | 11.0975
|  | PRESTON CANDOVER | SP |  |  | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 15.7205 | 10.0181 | 10.0179 | 10.0177 | 10.0176 | 10.0172 | 10.0168 | 10.0158 | 10.0148 | 10.0136 | 10.0119 | 10.0068 | 9.995 | 9.9804 | 9.9651 | 12.1807 | 12.1805 | 12.1802 | 12.1799 | 12.1793 | 12.1786 | 12.1769 | 12.1753 | 12.1732 | 12.1705 | 12.162 | 12.1422 | 12.1177 | 12.0922
CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN | MINIMUM HEADROOM | SY 74226 95039 | YES | 16.923 | 16.8616 | 16.7823 | 16.637 | 16.4599 | 16.2893 | 16.2326 | 16.1738 | 16.1101 | 16.0442 | 15.8597 | 15.5651 | 15.2856 | 15.0228 | 16.0038 | 15.9162 | 15.8032 | 15.5992 | 15.3894 | 15.1891 | 15.1226 | 15.0536 | 14.9788 | 14.9014 | 14.6848 | 14.3389 | 14.0108 | 13.7022 | 16.2004 | 16.116 | 16.0071 | 15.8104 | 15.6083 | 15.4153 | 15.3512 | 15.2846 | 15.2126 | 15.1379 | 14.9292 | 14.5958 | 14.2796 | 13.971
|  | PUDDLETOWN | CT |  |  | 16.932 | 16.8769 | 16.806 | 16.6805 | 16.531 | 16.381 | 16.2663 | 16.2076 | 16.144 | 16.078 | 15.8936 | 15.5988 | 15.3195 | 15.0568 | 16.0166 | 15.9381 | 15.837 | 15.6582 | 15.473 | 15.2968 | 15.1622 | 15.0933 | 15.0185 | 14.9411 | 14.7246 | 14.3785 | 14.0506 | 13.7422 | 16.2127 | 16.1371 | 16.0397 | 15.8674 | 15.6888 | 15.5191 | 15.3893 | 15.3229 | 15.2508 | 15.1762 | 14.9676 | 14.634 | 14.3179 | 14.011
|  | PUDDLETOWN | LW |  |  | 16.923 | 16.8616 | 16.7823 | 16.637 | 16.4599 | 16.2893 | 16.2326 | 16.1738 | 16.1101 | 16.0442 | 15.8597 | 15.5651 | 15.2856 | 15.0228 | 16.0038 | 15.9162 | 15.8032 | 15.5992 | 15.3894 | 15.1891 | 15.1226 | 15.0536 | 14.9788 | 14.9014 | 14.6848 | 14.3389 | 14.0108 | 13.7022 | 16.2004 | 16.116 | 16.0071 | 15.8104 | 15.6083 | 15.4153 | 15.3512 | 15.2846 | 15.2126 | 15.1379 | 14.9292 | 14.5958 | 14.2796 | 13.971
|  | PUDDLETOWN | ST |  |  | 16.9329 | 16.8832 | 16.8248 | 16.7357 | 16.6217 | 16.4736 | 16.4317 | 16.3885 | 16.3453 | 16.3002 | 16.1747 | 15.9763 | 15.7957 | 15.6248 | 16.0179 | 15.9471 | 15.8639 | 15.7368 | 15.5807 | 15.4056 | 15.3564 | 15.3056 | 15.2549 | 15.202 | 15.0546 | 14.8217 | 14.6097 | 14.409 | 16.214 | 16.1457 | 16.0656 | 15.9431 | 15.7927 | 15.6238 | 15.5765 | 15.5275 | 15.4786 | 15.4277 | 15.2856 | 15.0611 | 14.8568 | 14.6634
|  | PUDDLETOWN | SP |  |  | 16.9742 | 16.9583 | 16.9419 | 16.9252 | 16.8932 | 16.8609 | 16.8477 | 16.8341 | 16.8163 | 16.8018 | 16.7616 | 16.6985 | 16.6424 | 16.5844 | 16.0767 | 16.0539 | 16.0306 | 16.0069 | 15.9613 | 15.9153 | 15.8964 | 15.877 | 15.8517 | 15.8311 | 15.7738 | 15.684 | 15.6056 | 15.5358 | 16.2707 | 16.2487 | 16.2263 | 16.2034 | 16.1595 | 16.1151 | 16.0969 | 16.0782 | 16.0538 | 16.0339 | 15.9787 | 15.8922 | 15.8166 | 15.7493
AXMINSTER | YEOVIL BSP | PULHAM | MINIMUM HEADROOM | ST 71579 09451 | YES | 6.3 | 6.3 | 6.3 | 6.3 | 6.2938 | 6.2869 | 6.2791 | 6.269 | 6.2401 | 6.235 | 6.2083 | 6.1437 | 6.0153 | 6.0062 | 6.7643 | 6.7351 | 6.6968 | 6.6157 | 6.5346 | 6.4516 | 6.4092 | 6.3626 | 6.3012 | 6.2612 | 6.1313 | 5.8968 | 5.5928 | 5.411 | 6.7823 | 6.7526 | 6.7137 | 6.6311 | 6.5486 | 6.4643 | 6.4213 | 6.3741 | 6.3122 | 6.2715 | 6.1398 | 5.9023 | 5.5952 | 5.4104
|  | PULHAM | CT |  |  | 6.3 | 6.3 | 6.3 | 6.3 | 6.2992 | 6.2978 | 6.2957 | 6.2909 | 6.2795 | 6.2775 | 6.2673 | 6.184 | 6.0848 | 6.0541 | 6.7716 | 6.7478 | 6.7165 | 6.6502 | 6.5851 | 6.52 | 6.4548 | 6.4173 | 6.3736 | 6.3367 | 6.2233 | 5.9698 | 5.695 | 5.4916 | 6.7898 | 6.7655 | 6.7336 | 6.6662 | 6.6 | 6.5338 | 6.4675 | 6.4294 | 6.3851 | 6.3476 | 6.2324 | 5.9759 | 5.6981 | 5.4916
|  | PULHAM | LW |  |  | 6.3 | 6.3 | 6.3 | 6.3 | 6.2975 | 6.2923 | 6.283 | 6.269 | 6.2401 | 6.235 | 6.2083 | 6.1437 | 6.0153 | 6.0062 | 6.7643 | 6.7351 | 6.6968 | 6.6157 | 6.5346 | 6.4516 | 6.4092 | 6.3626 | 6.3012 | 6.2612 | 6.1313 | 5.8968 | 5.5928 | 5.411 | 6.7823 | 6.7526 | 6.7137 | 6.6311 | 6.5486 | 6.4643 | 6.4213 | 6.3741 | 6.3122 | 6.2715 | 6.1398 | 5.9023 | 5.5952 | 5.4104
|  | PULHAM | ST |  |  | 6.3 | 6.3 | 6.3 | 6.3 | 6.2938 | 6.2869 | 6.2791 | 6.2698 | 6.2532 | 6.2467 | 6.2195 | 6.1893 | 6.0845 | 6.0481 | 6.7669 | 6.7406 | 6.7095 | 6.6563 | 6.5849 | 6.4994 | 6.4701 | 6.4397 | 6.401 | 6.3706 | 6.2739 | 6.1309 | 5.9132 | 5.7643 | 6.785 | 6.7581 | 6.7265 | 6.6724 | 6.5998 | 6.513 | 6.4833 | 6.4525 | 6.4134 | 6.3827 | 6.2847 | 6.1397 | 5.92 | 5.7692
|  | PULHAM | SP |  |  | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.2999 | 6.2999 | 6.2998 | 6.2994 | 6.2983 | 6.2918 | 6.2868 | 6.2642 | 6.2425 | 6.7981 | 6.795 | 6.7921 | 6.7892 | 6.7759 | 6.7603 | 6.7525 | 6.7447 | 6.7345 | 6.7241 | 6.6907 | 6.6431 | 6.5795 | 6.5191 | 6.8167 | 6.8136 | 6.8106 | 6.8076 | 6.7941 | 6.7782 | 6.7703 | 6.7623 | 6.752 | 6.7415 | 6.7076 | 6.6592 | 6.5949 | 6.5339
LOVEDEAN GSP | FORT WIDLEY | PURBROOK | MINIMUM HEADROOM | SU 67047 07819 | NO | 8 | 8 | 8 | 8 | 7.9691 | 7.9054 | 7.8053 | 7.6667 | 7.4308 | 7.3946 | 7.2405 | 6.9246 | 6.3379 | 6.3008 | 4.9776 | 4.9614 | 4.9401 | 4.895 | 4.8204 | 4.7133 | 4.5597 | 4.3682 | 4.0798 | 3.987 | 3.6657 | 3.0741 | 2.2024 | 1.8849 | 4.9777 | 4.9615 | 4.9403 | 4.8953 | 4.8209 | 4.7139 | 4.5605 | 4.3691 | 4.0809 | 3.9883 | 3.6674 | 3.0767 | 2.2059 | 1.8892
|  | PURBROOK | CT |  |  | 8 | 8 | 8 | 8 | 7.9906 | 7.973 | 7.9469 | 7.9089 | 7.8408 | 7.8306 | 7.7857 | 7.4696 | 7.1252 | 7.0301 | 4.9815 | 4.968 | 4.9503 | 4.9129 | 4.8671 | 4.8135 | 4.7517 | 4.6608 | 4.5402 | 4.4733 | 4.2614 | 3.6694 | 3.0402 | 2.6647 | 4.9815 | 4.9681 | 4.9504 | 4.9131 | 4.8675 | 4.814 | 4.7523 | 4.6616 | 4.5411 | 4.4744 | 4.263 | 3.6718 | 3.0435 | 2.6689
|  | PURBROOK | LW |  |  | 8 | 8 | 8 | 8 | 7.9691 | 7.9054 | 7.8053 | 7.6667 | 7.4308 | 7.3946 | 7.2405 | 6.9246 | 6.3379 | 6.3008 | 4.9776 | 4.9614 | 4.9401 | 4.895 | 4.8204 | 4.7133 | 4.5597 | 4.3682 | 4.0798 | 3.987 | 3.6657 | 3.0741 | 2.2024 | 1.8849 | 4.9777 | 4.9615 | 4.9403 | 4.8953 | 4.8209 | 4.7139 | 4.5605 | 4.3691 | 4.0809 | 3.9883 | 3.6674 | 3.0767 | 2.2059 | 1.8892
|  | PURBROOK | ST |  |  | 8 | 8 | 8 | 8 | 7.9935 | 7.9805 | 7.9609 | 7.9318 | 7.8795 | 7.8583 | 7.7655 | 7.6592 | 7.3072 | 7.1895 | 4.9798 | 4.9656 | 4.9489 | 4.9203 | 4.8787 | 4.8235 | 4.7735 | 4.7146 | 4.6264 | 4.5667 | 4.3611 | 4.0716 | 3.536 | 3.2359 | 4.9798 | 4.9657 | 4.9491 | 4.9206 | 4.879 | 4.8239 | 4.7741 | 4.7153 | 4.6272 | 4.5676 | 4.3623 | 4.0734 | 3.5384 | 3.2388
|  | PURBROOK | SP |  |  | 8 | 8 | 8 | 8 | 7.9998 | 7.9992 | 7.9983 | 7.9969 | 7.9939 | 7.9821 | 7.9143 | 7.8604 | 7.6026 | 7.3513 | 4.9964 | 4.9947 | 4.9931 | 4.9916 | 4.984 | 4.9749 | 4.9651 | 4.955 | 4.9404 | 4.9137 | 4.8024 | 4.6791 | 4.3548 | 4.0406 | 4.9964 | 4.9947 | 4.9931 | 4.9916 | 4.9841 | 4.975 | 4.9652 | 4.9551 | 4.9406 | 4.9139 | 4.8027 | 4.6797 | 4.3556 | 4.0416
MINETY GSP | TOOTHILL BSP | QUARRY ROAD | MINIMUM HEADROOM | SU 15334 83380 | YES | 12.9931 | 12.9766 | 12.9471 | 12.9022 | 12.8508 | 12.774 | 12.5988 | 12.4095 | 12.2074 | 12.0501 | 11.5143 | 10.528 | 9.4098 | 8.4213 | 11.2145 | 11.2134 | 11.2114 | 11.2085 | 11.1787 | 11.1435 | 11.0998 | 11.0523 | 10.8977 | 10.7146 | 10.0915 | 8.9449 | 7.6558 | 6.4968 | 11.173 | 11.1602 | 11.1373 | 11.1025 | 11.0621 | 10.9895 | 10.846 | 10.6907 | 10.5204 | 10.3964 | 9.9731 | 8.9707 | 7.7114 | 6.5823
|  | QUARRY ROAD | CT |  |  | 12.9931 | 12.9766 | 12.9471 | 12.9022 | 12.8508 | 12.7757 | 12.6958 | 12.5393 | 12.3883 | 12.2384 | 11.7309 | 10.7613 | 9.7209 | 8.7229 | 11.2145 | 11.2134 | 11.2114 | 11.2085 | 11.2027 | 11.195 | 11.1867 | 11.172 | 11.0805 | 10.9047 | 10.31 | 9.1801 | 7.9688 | 6.8002 | 11.173 | 11.1602 | 11.1373 | 11.1025 | 11.0621 | 11.0031 | 10.9405 | 10.818 | 10.6989 | 10.5823 | 10.1873 | 9.2056 | 8.0241 | 6.8854
|  | QUARRY ROAD | LW |  |  | 12.9993 | 12.9873 | 12.9637 | 12.9314 | 12.8655 | 12.774 | 12.5988 | 12.4095 | 12.2074 | 12.0501 | 11.5143 | 10.528 | 9.4098 | 8.4213 | 11.2149 | 11.2141 | 11.2125 | 11.2104 | 11.1787 | 11.1435 | 11.0998 | 11.0523 | 10.8977 | 10.7146 | 10.0915 | 8.9449 | 7.6558 | 6.4968 | 11.1778 | 11.1685 | 11.1502 | 11.1252 | 11.0675 | 10.9895 | 10.846 | 10.6907 | 10.5204 | 10.3964 | 9.9731 | 8.9707 | 7.7114 | 6.5823
|  | QUARRY ROAD | ST |  |  | 13.0014 | 12.9929 | 12.977 | 12.9574 | 12.905 | 12.8351 | 12.7124 | 12.581 | 12.4345 | 12.3153 | 11.9069 | 11.213 | 10.4047 | 9.7259 | 11.215 | 11.2144 | 11.2134 | 11.2121 | 11.1818 | 11.1496 | 11.1131 | 11.0746 | 11.0177 | 10.9935 | 10.5544 | 9.7486 | 8.8276 | 8.0403 | 11.1795 | 11.1728 | 11.1605 | 11.1453 | 11.0982 | 11.0374 | 10.9354 | 10.8263 | 10.7014 | 10.605 | 10.2751 | 9.7256 | 8.8523 | 8.084
|  | QUARRY ROAD | SP |  |  | 13.004 | 12.9989 | 12.9896 | 12.98 | 12.9683 | 12.9496 | 12.9161 | 12.8805 | 12.8434 | 12.8011 | 12.6551 | 12.3873 | 12.0763 | 11.7549 | 11.2152 | 11.2148 | 11.2142 | 11.2136 | 11.2124 | 11.2108 | 11.2082 | 11.2054 | 11.2023 | 11.1974 | 11.1799 | 11.0785 | 10.7165 | 10.3419 | 11.1814 | 11.1775 | 11.1703 | 11.1628 | 11.1537 | 11.1391 | 11.113 | 11.0853 | 11.0563 | 11.023 | 10.9079 | 10.6992 | 10.454 | 10.2011
BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD | MINIMUM HEADROOM | SU 87062 55683 | YES | 31.1656 | 31.1537 | 31.1417 | 30.4125 | 30.3528 | 30.293 | 30.2332 | 30.1735 | 30.1137 | 30.0898 | 30.0181 | 29.8985 | 28.8367 | 27.3179 | 23.644 | 23.6241 | 23.6019 | 22.853 | 22.7735 | 22.6933 | 22.6158 | 22.5069 | 22.2082 | 21.9601 | 21.234 | 19.7292 | 18.0347 | 16.2851 | 23.97 | 23.9502 | 23.9279 | 23.179 | 23.0994 | 23.0192 | 22.9417 | 22.8634 | 22.7843 | 22.7423 | 22.3199 | 21.2401 | 19.6424 | 17.9334
|  | QUEENSMEAD | CT |  |  | 31.223 | 31.2158 | 31.2087 | 30.7711 | 30.7353 | 30.6994 | 30.6636 | 30.6277 | 30.5918 | 30.5775 | 30.5345 | 30.0114 | 28.8565 | 27.338 | 23.7018 | 23.6871 | 23.67 | 23.2138 | 23.159 | 23.1036 | 23.048 | 22.984 | 22.7093 | 22.4707 | 21.7735 | 19.8649 | 18.0577 | 16.3087 | 24.0279 | 24.0131 | 23.9961 | 23.5397 | 23.4849 | 23.4295 | 23.3738 | 23.3194 | 23.2643 | 23.2319 | 22.8507 | 21.3743 | 19.6648 | 17.9563
|  | QUEENSMEAD | LW |  |  | 31.1656 | 31.1537 | 31.1417 | 30.4125 | 30.3528 | 30.293 | 30.2332 | 30.1735 | 30.1137 | 30.0898 | 30.0181 | 29.8985 | 28.8367 | 27.3179 | 23.644 | 23.6241 | 23.6019 | 22.853 | 22.7735 | 22.6933 | 22.6158 | 22.5069 | 22.2082 | 21.9601 | 21.234 | 19.7292 | 18.0347 | 16.2851 | 23.97 | 23.9502 | 23.9279 | 23.179 | 23.0994 | 23.0192 | 22.9417 | 22.8634 | 22.7843 | 22.7423 | 22.3199 | 21.2401 | 19.6424 | 17.9334
|  | QUEENSMEAD | ST |  |  | 31.2517 | 31.2469 | 31.2421 | 30.9505 | 30.9265 | 30.9026 | 30.8787 | 30.8548 | 30.8309 | 30.8214 | 30.7927 | 30.7449 | 30.7162 | 30.4555 | 23.7341 | 23.7247 | 23.7146 | 23.4146 | 23.3805 | 23.3442 | 23.3059 | 23.2672 | 23.2303 | 23.2084 | 22.963 | 21.963 | 20.8692 | 19.7835 | 24.0601 | 24.0508 | 24.0406 | 23.7406 | 23.7064 | 23.6701 | 23.6318 | 23.5931 | 23.5562 | 23.5342 | 23.4694 | 23.0481 | 22.3546 | 21.3443
|  | QUEENSMEAD | SP |  |  | 31.2804 | 31.278 | 31.2756 | 31.1298 | 31.1178 | 31.1058 | 31.0939 | 31.0819 | 31.07 | 31.0652 | 31.0509 | 31.027 | 31.0126 | 30.9863 | 23.7662 | 23.7622 | 23.7582 | 23.6107 | 23.5948 | 23.5782 | 23.5609 | 23.5435 | 23.5247 | 23.5152 | 23.4868 | 23.4319 | 23.38 | 22.8777 | 24.0923 | 24.0883 | 24.0842 | 23.9367 | 23.9208 | 23.9043 | 23.887 | 23.8695 | 23.8507 | 23.8411 | 23.8127 | 23.7578 | 23.7058 | 23.6405
MELKSHAM GSP | WEST GRAFTON | RAMSBURY | MINIMUM HEADROOM | SU 27380 72108 | YES | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.5791 | 14.7333 | 13.8965 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.8204 | 13.9704 | 12.9894 | 12.0189 | 14.6899 | 14.6811 | 14.581 | 14.4839 | 14.388 | 14.1749 | 13.9351 | 13.6997 | 13.4624 | 13.2476 | 12.7903 | 11.9254 | 10.9272 | 9.9396
|  | RAMSBURY | CT |  |  | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.6288 | 14.783 | 13.9464 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.8782 | 14.0281 | 13.0471 | 12.0768 | 14.6903 | 14.6873 | 14.595 | 14.5085 | 14.4229 | 14.2198 | 13.9938 | 13.7585 | 13.5212 | 13.3063 | 12.8491 | 11.984 | 10.9858 | 9.9986
|  | RAMSBURY | LW |  |  | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.5791 | 14.7333 | 13.8965 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.8204 | 13.9704 | 12.9894 | 12.0189 | 14.6899 | 14.6811 | 14.581 | 14.4839 | 14.388 | 14.1749 | 13.9351 | 13.6997 | 13.4624 | 13.2476 | 12.7903 | 11.9254 | 10.9272 | 9.9396
|  | RAMSBURY | ST |  |  | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7435 | 15.2104 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.8065 | 14.161 | 13.5428 | 14.6908 | 14.6882 | 14.6325 | 14.5782 | 14.5115 | 14.3535 | 14.1736 | 13.9971 | 13.8375 | 13.6904 | 13.3743 | 12.7761 | 12.1193 | 11.4903
|  | RAMSBURY | SP |  |  | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 15.7614 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.9279 | 14.6931 | 14.6924 | 14.69 | 14.6896 | 14.6882 | 14.6436 | 14.5728 | 14.5059 | 14.4332 | 14.3754 | 14.252 | 14.0082 | 13.7143 | 13.4115
BRAMLEY (FLEE) | READING BSP | READING | MINIMUM HEADROOM | SU 74591 73788 | YES | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.487 | 9.4643 | 9.4413 | 9.4173 | 9.3803 | 9.3756 | 9.3605 | 9.289 | 9.2098 | 9.1702 | 5.451 | 5.4313 | 5.4055 | 5.3508 | 5.2877 | 5.2248 | 5.1647 | 5.0958 | 5.0142 | 4.9615 | 4.8048 | 4.5007 | 4.1817 | 3.9254 | 5.8458 | 5.8291 | 5.8072 | 5.7607 | 5.7056 | 5.6506 | 5.5924 | 5.5302 | 5.4554 | 5.4099 | 5.2746 | 5.0055 | 4.7226 | 4.5018
|  | READING | CT |  |  | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.487 | 9.4643 | 9.4413 | 9.4173 | 9.3803 | 9.3756 | 9.3605 | 9.289 | 9.2098 | 9.1702 | 5.4547 | 5.4377 | 5.4155 | 5.3683 | 5.3004 | 5.2326 | 5.1647 | 5.0958 | 5.0142 | 4.9615 | 4.8048 | 4.5007 | 4.1817 | 3.9254 | 5.849 | 5.8345 | 5.8156 | 5.7756 | 5.7146 | 5.6535 | 5.5924 | 5.5302 | 5.4554 | 5.4099 | 5.2746 | 5.0055 | 4.7226 | 4.5018
|  | READING | LW |  |  | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.4991 | 9.4887 | 9.4778 | 9.4665 | 9.4493 | 9.4469 | 9.4387 | 9.4266 | 9.3958 | 9.3434 | 5.451 | 5.4313 | 5.4055 | 5.3508 | 5.2877 | 5.2248 | 5.1685 | 5.1123 | 5.0506 | 5.0002 | 4.8504 | 4.6057 | 4.3351 | 4.0975 | 5.8458 | 5.8291 | 5.8072 | 5.7607 | 5.7056 | 5.6506 | 5.6011 | 5.5517 | 5.4967 | 5.4536 | 5.3251 | 5.1154 | 4.881 | 4.679
|  | READING | ST |  |  | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 5.5433 | 5.4537 | 5.4419 | 5.4215 | 5.3966 | 5.3665 | 5.3367 | 5.3073 | 5.2769 | 5.2441 | 5.1486 | 4.994 | 4.8397 | 4.6862 | 5.9242 | 5.8481 | 5.838 | 5.8207 | 5.7996 | 5.774 | 5.7488 | 5.7238 | 5.6979 | 5.6701 | 5.589 | 5.4577 | 5.3266 | 5.1962
|  | READING | SP |  |  | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 9.5092 | 5.5533 | 5.5513 | 5.4698 | 5.468 | 5.4592 | 5.4488 | 5.4384 | 5.4281 | 5.4149 | 5.4021 | 5.3653 | 5.3068 | 5.251 | 5.1984 | 5.9327 | 5.9309 | 5.8618 | 5.8602 | 5.8527 | 5.8439 | 5.8351 | 5.8263 | 5.8151 | 5.8043 | 5.773 | 5.7233 | 5.6759 | 5.6312
BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN | MINIMUM HEADROOM | SU 71540 74122 | YES | 28.1714 | 28.1714 | 28.1714 | 28.1714 | 28.1683 | 28.162 | 28.152 | 28.1383 | 28.1106 | 28.1058 | 28.0814 | 27.5881 | 26.7763 | 26.0867 | 12.591 | 12.5898 | 12.5881 | 12.5847 | 12.5778 | 12.567 | 12.5484 | 12.5257 | 12.49 | 12.477 | 12.0843 | 11.264 | 10.3663 | 9.5927 | 13.0034 | 13.0034 | 13.0034 | 13.0034 | 13.0003 | 12.994 | 12.984 | 12.9703 | 12.9426 | 12.7957 | 12.3471 | 11.5922 | 10.7151 | 9.9617
|  | READING TOWN | CT |  |  | 28.1714 | 28.1714 | 28.1714 | 28.1714 | 28.1705 | 28.1687 | 28.1661 | 28.1623 | 28.154 | 28.1525 | 28.1445 | 27.7568 | 26.9872 | 26.2833 | 12.5912 | 12.5901 | 12.5887 | 12.5857 | 12.5814 | 12.5756 | 12.5687 | 12.5561 | 12.5397 | 12.53 | 12.2735 | 11.4464 | 10.5911 | 9.8031 | 13.0034 | 13.0034 | 13.0034 | 13.0034 | 13.0025 | 13.0007 | 12.9981 | 12.9943 | 12.986 | 12.9559 | 12.5237 | 11.7714 | 10.9366 | 10.1688
|  | READING TOWN | LW |  |  | 28.1714 | 28.1714 | 28.1714 | 28.1714 | 28.1683 | 28.162 | 28.152 | 28.1383 | 28.1106 | 28.1058 | 28.0814 | 27.5881 | 26.7763 | 26.0867 | 12.591 | 12.5898 | 12.5881 | 12.5847 | 12.5778 | 12.567 | 12.5484 | 12.5257 | 12.49 | 12.477 | 12.0843 | 11.264 | 10.3663 | 9.5927 | 13.0034 | 13.0034 | 13.0034 | 13.0034 | 13.0003 | 12.994 | 12.984 | 12.9703 | 12.9426 | 12.7957 | 12.3471 | 11.5922 | 10.7151 | 9.9617
|  | READING TOWN | ST |  |  | 28.1714 | 28.1714 | 28.1714 | 28.1714 | 28.1707 | 28.1694 | 28.1675 | 28.1646 | 28.1582 | 28.1551 | 28.1384 | 28.1166 | 27.862 | 27.3908 | 12.5913 | 12.5904 | 12.5892 | 12.5873 | 12.5839 | 12.579 | 12.5731 | 12.5661 | 12.5542 | 12.5455 | 12.5129 | 12.1496 | 11.5693 | 11.0435 | 13.0034 | 13.0034 | 13.0034 | 13.0034 | 13.0027 | 13.0015 | 12.9995 | 12.9966 | 12.9902 | 12.9871 | 12.887 | 12.4094 | 11.8796 | 11.3773
|  | READING TOWN | SP |  |  | 28.1714 | 28.1714 | 28.1714 | 28.1714 | 28.1714 | 28.1713 | 28.1712 | 28.1711 | 28.1708 | 28.1698 | 28.1638 | 28.159 | 28.1362 | 28.1139 | 12.5924 | 12.5923 | 12.5921 | 12.592 | 12.5913 | 12.5902 | 12.5888 | 12.5873 | 12.5857 | 12.5825 | 12.5703 | 12.5559 | 12.5239 | 12.493 | 13.0034 | 13.0034 | 13.0034 | 13.0034 | 13.0034 | 13.0033 | 13.0032 | 13.0031 | 13.0029 | 13.0018 | 12.9958 | 12.991 | 12.9682 | 12.9454
MANNINGTON GSP | REDHILL BSP | REDHILL | MINIMUM HEADROOM | SZ 08512 96149 | YES | 67.0996 | 67.0844 | 67.0693 | 66.147 | 66.0714 | 65.9958 | 65.9202 | 65.8446 | 65.769 | 65.7387 | 65.648 | 64.3973 | 62.0092 | 59.6523 | 51.8752 | 51.8022 | 51.7573 | 50.7731 | 50.6372 | 50.5014 | 50.3808 | 50.2271 | 50.0427 | 49.896 | 49.4475 | 46.953 | 44.1183 | 41.359 | 52.2515 | 52.2093 | 52.1803 | 51.229 | 51.1252 | 51.0215 | 50.9249 | 50.8283 | 50.7317 | 50.5847 | 49.4976 | 46.9188 | 44.1868 | 41.5298
|  | REDHILL | CT |  |  | 67.1721 | 67.1631 | 67.154 | 66.6006 | 66.5552 | 66.5099 | 66.4645 | 66.4191 | 66.3738 | 66.3556 | 66.3012 | 64.3973 | 62.0092 | 59.6523 | 51.9443 | 51.8748 | 51.8327 | 51.2105 | 51.0982 | 50.9861 | 50.8332 | 50.6787 | 50.5245 | 50.3898 | 49.8967 | 46.953 | 44.1183 | 41.359 | 52.3224 | 52.2851 | 52.2606 | 51.6751 | 51.5984 | 51.5218 | 51.4455 | 51.3792 | 51.2042 | 50.8735 | 49.7724 | 46.9188 | 44.1868 | 41.5298
|  | REDHILL | LW |  |  | 67.0996 | 67.0844 | 67.0693 | 66.147 | 66.0714 | 65.9958 | 65.9202 | 65.8446 | 65.769 | 65.7387 | 65.648 | 64.4965 | 62.3419 | 59.9846 | 51.8752 | 51.8022 | 51.7573 | 50.7731 | 50.6372 | 50.5014 | 50.3808 | 50.2271 | 50.0427 | 49.896 | 49.4475 | 47.2047 | 44.5122 | 41.7523 | 52.2515 | 52.2093 | 52.1803 | 51.229 | 51.1252 | 51.0215 | 50.9249 | 50.8283 | 50.7317 | 50.5847 | 49.4976 | 47.1549 | 44.5651 | 41.9076
|  | REDHILL | ST |  |  | 67.2084 | 67.2024 | 67.1963 | 66.8274 | 66.7972 | 66.7669 | 66.7367 | 66.7064 | 66.6762 | 66.6641 | 66.6278 | 66.5673 | 66.0252 | 64.8724 | 51.9977 | 51.9794 | 51.9236 | 51.5303 | 51.4703 | 51.404 | 51.3387 | 51.2735 | 51.2127 | 51.1678 | 50.9814 | 50.4364 | 49.0446 | 47.3132 | 52.3667 | 52.3549 | 52.3256 | 51.9453 | 51.9011 | 51.8541 | 51.8074 | 51.7609 | 51.7163 | 51.6889 | 51.6059 | 50.6308 | 48.963 | 47.2973
|  | REDHILL | SP |  |  | 67.2447 | 67.2417 | 67.2387 | 67.0542 | 67.0391 | 67.024 | 67.0088 | 66.9937 | 66.9786 | 66.9726 | 66.9544 | 66.9242 | 66.906 | 66.8728 | 52.0463 | 52.0407 | 51.9999 | 51.813 | 51.7885 | 51.7622 | 51.735 | 51.7079 | 51.6774 | 51.6586 | 51.6017 | 51.4927 | 51.3837 | 51.1818 | 52.4087 | 52.4045 | 52.3839 | 52.1982 | 52.1787 | 52.1584 | 52.1376 | 52.1169 | 52.0946 | 52.0826 | 52.0463 | 51.9793 | 51.9187 | 51.8423
CHICKERELL GSP | CHICKERELL BSP | REDLANDS | MINIMUM HEADROOM | SY 67131 82321 | YES | 100.627 | 100.6152 | 100.6033 | 99.8796 | 99.8202 | 99.7609 | 99.7016 | 99.6423 | 99.583 | 99.5592 | 99.488 | 99.3694 | 98.1874 | 96.8035 | 97.9196 | 97.9078 | 97.8959 | 97.1722 | 97.1129 | 97.0535 | 96.9942 | 96.9349 | 96.8756 | 96.7179 | 95.2547 | 93.0843 | 91.3807 | 89.7883 | 98.1402 | 98.1284 | 98.1165 | 97.3928 | 97.3335 | 97.2741 | 97.2148 | 97.1555 | 97.0962 | 97.0724 | 95.8287 | 93.6626 | 91.962 | 90.3726
|  | REDLANDS | CT |  |  | 100.684 | 100.6769 | 100.6697 | 100.2355 | 100.1999 | 100.1643 | 100.1287 | 100.0931 | 100.0575 | 100.0433 | 100.0006 | 99.4814 | 98.1874 | 96.8035 | 97.9766 | 97.9695 | 97.9623 | 97.5281 | 97.4925 | 97.4569 | 97.4213 | 97.3857 | 97.1799 | 96.7452 | 95.3107 | 93.0843 | 91.3807 | 89.7883 | 98.1972 | 98.1901 | 98.1829 | 97.7487 | 97.7131 | 97.6775 | 97.6419 | 97.6063 | 97.5707 | 97.3174 | 95.8856 | 93.6626 | 91.962 | 90.3726
|  | REDLANDS | LW |  |  | 100.627 | 100.6152 | 100.6033 | 99.8796 | 99.8202 | 99.7609 | 99.7016 | 99.6423 | 99.583 | 99.5592 | 99.488 | 99.3694 | 98.5788 | 97.1948 | 97.9196 | 97.9078 | 97.8959 | 97.1722 | 97.1129 | 97.0535 | 96.9942 | 96.9349 | 96.8756 | 96.7179 | 95.2547 | 93.429 | 91.8371 | 90.2446 | 98.1402 | 98.1284 | 98.1165 | 97.3928 | 97.3335 | 97.2741 | 97.2148 | 97.1555 | 97.0962 | 97.0724 | 95.8287 | 94.0064 | 92.4176 | 90.828
|  | REDLANDS | ST |  |  | 100.7124 | 100.7077 | 100.703 | 100.4135 | 100.3897 | 100.366 | 100.3423 | 100.3185 | 100.2948 | 100.2853 | 100.2569 | 100.2094 | 100.1809 | 100.1287 | 98.0051 | 98.0003 | 97.9956 | 97.7061 | 97.6823 | 97.6586 | 97.6349 | 97.6112 | 97.5874 | 97.5779 | 97.5495 | 97.4928 | 96.4855 | 95.5003 | 98.2257 | 98.2209 | 98.2162 | 97.9267 | 97.9029 | 97.8792 | 97.8555 | 97.8318 | 97.808 | 97.7985 | 97.7701 | 97.7226 | 97.0584 | 96.0751
|  | REDLANDS | SP |  |  | 100.7409 | 100.7385 | 100.7362 | 100.5914 | 100.5796 | 100.5677 | 100.5558 | 100.544 | 100.5321 | 100.5274 | 100.5131 | 100.4894 | 100.4752 | 100.4491 | 98.0335 | 98.0312 | 98.0288 | 97.884 | 97.8722 | 97.8603 | 97.8484 | 97.8366 | 97.8247 | 97.82 | 97.8057 | 97.782 | 97.7678 | 97.7417 | 98.2541 | 98.2518 | 98.2494 | 98.1046 | 98.0928 | 98.0809 | 98.069 | 98.0572 | 98.0453 | 98.0406 | 98.0263 | 98.0026 | 97.9884 | 97.9623
MANNINGTON GSP | SALISBURY | REDLYNCH | MINIMUM HEADROOM | SU 19073 20576 | YES | 44.2894 | 43.7184 | 43.6744 | 43.5931 | 43.5039 | 43.4042 | 43.2012 | 42.9959 | 42.7882 | 42.5651 | 41.8813 | 40.4816 | 38.8749 | 37.2815 | 40.9615 | 40.3115 | 40.2613 | 40.1687 | 40.0672 | 39.9538 | 39.7226 | 39.4889 | 39.2525 | 38.9984 | 38.1999 | 36.5566 | 34.6703 | 32.7996 | 41.3364 | 40.6904 | 40.6405 | 40.5485 | 40.4476 | 40.3349 | 40.1051 | 39.8729 | 39.6378 | 39.3854 | 38.6116 | 37.0279 | 35.2099 | 33.4069
|  | REDLYNCH | CT |  |  | 44.2894 | 43.7184 | 43.6744 | 43.5931 | 43.5039 | 43.4042 | 43.3506 | 43.1455 | 42.9378 | 42.7145 | 42.0308 | 40.6311 | 39.0245 | 37.4317 | 40.9615 | 40.3115 | 40.2613 | 40.1687 | 40.0672 | 39.9538 | 39.8927 | 39.6592 | 39.4227 | 39.1686 | 38.3755 | 36.7321 | 34.8459 | 32.9758 | 41.3364 | 40.6904 | 40.6405 | 40.5485 | 40.4476 | 40.3349 | 40.2742 | 40.0421 | 39.8071 | 39.5545 | 38.7808 | 37.197 | 35.3792 | 33.5768
|  | REDLYNCH | LW |  |  | 44.2894 | 43.7184 | 43.6744 | 43.5931 | 43.5039 | 43.4042 | 43.2012 | 42.9959 | 42.7882 | 42.5651 | 41.8813 | 40.4816 | 38.8749 | 37.2815 | 40.9615 | 40.3115 | 40.2613 | 40.1687 | 40.0672 | 39.9538 | 39.7226 | 39.4889 | 39.2525 | 38.9984 | 38.1999 | 36.5566 | 34.6703 | 32.7996 | 41.3364 | 40.6904 | 40.6405 | 40.5485 | 40.4476 | 40.3349 | 40.1051 | 39.8729 | 39.6378 | 39.3854 | 38.6116 | 37.0279 | 35.2099 | 33.4069
|  | REDLYNCH | ST |  |  | 44.9187 | 44.276 | 43.709 | 43.6632 | 43.6075 | 43.5402 | 43.3878 | 43.2347 | 43.0932 | 42.9408 | 42.475 | 41.5185 | 40.4672 | 39.4464 | 41.6779 | 40.9462 | 40.3007 | 40.2486 | 40.1852 | 40.1086 | 39.9351 | 39.7608 | 39.5996 | 39.4261 | 38.8958 | 37.7739 | 36.5396 | 35.3412 | 42.0486 | 41.3213 | 40.6797 | 40.6279 | 40.5649 | 40.4888 | 40.3163 | 40.1431 | 39.9829 | 39.8105 | 39.2834 | 38.2011 | 37.0115 | 35.8565
|  | REDLYNCH | SP |  |  | 45.1337 | 44.9183 | 43.7458 | 43.7276 | 43.7027 | 43.6749 | 43.6279 | 43.5809 | 43.5202 | 43.4576 | 43.2662 | 42.8793 | 42.416 | 41.948 | 41.9227 | 41.6774 | 40.3426 | 40.3219 | 40.2937 | 40.2621 | 40.2088 | 40.1553 | 40.0864 | 40.0156 | 39.7992 | 39.3594 | 38.8341 | 38.2872 | 42.2918 | 42.048 | 40.7214 | 40.7008 | 40.6727 | 40.6414 | 40.5883 | 40.5351 | 40.4666 | 40.3963 | 40.1811 | 39.744 | 39.2218 | 38.6939
NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK | MINIMUM HEADROOM | SU 39267 13050 | YES | 22.7248 | 22.7248 | 22.7248 | 26.5048 | 26.3745 | 26.2395 | 26.0977 | 25.9501 | 25.7247 | 25.6933 | 25.5841 | 25.4163 | 24.5395 | 23.6557 | 17.5018 | 17.4964 | 17.4942 | 24.5705 | 24.436 | 24.2962 | 24.1412 | 23.9556 | 23.5877 | 23.4048 | 22.6971 | 21.5413 | 20.1797 | 19.1462 | 22.1302 | 22.1245 | 22.1223 | 25.8985 | 25.7639 | 25.6239 | 25.4685 | 25.3054 | 25.0646 | 25.0197 | 24.6746 | 23.5546 | 22.2304 | 21.2335
|  | REGENTS PARK | CT |  |  | 22.7248 | 22.7248 | 22.7248 | 26.5048 | 26.4848 | 26.4643 | 26.4434 | 26.4213 | 26.3867 | 26.3822 | 26.3672 | 26.2896 | 25.7705 | 24.8893 | 17.5018 | 17.4964 | 17.4942 | 24.5705 | 24.5464 | 24.521 | 24.4949 | 24.4577 | 24.3262 | 24.1971 | 23.6228 | 22.5568 | 21.4317 | 20.4009 | 22.1302 | 22.1245 | 22.1223 | 25.8985 | 25.8742 | 25.8487 | 25.8224 | 25.7848 | 25.7348 | 25.7169 | 25.5952 | 24.5649 | 23.4773 | 22.4831
|  | REGENTS PARK | LW |  |  | 22.7248 | 22.7248 | 22.7248 | 26.5048 | 26.3745 | 26.2395 | 26.0977 | 25.9501 | 25.7247 | 25.6933 | 25.5841 | 25.4163 | 24.5395 | 23.6557 | 17.5018 | 17.4964 | 17.4942 | 24.5705 | 24.436 | 24.2962 | 24.1412 | 23.9556 | 23.5877 | 23.4048 | 22.6971 | 21.5413 | 20.1797 | 19.1462 | 22.1302 | 22.1245 | 22.1223 | 25.8985 | 25.7639 | 25.6239 | 25.4685 | 25.3054 | 25.0646 | 25.0197 | 24.6746 | 23.5546 | 22.2304 | 21.2335
|  | REGENTS PARK | ST |  |  | 22.7248 | 22.7248 | 22.7248 | 26.5048 | 26.5029 | 26.5009 | 26.4986 | 26.4962 | 26.492 | 26.4904 | 26.484 | 26.4772 | 26.4544 | 26.4463 | 17.5021 | 17.5014 | 17.4954 | 24.5732 | 24.5686 | 24.5633 | 24.5531 | 24.5414 | 24.5271 | 24.4749 | 24.2447 | 23.57 | 22.8747 | 22.2151 | 22.1304 | 22.1297 | 22.1236 | 25.9013 | 25.8966 | 25.8912 | 25.8807 | 25.8688 | 25.8542 | 25.8434 | 25.8132 | 25.5482 | 24.8773 | 24.2413
|  | REGENTS PARK | SP |  |  | 22.7248 | 22.7248 | 22.7248 | 26.5048 | 26.501 | 26.4972 | 26.4935 | 26.4896 | 26.4836 | 26.4669 | 26.4131 | 26.3872 | 26.304 | 26.2337 | 17.5024 | 17.502 | 17.4967 | 24.5755 | 24.5704 | 24.5652 | 24.5587 | 24.5517 | 24.5423 | 24.522 | 24.4593 | 24.4187 | 24.1952 | 23.9738 | 22.1307 | 22.1303 | 22.1248 | 25.9037 | 25.8985 | 25.8933 | 25.8867 | 25.8796 | 25.87 | 25.8496 | 25.7867 | 25.7456 | 25.6469 | 25.5618
COWLEY GSP | WITNEY BSP | RISSINGTON | MINIMUM HEADROOM | SP 19225 19563 | NO | 15.9545 | 15.9335 | 15.9059 | 15.8477 | 15.7904 | 15.7329 | 15.6384 | 15.5399 | 15.4306 | 15.3335 | 15.0382 | 14.5347 | 13.9685 | 13.4995 | 12.7545 | 12.7315 | 12.7014 | 12.6377 | 12.5751 | 12.5124 | 12.4103 | 12.3036 | 12.1862 | 12.0804 | 11.7594 | 11.2133 | 10.5886 | 10.0406 | 13.1381 | 13.1192 | 13.0945 | 13.0423 | 12.9908 | 12.939 | 12.8528 | 12.7633 | 12.6628 | 12.5753 | 12.3065 | 11.7311 | 11.0904 | 10.5481
|  | RISSINGTON | CT |  |  | 15.9545 | 15.9335 | 15.9059 | 15.8477 | 15.7904 | 15.7329 | 15.6752 | 15.5849 | 15.4916 | 15.3973 | 15.1156 | 14.6065 | 14.0752 | 13.5944 | 12.7545 | 12.7315 | 12.7014 | 12.6377 | 12.5751 | 12.5124 | 12.4495 | 12.351 | 12.2496 | 12.1465 | 11.8391 | 11.2874 | 10.6993 | 10.1399 | 13.1381 | 13.1192 | 13.0945 | 13.0423 | 12.9908 | 12.939 | 12.8871 | 12.8057 | 12.7213 | 12.6365 | 12.3831 | 11.8068 | 11.201 | 10.647
|  | RISSINGTON | LW |  |  | 15.9552 | 15.9349 | 15.9082 | 15.8516 | 15.7943 | 15.7346 | 15.6384 | 15.5399 | 15.4306 | 15.3335 | 15.0382 | 14.5347 | 13.9685 | 13.4995 | 12.7553 | 12.7331 | 12.7038 | 12.642 | 12.5795 | 12.5148 | 12.4103 | 12.3036 | 12.1862 | 12.0804 | 11.7594 | 11.2133 | 10.5886 | 10.0406 | 13.1387 | 13.1205 | 13.0965 | 13.0458 | 12.9941 | 12.94 | 12.8528 | 12.7633 | 12.6628 | 12.5753 | 12.3065 | 11.7311 | 11.0904 | 10.5481
|  | RISSINGTON | ST |  |  | 15.9706 | 15.9617 | 15.9512 | 15.9332 | 15.9105 | 15.8828 | 15.8196 | 15.7566 | 15.6922 | 15.6261 | 15.4268 | 15.1064 | 14.7401 | 14.4164 | 12.7721 | 12.7624 | 12.7509 | 12.7312 | 12.7065 | 12.6762 | 12.6073 | 12.5386 | 12.4687 | 12.3966 | 12.1799 | 11.8312 | 11.4365 | 11.0847 | 13.1526 | 13.1446 | 13.1351 | 13.119 | 13.0986 | 13.0736 | 13.0168 | 12.96 | 12.9016 | 12.842 | 12.6618 | 12.3725 | 11.9666 | 11.5953
|  | RISSINGTON | SP |  |  | 15.9788 | 15.9766 | 15.9745 | 15.9725 | 15.9635 | 15.9527 | 15.9318 | 15.9112 | 15.8843 | 15.8588 | 15.7822 | 15.6633 | 15.5344 | 15.4115 | 12.7811 | 12.7787 | 12.7764 | 12.7742 | 12.7643 | 12.7525 | 12.7297 | 12.7072 | 12.6778 | 12.65 | 12.5667 | 12.437 | 12.2977 | 12.1651 | 13.1599 | 13.1579 | 13.1561 | 13.1543 | 13.1462 | 13.1365 | 13.1177 | 13.0992 | 13.0751 | 13.0521 | 12.9828 | 12.8758 | 12.7581 | 12.646
BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE | MINIMUM HEADROOM | SU 47846 67187 | YES | 34.1817 | 34.1659 | 34.15 | 33.1814 | 33.102 | 33.0226 | 32.9432 | 32.8638 | 32.7844 | 32.7527 | 32.6574 | 32.4986 | 32.4033 | 31.986 | 25.7165 | 25.6995 | 25.6822 | 24.7107 | 24.6285 | 24.5462 | 24.4612 | 24.3762 | 24.2912 | 24.2534 | 24.1395 | 23.9417 | 23.8011 | 22.9411 | 26.3692 | 26.3522 | 26.3348 | 25.3632 | 25.2809 | 25.1986 | 25.1134 | 25.0282 | 24.943 | 24.905 | 24.7905 | 24.2768 | 23.425 | 22.4745
|  | RIVERSIDE | CT |  |  | 34.258 | 34.2484 | 34.2389 | 33.6577 | 33.6101 | 33.5625 | 33.5148 | 33.4672 | 33.4196 | 33.4005 | 33.3433 | 32.6485 | 32.4033 | 32.044 | 25.7928 | 25.7823 | 25.7714 | 25.1876 | 25.1373 | 25.087 | 25.0367 | 24.9834 | 24.9302 | 24.9051 | 24.8293 | 24.0954 | 23.8049 | 23.0091 | 26.4455 | 26.4349 | 26.424 | 25.8401 | 25.7898 | 25.7394 | 25.689 | 25.6355 | 25.5821 | 25.5568 | 25.4804 | 24.4892 | 23.4907 | 22.5404
|  | RIVERSIDE | LW |  |  | 34.1817 | 34.1659 | 34.15 | 33.1814 | 33.102 | 33.0226 | 32.9432 | 32.8638 | 32.7844 | 32.7527 | 32.6574 | 32.4986 | 32.4033 | 31.986 | 25.7165 | 25.6995 | 25.6822 | 24.7107 | 24.6285 | 24.5462 | 24.4612 | 24.3762 | 24.2912 | 24.2534 | 24.1395 | 23.9417 | 23.8011 | 22.9411 | 26.3692 | 26.3522 | 26.3348 | 25.3632 | 25.2809 | 25.1986 | 25.1134 | 25.0282 | 24.943 | 24.905 | 24.7905 | 24.2768 | 23.425 | 22.4745
|  | RIVERSIDE | ST |  |  | 34.2961 | 34.2897 | 34.2834 | 33.8959 | 33.8642 | 33.8324 | 33.8007 | 33.7689 | 33.7371 | 33.7244 | 33.6863 | 33.6228 | 33.5847 | 33.5148 | 25.8312 | 25.824 | 25.8167 | 25.4278 | 25.3941 | 25.3601 | 25.3253 | 25.2906 | 25.255 | 25.2382 | 25.1874 | 25.0973 | 25.0295 | 24.9306 | 26.4838 | 26.4767 | 26.4694 | 26.0803 | 26.0466 | 26.0125 | 25.9777 | 25.9429 | 25.9071 | 25.8902 | 25.839 | 25.7481 | 25.3908 | 24.845
|  | RIVERSIDE | SP |  |  | 34.3342 | 34.331 | 34.3278 | 34.1341 | 34.1182 | 34.1023 | 34.0865 | 34.0706 | 34.0547 | 34.0484 | 34.0293 | 33.9975 | 33.9785 | 33.9436 | 25.8701 | 25.8667 | 25.8633 | 25.6694 | 25.6531 | 25.6366 | 25.6198 | 25.603 | 25.586 | 25.578 | 25.5541 | 25.5118 | 25.4801 | 25.4322 | 26.5228 | 26.5194 | 26.516 | 26.3221 | 26.3057 | 26.2892 | 26.2724 | 26.2556 | 26.2385 | 26.2306 | 26.2065 | 26.1638 | 26.1317 | 26.0834
MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE | MINIMUM HEADROOM | SU 11617 17810 | YES | 26.4266 | 26.4266 | 26.4266 | 26.4266 | 26.3935 | 26.3585 | 26.3213 | 26.2818 | 26.2203 | 26.2116 | 26.1798 | 26.1229 | 25.8345 | 25.4562 | 23.834 | 23.8163 | 23.7931 | 23.744 | 23.6631 | 23.5808 | 23.4596 | 23.3369 | 23.1929 | 23.0952 | 22.8008 | 22.3118 | 21.74 | 21.2935 | 25.4841 | 25.4841 | 25.4841 | 25.4841 | 25.4509 | 25.416 | 25.3787 | 25.3393 | 25.2778 | 25.269 | 25.2372 | 25.1804 | 24.7938 | 24.3487
|  | ROCKBOURNE | CT |  |  | 26.4266 | 26.4266 | 26.4266 | 26.4266 | 26.4193 | 26.4117 | 26.4037 | 26.3952 | 26.3814 | 26.3795 | 26.3728 | 26.3352 | 26.1816 | 25.7991 | 23.8366 | 23.8209 | 23.8002 | 23.7565 | 23.7067 | 23.6568 | 23.607 | 23.5153 | 23.4191 | 23.3282 | 23.0591 | 22.5891 | 22.0971 | 21.6465 | 25.4841 | 25.4841 | 25.4841 | 25.4841 | 25.4767 | 25.4691 | 25.4611 | 25.4526 | 25.4388 | 25.437 | 25.4303 | 25.3926 | 25.1508 | 24.7015
|  | ROCKBOURNE | LW |  |  | 26.4266 | 26.4266 | 26.4266 | 26.4266 | 26.3935 | 26.3585 | 26.3213 | 26.2818 | 26.2203 | 26.2116 | 26.1798 | 26.1229 | 25.8345 | 25.4562 | 23.834 | 23.8163 | 23.7931 | 23.744 | 23.6631 | 23.5808 | 23.4596 | 23.3369 | 23.1929 | 23.0952 | 22.8008 | 22.3118 | 21.74 | 21.2935 | 25.4841 | 25.4841 | 25.4841 | 25.4841 | 25.4509 | 25.416 | 25.3787 | 25.3393 | 25.2778 | 25.269 | 25.2372 | 25.1804 | 24.7938 | 24.3487
|  | ROCKBOURNE | ST |  |  | 26.4266 | 26.4266 | 26.4266 | 26.4266 | 26.409 | 26.391 | 26.3724 | 26.353 | 26.3226 | 26.312 | 26.2768 | 26.2462 | 26.1437 | 26.111 | 23.9934 | 23.8471 | 23.8416 | 23.8322 | 23.8031 | 23.7711 | 23.7141 | 23.6567 | 23.57 | 23.4987 | 23.2866 | 22.9685 | 22.5784 | 22.2602 | 25.4841 | 25.4841 | 25.4841 | 25.4841 | 25.4664 | 25.4484 | 25.4298 | 25.4104 | 25.38 | 25.3695 | 25.3342 | 25.3036 | 25.2011 | 25.1684
|  | ROCKBOURNE | SP |  |  | 26.4266 | 26.4266 | 26.4266 | 26.4266 | 26.4266 | 26.4266 | 26.4266 | 26.4266 | 26.4265 | 26.4263 | 26.4248 | 26.4237 | 26.4184 | 26.4132 | 23.9984 | 23.9976 | 23.8553 | 23.8546 | 23.8514 | 23.8476 | 23.8349 | 23.8225 | 23.8063 | 23.7825 | 23.7128 | 23.6029 | 23.4935 | 23.3901 | 25.4841 | 25.4841 | 25.4841 | 25.4841 | 25.484 | 25.484 | 25.484 | 25.484 | 25.4839 | 25.4837 | 25.4823 | 25.4812 | 25.4758 | 25.4706
NURSLING GSP | ROWNHAMS | ROMSEY | MINIMUM HEADROOM | SU 36092 21110 | YES | 23.5309 | 23.5048 | 23.4773 | 22.6531 | 22.5651 | 22.474 | 22.3986 | 22.3227 | 22.2466 | 22.2095 | 22.0855 | 21.8756 | 21.5438 | 20.8435 | 17.3679 | 17.2988 | 17.2239 | 16.3193 | 16.157 | 15.9814 | 15.8735 | 15.6794 | 15.4697 | 15.2928 | 14.5894 | 13.2915 | 12.4258 | 11.6265 | 17.8164 | 17.716 | 17.6065 | 16.6415 | 16.2671 | 15.8501 | 15.6494 | 15.4415 | 15.2322 | 15.0558 | 14.3543 | 13.0603 | 12.1966 | 11.3993
|  | ROMSEY | CT |  |  | 23.5939 | 23.5731 | 23.551 | 23.0469 | 22.9852 | 22.9205 | 22.8558 | 22.8061 | 22.7563 | 22.7297 | 22.6372 | 21.9846 | 21.5438 | 20.8435 | 17.4311 | 17.3675 | 17.2982 | 16.7142 | 16.5788 | 16.43 | 16.1553 | 15.9731 | 15.7897 | 15.6232 | 14.9513 | 13.2915 | 12.4258 | 11.6265 | 17.8797 | 17.785 | 17.6812 | 17.0391 | 16.6935 | 16.3049 | 15.9176 | 15.7358 | 15.5528 | 15.3868 | 14.7168 | 13.0603 | 12.1966 | 11.3993
|  | ROMSEY | LW |  |  | 23.5309 | 23.5048 | 23.4773 | 22.6531 | 22.5651 | 22.474 | 22.3986 | 22.3227 | 22.2466 | 22.2095 | 22.0855 | 21.8756 | 21.7174 | 21.017 | 17.3679 | 17.2988 | 17.2239 | 16.3193 | 16.157 | 15.9814 | 15.8735 | 15.6794 | 15.4697 | 15.2928 | 14.5894 | 13.3722 | 12.6303 | 11.8309 | 17.8164 | 17.716 | 17.6065 | 16.6415 | 16.2671 | 15.8501 | 15.6494 | 15.4415 | 15.2322 | 15.0558 | 14.3543 | 13.1404 | 12.4005 | 11.6031
|  | ROMSEY | ST |  |  | 23.6281 | 23.6125 | 23.5967 | 23.2618 | 23.2185 | 23.1695 | 23.134 | 23.0982 | 23.0649 | 23.047 | 22.9836 | 22.8754 | 22.8125 | 22.7243 | 17.4743 | 17.4242 | 17.3735 | 16.9896 | 16.8895 | 16.7652 | 16.6991 | 16.6318 | 16.5752 | 16.5326 | 16.1063 | 15.2842 | 14.8192 | 14.3417 | 17.9295 | 17.8543 | 17.7781 | 17.3585 | 17.2171 | 16.8862 | 16.7328 | 16.5754 | 16.4523 | 16.339 | 15.8691 | 15.0494 | 14.5857 | 14.1094
|  | ROMSEY | SP |  |  | 23.6684 | 23.6623 | 23.6571 | 23.4956 | 23.4786 | 23.4599 | 23.4433 | 23.4266 | 23.4093 | 23.4012 | 23.3729 | 23.3241 | 23.2951 | 23.2529 | 17.5438 | 17.526 | 17.5124 | 17.346 | 17.3162 | 17.2789 | 17.2507 | 17.2223 | 17.1912 | 17.1734 | 17.1037 | 16.9801 | 16.9074 | 16.821 | 18.0203 | 17.9939 | 17.9743 | 17.8042 | 17.765 | 17.7142 | 17.6777 | 17.6407 | 17.5996 | 17.5747 | 17.4748 | 17.2734 | 17.0757 | 16.8631
LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN | MINIMUM HEADROOM | SZ 89974 99335 | NO | 2.7303 | 2.7287 | 2.7267 | 2.7225 | 2.7184 | 2.7143 | 2.7011 | 2.6878 | 2.6746 | 2.6604 | 2.6183 | 2.5488 | 2.4769 | 2.4062 | 1.997 | 1.9949 | 1.992 | 1.986 | 1.9801 | 1.9742 | 1.9555 | 1.9365 | 1.9176 | 1.8973 | 1.8372 | 1.738 | 1.6354 | 1.5343 | 1.999 | 1.9982 | 1.9972 | 1.995 | 1.993 | 1.9909 | 1.9843 | 1.9776 | 1.9709 | 1.9637 | 1.9425 | 1.9075 | 1.8712 | 1.8355
|  | ROSE GREEN | CT |  |  | 2.7303 | 2.7287 | 2.7267 | 2.7225 | 2.7184 | 2.7143 | 2.7102 | 2.6969 | 2.6837 | 2.6694 | 2.6274 | 2.5578 | 2.486 | 2.4153 | 1.997 | 1.9949 | 1.992 | 1.986 | 1.9801 | 1.9742 | 1.9684 | 1.9494 | 1.9305 | 1.9102 | 1.8501 | 1.7509 | 1.6483 | 1.5473 | 1.999 | 1.9982 | 1.9972 | 1.995 | 1.993 | 1.9909 | 1.9888 | 1.9821 | 1.9755 | 1.9683 | 1.9471 | 1.912 | 1.8758 | 1.8401
|  | ROSE GREEN | LW |  |  | 2.7303 | 2.7288 | 2.7268 | 2.7227 | 2.7186 | 2.7146 | 2.7011 | 2.6878 | 2.6746 | 2.6604 | 2.6183 | 2.5488 | 2.4769 | 2.4062 | 1.9971 | 1.9949 | 1.9921 | 1.9862 | 1.9804 | 1.9747 | 1.9555 | 1.9365 | 1.9176 | 1.8973 | 1.8372 | 1.738 | 1.6354 | 1.5343 | 1.999 | 1.9982 | 1.9972 | 1.9951 | 1.9931 | 1.991 | 1.9843 | 1.9776 | 1.9709 | 1.9637 | 1.9425 | 1.9075 | 1.8712 | 1.8355
|  | ROSE GREEN | ST |  |  | 2.731 | 2.7301 | 2.729 | 2.7271 | 2.7248 | 2.722 | 2.715 | 2.708 | 2.699 | 2.6893 | 2.6609 | 2.6147 | 2.5684 | 2.5225 | 1.9981 | 1.9968 | 1.9952 | 1.9926 | 1.9893 | 1.9853 | 1.9752 | 1.9652 | 1.9524 | 1.9385 | 1.898 | 1.832 | 1.7659 | 1.7004 | 1.9993 | 1.9989 | 1.9983 | 1.9974 | 1.9962 | 1.9948 | 1.9912 | 1.9877 | 1.9832 | 1.9783 | 1.964 | 1.9407 | 1.9173 | 1.8942
|  | ROSE GREEN | SP |  |  | 2.732 | 2.7319 | 2.7317 | 2.7316 | 2.7309 | 2.7302 | 2.7278 | 2.7255 | 2.7224 | 2.7186 | 2.7077 | 2.6903 | 2.6735 | 2.6576 | 1.9995 | 1.9993 | 1.9991 | 1.9989 | 1.998 | 1.9969 | 1.9935 | 1.9902 | 1.9858 | 1.9804 | 1.9649 | 1.9399 | 1.916 | 1.8933 | 1.9998 | 1.9998 | 1.9997 | 1.9996 | 1.9993 | 1.9989 | 1.9977 | 1.9965 | 1.995 | 1.9931 | 1.9876 | 1.9788 | 1.9703 | 1.9623
COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL | MINIMUM HEADROOM | SP 53637 03027 | NO | 26.4501 | 26.4355 | 26.4209 | 25.5285 | 25.453 | 25.375 | 25.2944 | 25.2108 | 25.1166 | 25.0837 | 24.9775 | 24.7862 | 24.6107 | 23.497 | 24.2873 | 24.2726 | 24.258 | 23.3656 | 23.2901 | 23.2122 | 23.1315 | 23.0479 | 22.9537 | 22.9208 | 22.6437 | 21.2528 | 19.9059 | 18.6045 | 24.5296 | 24.515 | 24.5004 | 23.6079 | 23.5325 | 23.4545 | 23.3738 | 23.2902 | 23.1961 | 23.0784 | 21.9279 | 20.5817 | 19.3203 | 18.1015
|  | ROSE HILL | CT |  |  | 26.5204 | 26.5116 | 26.5028 | 25.9674 | 25.9228 | 25.8776 | 25.8317 | 25.7849 | 25.7347 | 25.716 | 25.6573 | 24.9671 | 24.6854 | 23.5903 | 24.3575 | 24.3487 | 24.3399 | 23.8045 | 23.7599 | 23.7147 | 23.6688 | 23.6221 | 23.5718 | 23.5531 | 23.3558 | 21.468 | 20.0152 | 18.7031 | 24.5998 | 24.5911 | 24.5823 | 24.0468 | 24.0022 | 23.957 | 23.9112 | 23.8644 | 23.8142 | 23.7426 | 22.6398 | 20.7944 | 19.427 | 18.1976
|  | ROSE HILL | LW |  |  | 26.4501 | 26.4355 | 26.4209 | 25.5285 | 25.453 | 25.375 | 25.2944 | 25.2108 | 25.1166 | 25.0837 | 24.9775 | 24.7862 | 24.6107 | 23.497 | 24.2873 | 24.2726 | 24.258 | 23.3656 | 23.2901 | 23.2122 | 23.1315 | 23.0479 | 22.9537 | 22.9208 | 22.6437 | 21.2528 | 19.9059 | 18.6045 | 24.5296 | 24.515 | 24.5004 | 23.6079 | 23.5325 | 23.4545 | 23.3738 | 23.2902 | 23.1961 | 23.0784 | 21.9279 | 20.5817 | 19.3203 | 18.1015
|  | ROSE HILL | ST |  |  | 26.5555 | 26.5496 | 26.5438 | 26.1868 | 26.1571 | 26.1268 | 26.0961 | 26.0646 | 26.0305 | 26.0164 | 25.9687 | 25.8937 | 25.8005 | 25.715 | 24.3926 | 24.3867 | 24.3809 | 24.0239 | 23.9942 | 23.9639 | 23.9332 | 23.9018 | 23.8676 | 23.8536 | 23.8058 | 23.7308 | 23.04 | 22.2318 | 24.635 | 24.6291 | 24.6233 | 24.2663 | 24.2365 | 24.2063 | 24.1756 | 24.1441 | 24.11 | 24.0959 | 23.9707 | 23.1191 | 22.3262 | 21.5571
|  | ROSE HILL | SP |  |  | 26.5906 | 26.5877 | 26.5847 | 26.4063 | 26.3916 | 26.3769 | 26.3623 | 26.3475 | 26.3327 | 26.3261 | 26.3039 | 26.2711 | 26.2362 | 26.1871 | 24.4277 | 24.4248 | 24.4219 | 24.2434 | 24.2287 | 24.2141 | 24.1994 | 24.1846 | 24.1698 | 24.1632 | 24.1411 | 24.1082 | 24.0733 | 24.0242 | 24.6701 | 24.6671 | 24.6642 | 24.4857 | 24.4711 | 24.4564 | 24.4417 | 24.427 | 24.4122 | 24.4055 | 24.3834 | 24.3505 | 24.3157 | 24.2666
MELKSHAM GSP | CHIPPENHAM | ROWDEN | MINIMUM HEADROOM | ST 90805 72608 | YES | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.2857 | 26.0198 | 25.742 | 25.454 | 25.0167 | 24.9562 | 24.7485 | 24.438 | 23.6791 | 23.6344 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.2466 | 19.9806 | 19.7028 | 19.4149 | 18.9776 | 18.917 | 18.7094 | 18.0881 | 16.3464 | 15.3454 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 18.9834 | 18.7174 | 18.4396 | 18.1343 | 17.5381 | 17.3161 | 16.6413 | 15.454 | 13.7735 | 12.832
|  | ROWDEN | CT |  |  | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.3307 | 19.3482 | 18.3926 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.1839 | 19.0224 | 18.5554 | 17.6881 | 16.7668 | 15.8706
|  | ROWDEN | LW |  |  | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.2857 | 26.0198 | 25.742 | 25.454 | 25.0167 | 24.9562 | 24.7485 | 24.438 | 23.6791 | 23.6344 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.2466 | 19.9806 | 19.7028 | 19.4149 | 18.9776 | 18.917 | 18.7094 | 18.0881 | 16.3464 | 15.3454 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 18.9834 | 18.7174 | 18.4396 | 18.1343 | 17.5381 | 17.3161 | 16.6413 | 15.454 | 13.7735 | 12.832
|  | ROWDEN | ST |  |  | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.4499 | 19.8312 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 18.9459 | 18.3925 | 17.7999 | 17.2197
|  | ROWDEN | SP |  |  | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 26.5435 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 20.5043 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.2411 | 19.0976 | 18.8892
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK | MINIMUM HEADROOM | SU 58018 00782 | YES | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.8703 | 30.7777 | 30.6836 | 30.5853 | 30.4338 | 30.4146 | 30.246 | 28.0155 | 26.3634 | 24.9524 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.5378 | 23.4453 | 23.3511 | 23.2529 | 23.1013 | 23.0821 | 21.98 | 19.4199 | 17.5406 | 15.9048 | 23.5589 | 23.5513 | 23.5439 | 23.5303 | 23.4232 | 23.3105 | 23.1926 | 23.075 | 22.898 | 22.7811 | 21.0462 | 18.5598 | 16.7313 | 15.1458
|  | ROWNER PARK | CT |  |  | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.8703 | 30.7777 | 30.6836 | 30.5853 | 30.4338 | 30.4146 | 30.246 | 28.0155 | 26.3634 | 24.9524 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.5378 | 23.4453 | 23.3511 | 23.2529 | 23.1013 | 23.0821 | 21.98 | 19.4199 | 17.5406 | 15.9048 | 23.5589 | 23.5513 | 23.5439 | 23.5303 | 23.4232 | 23.3105 | 23.1926 | 23.075 | 22.898 | 22.7811 | 21.0462 | 18.5598 | 16.7313 | 15.1458
|  | ROWNER PARK | LW |  |  | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9183 | 28.9727 | 27.6315 | 26.3044 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 22.6632 | 20.3879 | 18.8195 | 17.2676 | 23.5591 | 23.5516 | 23.5443 | 23.531 | 23.5152 | 23.4954 | 23.4747 | 23.4554 | 23.4299 | 23.3969 | 21.7269 | 19.5253 | 18.0078 | 16.5062
|  | ROWNER PARK | ST |  |  | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9458 | 30.93 | 30.9139 | 30.8972 | 30.8715 | 30.8628 | 30.8349 | 30.8118 | 29.8713 | 29.0014 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.6134 | 23.5976 | 23.5815 | 23.5648 | 23.5391 | 23.5303 | 23.5025 | 22.5831 | 21.4769 | 20.4634 | 23.5629 | 23.5586 | 23.5553 | 23.5508 | 23.5278 | 23.5008 | 23.4712 | 23.4419 | 23.399 | 23.3713 | 23.1582 | 21.6446 | 20.5718 | 19.5904
|  | ROWNER PARK | SP |  |  | 30.9613 | 30.9613 | 30.9613 | 30.9613 | 30.9611 | 30.9608 | 30.9606 | 30.9604 | 30.96 | 30.959 | 30.9557 | 30.9542 | 30.9493 | 30.9452 | 23.6289 | 23.6289 | 23.6289 | 23.6289 | 23.6286 | 23.6284 | 23.6282 | 23.6279 | 23.6276 | 23.6265 | 23.6233 | 23.6217 | 23.6168 | 23.6128 | 23.5652 | 23.5631 | 23.5621 | 23.5614 | 23.5579 | 23.5528 | 23.5471 | 23.542 | 23.5346 | 23.5261 | 23.4932 | 23.4533 | 23.4221 | 23.391
FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE | MINIMUM HEADROOM | SZ 59554 91973 | NO | 33.5806 | 33.5806 | 33.5806 | 33.5806 | 33.5572 | 33.5309 | 33.5013 | 33.4684 | 33.4139 | 33.4058 | 33.3726 | 33.3053 | 32.9325 | 31.9745 | 26.8216 | 26.8216 | 26.8216 | 26.8216 | 26.7982 | 26.7719 | 26.6536 | 26.4051 | 26.1364 | 25.8959 | 25.1791 | 23.9659 | 22.6659 | 21.5132 | 27.7611 | 27.7536 | 27.7022 | 27.6858 | 27.6488 | 27.6098 | 27.5671 | 27.5211 | 27.4535 | 27.4317 | 26.8552 | 25.7133 | 24.4878 | 23.4185
|  | RYDE | CT |  |  | 33.5806 | 33.5806 | 33.5806 | 33.5806 | 33.58 | 33.5788 | 33.5771 | 33.5746 | 33.5692 | 33.5682 | 33.5629 | 33.5197 | 33.365 | 32.4012 | 26.8216 | 26.8216 | 26.8216 | 26.8216 | 26.821 | 26.8198 | 26.8181 | 26.6554 | 26.4359 | 26.208 | 25.5194 | 24.3297 | 23.1241 | 21.9656 | 27.762 | 27.7551 | 27.7044 | 27.6897 | 27.6771 | 27.6647 | 27.6517 | 27.6361 | 27.6176 | 27.6028 | 27.1862 | 26.0678 | 24.935 | 23.8599
|  | RYDE | LW |  |  | 33.5806 | 33.5806 | 33.5806 | 33.5806 | 33.5572 | 33.5309 | 33.5013 | 33.4684 | 33.4139 | 33.4058 | 33.3726 | 33.3053 | 32.9325 | 31.9745 | 26.8216 | 26.8216 | 26.8216 | 26.8216 | 26.7982 | 26.7719 | 26.6536 | 26.4051 | 26.1364 | 25.8959 | 25.1791 | 23.9659 | 22.6659 | 21.5132 | 27.7611 | 27.7536 | 27.7022 | 27.6858 | 27.6488 | 27.6098 | 27.5671 | 27.5211 | 27.4535 | 27.4317 | 26.8552 | 25.7133 | 24.4878 | 23.4185
|  | RYDE | ST |  |  | 33.5806 | 33.5806 | 33.5806 | 33.5806 | 33.5802 | 33.5793 | 33.578 | 33.5761 | 33.5719 | 33.5699 | 33.559 | 33.5447 | 33.4945 | 33.4762 | 26.8216 | 26.8216 | 26.8216 | 26.8216 | 26.8211 | 26.8203 | 26.819 | 26.8171 | 26.8129 | 26.8109 | 26.8 | 26.181 | 25.3846 | 24.632 | 27.7629 | 27.7573 | 27.751 | 27.7417 | 27.7319 | 27.7205 | 27.7111 | 27.7011 | 27.688 | 27.6766 | 27.6385 | 27.5791 | 27.0555 | 26.3486
|  | RYDE | SP |  |  | 33.5806 | 33.5806 | 33.5806 | 33.5806 | 33.5806 | 33.5805 | 33.5805 | 33.5804 | 33.5802 | 33.5795 | 33.5756 | 33.5725 | 33.5575 | 33.5429 | 26.8216 | 26.8216 | 26.8216 | 26.8216 | 26.8216 | 26.8215 | 26.8215 | 26.8214 | 26.8212 | 26.8205 | 26.8166 | 26.8135 | 26.7985 | 26.7839 | 27.7671 | 27.765 | 27.7631 | 27.7612 | 27.7587 | 27.756 | 27.7533 | 27.7505 | 27.7468 | 27.7425 | 27.728 | 27.7076 | 27.6764 | 27.6465
MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL | MINIMUM HEADROOM | SU 14215 30481 | YES | 33.6052 | 33.6032 | 33.6006 | 33.5957 | 33.5907 | 33.5855 | 33.5797 | 33.5634 | 33.5471 | 33.5298 | 33.4748 | 33.236 | 32.6488 | 32.0528 | 18.7238 | 18.7232 | 18.7224 | 18.7209 | 18.7193 | 18.7177 | 18.716 | 18.711 | 18.706 | 18.7007 | 18.6839 | 18.646 | 17.8403 | 16.8804 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.2154 | 17.2584
|  | SALISBURY CENTRAL | CT |  |  | 33.6052 | 33.6032 | 33.6006 | 33.5957 | 33.5907 | 33.5855 | 33.5803 | 33.564 | 33.5477 | 33.5303 | 33.4754 | 33.2379 | 32.6508 | 32.0554 | 18.7238 | 18.7232 | 18.7224 | 18.7209 | 18.7193 | 18.7177 | 18.7161 | 18.7112 | 18.7062 | 18.7009 | 18.6841 | 18.6462 | 17.8436 | 16.884 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.2187 | 17.2621
|  | SALISBURY CENTRAL | LW |  |  | 33.6064 | 33.6053 | 33.6038 | 33.6014 | 33.5988 | 33.596 | 33.5797 | 33.5634 | 33.5471 | 33.5298 | 33.4748 | 33.236 | 32.6488 | 32.0528 | 18.7242 | 18.7238 | 18.7234 | 18.7226 | 18.7218 | 18.7209 | 18.716 | 18.711 | 18.706 | 18.7007 | 18.6839 | 18.646 | 17.8403 | 16.8804 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.2154 | 17.2584
|  | SALISBURY CENTRAL | ST |  |  | 33.6068 | 33.606 | 33.6051 | 33.6038 | 33.6022 | 33.6002 | 33.5933 | 33.5864 | 33.5752 | 33.5634 | 33.5259 | 33.4407 | 33.2044 | 32.8285 | 18.7243 | 18.724 | 18.7237 | 18.7233 | 18.7228 | 18.7223 | 18.7201 | 18.718 | 18.7146 | 18.711 | 18.6995 | 18.6735 | 18.6436 | 18.1332 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.5075
|  | SALISBURY CENTRAL | SP |  |  | 33.6072 | 33.6068 | 33.6064 | 33.606 | 33.6053 | 33.6046 | 33.6024 | 33.6001 | 33.5973 | 33.5926 | 33.578 | 33.5436 | 33.5004 | 33.4555 | 18.7244 | 18.7243 | 18.7241 | 18.724 | 18.7238 | 18.7236 | 18.7229 | 18.7222 | 18.7213 | 18.7199 | 18.7155 | 18.7049 | 18.6917 | 18.678 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072 | 18.8072
BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST | MINIMUM HEADROOM | SU 83597 60930 | YES | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.8268 | 35.6108 | 34.4272 | 34.624 | 34.6216 | 34.6044 | 34.5986 | 34.5933 | 34.5875 | 34.5731 | 34.5601 | 34.5477 | 34.5348 | 34.4973 | 33.8535 | 32.4315 | 31.0473 | 34.9256 | 34.9222 | 34.8973 | 34.889 | 34.8814 | 34.873 | 34.8521 | 34.8333 | 34.8154 | 34.7967 | 34.7425 | 33.6 | 32.2765 | 30.9881
|  | SANDHURST | CT |  |  | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 35.7719 | 34.5885 | 34.624 | 34.6216 | 34.6044 | 34.5987 | 34.5934 | 34.5876 | 34.5815 | 34.5685 | 34.5561 | 34.5432 | 34.5057 | 34.0417 | 32.6199 | 31.236 | 34.9257 | 34.9222 | 34.8973 | 34.8891 | 34.8814 | 34.8731 | 34.8642 | 34.8454 | 34.8275 | 34.8088 | 34.7546 | 33.7752 | 32.4518 | 31.1638
|  | SANDHURST | LW |  |  | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.8268 | 35.6108 | 34.4272 | 34.624 | 34.6216 | 34.6044 | 34.5986 | 34.5933 | 34.5875 | 34.5731 | 34.5601 | 34.5477 | 34.5348 | 34.4973 | 33.8535 | 32.4315 | 31.0473 | 34.9256 | 34.9222 | 34.8973 | 34.889 | 34.8814 | 34.873 | 34.8521 | 34.8333 | 34.8154 | 34.7967 | 34.7425 | 33.6 | 32.2765 | 30.9881
|  | SANDHURST | ST |  |  | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.4903 | 34.6247 | 34.6231 | 34.6073 | 34.6042 | 34.601 | 34.5971 | 34.5894 | 34.5826 | 34.5741 | 34.5653 | 34.54 | 34.4985 | 34.3587 | 33.4599 | 34.9267 | 34.9244 | 34.9015 | 34.897 | 34.8924 | 34.8868 | 34.8756 | 34.8658 | 34.8536 | 34.8409 | 34.8042 | 34.7442 | 34.0702 | 33.2337
|  | SANDHURST | SP |  |  | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 36.9036 | 34.6256 | 34.6248 | 34.6102 | 34.6091 | 34.6078 | 34.6064 | 34.6041 | 34.6022 | 34.6001 | 34.5967 | 34.5869 | 34.5711 | 34.556 | 34.5419 | 34.928 | 34.9268 | 34.9057 | 34.9041 | 34.9023 | 34.9002 | 34.8969 | 34.8942 | 34.8911 | 34.8862 | 34.872 | 34.8491 | 34.8274 | 34.8069
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN | MINIMUM HEADROOM | SZ 59877 85052 | NO | 62.6753 | 62.6558 | 62.6363 | 61.4446 | 61.346 | 61.2466 | 61.1462 | 61.0446 | 60.9393 | 60.8989 | 60.7749 | 60.5631 | 60.4137 | 60.1966 | 47.78 | 47.756 | 47.7307 | 46.5267 | 46.4162 | 46.3048 | 46.1897 | 46.0737 | 45.9539 | 45.8979 | 45.7278 | 44.7773 | 42.9824 | 41.1437 | 48.5094 | 48.4899 | 48.4704 | 47.2787 | 47.1801 | 47.0807 | 46.9802 | 46.8787 | 46.7734 | 46.733 | 46.5808 | 45.6078 | 43.7841 | 41.9171
|  | SANDOWN | CT |  |  | 62.7691 | 62.7574 | 62.7457 | 62.0307 | 61.9718 | 61.9127 | 61.8534 | 61.7937 | 61.7328 | 61.7089 | 61.6364 | 60.7632 | 60.4411 | 60.2199 | 47.874 | 47.8581 | 47.8408 | 47.114 | 47.0437 | 46.9732 | 46.9026 | 46.8284 | 46.7531 | 46.7137 | 46.595 | 45.0931 | 43.1258 | 41.2832 | 48.6032 | 48.5915 | 48.5798 | 47.8647 | 47.8059 | 47.7468 | 47.6874 | 47.6278 | 47.5669 | 47.543 | 47.4491 | 45.9256 | 43.9295 | 42.0586
|  | SANDOWN | LW |  |  | 62.6753 | 62.6558 | 62.6363 | 61.4446 | 61.346 | 61.2466 | 61.1462 | 61.0446 | 60.9393 | 60.8989 | 60.7749 | 60.5631 | 60.4137 | 60.1966 | 47.78 | 47.756 | 47.7307 | 46.5267 | 46.4162 | 46.3048 | 46.1897 | 46.0737 | 45.9539 | 45.8979 | 45.7278 | 44.7773 | 42.9824 | 41.1437 | 48.5094 | 48.4899 | 48.4704 | 47.2787 | 47.1801 | 47.0807 | 46.9802 | 46.8787 | 46.7734 | 46.733 | 46.5808 | 45.6078 | 43.7841 | 41.9171
|  | SANDOWN | ST |  |  | 62.816 | 62.8082 | 62.8004 | 62.3237 | 62.2844 | 62.245 | 62.2054 | 62.1655 | 62.1247 | 62.1082 | 62.0567 | 61.9725 | 61.9043 | 61.8106 | 47.9239 | 47.9141 | 47.9039 | 47.4231 | 47.3789 | 47.3334 | 47.2846 | 47.2358 | 47.185 | 47.1579 | 47.0754 | 46.9395 | 46.8192 | 45.7742 | 48.6501 | 48.6423 | 48.6345 | 48.1578 | 48.1185 | 48.0791 | 48.0395 | 47.9996 | 47.9587 | 47.9423 | 47.8908 | 47.7951 | 47.6652 | 46.6003
|  | SANDOWN | SP |  |  | 62.8629 | 62.859 | 62.8551 | 62.6167 | 62.5972 | 62.5776 | 62.5581 | 62.5385 | 62.5189 | 62.5108 | 62.4857 | 62.4453 | 62.4155 | 62.3663 | 47.9727 | 47.9684 | 47.964 | 47.7252 | 47.7037 | 47.6818 | 47.6592 | 47.6367 | 47.6132 | 47.601 | 47.5639 | 47.5039 | 47.4549 | 47.3874 | 48.697 | 48.6931 | 48.6892 | 48.4508 | 48.4313 | 48.4117 | 48.3922 | 48.3726 | 48.353 | 48.3449 | 48.3198 | 48.2794 | 48.2496 | 48.2004
LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY | MINIMUM HEADROOM | SZ 85667 94289 | NO | 36.7567 | 36.7567 | 36.7567 | 36.7567 | 36.7337 | 36.7101 | 36.6858 | 36.6601 | 36.6199 | 36.6147 | 36.597 | 36.5026 | 35.6946 | 34.0844 | 35.2913 | 35.2624 | 35.2532 | 35.2341 | 35.208 | 35.1703 | 35.132 | 35.0828 | 35.0191 | 34.9887 | 34.7482 | 33.0048 | 31.0801 | 29.2025 | 35.3988 | 35.3778 | 35.371 | 35.3571 | 35.3318 | 35.2979 | 35.2634 | 35.2206 | 35.1632 | 35.1397 | 35.0666 | 33.3888 | 31.4417 | 29.5418
|  | SELSEY | CT |  |  | 36.7567 | 36.7567 | 36.7567 | 36.7567 | 36.7337 | 36.7101 | 36.6858 | 36.6601 | 36.6199 | 36.6147 | 36.597 | 36.5026 | 35.7216 | 34.0872 | 35.2936 | 35.2665 | 35.2595 | 35.2451 | 35.208 | 35.1703 | 35.132 | 35.0828 | 35.0191 | 34.9887 | 34.8952 | 33.1646 | 31.1601 | 29.2584 | 35.4005 | 35.3807 | 35.3756 | 35.3651 | 35.3318 | 35.2979 | 35.2634 | 35.2206 | 35.1632 | 35.1397 | 35.0666 | 33.553 | 31.526 | 29.6021
|  | SELSEY | LW |  |  | 36.7567 | 36.7567 | 36.7567 | 36.7567 | 36.7559 | 36.7541 | 36.7512 | 36.7473 | 36.7395 | 36.7381 | 36.7312 | 36.7144 | 35.6946 | 34.0844 | 35.2913 | 35.2624 | 35.2532 | 35.2341 | 35.2145 | 35.1941 | 35.1675 | 35.1401 | 35.1087 | 35.0822 | 34.7482 | 33.0048 | 31.0801 | 29.2025 | 35.3988 | 35.3778 | 35.371 | 35.3571 | 35.3426 | 35.3272 | 35.3071 | 35.2859 | 35.261 | 35.2413 | 35.1008 | 33.3888 | 31.4417 | 29.5418
|  | SELSEY | ST |  |  | 36.7567 | 36.7567 | 36.7567 | 36.7567 | 36.751 | 36.7449 | 36.7386 | 36.7318 | 36.7207 | 36.7167 | 36.702 | 36.6878 | 36.6372 | 36.5538 | 35.3092 | 35.2903 | 35.2633 | 35.2545 | 35.2381 | 35.2191 | 35.1945 | 35.1697 | 35.1426 | 35.1214 | 35.0553 | 34.5978 | 33.3191 | 32.0922 | 35.4118 | 35.3981 | 35.3784 | 35.372 | 35.3584 | 35.343 | 35.3233 | 35.3034 | 35.2806 | 35.2641 | 35.2119 | 34.9647 | 33.7077 | 32.4665
|  | SELSEY | SP |  |  | 36.7567 | 36.7567 | 36.7567 | 36.7567 | 36.7544 | 36.7521 | 36.7498 | 36.7474 | 36.7437 | 36.7333 | 36.6994 | 36.6828 | 36.6282 | 36.5816 | 35.3138 | 35.2985 | 35.2759 | 35.2752 | 35.2699 | 35.2642 | 35.256 | 35.2477 | 35.2364 | 35.2193 | 35.1655 | 35.1124 | 35.0186 | 34.9333 | 35.4152 | 35.4041 | 35.3876 | 35.3871 | 35.3826 | 35.3778 | 35.3711 | 35.3645 | 35.3552 | 35.3399 | 35.2916 | 35.2483 | 35.1651 | 35.0903
MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY | MINIMUM HEADROOM | ST 85605 23325 | YES | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2547 | 18.4291 | 18.1606 | 18.1598 | 18.1587 | 18.156 | 18.1534 | 18.1506 | 18.142 | 18.1334 | 18.1247 | 18.116 | 17.972 | 17.034 | 16.0583 | 15.1001 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 17.7728 | 16.8774 | 15.9211
|  | SHAFTESBURY | CT |  |  | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 18.5393 | 18.1606 | 18.1598 | 18.1587 | 18.156 | 18.1534 | 18.1506 | 18.1478 | 18.1392 | 18.1304 | 18.1217 | 18.0963 | 17.1615 | 16.1859 | 15.228 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 17.8833 | 17.0048 | 16.0488
|  | SHAFTESBURY | LW |  |  | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2547 | 18.4291 | 18.1606 | 18.1598 | 18.1587 | 18.156 | 18.1534 | 18.1506 | 18.142 | 18.1334 | 18.1247 | 18.116 | 17.972 | 17.034 | 16.0583 | 15.1001 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 17.7728 | 16.8774 | 15.9211
|  | SHAFTESBURY | ST |  |  | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 18.161 | 18.1605 | 18.1599 | 18.1586 | 18.157 | 18.1551 | 18.151 | 18.1469 | 18.141 | 18.135 | 18.1179 | 17.9549 | 17.3257 | 16.704 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.0256 | 17.4868
|  | SHAFTESBURY | SP |  |  | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 19.2597 | 18.1615 | 18.1614 | 18.1613 | 18.1611 | 18.1606 | 18.16 | 18.1589 | 18.1578 | 18.1565 | 18.1542 | 18.1475 | 18.1369 | 18.1264 | 18.1165 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371 | 18.371
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET | MINIMUM HEADROOM | SZ 40828 88643 | NO | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.1554 | 14.1031 | 13.0206 | 11.9563 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8117 | 14.7993 | 14.7484 | 14.6933 | 14.6376 | 14.5775 | 14.0522 | 12.7813 | 11.4737 | 10.1883 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.6743 | 14.398 | 13.6078 | 12.3393 | 11.0342 | 9.7512
|  | SHALFLEET | CT |  |  | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.2402 | 14.1877 | 13.1053 | 12.0411 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8118 | 14.7993 | 14.7698 | 14.7147 | 14.6591 | 14.5989 | 14.1546 | 12.8834 | 11.5761 | 10.2907 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.7727 | 14.4964 | 13.71 | 12.4412 | 11.1363 | 9.8534
|  | SHALFLEET | LW |  |  | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.1554 | 14.1031 | 13.0206 | 11.9563 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8117 | 14.7993 | 14.7484 | 14.6933 | 14.6376 | 14.5775 | 14.0522 | 12.7813 | 11.4737 | 10.1883 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.6743 | 14.398 | 13.6078 | 12.3393 | 11.0342 | 9.7512
|  | SHALFLEET | ST |  |  | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.2178 | 14.5201 | 13.8298 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8086 | 14.7959 | 14.7581 | 14.7171 | 14.605 | 14.1276 | 13.2849 | 12.4511 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.5244 | 13.683 | 12.8419 | 12.0097
|  | SHALFLEET | SP |  |  | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 15.6222 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8136 | 14.8097 | 14.7629 | 14.698 | 14.6362 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.8264 | 14.6675
FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN | MINIMUM HEADROOM | SZ 57809 81912 | NO | 28.7297 | 28.7297 | 28.7297 | 28.7297 | 28.5647 | 28.393 | 28.2121 | 28.0231 | 27.7331 | 27.6925 | 27.5497 | 27.3261 | 26.9403 | 26.4867 | 26.7482 | 26.5631 | 26.5351 | 26.4877 | 26.2893 | 26.0815 | 25.7573 | 25.426 | 24.995 | 24.8045 | 24.2183 | 23.2401 | 22.0571 | 21.2489 | 27.112 | 27.1008 | 27.0991 | 27.0962 | 26.9292 | 26.7553 | 26.5658 | 26.3681 | 26.0695 | 26.0198 | 25.6554 | 24.6383 | 23.4301 | 22.598
|  | SHANKLIN | CT |  |  | 28.7297 | 28.7297 | 28.7297 | 28.7297 | 28.7293 | 28.7285 | 28.7273 | 28.7257 | 28.7219 | 28.7213 | 28.7177 | 28.6883 | 28.6554 | 28.3123 | 26.7482 | 26.5631 | 26.5351 | 26.4877 | 26.4539 | 26.4171 | 26.3788 | 26.2348 | 26.0902 | 25.9396 | 25.4927 | 24.7128 | 23.8827 | 23.0894 | 27.112 | 27.1008 | 27.0991 | 27.0962 | 27.0938 | 27.0908 | 27.0874 | 27.0771 | 27.0648 | 27.0551 | 26.9346 | 26.1145 | 25.2592 | 24.4412
|  | SHANKLIN | LW |  |  | 28.7297 | 28.7297 | 28.7297 | 28.7297 | 28.5647 | 28.393 | 28.2121 | 28.0231 | 27.7331 | 27.6925 | 27.5497 | 27.3261 | 26.9403 | 26.4867 | 26.7482 | 26.5631 | 26.5351 | 26.4877 | 26.2893 | 26.0815 | 25.7573 | 25.426 | 24.995 | 24.8045 | 24.2183 | 23.2401 | 22.0571 | 21.2489 | 27.112 | 27.1008 | 27.0991 | 27.0962 | 26.9292 | 26.7553 | 26.5658 | 26.3681 | 26.0695 | 26.0198 | 25.6554 | 24.6383 | 23.4301 | 22.598
|  | SHANKLIN | ST |  |  | 28.7297 | 28.7297 | 28.7297 | 28.7297 | 28.7294 | 28.7288 | 28.728 | 28.7267 | 28.7238 | 28.7224 | 28.715 | 28.7053 | 28.6711 | 28.6586 | 26.8711 | 26.7337 | 26.5637 | 26.5392 | 26.5198 | 26.4944 | 26.4102 | 26.3263 | 26.2272 | 26.1235 | 25.8167 | 25.3094 | 24.7798 | 24.2588 | 27.1195 | 27.1112 | 27.1009 | 27.0994 | 27.0979 | 27.0958 | 27.0899 | 27.0836 | 27.0749 | 27.0673 | 27.0417 | 26.7435 | 26.1842 | 25.6471
|  | SHANKLIN | SP |  |  | 28.7297 | 28.7297 | 28.7297 | 28.7297 | 28.7297 | 28.7297 | 28.7296 | 28.7296 | 28.7295 | 28.729 | 28.7263 | 28.7242 | 28.714 | 28.704 | 26.8809 | 26.7538 | 26.7469 | 26.7399 | 26.7344 | 26.7271 | 26.7027 | 26.6786 | 26.6478 | 26.6077 | 26.4894 | 26.297 | 26.1041 | 25.9205 | 27.1201 | 27.1124 | 27.112 | 27.1115 | 27.1112 | 27.1107 | 27.1092 | 27.1077 | 27.1057 | 27.1029 | 27.0932 | 27.0795 | 27.0582 | 27.0377
AXMINSTER | YEOVIL BSP | SHERBORNE | MINIMUM HEADROOM | ST 63978 18163 | YES | 17.2803 | 17.2702 | 17.2539 | 17.2184 | 17.1671 | 17.1121 | 17.0114 | 16.9146 | 16.8056 | 16.7236 | 16.4772 | 16.0681 | 15.6059 | 15.2374 | 15.672 | 15.659 | 15.6381 | 15.5926 | 15.5308 | 15.4651 | 15.3413 | 15.2232 | 15.0938 | 14.9902 | 14.6806 | 14.1691 | 13.602 | 13.131 | 14.9913 | 14.9849 | 14.9747 | 14.9525 | 14.9148 | 14.8741 | 14.8038 | 14.735 | 14.653 | 14.5995 | 14.4364 | 14.1624 | 13.8386 | 13.6052
|  | SHERBORNE | CT |  |  | 17.2807 | 17.2708 | 17.2548 | 17.2201 | 17.1835 | 17.1451 | 17.1054 | 17.0284 | 16.9517 | 16.8745 | 16.6472 | 16.2503 | 15.8407 | 15.4669 | 15.6725 | 15.6598 | 15.6393 | 15.5948 | 15.5479 | 15.4989 | 15.4484 | 15.3502 | 15.253 | 15.1542 | 14.8638 | 14.3644 | 13.85 | 13.3738 | 14.9915 | 14.9853 | 14.9753 | 14.9535 | 14.9304 | 14.9059 | 14.8806 | 14.8316 | 14.7818 | 14.7331 | 14.5891 | 14.3272 | 14.056 | 13.8172
|  | SHERBORNE | LW |  |  | 17.2803 | 17.2702 | 17.2539 | 17.2184 | 17.1671 | 17.1121 | 17.0114 | 16.9146 | 16.8056 | 16.7236 | 16.4772 | 16.0681 | 15.6059 | 15.2374 | 15.672 | 15.659 | 15.6381 | 15.5926 | 15.5308 | 15.4651 | 15.3413 | 15.2232 | 15.0938 | 14.9902 | 14.6806 | 14.1691 | 13.602 | 13.131 | 14.9913 | 14.9849 | 14.9747 | 14.9525 | 14.9148 | 14.8741 | 14.8038 | 14.735 | 14.653 | 14.5995 | 14.4364 | 14.1624 | 13.8386 | 13.6052
|  | SHERBORNE | ST |  |  | 17.2847 | 17.2781 | 17.2681 | 17.2498 | 17.2266 | 17.1985 | 17.145 | 17.0954 | 17.0427 | 16.9889 | 16.8297 | 16.5773 | 16.298 | 16.0473 | 15.6777 | 15.6691 | 15.6563 | 15.6328 | 15.6031 | 15.5674 | 15.499 | 15.4358 | 15.3691 | 15.3006 | 15.0988 | 14.7782 | 14.4314 | 14.114 | 14.994 | 14.9898 | 14.9836 | 14.9721 | 14.9574 | 14.9396 | 14.9057 | 14.874 | 14.8397 | 14.8054 | 14.7023 | 14.5397 | 14.3496 | 14.187
|  | SHERBORNE | SP |  |  | 17.2921 | 17.2911 | 17.2888 | 17.285 | 17.2774 | 17.2687 | 17.2515 | 17.2363 | 17.2176 | 17.1968 | 17.1357 | 17.0422 | 16.9442 | 16.8521 | 15.6871 | 15.6858 | 15.6828 | 15.678 | 15.6682 | 15.6571 | 15.635 | 15.6155 | 15.5916 | 15.5651 | 15.4875 | 15.3683 | 15.2461 | 15.1312 | 14.9987 | 14.998 | 14.9966 | 14.9942 | 14.9894 | 14.984 | 14.9732 | 14.9636 | 14.9518 | 14.9386 | 14.8991 | 14.8395 | 14.7736 | 14.7115
MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE | MINIMUM HEADROOM | SP 03884 19102 | YES | 33.6095 | 33.5849 | 33.553 | 33.4961 | 33.4501 | 33.4039 | 33.2527 | 33.1021 | 32.9526 | 32.7926 | 32.3201 | 31.5335 | 30.7204 | 29.9209 | 31.8427 | 31.8139 | 31.7764 | 31.7096 | 31.6556 | 31.6013 | 31.4238 | 31.247 | 31.0716 | 30.8837 | 30.3289 | 29.4054 | 28.4508 | 27.5122 | 32.303 | 32.2809 | 32.2523 | 32.2012 | 32.16 | 32.1185 | 31.9828 | 31.8477 | 31.7068 | 31.5238 | 30.9835 | 30.0839 | 29.154 | 28.2398
|  | SHIPTON OLIFFE | CT |  |  | 33.6095 | 33.5849 | 33.553 | 33.4961 | 33.4501 | 33.4039 | 33.3567 | 33.2062 | 33.0567 | 32.8967 | 32.4243 | 31.6376 | 30.8247 | 30.0254 | 31.8427 | 31.8139 | 31.7764 | 31.7096 | 31.6556 | 31.6013 | 31.5459 | 31.3692 | 31.1938 | 31.0058 | 30.4513 | 29.5276 | 28.5733 | 27.6348 | 32.303 | 32.2809 | 32.2523 | 32.2012 | 32.16 | 32.1185 | 32.0761 | 31.9411 | 31.807 | 31.6428 | 31.1027 | 30.203 | 29.2734 | 28.3592
|  | SHIPTON OLIFFE | LW |  |  | 33.6095 | 33.5849 | 33.553 | 33.4961 | 33.4501 | 33.4039 | 33.2527 | 33.1021 | 32.9526 | 32.7926 | 32.3201 | 31.5335 | 30.7204 | 29.9209 | 31.8427 | 31.8139 | 31.7764 | 31.7096 | 31.6556 | 31.6013 | 31.4238 | 31.247 | 31.0716 | 30.8837 | 30.3289 | 29.4054 | 28.4508 | 27.5122 | 32.303 | 32.2809 | 32.2523 | 32.2012 | 32.16 | 32.1185 | 31.9828 | 31.8477 | 31.7068 | 31.5238 | 30.9835 | 30.0839 | 29.154 | 28.2398
|  | SHIPTON OLIFFE | ST |  |  | 33.6107 | 33.5896 | 33.5646 | 33.5268 | 33.4883 | 33.4416 | 33.355 | 33.2692 | 33.1672 | 33.058 | 32.7397 | 32.2152 | 31.6911 | 31.1716 | 31.8442 | 31.8193 | 31.79 | 31.7456 | 31.7004 | 31.6456 | 31.5439 | 31.4433 | 31.3234 | 31.1953 | 30.8216 | 30.2058 | 29.5904 | 28.9805 | 32.3041 | 32.2851 | 32.2627 | 32.2287 | 32.1942 | 32.1523 | 32.0746 | 31.9977 | 31.9061 | 31.8081 | 31.4634 | 30.8635 | 30.2641 | 29.67
|  | SHIPTON OLIFFE | SP |  |  | 33.629 | 33.6231 | 33.617 | 33.6114 | 33.6042 | 33.5955 | 33.5744 | 33.5534 | 33.5263 | 33.484 | 33.3614 | 33.1627 | 32.9711 | 32.7896 | 31.8657 | 31.8587 | 31.8515 | 31.845 | 31.8365 | 31.8263 | 31.8016 | 31.7769 | 31.745 | 31.6954 | 31.5515 | 31.3182 | 31.0932 | 30.8801 | 32.3205 | 32.3152 | 32.3097 | 32.3047 | 32.2982 | 32.2904 | 32.2715 | 32.2527 | 32.2283 | 32.1904 | 32.0804 | 31.9021 | 31.7279 | 31.5204
NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY | MINIMUM HEADROOM | SU 39988 13808 | YES | 16.3105 | 16.3092 | 16.2824 | 16.2802 | 16.0972 | 15.9103 | 15.7204 | 15.5161 | 15.2039 | 15.1534 | 14.9888 | 14.0547 | 12.787 | 12.0864 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.3699 | 12.1858 | 11.9988 | 11.8035 | 11.5024 | 11.4643 | 10.9568 | 9.3717 | 8.0079 | 7.2142 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 11.8239 | 11.6399 | 11.4529 | 11.2576 | 10.9565 | 10.9183 | 10.7958 | 9.9682 | 8.6212 | 7.8438
|  | SHIRLEY | CT |  |  | 16.3113 | 16.3105 | 16.2824 | 16.2802 | 16.0972 | 15.9103 | 15.7204 | 15.5161 | 15.2039 | 15.1534 | 14.9888 | 14.0547 | 12.787 | 12.0864 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.3699 | 12.1858 | 11.9988 | 11.8035 | 11.5024 | 11.4643 | 10.9568 | 9.3717 | 8.0079 | 7.2142 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 11.8239 | 11.6399 | 11.4529 | 11.2576 | 10.9565 | 10.9183 | 10.7958 | 9.9682 | 8.6212 | 7.8438
|  | SHIRLEY | LW |  |  | 16.3113 | 16.3105 | 16.2824 | 16.2802 | 16.2782 | 16.2752 | 16.2664 | 16.2575 | 16.2463 | 16.234 | 16.192 | 15.7579 | 15.2052 | 14.6704 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.0816 | 11.0625 | 10.4136 | 9.7857 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 11.6612 | 11.0291 | 10.4175
|  | SHIRLEY | ST |  |  | 16.3105 | 16.3092 | 16.3076 | 16.305 | 16.3018 | 16.2973 | 16.293 | 16.2887 | 16.2811 | 16.2727 | 16.2435 | 16.1942 | 16.1649 | 15.9488 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.1132 | 11.694 | 11.2866 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 11.8794
|  | SHIRLEY | SP |  |  | 16.3122 | 16.3121 | 16.312 | 16.3119 | 16.3116 | 16.3109 | 16.3094 | 16.3078 | 16.3053 | 16.302 | 16.2906 | 16.2707 | 16.2598 | 16.2495 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.5508 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048 | 12.0048
MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM | MINIMUM HEADROOM | SU 23782 87902 | NO | 5.5275 | 5.5091 | 5.4851 | 5.4343 | 5.37 | 5.2929 | 5.2029 | 5.1106 | 4.9754 | 4.9171 | 4.7361 | 4.5476 | 4.1231 | 3.9314 | 2.9703 | 2.9487 | 2.9204 | 2.8606 | 2.7875 | 2.7147 | 2.6268 | 2.5317 | 2.3935 | 2.332 | 2.1416 | 1.9378 | 1.4982 | 1.2914 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.8429 | 3.7704 | 3.6963 | 3.6198 | 3.5015 | 3.4613 | 3.3331 | 3.1655 | 2.7261 | 2.5196
|  | SHRIVENHAM | CT |  |  | 5.5275 | 5.5091 | 5.4851 | 5.4343 | 5.37 | 5.3059 | 5.242 | 5.201 | 5.1513 | 5.1216 | 5.0331 | 4.8546 | 4.6616 | 4.5176 | 2.9703 | 2.9487 | 2.9204 | 2.8606 | 2.7875 | 2.7147 | 2.6422 | 2.5968 | 2.5428 | 2.5083 | 2.4058 | 2.2045 | 1.9879 | 1.8207 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.8993 | 3.8841 | 3.8685 | 3.8243 | 3.7704 | 3.736 | 3.6338 | 3.4329 | 3.2169 | 3.0501
|  | SHRIVENHAM | LW |  |  | 5.5352 | 5.5226 | 5.506 | 5.471 | 5.4371 | 5.4034 | 5.3783 | 5.3535 | 5.3289 | 5.3023 | 5.2239 | 5.0954 | 4.963 | 4.8328 | 2.9795 | 2.9646 | 2.9451 | 2.9039 | 2.8639 | 2.8242 | 2.7947 | 2.7654 | 2.7364 | 2.7051 | 2.6128 | 2.4614 | 2.3054 | 2.152 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.8405 | 3.6895 | 3.534 | 3.3811
|  | SHRIVENHAM | ST |  |  | 5.5377 | 5.5272 | 5.5149 | 5.4938 | 5.3966 | 5.2929 | 5.2029 | 5.1106 | 4.9754 | 4.9171 | 4.7361 | 4.5476 | 4.1231 | 3.9314 | 2.9824 | 2.97 | 2.9555 | 2.9307 | 2.8289 | 2.7196 | 2.6268 | 2.5317 | 2.3935 | 2.332 | 2.1416 | 1.9378 | 1.4982 | 1.2914 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.8429 | 3.7704 | 3.6963 | 3.6198 | 3.5015 | 3.4613 | 3.3331 | 3.1655 | 2.7261 | 2.5196
|  | SHRIVENHAM | SP |  |  | 5.5498 | 5.5485 | 5.5472 | 5.546 | 5.5384 | 5.5296 | 5.522 | 5.5144 | 5.5041 | 5.488 | 5.439 | 5.3931 | 5.3195 | 5.2546 | 2.9967 | 2.9951 | 2.9936 | 2.9922 | 2.9836 | 2.9736 | 2.965 | 2.9565 | 2.9449 | 2.9276 | 2.8749 | 2.8232 | 2.7442 | 2.6741 | 3.9144 | 3.9144 | 3.9144 | 3.9144 | 3.9123 | 3.9102 | 3.9082 | 3.9061 | 3.9029 | 3.8939 | 3.8653 | 3.8517 | 3.8089 | 3.7731
MANNINGTON GSP | SHAFTESBURY BSP | SHROTON | MINIMUM HEADROOM | ST 85356 13659 | YES | 36.5445 | 36.5247 | 36.4986 | 36.4456 | 36.3656 | 36.2841 | 36.2025 | 36.1196 | 36.0203 | 35.959 | 35.7636 | 35.2428 | 33.8498 | 32.4862 | 34.0217 | 34.0154 | 34.0071 | 33.9904 | 33.9457 | 33.8999 | 33.8533 | 33.8054 | 33.7411 | 33.7172 | 33.6398 | 32.5683 | 30.6634 | 28.8345 | 34.9172 | 34.8994 | 34.876 | 34.8285 | 34.7538 | 34.6776 | 34.6012 | 34.5236 | 34.4295 | 34.3738 | 34.1961 | 32.7473 | 30.9013 | 29.1315
|  | SHROTON | CT |  |  | 36.5445 | 36.5247 | 36.4986 | 36.4456 | 36.3936 | 36.3413 | 36.2892 | 36.238 | 36.1867 | 36.1321 | 35.9595 | 35.4701 | 34.1632 | 32.8044 | 34.0217 | 34.0154 | 34.0071 | 33.9904 | 33.9739 | 33.9574 | 33.9409 | 33.9247 | 33.9085 | 33.8912 | 33.8367 | 32.794 | 30.9752 | 29.1516 | 34.9172 | 34.8994 | 34.876 | 34.8285 | 34.7818 | 34.7348 | 34.6881 | 34.6421 | 34.5961 | 34.547 | 34.3922 | 32.9731 | 31.2133 | 29.4488
|  | SHROTON | LW |  |  | 36.5446 | 36.5248 | 36.4988 | 36.4459 | 36.3656 | 36.2841 | 36.2025 | 36.1196 | 36.0203 | 35.959 | 35.7636 | 35.2428 | 33.8498 | 32.4862 | 34.0217 | 34.0154 | 34.0072 | 33.9905 | 33.9457 | 33.8999 | 33.8533 | 33.8054 | 33.7411 | 33.7172 | 33.6398 | 32.5683 | 30.6634 | 28.8345 | 34.9173 | 34.8995 | 34.8762 | 34.8287 | 34.7538 | 34.6776 | 34.6012 | 34.5236 | 34.4295 | 34.3738 | 34.1961 | 32.7473 | 30.9013 | 29.1315
|  | SHROTON | ST |  |  | 36.5553 | 36.5438 | 36.5303 | 36.5081 | 36.4808 | 36.4478 | 36.4109 | 36.374 | 36.339 | 36.3017 | 36.1841 | 35.9199 | 35.5934 | 34.7567 | 34.0251 | 34.0214 | 34.0172 | 34.0101 | 34.0015 | 33.9911 | 33.9794 | 33.9677 | 33.9567 | 33.9449 | 33.9077 | 33.8241 | 32.9656 | 31.8012 | 34.9269 | 34.9166 | 34.9045 | 34.8845 | 34.86 | 34.8305 | 34.7973 | 34.7642 | 34.7328 | 34.6993 | 34.5937 | 34.2944 | 33.1392 | 32.0125
|  | SHROTON | SP |  |  | 36.5662 | 36.5635 | 36.5608 | 36.5581 | 36.5495 | 36.5394 | 36.5264 | 36.5135 | 36.4971 | 36.4826 | 36.4369 | 36.3304 | 36.1979 | 36.0601 | 34.0285 | 34.0277 | 34.0268 | 34.0259 | 34.0232 | 34.02 | 34.0159 | 34.0118 | 34.0067 | 34.0021 | 33.9876 | 33.9539 | 33.9121 | 33.8685 | 34.9367 | 34.9343 | 34.9319 | 34.9294 | 34.9217 | 34.9127 | 34.901 | 34.8894 | 34.8747 | 34.8617 | 34.8206 | 34.725 | 34.6062 | 34.4824
LALEHAM | STAINES | SIDNEY ROAD | MINIMUM HEADROOM | TQ 04100 71760 | NO | 17.4306 | 17.4306 | 17.4306 | 17.4306 | 17.4106 | 17.39 | 17.3684 | 17.346 | 17.312 | 17.3073 | 17.2869 | 17.2531 | 17.1964 | 16.896 | 16.8479 | 16.8446 | 16.8406 | 16.8333 | 16.8105 | 16.7847 | 16.7592 | 16.7329 | 16.695 | 16.6862 | 16.6537 | 16.2735 | 15.8585 | 15.5042 | 17.1363 | 17.1328 | 17.1285 | 17.1206 | 17.0977 | 17.0716 | 17.0458 | 17.0191 | 16.9809 | 16.9719 | 16.9386 | 16.7936 | 16.3794 | 16.0256
|  | SIDNEY ROAD | CT |  |  | 17.4306 | 17.4306 | 17.4306 | 17.4306 | 17.4166 | 17.4023 | 17.3878 | 17.3726 | 17.3492 | 17.3462 | 17.3336 | 17.2676 | 17.1995 | 16.896 | 16.8479 | 16.8446 | 16.8406 | 16.8333 | 16.8133 | 16.793 | 16.7725 | 16.7533 | 16.726 | 16.7189 | 16.6924 | 16.2735 | 15.8585 | 15.5042 | 17.1363 | 17.1328 | 17.1285 | 17.1206 | 17.1003 | 17.0795 | 17.0586 | 17.0391 | 17.0115 | 17.0042 | 16.9787 | 16.7936 | 16.3794 | 16.0256
|  | SIDNEY ROAD | LW |  |  | 17.4306 | 17.4306 | 17.4306 | 17.4306 | 17.4106 | 17.39 | 17.3684 | 17.346 | 17.312 | 17.3073 | 17.2869 | 17.2531 | 17.1964 | 16.9977 | 16.8483 | 16.8454 | 16.8419 | 16.8355 | 16.8105 | 16.7847 | 16.7592 | 16.7329 | 16.695 | 16.6862 | 16.6537 | 16.3685 | 15.9646 | 15.6223 | 17.1368 | 17.1337 | 17.1299 | 17.123 | 17.0977 | 17.0716 | 17.0458 | 17.0191 | 16.9809 | 16.9719 | 16.9386 | 16.8836 | 16.4852 | 16.1436
|  | SIDNEY ROAD | ST |  |  | 17.4306 | 17.4306 | 17.4306 | 17.4306 | 17.4196 | 17.4084 | 17.397 | 17.3852 | 17.3669 | 17.3607 | 17.3376 | 17.3177 | 17.2607 | 17.2442 | 16.85 | 16.8483 | 16.8466 | 16.8441 | 16.831 | 16.8173 | 16.8032 | 16.7887 | 16.7677 | 16.7588 | 16.7276 | 16.6944 | 16.6248 | 16.4432 | 17.1385 | 17.1368 | 17.1349 | 17.1322 | 17.119 | 17.1051 | 17.0908 | 17.0762 | 17.055 | 17.0458 | 17.0141 | 16.98 | 16.9095 | 16.8797
|  | SIDNEY ROAD | SP |  |  | 17.4306 | 17.4306 | 17.4306 | 17.4306 | 17.4292 | 17.4277 | 17.4263 | 17.4248 | 17.4225 | 17.4161 | 17.3958 | 17.386 | 17.348 | 17.3162 | 16.851 | 16.8502 | 16.8495 | 16.8488 | 16.8467 | 16.8444 | 16.842 | 16.8395 | 16.836 | 16.8286 | 16.8052 | 16.7903 | 16.7477 | 16.7116 | 17.1396 | 17.1388 | 17.1381 | 17.1373 | 17.1351 | 17.1328 | 17.1303 | 17.1278 | 17.1242 | 17.1166 | 17.093 | 17.0778 | 17.0349 | 16.9985
NURSLING GSP | ROWNHAMS | SILKSTEAD | MINIMUM HEADROOM | SU 44578 24565 | YES | 25.3632 | 25.2586 | 25.2333 | 25.1732 | 25.1095 | 25.0408 | 24.9035 | 24.7602 | 24.6009 | 24.4686 | 24.0705 | 23.4027 | 22.6496 | 22.0436 | 23.3102 | 23.1895 | 23.1603 | 23.0909 | 23.0179 | 22.9399 | 22.7833 | 22.6206 | 22.442 | 22.2903 | 21.8355 | 21.0761 | 20.2292 | 19.5313 | 23.6029 | 23.5119 | 23.4898 | 23.4375 | 23.3816 | 23.3208 | 23.1998 | 23.0729 | 22.9297 | 22.8139 | 22.4636 | 21.8729 | 21.1989 | 20.6705
|  | SILKSTEAD | CT |  |  | 25.3656 | 25.2626 | 25.2396 | 25.1842 | 25.1277 | 25.0693 | 25.0095 | 24.8789 | 24.7436 | 24.6153 | 24.2379 | 23.5615 | 22.8611 | 22.237 | 23.3129 | 23.1941 | 23.1675 | 23.1036 | 23.0386 | 22.9714 | 22.903 | 22.7529 | 22.5984 | 22.4506 | 22.0165 | 21.2486 | 20.4544 | 19.7383 | 23.6049 | 23.5154 | 23.4953 | 23.4471 | 23.3978 | 23.3467 | 23.2943 | 23.18 | 23.061 | 22.9491 | 22.6194 | 22.0203 | 21.399 | 20.8523
|  | SILKSTEAD | LW |  |  | 25.3632 | 25.2586 | 25.2333 | 25.1732 | 25.1095 | 25.0408 | 24.9035 | 24.7602 | 24.6009 | 24.4686 | 24.0705 | 23.4027 | 22.6496 | 22.0436 | 23.3102 | 23.1895 | 23.1603 | 23.0909 | 23.0179 | 22.9399 | 22.7833 | 22.6206 | 22.442 | 22.2903 | 21.8355 | 21.0761 | 20.2292 | 19.5313 | 23.6029 | 23.5119 | 23.4898 | 23.4375 | 23.3816 | 23.3208 | 23.1998 | 23.0729 | 22.9297 | 22.8139 | 22.4636 | 21.8729 | 21.1989 | 20.6705
|  | SILKSTEAD | ST |  |  | 25.3686 | 25.3538 | 25.2509 | 25.2165 | 25.1557 | 25.0853 | 25.0033 | 24.9186 | 24.7959 | 24.6957 | 24.3948 | 23.9457 | 23.3659 | 22.9168 | 23.3164 | 23.2993 | 23.1805 | 23.1408 | 23.0735 | 22.9954 | 22.9039 | 22.8097 | 22.6738 | 22.5604 | 22.2212 | 21.7112 | 21.071 | 20.5621 | 23.6076 | 23.5946 | 23.5051 | 23.4752 | 23.4199 | 23.3561 | 23.282 | 23.2054 | 23.0937 | 23.0047 | 22.7361 | 22.3383 | 21.8095 | 21.4107
|  | SILKSTEAD | SP |  |  | 25.3856 | 25.3836 | 25.3817 | 25.3772 | 25.3653 | 25.3515 | 25.3314 | 25.3111 | 25.2855 | 25.2475 | 25.1338 | 24.9734 | 24.7878 | 24.6146 | 23.336 | 23.3337 | 23.3315 | 23.3264 | 23.3128 | 23.297 | 23.2739 | 23.2506 | 23.2212 | 23.178 | 23.0496 | 22.8661 | 22.6587 | 22.465 | 23.6223 | 23.6206 | 23.6189 | 23.6151 | 23.6046 | 23.5925 | 23.5749 | 23.5571 | 23.5346 | 23.5009 | 23.3998 | 23.2588 | 23.0916 | 22.9356
BRAMLEY (FLEE) | READING BSP | SILVER STREET | MINIMUM HEADROOM | SU 71957 72821 | YES | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.2526 | 32.1974 | 32.1397 | 32.0362 | 31.7606 | 31.5454 | 30.5227 | 29.5375 | 28.5387 | 27.6692 | 32.9578 | 32.9372 | 32.933 | 32.9247 | 32.8631 | 32.7983 | 32.731 | 32.6624 | 32.5594 | 32.5333 | 31.6773 | 30.6084 | 29.475 | 28.4729 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5158 | 33.4606 | 33.4029 | 33.3432 | 33.2524 | 33.2398 | 33.1967 | 32.5529 | 31.4392 | 30.4566
|  | SILVER STREET | CT |  |  | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.2723 | 32.0874 | 31.8848 | 30.9052 | 29.9846 | 29.1111 | 28.2515 | 32.9578 | 32.9372 | 32.933 | 32.9247 | 32.916 | 32.9063 | 32.898 | 32.8892 | 32.8769 | 32.8635 | 32.0604 | 31.0571 | 30.049 | 29.0568 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.0013 | 32.013 | 31.0403
|  | SILVER STREET | LW |  |  | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.2526 | 32.1974 | 32.1397 | 32.0362 | 31.7606 | 31.5454 | 30.5227 | 29.5375 | 28.5387 | 27.6692 | 32.9579 | 32.9373 | 32.9332 | 32.9251 | 32.8631 | 32.7983 | 32.731 | 32.6624 | 32.5594 | 32.5333 | 31.6773 | 30.6084 | 29.475 | 28.4729 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5158 | 33.4606 | 33.4029 | 33.3432 | 33.2524 | 33.2398 | 33.1967 | 32.5529 | 31.4392 | 30.4566
|  | SILVER STREET | ST |  |  | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.2278 | 31.5357 | 30.9026 | 30.3347 | 29.7821 | 32.9592 | 32.9538 | 32.9374 | 32.9326 | 32.9266 | 32.9191 | 32.9111 | 32.9038 | 32.8955 | 32.8862 | 32.7323 | 32.0577 | 31.4528 | 30.8233 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.3975 | 32.7721
|  | SILVER STREET | SP |  |  | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.3061 | 32.2995 | 32.0639 | 31.8288 | 32.9616 | 32.9587 | 32.9445 | 32.9435 | 32.9416 | 32.9392 | 32.9363 | 32.9337 | 32.9296 | 32.926 | 32.9078 | 32.891 | 32.8754 | 32.8597 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693 | 33.5693
MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD | MINIMUM HEADROOM | SZ 18262 93590 | YES | 15.6109 | 15.6109 | 15.6109 | 15.6109 | 15.2972 | 14.9703 | 14.6255 | 14.2646 | 13.7099 | 13.6321 | 13.2878 | 12.485 | 11.3115 | 10.897 | 11.3898 | 11.2917 | 11.1631 | 10.891 | 10.3106 | 9.7135 | 9.2857 | 8.8426 | 8.2065 | 8.041 | 7.507 | 6.6307 | 5.3812 | 4.8918 | 11.6238 | 11.5301 | 11.4071 | 11.147 | 10.5809 | 10.0036 | 9.5818 | 9.1447 | 8.5145 | 8.3555 | 7.8403 | 6.9955 | 5.7786 | 5.3213
|  | SOMERFORD | CT |  |  | 15.6109 | 15.6109 | 15.6109 | 15.6109 | 15.4951 | 15.3765 | 15.2551 | 15.1273 | 14.9278 | 14.9021 | 14.728 | 13.9448 | 13.129 | 12.6549 | 11.4047 | 11.3174 | 11.203 | 10.9611 | 10.6105 | 10.2518 | 9.8928 | 9.6828 | 9.4018 | 9.2884 | 8.9433 | 8.0866 | 7.1949 | 6.6459 | 11.638 | 11.5546 | 11.4452 | 11.2139 | 10.8736 | 10.5322 | 10.1905 | 9.9865 | 9.7115 | 9.6045 | 9.2783 | 8.4531 | 7.5939 | 7.077
|  | SOMERFORD | LW |  |  | 15.6109 | 15.6109 | 15.6109 | 15.6109 | 15.2972 | 14.9703 | 14.6255 | 14.2646 | 13.7099 | 13.6321 | 13.2878 | 12.485 | 11.3115 | 10.897 | 11.3898 | 11.2917 | 11.1631 | 10.891 | 10.3106 | 9.7135 | 9.2857 | 8.8426 | 8.2065 | 8.041 | 7.507 | 6.6307 | 5.3812 | 4.8918 | 11.6238 | 11.5301 | 11.4071 | 11.147 | 10.5809 | 10.0036 | 9.5818 | 9.1447 | 8.5145 | 8.3555 | 7.8403 | 6.9955 | 5.7786 | 5.3213
|  | SOMERFORD | ST |  |  | 15.6109 | 15.6109 | 15.6109 | 15.6109 | 15.6102 | 15.609 | 15.607 | 15.6041 | 15.5977 | 15.5946 | 15.578 | 15.5562 | 15.3619 | 15.0972 | 11.4212 | 11.3477 | 11.2612 | 11.1129 | 10.9303 | 10.709 | 10.6351 | 10.5612 | 10.4992 | 10.4363 | 10.2445 | 9.9354 | 9.5712 | 9.2579 | 11.6538 | 11.5836 | 11.5009 | 11.3591 | 11.1845 | 10.9731 | 10.9043 | 10.8357 | 10.7777 | 10.7191 | 10.5402 | 10.252 | 9.9087 | 9.6163
|  | SOMERFORD | SP |  |  | 15.6109 | 15.6109 | 15.6109 | 15.6109 | 15.6109 | 15.6108 | 15.6107 | 15.6106 | 15.6103 | 15.6093 | 15.6033 | 15.5985 | 15.5757 | 15.5535 | 11.5049 | 11.4946 | 11.4847 | 11.4752 | 11.4312 | 11.3784 | 11.3538 | 11.3293 | 11.2979 | 11.2744 | 11.2029 | 11.0918 | 10.9668 | 10.8476 | 11.7339 | 11.724 | 11.7145 | 11.7055 | 11.6634 | 11.6129 | 11.5894 | 11.566 | 11.536 | 11.5135 | 11.4448 | 11.3384 | 11.2179 | 11.1029
LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTEAD | MINIMUM HEADROOM | SU 94025 00705 | YES | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1614 | 43.1521 | 43.1427 | 43.1329 | 43.1177 | 43.1158 | 43.1096 | 43.0812 | 42.341 | 41.0476 | 32.0131 | 31.9691 | 31.9114 | 31.7919 | 31.6661 | 31.5403 | 31.4152 | 31.3608 | 31.3009 | 31.2515 | 31.0911 | 30.6833 | 30.0624 | 28.5538 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3227 | 32.3135 | 32.2144 | 32.1168 | 31.991 | 31.8604 | 31.436 | 30.3682 | 28.9602 | 27.565
|  | SOUTH BERSTEAD | CT |  |  | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1614 | 43.1521 | 43.1427 | 43.1329 | 43.1177 | 43.1158 | 43.1096 | 43.0812 | 42.341 | 41.0476 | 32.0131 | 31.9691 | 31.9114 | 31.7919 | 31.6661 | 31.5403 | 31.4152 | 31.3608 | 31.3009 | 31.2515 | 31.0911 | 30.6833 | 30.0624 | 28.5538 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3227 | 32.3135 | 32.2144 | 32.1168 | 31.991 | 31.8604 | 31.436 | 30.3682 | 28.9602 | 27.565
|  | SOUTH BERSTEAD | LW |  |  | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 42.8145 | 41.5294 | 32.0199 | 31.9809 | 31.9296 | 31.8238 | 31.7204 | 31.6169 | 31.5728 | 31.5283 | 31.4835 | 31.4361 | 31.2819 | 30.9026 | 30.4332 | 29.0985 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3212 | 32.2286 | 31.8492 | 30.8207 | 29.4617 | 28.0748
|  | SOUTH BERSTEAD | ST |  |  | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 32.0446 | 32.0243 | 32.0004 | 31.9606 | 31.9117 | 31.8527 | 31.8076 | 31.7625 | 31.732 | 31.6996 | 31.5941 | 31.3313 | 31.0218 | 30.7211 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 31.9832 | 31.1439 | 30.3064
|  | SOUTH BERSTEAD | SP |  |  | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 43.1705 | 32.0638 | 32.0591 | 32.0543 | 32.0497 | 32.0327 | 32.0127 | 31.9942 | 31.9759 | 31.9525 | 31.9399 | 31.8989 | 31.7914 | 31.6505 | 31.5016 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318 | 32.3318
MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE | MINIMUM HEADROOM | SZ 13563 92074 | YES | 36.944 | 36.9298 | 36.9156 | 36.0476 | 35.9765 | 35.9053 | 35.8342 | 35.7631 | 35.6919 | 35.6339 | 35.345 | 35.0834 | 34.3261 | 34.0531 | 25.0804 | 25.0662 | 25.052 | 24.184 | 24.1129 | 24.0417 | 23.9706 | 23.8995 | 23.8283 | 23.7703 | 23.0016 | 21.3395 | 19.5547 | 17.734 | 25.1539 | 25.1396 | 25.1254 | 24.2575 | 24.1863 | 24.1152 | 24.044 | 23.9729 | 23.9018 | 23.8437 | 23.5548 | 22.0984 | 20.3563 | 18.5774
|  | SOUTHBOURNE | CT |  |  | 37.0123 | 37.0038 | 36.9952 | 36.4745 | 36.4318 | 36.3891 | 36.3464 | 36.3037 | 36.2611 | 36.244 | 36.1928 | 35.5701 | 35.3504 | 34.7145 | 25.1487 | 25.1402 | 25.1316 | 24.6109 | 24.5682 | 24.5255 | 24.4828 | 24.4401 | 24.3974 | 24.3804 | 23.8884 | 21.7586 | 19.8436 | 18.0234 | 25.2221 | 25.2136 | 25.2051 | 24.6843 | 24.6416 | 24.5989 | 24.5563 | 24.5136 | 24.4709 | 24.4538 | 24.4026 | 22.514 | 20.6379 | 18.8594
|  | SOUTHBOURNE | LW |  |  | 36.944 | 36.9298 | 36.9156 | 36.0476 | 35.9765 | 35.9053 | 35.8342 | 35.7631 | 35.6919 | 35.6635 | 35.5781 | 35.4358 | 35.3504 | 34.4664 | 25.0804 | 25.0662 | 25.052 | 24.184 | 24.1129 | 24.0417 | 23.9706 | 23.8995 | 23.8283 | 23.7999 | 23.0016 | 21.3395 | 19.5547 | 17.734 | 25.1539 | 25.1396 | 25.1254 | 24.2575 | 24.1863 | 24.1152 | 24.044 | 23.9729 | 23.9018 | 23.8733 | 23.7837 | 22.0984 | 20.3563 | 18.5774
|  | SOUTHBOURNE | ST |  |  | 37.0465 | 37.0408 | 37.0351 | 36.6879 | 36.5175 | 36.3449 | 36.1692 | 35.9887 | 35.7251 | 35.6339 | 35.345 | 35.0834 | 34.3261 | 34.0531 | 25.1829 | 25.1772 | 25.1715 | 24.8243 | 24.6539 | 24.4813 | 24.3056 | 24.1251 | 23.8615 | 23.7703 | 23.4814 | 22.3663 | 20.5545 | 19.2123 | 25.2563 | 25.2506 | 25.2449 | 24.8977 | 24.7274 | 24.5547 | 24.3791 | 24.1986 | 23.9349 | 23.8437 | 23.5548 | 23.1436 | 21.3096 | 19.9899
|  | SOUTHBOURNE | SP |  |  | 37.0806 | 37.0778 | 37.0749 | 36.9013 | 36.8871 | 36.8729 | 36.8586 | 36.8444 | 36.8302 | 36.8245 | 36.8074 | 36.779 | 36.7619 | 36.7306 | 25.217 | 25.2142 | 25.2113 | 25.0377 | 25.0235 | 25.0093 | 24.995 | 24.9808 | 24.9666 | 24.9609 | 24.9438 | 24.9154 | 24.8983 | 24.867 | 25.2904 | 25.2876 | 25.2848 | 25.1112 | 25.0969 | 25.0827 | 25.0685 | 25.0543 | 25.04 | 25.0343 | 25.0173 | 24.9888 | 24.9717 | 24.9404
BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE | MINIMUM HEADROOM | SU 68199 71325 | YES | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.1503 | 23.5632 | 23.5485 | 23.5473 | 23.5448 | 23.5424 | 23.5399 | 23.5287 | 23.5176 | 23.5065 | 23.4946 | 23.4588 | 22.6737 | 21.264 | 19.8659 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 23.2826 | 21.7813
|  | SOUTHCOTE | CT |  |  | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.3061 | 23.5632 | 23.5485 | 23.5473 | 23.5448 | 23.5424 | 23.5399 | 23.5374 | 23.5263 | 23.5152 | 23.5033 | 23.4675 | 22.8438 | 21.4342 | 20.0371 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 23.4654 | 21.9652
|  | SOUTHCOTE | LW |  |  | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.1503 | 23.5632 | 23.5485 | 23.5473 | 23.5448 | 23.5424 | 23.5399 | 23.5287 | 23.5176 | 23.5065 | 23.4946 | 23.4588 | 22.6737 | 21.264 | 19.8659 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 23.2826 | 21.7813
|  | SOUTHCOTE | ST |  |  | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 23.5636 | 23.563 | 23.5486 | 23.5474 | 23.546 | 23.5443 | 23.5385 | 23.5328 | 23.5252 | 23.5171 | 23.4929 | 23.4485 | 22.8426 | 21.9403 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.0088
|  | SOUTHCOTE | SP |  |  | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 31.376 | 23.5641 | 23.564 | 23.5501 | 23.55 | 23.5495 | 23.549 | 23.5475 | 23.546 | 23.544 | 23.5409 | 23.5315 | 23.5143 | 23.4957 | 23.4774 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103 | 24.103
AXMINSTER | YEOVIL BSP | SPARKFORD | MINIMUM HEADROOM | ST 60767 25496 | YES | 23.7447 | 23.7396 | 23.7328 | 23.7195 | 23.6738 | 23.6269 | 23.5797 | 23.531 | 23.4634 | 23.4426 | 23.3724 | 23.0621 | 21.2709 | 19.5329 | 17.7221 | 17.7181 | 17.7129 | 17.7026 | 17.6599 | 17.6161 | 17.5716 | 17.5257 | 17.461 | 17.4431 | 17.3829 | 16.2565 | 14.1622 | 12.1182 | 17.9142 | 17.91 | 17.9044 | 17.8934 | 17.85 | 17.8054 | 17.7602 | 17.7137 | 17.6483 | 17.6297 | 17.567 | 16.7127 | 14.6223 | 12.5822
|  | SPARKFORD | CT |  |  | 23.7451 | 23.7403 | 23.734 | 23.7215 | 23.709 | 23.6964 | 23.6838 | 23.6713 | 23.6587 | 23.6455 | 23.6014 | 23.3646 | 21.6495 | 19.9172 | 17.7224 | 17.7187 | 17.7138 | 17.7041 | 17.6945 | 17.6847 | 17.6749 | 17.6653 | 17.6556 | 17.6453 | 17.6112 | 16.5657 | 14.5476 | 12.5092 | 17.9146 | 17.9106 | 17.9053 | 17.895 | 17.8847 | 17.8742 | 17.8637 | 17.8534 | 17.843 | 17.832 | 17.7955 | 17.0218 | 15.0076 | 12.973
|  | SPARKFORD | LW |  |  | 23.7447 | 23.7396 | 23.7328 | 23.7195 | 23.6738 | 23.6269 | 23.5797 | 23.531 | 23.4634 | 23.4426 | 23.3724 | 23.0621 | 21.2709 | 19.5329 | 17.7221 | 17.7181 | 17.7129 | 17.7026 | 17.6599 | 17.6161 | 17.5716 | 17.5257 | 17.461 | 17.4431 | 17.3829 | 16.2565 | 14.1622 | 12.1182 | 17.9142 | 17.91 | 17.9044 | 17.8934 | 17.85 | 17.8054 | 17.7602 | 17.7137 | 17.6483 | 17.6297 | 17.567 | 16.7127 | 14.6223 | 12.5822
|  | SPARKFORD | ST |  |  | 23.7467 | 23.7433 | 23.7393 | 23.7327 | 23.7129 | 23.6912 | 23.6647 | 23.6378 | 23.6097 | 23.5941 | 23.5427 | 23.4444 | 22.9038 | 21.7874 | 17.7237 | 17.721 | 17.7179 | 17.7128 | 17.6948 | 17.6754 | 17.6521 | 17.6284 | 17.6022 | 17.5886 | 17.5441 | 17.4492 | 16.0543 | 14.7437 | 17.9159 | 17.9131 | 17.9097 | 17.9043 | 17.8859 | 17.8659 | 17.8418 | 17.8173 | 17.7907 | 17.7766 | 17.7304 | 17.6459 | 16.5111 | 15.203
|  | SPARKFORD | SP |  |  | 23.7499 | 23.749 | 23.7482 | 23.7473 | 23.7352 | 23.723 | 23.7089 | 23.6946 | 23.6737 | 23.6288 | 23.4857 | 23.3899 | 23.148 | 22.9353 | 17.7261 | 17.7255 | 17.7248 | 17.7241 | 17.7126 | 17.701 | 17.688 | 17.6748 | 17.6552 | 17.6111 | 17.4707 | 17.3824 | 17.1506 | 16.9488 | 17.9186 | 17.9178 | 17.9171 | 17.9164 | 17.9048 | 17.893 | 17.8797 | 17.8662 | 17.8464 | 17.8021 | 17.661 | 17.5709 | 17.3367 | 17.1322
MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST | MINIMUM HEADROOM | ST 84368 68717 | NO | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4261 | 22.404 | 22.3809 | 22.357 | 22.3207 | 22.3157 | 22.2985 | 21.641 | 19.8153 | 18.0278 | 22.0741 | 22.0684 | 22.0665 | 22.0633 | 22.0385 | 22.0128 | 21.9816 | 21.9493 | 21.9045 | 21.8906 | 21.4851 | 19.882 | 17.7635 | 15.6793 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1231 | 22.101 | 22.078 | 22.0541 | 22.0178 | 22.0127 | 21.9955 | 20.6782 | 18.5353 | 16.4265
|  | SPRING QUARRY WEST | CT |  |  | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4276 | 22.4074 | 22.3868 | 22.3653 | 22.3322 | 22.328 | 22.3146 | 21.7214 | 19.8804 | 18.0786 | 22.0743 | 22.0687 | 22.067 | 22.0642 | 22.0413 | 22.0178 | 21.9939 | 21.9641 | 21.9225 | 21.9094 | 21.6156 | 19.9787 | 17.8449 | 15.7465 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1246 | 22.1044 | 22.0838 | 22.0624 | 22.0293 | 22.0251 | 22.0116 | 20.7762 | 18.618 | 16.495
|  | SPRING QUARRY WEST | LW |  |  | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4261 | 22.404 | 22.3809 | 22.357 | 22.3207 | 22.3157 | 22.2985 | 21.641 | 19.8153 | 18.0278 | 22.0741 | 22.0684 | 22.0665 | 22.0633 | 22.0385 | 22.0128 | 21.9816 | 21.9493 | 21.9045 | 21.8906 | 21.4851 | 19.882 | 17.7635 | 15.6793 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1231 | 22.101 | 22.078 | 22.0541 | 22.0178 | 22.0127 | 21.9955 | 20.6782 | 18.5353 | 16.4265
|  | SPRING QUARRY WEST | ST |  |  | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 21.4265 | 20.2986 | 22.0743 | 22.0732 | 22.0674 | 22.0654 | 22.0629 | 22.0599 | 22.0548 | 22.0495 | 22.0438 | 22.0377 | 22.0165 | 20.9643 | 19.6023 | 18.2868 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 21.7598 | 20.393 | 19.0619
|  | SPRING QUARRY WEST | SP |  |  | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.4475 | 22.0752 | 22.0747 | 22.0699 | 22.0694 | 22.0686 | 22.0676 | 22.0659 | 22.0641 | 22.0619 | 22.0595 | 22.0512 | 22.0248 | 21.5643 | 20.8617 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 22.1445 | 21.6587
NORTH HYDE GSP | NORTH HYDE (D) | SPRINGFIELD ROAD | MINIMUM HEADROOM | TQ 11409 80620 | YES | 7.7044 | 7.6607 | 7.6318 | 7.6128 | 7.5895 | 7.5614 | 7.5498 | 7.5152 | 7.4522 | 7.4202 | 7.3247 | 7.1214 | 6.9054 | 6.7224 | 5.4397 | 5.3793 | 5.3394 | 5.3132 | 5.281 | 5.2421 | 5.2261 | 5.2102 | 5.1415 | 5.0992 | 4.9732 | 4.7194 | 4.4532 | 4.2468 | 5.3088 | 5.2466 | 5.2054 | 5.1783 | 5.1451 | 5.1051 | 5.0885 | 5.0721 | 5.0055 | 4.9619 | 4.8324 | 4.5729 | 4.3007 | 4.0885
|  | SPRINGFIELD ROAD | CT |  |  | 7.7044 | 7.6607 | 7.6579 | 7.6519 | 7.6234 | 7.5944 | 7.5651 | 7.5152 | 7.4522 | 7.4202 | 7.3247 | 7.1214 | 6.9054 | 6.7224 | 5.4397 | 5.3793 | 5.3754 | 5.3672 | 5.3364 | 5.3053 | 5.2738 | 5.2142 | 5.1415 | 5.0992 | 4.9732 | 4.7194 | 4.4532 | 4.2468 | 5.3088 | 5.2466 | 5.2426 | 5.2341 | 5.203 | 5.1716 | 5.1399 | 5.0792 | 5.0055 | 4.9619 | 4.8324 | 4.5729 | 4.3007 | 4.0885
|  | SPRINGFIELD ROAD | LW |  |  | 7.7044 | 7.6607 | 7.6579 | 7.6519 | 7.6461 | 7.6403 | 7.6147 | 7.5893 | 7.5641 | 7.537 | 7.4569 | 7.3248 | 7.1824 | 7.0202 | 5.4397 | 5.3793 | 5.3754 | 5.3672 | 5.3592 | 5.3512 | 5.3158 | 5.2807 | 5.2459 | 5.2084 | 5.0977 | 4.9153 | 4.7267 | 4.5412 | 5.3088 | 5.2466 | 5.2426 | 5.2341 | 5.2258 | 5.2176 | 5.181 | 5.1448 | 5.109 | 5.0703 | 4.9561 | 4.7679 | 4.5733 | 4.3819
|  | SPRINGFIELD ROAD | ST |  |  | 7.8281 | 7.6844 | 7.6318 | 7.6128 | 7.5895 | 7.5614 | 7.5498 | 7.5382 | 7.521 | 7.5025 | 7.4485 | 7.3607 | 7.2727 | 7.179 | 5.6106 | 5.4121 | 5.3394 | 5.3132 | 5.281 | 5.2421 | 5.2261 | 5.2102 | 5.1864 | 5.1608 | 5.0862 | 4.9649 | 4.8434 | 4.7227 | 5.4851 | 5.2804 | 5.2054 | 5.1783 | 5.1451 | 5.1051 | 5.0885 | 5.0721 | 5.0476 | 5.0212 | 4.9442 | 4.8191 | 4.6937 | 4.5692
|  | SPRINGFIELD ROAD | SP |  |  | 7.8411 | 7.7066 | 7.7064 | 7.7062 | 7.7053 | 7.7042 | 7.7 | 7.6959 | 7.6904 | 7.6832 | 7.6624 | 7.6291 | 7.5972 | 7.5671 | 5.6285 | 5.4428 | 5.4425 | 5.4422 | 5.441 | 5.4395 | 5.4337 | 5.428 | 5.4204 | 5.4105 | 5.3817 | 5.3357 | 5.2916 | 5.25 | 5.5036 | 5.312 | 5.3117 | 5.3115 | 5.3102 | 5.3086 | 5.3026 | 5.2967 | 5.2889 | 5.2787 | 5.249 | 5.2016 | 5.1561 | 5.1132
NURSLING GSP | WINCHESTER | ST CROSS | MINIMUM HEADROOM | SU 47287 28156 | YES | 32.7537 | 32.7363 | 32.7135 | 32.6653 | 32.5452 | 32.4238 | 32.3012 | 32.1645 | 31.9834 | 31.9069 | 31.6176 | 31.0426 | 30.3841 | 29.9511 | 30.3414 | 30.319 | 30.2897 | 30.2277 | 30.0941 | 29.9594 | 29.8237 | 29.6708 | 29.4737 | 29.3802 | 29.0881 | 28.412 | 27.6926 | 27.1998 | 30.9652 | 30.9423 | 30.9122 | 30.8486 | 30.7134 | 30.5772 | 30.4399 | 30.285 | 30.0861 | 29.9905 | 29.7027 | 29.0444 | 28.3436 | 27.869
|  | ST CROSS | CT |  |  | 32.7537 | 32.7363 | 32.7135 | 32.6653 | 32.5452 | 32.4238 | 32.3012 | 32.1645 | 31.9834 | 31.9072 | 31.66 | 31.0426 | 30.3841 | 29.9511 | 30.3414 | 30.319 | 30.2897 | 30.2277 | 30.0941 | 29.9594 | 29.8237 | 29.6708 | 29.4737 | 29.3802 | 29.0881 | 28.412 | 27.6926 | 27.1998 | 30.9652 | 30.9423 | 30.9122 | 30.8486 | 30.7134 | 30.5772 | 30.4399 | 30.285 | 30.0861 | 29.9905 | 29.7027 | 29.0444 | 28.3436 | 27.869
|  | ST CROSS | LW |  |  | 32.7566 | 32.7414 | 32.7215 | 32.6794 | 32.6209 | 32.5607 | 32.4819 | 32.4012 | 32.3052 | 32.2391 | 32.0235 | 31.6288 | 31.1771 | 30.8156 | 30.3451 | 30.3256 | 30.3 | 30.2458 | 30.1755 | 30.1037 | 30.0086 | 29.9118 | 29.7998 | 29.7164 | 29.4545 | 29.0011 | 28.4886 | 28.0672 | 30.9691 | 30.9491 | 30.9227 | 30.8671 | 30.7955 | 30.7223 | 30.6253 | 30.5265 | 30.4127 | 30.3272 | 30.0682 | 29.6326 | 29.1387 | 28.7355
|  | ST CROSS | ST |  |  | 32.7603 | 32.7483 | 32.7341 | 32.7099 | 32.5897 | 32.4618 | 32.3276 | 32.1905 | 32.0001 | 31.9069 | 31.6176 | 31.2643 | 30.6207 | 30.2672 | 30.3499 | 30.3345 | 30.3162 | 30.285 | 30.1563 | 30.0181 | 29.8726 | 29.7241 | 29.5228 | 29.4178 | 29.0941 | 28.6911 | 28.0084 | 27.616 | 30.974 | 30.9582 | 30.9394 | 30.9074 | 30.7777 | 30.6382 | 30.4914 | 30.3416 | 30.139 | 30.0326 | 29.7049 | 29.3061 | 28.6353 | 28.2547
|  | ST CROSS | SP |  |  | 32.7741 | 32.7725 | 32.771 | 32.7695 | 32.7628 | 32.7548 | 32.7413 | 32.728 | 32.7109 | 32.6945 | 32.6456 | 32.5691 | 32.4869 | 32.4088 | 30.3677 | 30.3656 | 30.3637 | 30.3618 | 30.3532 | 30.3428 | 30.3255 | 30.3084 | 30.2864 | 30.2655 | 30.2033 | 30.1054 | 30.0026 | 29.9052 | 30.9923 | 30.9902 | 30.9881 | 30.9862 | 30.9773 | 30.9668 | 30.9489 | 30.9314 | 30.9088 | 30.8874 | 30.8236 | 30.7232 | 30.618 | 30.5182
COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES | MINIMUM HEADROOM | SP 51259 05741 | YES | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9054 | 32.8982 | 32.8908 | 32.8831 | 32.8713 | 32.8673 | 32.8254 | 32.6776 | 31.0841 | 29.2709 | 27.5143 | 27.5125 | 27.51 | 27.5035 | 27.49 | 27.4759 | 27.4614 | 27.4284 | 27.3913 | 27.3621 | 27.2661 | 26.2096 | 23.9497 | 21.6707 | 27.8816 | 27.8801 | 27.8781 | 27.8748 | 27.8649 | 27.8546 | 27.8441 | 27.8243 | 27.8005 | 27.7854 | 27.7356 | 26.3823 | 24.1439 | 21.8864
|  | ST EBBES | CT |  |  | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9062 | 32.8997 | 32.8931 | 32.8863 | 32.8757 | 32.8743 | 32.8254 | 32.6776 | 31.1055 | 29.2865 | 27.5143 | 27.5125 | 27.51 | 27.5035 | 27.49 | 27.4759 | 27.4614 | 27.4284 | 27.3913 | 27.3621 | 27.2661 | 26.2851 | 23.9996 | 21.7149 | 27.8816 | 27.8801 | 27.8781 | 27.8748 | 27.8649 | 27.8546 | 27.8441 | 27.8243 | 27.8005 | 27.7854 | 27.7356 | 26.4565 | 24.1924 | 21.9293
|  | ST EBBES | LW |  |  | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9079 | 32.8582 | 32.7316 | 31.0841 | 29.2709 | 27.5143 | 27.5125 | 27.51 | 27.5035 | 27.4964 | 27.4887 | 27.4628 | 27.4366 | 27.4102 | 27.3823 | 27.2906 | 26.2096 | 23.9497 | 21.6707 | 27.8816 | 27.8801 | 27.8781 | 27.8748 | 27.8713 | 27.8675 | 27.8546 | 27.8416 | 27.8285 | 27.8147 | 27.7692 | 26.3823 | 24.1439 | 21.8864
|  | ST EBBES | ST |  |  | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9054 | 32.8982 | 32.8908 | 32.8831 | 32.8713 | 32.8673 | 32.8522 | 32.7539 | 32.6153 | 31.4596 | 27.5149 | 27.5136 | 27.5121 | 27.5099 | 27.4987 | 27.4862 | 27.472 | 27.4573 | 27.4275 | 27.4044 | 27.3287 | 27.156 | 25.9084 | 24.4507 | 27.8821 | 27.8811 | 27.8798 | 27.8781 | 27.8688 | 27.859 | 27.8482 | 27.837 | 27.8163 | 27.8028 | 27.7588 | 27.5947 | 26.0831 | 24.6391
|  | ST EBBES | SP |  |  | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.9126 | 32.8729 | 32.8216 | 27.5157 | 27.5151 | 27.5144 | 27.5138 | 27.5127 | 27.5116 | 27.5102 | 27.5082 | 27.5055 | 27.4981 | 27.4735 | 27.4067 | 27.3176 | 27.2231 | 27.8827 | 27.8822 | 27.8817 | 27.8812 | 27.8804 | 27.8794 | 27.8783 | 27.8771 | 27.8758 | 27.8721 | 27.8599 | 27.8268 | 27.7826 | 27.6528
BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS | MINIMUM HEADROOM | SU 47113 66363 | YES | 32.1192 | 32.1192 | 32.1192 | 32.1192 | 32.1181 | 32.1158 | 32.1121 | 32.1071 | 32.0969 | 32.0952 | 32.0863 | 32.0645 | 32.0221 | 31.3427 | 24.5457 | 24.5337 | 24.5233 | 24.5012 | 24.4787 | 24.455 | 24.4376 | 24.4278 | 24.4108 | 24.4 | 24.0606 | 23.0437 | 21.967 | 20.9253 | 24.8311 | 24.8158 | 24.8025 | 24.7744 | 24.7459 | 24.7164 | 24.593 | 24.4071 | 24.222 | 24.0251 | 23.4406 | 22.444 | 21.4088 | 20.4078
|  | ST JOHNS | CT |  |  | 32.1192 | 32.1192 | 32.1192 | 32.1192 | 32.1189 | 32.1183 | 32.1173 | 32.1159 | 32.1129 | 32.1123 | 32.1094 | 32.0852 | 32.0582 | 31.3427 | 24.5459 | 24.534 | 24.5238 | 24.5022 | 24.4808 | 24.4592 | 24.4376 | 24.4278 | 24.4163 | 24.4068 | 24.0606 | 23.0437 | 21.967 | 20.9253 | 24.8313 | 24.8162 | 24.8032 | 24.7756 | 24.7484 | 24.7211 | 24.593 | 24.4071 | 24.222 | 24.0251 | 23.4406 | 22.444 | 21.4088 | 20.4078
|  | ST JOHNS | LW |  |  | 32.1192 | 32.1192 | 32.1192 | 32.1192 | 32.1181 | 32.1158 | 32.1121 | 32.1071 | 32.0969 | 32.0952 | 32.0863 | 32.0645 | 32.0221 | 31.5094 | 24.5457 | 24.5337 | 24.5233 | 24.5012 | 24.4787 | 24.455 | 24.4428 | 24.4293 | 24.4108 | 24.4 | 24.2545 | 23.257 | 22.1648 | 21.1283 | 24.8311 | 24.8158 | 24.8025 | 24.7744 | 24.7459 | 24.7164 | 24.7019 | 24.623 | 24.4306 | 24.2326 | 23.642 | 22.6481 | 21.5973 | 20.6015
|  | ST JOHNS | ST |  |  | 32.1192 | 32.1192 | 32.1192 | 32.1192 | 32.119 | 32.1185 | 32.1178 | 32.1168 | 32.1144 | 32.1133 | 32.1072 | 32.0992 | 32.0711 | 32.0609 | 24.5521 | 24.5488 | 24.5409 | 24.5342 | 24.5258 | 24.5154 | 24.5084 | 24.5011 | 24.493 | 24.4857 | 24.4616 | 24.4238 | 24.3658 | 23.9564 | 24.8392 | 24.835 | 24.8249 | 24.8165 | 24.8058 | 24.7926 | 24.7839 | 24.7749 | 24.7652 | 24.7562 | 24.7271 | 24.6675 | 23.9893 | 23.3344
|  | ST JOHNS | SP |  |  | 32.1192 | 32.1192 | 32.1192 | 32.1192 | 32.1192 | 32.1192 | 32.1192 | 32.1191 | 32.119 | 32.1187 | 32.1165 | 32.1147 | 32.1063 | 32.0982 | 24.5553 | 24.5546 | 24.5539 | 24.5532 | 24.55 | 24.5462 | 24.5439 | 24.5415 | 24.5385 | 24.5357 | 24.5266 | 24.5135 | 24.4941 | 24.4754 | 24.8434 | 24.8424 | 24.8415 | 24.8407 | 24.8366 | 24.8318 | 24.8288 | 24.8258 | 24.822 | 24.8185 | 24.8075 | 24.7912 | 24.7688 | 24.7473
COWLEY GSP | WITNEY BSP | STANDLAKE | MINIMUM HEADROOM | SP 38923 02349 | YES | 36.7419 | 36.7168 | 36.6917 | 35.1599 | 35.0343 | 34.9087 | 34.7832 | 34.6576 | 34.5321 | 34.4818 | 34.3312 | 34.0801 | 33.2173 | 31.941 | 34.5191 | 34.4874 | 34.4534 | 32.9038 | 32.7618 | 32.6201 | 32.4877 | 32.3552 | 32.2226 | 32.1649 | 31.9908 | 31.685 | 30.3501 | 28.8998 | 35.1054 | 35.0803 | 35.0469 | 33.4973 | 33.3552 | 33.2135 | 33.0811 | 32.9485 | 32.8159 | 32.7582 | 32.584 | 32.278 | 32.0478 | 31.7053
|  | STANDLAKE | CT |  |  | 36.8624 | 36.8474 | 36.8323 | 35.9132 | 35.8379 | 35.7625 | 35.6872 | 35.6119 | 35.5365 | 35.5064 | 35.416 | 34.3171 | 33.2173 | 31.941 | 34.6392 | 34.6173 | 34.593 | 33.6553 | 33.5627 | 33.4705 | 33.3784 | 33.2961 | 33.2137 | 33.1761 | 33.0622 | 31.9083 | 30.3501 | 28.8998 | 35.226 | 35.2108 | 35.1865 | 34.2488 | 34.1562 | 34.0639 | 33.9717 | 33.8894 | 33.807 | 33.7694 | 33.6554 | 32.5017 | 32.0478 | 31.7053
|  | STANDLAKE | LW |  |  | 36.7419 | 36.7168 | 36.6917 | 35.1599 | 35.0343 | 34.9087 | 34.7832 | 34.6576 | 34.5321 | 34.4818 | 34.3312 | 34.0801 | 33.4193 | 32.1431 | 34.5191 | 34.4874 | 34.4534 | 32.9038 | 32.7618 | 32.6201 | 32.4877 | 32.3552 | 32.2226 | 32.1649 | 31.9908 | 31.685 | 30.5873 | 29.137 | 35.1054 | 35.0803 | 35.0469 | 33.4973 | 33.3552 | 33.2135 | 33.0811 | 32.9485 | 32.8159 | 32.7582 | 32.584 | 32.278 | 32.0612 | 31.7187
|  | STANDLAKE | ST |  |  | 36.9227 | 36.9126 | 36.9026 | 36.2899 | 36.2397 | 36.1894 | 36.1392 | 36.089 | 36.0388 | 36.0187 | 35.9584 | 35.858 | 35.7977 | 35.6872 | 34.7039 | 34.6904 | 34.6761 | 34.0566 | 33.9987 | 33.9396 | 33.8829 | 33.8262 | 33.7712 | 33.7461 | 33.6698 | 33.5317 | 33.4281 | 33.2196 | 35.2862 | 35.2762 | 35.2661 | 34.6501 | 34.5923 | 34.5331 | 34.4764 | 34.4197 | 34.3646 | 34.3395 | 34.2632 | 34.1249 | 34.0212 | 33.8685
|  | STANDLAKE | SP |  |  | 36.983 | 36.9779 | 36.9729 | 36.6666 | 36.6225 | 36.5788 | 36.535 | 36.491 | 36.4363 | 36.3439 | 36.0528 | 35.8783 | 35.4567 | 35.0741 | 34.7669 | 34.7608 | 34.7547 | 34.4471 | 34.4001 | 34.3532 | 34.3069 | 34.2603 | 34.2024 | 34.1081 | 33.8108 | 33.6211 | 33.1802 | 32.7774 | 35.3465 | 35.3415 | 35.3364 | 35.0301 | 34.986 | 34.9423 | 34.8986 | 34.8539 | 34.7959 | 34.7017 | 34.4044 | 34.2145 | 33.7736 | 33.3708
MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN | MINIMUM HEADROOM | SU 17585 90987 | NO | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 23.9993 | 23.9988 | 23.9981 | 23.9968 | 23.9955 | 23.9894 | 23.9819 | 23.9731 | 23.9629 | 23.952 | 23.9071 | 23.8652 | 23.8391 | 23.8133 | 23.9925 | 23.9868 | 23.9793 | 23.9656 | 23.9515 | 23.8847 | 23.8031 | 23.7076 | 23.597 | 23.4777 | 22.9899 | 22.5346 | 22.2514 | 21.9703
|  | STANTON FITZWARREN | CT |  |  | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 23.9993 | 23.9988 | 23.9981 | 23.9969 | 23.9957 | 23.9896 | 23.9821 | 23.9733 | 23.9631 | 23.9521 | 23.9072 | 23.8654 | 23.8393 | 23.8134 | 23.9927 | 23.9872 | 23.9798 | 23.9665 | 23.9529 | 23.8865 | 23.805 | 23.7094 | 23.5989 | 23.4796 | 22.9917 | 22.5365 | 22.2532 | 21.9721
|  | STANTON FITZWARREN | LW |  |  | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 23.9993 | 23.9988 | 23.9981 | 23.9968 | 23.9955 | 23.9894 | 23.9819 | 23.9731 | 23.9629 | 23.952 | 23.9071 | 23.8652 | 23.8391 | 23.8133 | 23.9925 | 23.9868 | 23.9793 | 23.9656 | 23.9515 | 23.8847 | 23.8031 | 23.7076 | 23.597 | 23.4777 | 22.9899 | 22.5346 | 22.2514 | 21.9703
|  | STANTON FITZWARREN | ST |  |  | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 23.9995 | 23.9991 | 23.9987 | 23.998 | 23.9972 | 23.993 | 23.9879 | 23.9819 | 23.9751 | 23.9676 | 23.9353 | 23.9048 | 23.8875 | 23.8712 | 23.9943 | 23.9903 | 23.9854 | 23.9781 | 23.9691 | 23.9235 | 23.8681 | 23.8034 | 23.7296 | 23.6476 | 23.2964 | 22.9655 | 22.7768 | 22.5998
|  | STANTON FITZWARREN | SP |  |  | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 32.4555 | 23.9998 | 23.9996 | 23.9995 | 23.9994 | 23.9991 | 23.9972 | 23.995 | 23.9926 | 23.9898 | 23.9868 | 23.9739 | 23.9612 | 23.9527 | 23.9435 | 23.9974 | 23.996 | 23.9945 | 23.993 | 23.9901 | 23.9699 | 23.9459 | 23.9192 | 23.8891 | 23.8565 | 23.7165 | 23.5786 | 23.4854 | 23.3862
LALEHAM | STAINES | STANWELL | MINIMUM HEADROOM | TQ 06003 72766 | NO | 8.7877 | 8.7877 | 17.2877 | 17.2877 | 17.2646 | 17.2408 | 17.2163 | 17.1903 | 17.1493 | 17.1439 | 17.0662 | 16.762 | 16.4408 | 16.1992 | 6.5974 | 6.5974 | 15.3974 | 15.3974 | 15.3743 | 15.3505 | 15.3259 | 15.2999 | 15.2474 | 15.1918 | 15.0246 | 14.6822 | 14.3214 | 14.0409 | 7.7645 | 7.6722 | 14.9316 | 14.8457 | 14.7612 | 14.6763 | 14.6029 | 14.5335 | 14.4493 | 14.3974 | 14.2353 | 13.9001 | 13.5468 | 13.2736
|  | STANWELL | CT |  |  | 8.7877 | 8.7877 | 17.2877 | 17.2877 | 17.2646 | 17.2408 | 17.2163 | 17.1903 | 17.1493 | 17.1439 | 17.0662 | 16.762 | 16.4408 | 16.1992 | 6.5974 | 6.5974 | 15.3974 | 15.3974 | 15.3743 | 15.3505 | 15.3259 | 15.2999 | 15.2474 | 15.1918 | 15.0246 | 14.6822 | 14.3214 | 14.0409 | 7.7718 | 7.6847 | 14.9511 | 14.8798 | 14.7875 | 14.6952 | 14.6029 | 14.5335 | 14.4493 | 14.3974 | 14.2353 | 13.9001 | 13.5468 | 13.2736
|  | STANWELL | LW |  |  | 8.7877 | 8.7877 | 17.2877 | 17.2877 | 17.2866 | 17.2842 | 17.2804 | 17.2752 | 17.2647 | 17.2629 | 17.1593 | 16.9289 | 16.6695 | 16.4545 | 6.5974 | 6.5974 | 15.3974 | 15.3974 | 15.3962 | 15.3938 | 15.3901 | 15.3785 | 15.3213 | 15.2692 | 15.1113 | 14.8426 | 14.5437 | 14.2897 | 7.7645 | 7.6722 | 14.9316 | 14.8457 | 14.7612 | 14.6763 | 14.6286 | 14.5799 | 14.5263 | 14.4768 | 14.3232 | 14.0617 | 13.7703 | 13.5236
|  | STANWELL | ST |  |  | 8.7877 | 8.7877 | 17.2877 | 17.2877 | 17.2875 | 17.287 | 17.2863 | 17.2852 | 17.2827 | 17.2816 | 17.2753 | 17.1775 | 17.0098 | 16.8615 | 6.5974 | 6.5974 | 15.3974 | 15.3974 | 15.3971 | 15.3966 | 15.3959 | 15.3948 | 15.3924 | 15.3912 | 15.3022 | 15.1303 | 14.9372 | 14.7636 | 7.7687 | 7.7417 | 14.9487 | 14.8943 | 14.8274 | 14.7465 | 14.7098 | 14.6731 | 14.6412 | 14.6084 | 14.5092 | 14.3421 | 14.1537 | 13.9849
|  | STANWELL | SP |  |  | 8.7877 | 8.7877 | 17.2877 | 17.2877 | 17.2862 | 17.2846 | 17.283 | 17.2814 | 17.2788 | 17.2716 | 17.2477 | 17.2355 | 17.1944 | 17.1588 | 6.5974 | 6.5974 | 15.3974 | 15.3974 | 15.3958 | 15.3942 | 15.3927 | 15.391 | 15.3885 | 15.3813 | 15.3573 | 15.3452 | 15.304 | 15.2684 | 7.8004 | 7.7971 | 15.0327 | 15.0297 | 15.0142 | 14.9961 | 14.9829 | 14.9698 | 14.9524 | 14.933 | 14.8733 | 14.8038 | 14.7072 | 14.6193
MANNINGTON GSP | SALISBURY | STAPLEFORD | MINIMUM HEADROOM | SU 06871 37078 | YES | 18.082 | 17.3271 | 17.1881 | 16.3665 | 16.0956 | 15.8445 | 15.5331 | 15.207 | 14.8422 | 14.511 | 13.5466 | 12.5533 | 11.6224 | 10.8632 | 7.7571 | 6.8092 | 6.644 | 5.7877 | 5.4728 | 5.1823 | 4.82 | 4.4404 | 4.0168 | 3.623 | 2.4785 | 1.3142 | 0.25196 | -0.63184 | 8.8448 | 7.9727 | 7.82 | 6.9801 | 6.6862 | 6.4144 | 6.0762 | 5.722 | 5.3263 | 4.9622 | 3.9032 | 2.8201 | 1.8202 | 0.99557
|  | STAPLEFORD | CT |  |  | 18.1293 | 17.3744 | 17.2352 | 16.665 | 16.393 | 16.1428 | 15.9083 | 15.5964 | 15.2453 | 14.9224 | 13.9885 | 12.5777 | 11.6224 | 10.8632 | 7.8026 | 6.8548 | 6.6884 | 6.0816 | 5.7637 | 5.4722 | 5.1998 | 4.8346 | 4.4247 | 4.0391 | 2.9251 | 1.3434 | 0.25196 | -0.63184 | 8.8908 | 8.0192 | 7.8656 | 7.2762 | 6.9801 | 6.7082 | 6.4539 | 6.1139 | 5.7319 | 5.3761 | 4.3476 | 2.847 | 1.8202 | 0.99557
|  | STAPLEFORD | LW |  |  | 18.082 | 17.3271 | 17.1881 | 16.3665 | 16.0956 | 15.8445 | 15.5331 | 15.207 | 14.8422 | 14.511 | 13.5466 | 12.5533 | 11.7215 | 10.9894 | 7.7571 | 6.8092 | 6.644 | 5.7877 | 5.4728 | 5.1823 | 4.82 | 4.4404 | 4.0168 | 3.623 | 2.4785 | 1.3142 | 0.34631 | -0.51041 | 8.8448 | 7.9727 | 7.82 | 6.9801 | 6.6862 | 6.4144 | 6.0762 | 5.722 | 5.3263 | 4.9622 | 3.9032 | 2.8201 | 1.9169 | 1.1193
|  | STAPLEFORD | ST |  |  | 18.2071 | 18.1279 | 17.3656 | 17.0071 | 16.838 | 16.6798 | 16.4837 | 16.2787 | 16.0327 | 15.8032 | 15.119 | 14.4631 | 13.8583 | 13.3686 | 7.9025 | 7.7914 | 6.8394 | 6.461 | 6.2649 | 6.0821 | 5.8539 | 5.6152 | 5.3296 | 5.0571 | 4.2467 | 3.4736 | 2.7807 | 2.21 | 8.9848 | 8.8823 | 8.0069 | 7.6379 | 7.4546 | 7.2835 | 7.0706 | 6.8478 | 6.5811 | 6.329 | 5.5785 | 4.861 | 4.2099 | 3.6777
|  | STAPLEFORD | SP |  |  | 18.2424 | 18.2112 | 17.4553 | 17.2725 | 17.1933 | 17.1257 | 17.0525 | 16.9784 | 16.8927 | 16.8048 | 16.5438 | 16.2931 | 16.0977 | 15.9159 | 7.9418 | 7.8984 | 6.9414 | 6.7478 | 6.6547 | 6.5754 | 6.4893 | 6.4022 | 6.3013 | 6.1963 | 5.8856 | 5.5887 | 5.3601 | 5.1499 | 9.023 | 8.9829 | 8.103 | 7.9146 | 7.828 | 7.7543 | 7.6743 | 7.5934 | 7.4997 | 7.4028 | 7.1157 | 6.8407 | 6.628 | 6.4312
COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH | MINIMUM HEADROOM | SU 77124 94355 | YES | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9663 | 33.9477 | 33.9283 | 33.9082 | 33.8777 | 33.8734 | 33.7246 | 32.7771 | 31.7824 | 30.8262 | 32.9085 | 32.9061 | 32.8999 | 32.8913 | 32.8631 | 32.8326 | 32.7966 | 32.7457 | 32.6488 | 32.4752 | 31.4249 | 30.2482 | 29.0622 | 27.9528 | 32.7043 | 32.6987 | 32.6844 | 32.6645 | 32.6229 | 32.5768 | 32.519 | 32.4547 | 32.383 | 32.3392 | 32.1882 | 31.4016 | 30.2021 | 29.0796
|  | STOKENCHURCH | CT |  |  | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.8989 | 32.973 | 32.0242 | 31.0712 | 32.9085 | 32.9061 | 32.8999 | 32.8913 | 32.8811 | 32.8692 | 32.8561 | 32.8348 | 32.7684 | 32.6471 | 31.6113 | 30.4562 | 29.3124 | 28.2063 | 32.7043 | 32.6987 | 32.6844 | 32.6645 | 32.6409 | 32.6134 | 32.583 | 32.5388 | 32.4976 | 32.4581 | 32.3216 | 31.6104 | 30.453 | 29.3338
|  | STOKENCHURCH | LW |  |  | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9663 | 33.9477 | 33.9283 | 33.9082 | 33.8777 | 33.8734 | 33.7246 | 32.7771 | 31.7824 | 30.8262 | 32.9085 | 32.9061 | 32.8999 | 32.8913 | 32.8631 | 32.8326 | 32.7966 | 32.7457 | 32.6488 | 32.4752 | 31.4249 | 30.2482 | 29.0622 | 27.9528 | 32.7043 | 32.6987 | 32.6844 | 32.6645 | 32.6229 | 32.5768 | 32.519 | 32.4547 | 32.383 | 32.3392 | 32.1882 | 31.4016 | 30.2021 | 29.0796
|  | STOKENCHURCH | ST |  |  | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.969 | 33.3613 | 32.7993 | 32.9086 | 32.9069 | 32.9026 | 32.897 | 32.8903 | 32.8823 | 32.8721 | 32.8603 | 32.8483 | 32.8335 | 32.5157 | 31.6988 | 30.9407 | 30.2395 | 32.7047 | 32.7005 | 32.6907 | 32.6777 | 32.6622 | 32.6438 | 32.6202 | 32.5928 | 32.5651 | 32.538 | 32.4408 | 32.3331 | 32.1006 | 31.3911
|  | STOKENCHURCH | SP |  |  | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 33.9843 | 32.9088 | 32.9076 | 32.9049 | 32.9017 | 32.8982 | 32.8944 | 32.8903 | 32.8857 | 32.8815 | 32.8769 | 32.8602 | 32.8408 | 32.7731 | 32.6051 | 32.7051 | 32.7023 | 32.696 | 32.6886 | 32.6805 | 32.6718 | 32.6622 | 32.6516 | 32.6419 | 32.6312 | 32.5925 | 32.5476 | 32.5006 | 32.4526
MINETY GSP | STRATTON (2 X 60) | STRATTON | MINIMUM HEADROOM | SU 16998 88837 | NO | 15.9094 | 15.9094 | 15.9094 | 15.9094 | 15.891 | 15.8718 | 15.8516 | 15.8301 | 15.7952 | 15.7826 | 15.642 | 15.3452 | 14.9945 | 14.7375 | 12.2144 | 12.2055 | 12.1937 | 12.1688 | 12.1421 | 12.1081 | 12.0659 | 12.0207 | 11.962 | 11.9194 | 11.7183 | 11.3223 | 10.8696 | 10.5122 | 12.1154 | 12.1013 | 12.0827 | 12.0434 | 12.0027 | 11.9596 | 11.8938 | 11.8252 | 11.7458 | 11.6808 | 11.4808 | 11.1376 | 10.7392 | 10.4352
|  | STRATTON | CT |  |  | 15.9094 | 15.9094 | 15.9094 | 15.9094 | 15.9086 | 15.9071 | 15.905 | 15.9019 | 15.895 | 15.8932 | 15.7353 | 15.4329 | 15.1172 | 14.8481 | 12.2161 | 12.2084 | 12.1983 | 12.1769 | 12.1553 | 12.1333 | 12.1107 | 12.0714 | 12.0287 | 11.9888 | 11.828 | 11.4264 | 11.0087 | 10.6394 | 12.1181 | 12.106 | 12.09 | 12.0561 | 12.0225 | 11.9885 | 11.9541 | 11.8939 | 11.8304 | 11.7681 | 11.5818 | 11.233 | 10.8696 | 10.5536
|  | STRATTON | LW |  |  | 15.9094 | 15.9094 | 15.9094 | 15.9094 | 15.9068 | 15.9016 | 15.8934 | 15.882 | 15.859 | 15.8136 | 15.642 | 15.3452 | 14.9945 | 14.7375 | 12.2144 | 12.2055 | 12.1937 | 12.1688 | 12.1421 | 12.113 | 12.0683 | 12.0207 | 11.962 | 11.9194 | 11.7183 | 11.3223 | 10.8696 | 10.5122 | 12.1154 | 12.1013 | 12.0827 | 12.0434 | 12.0027 | 11.9596 | 11.8938 | 11.8252 | 11.7458 | 11.6808 | 11.4808 | 11.1376 | 10.7392 | 10.4352
|  | STRATTON | ST |  |  | 15.9094 | 15.9094 | 15.9094 | 15.9094 | 15.891 | 15.8718 | 15.8516 | 15.8301 | 15.7952 | 15.7826 | 15.6964 | 15.4878 | 15.1754 | 14.9625 | 12.259 | 12.209 | 12.2004 | 12.1856 | 12.1491 | 12.1081 | 12.0659 | 12.0228 | 11.9634 | 11.9244 | 11.8019 | 11.5591 | 11.181 | 10.9029 | 12.1858 | 12.1069 | 12.0933 | 12.0699 | 12.0229 | 11.9692 | 11.9143 | 11.8586 | 11.785 | 11.7308 | 11.5638 | 11.3243 | 10.9812 | 10.7378
|  | STRATTON | SP |  |  | 15.9094 | 15.9094 | 15.9094 | 15.9094 | 15.9094 | 15.9093 | 15.9092 | 15.9091 | 15.9089 | 15.9081 | 15.9031 | 15.8991 | 15.8802 | 15.8618 | 12.2674 | 12.2665 | 12.223 | 12.2222 | 12.2182 | 12.2134 | 12.2062 | 12.199 | 12.1896 | 12.1785 | 12.1439 | 12.0932 | 12.0299 | 11.9696 | 12.1991 | 12.1977 | 12.129 | 12.1276 | 12.1214 | 12.1139 | 12.1025 | 12.0912 | 12.0765 | 12.0595 | 12.0077 | 11.9299 | 11.8408 | 11.7563
LALEHAM | STAINES | SUNBURY CROSS | MINIMUM HEADROOM | TQ 10053 69996 | NO | 13.0729 | 13.0729 | 13.0729 | 33.2729 | 33.2502 | 33.2268 | 33.2024 | 33.177 | 33.1385 | 33.1326 | 33.0929 | 33.061 | 32.9576 | 32.5723 | 9.6154 | 9.6141 | 9.6125 | 29.7092 | 29.6855 | 29.6595 | 29.6292 | 29.5981 | 29.5539 | 29.5425 | 29.5058 | 29.4106 | 28.828 | 28.3032 | 12.0598 | 12.0585 | 12.0569 | 29.8535 | 29.8299 | 29.8038 | 29.7735 | 29.7424 | 29.6982 | 29.6867 | 29.6501 | 29.2331 | 28.6738 | 28.1718
|  | SUNBURY CROSS | CT |  |  | 13.0729 | 13.0729 | 13.0729 | 33.2729 | 33.2616 | 33.25 | 33.2382 | 33.2259 | 33.207 | 33.2046 | 33.1969 | 33.1613 | 33.0839 | 32.6482 | 9.6154 | 9.6141 | 9.6125 | 29.7092 | 29.6945 | 29.6796 | 29.6646 | 29.6466 | 29.622 | 29.6135 | 29.5877 | 29.4771 | 28.9086 | 28.3778 | 12.0598 | 12.0585 | 12.0569 | 29.8535 | 29.8389 | 29.824 | 29.809 | 29.7909 | 29.7663 | 29.7577 | 29.7319 | 29.3 | 28.7547 | 28.2468
|  | SUNBURY CROSS | LW |  |  | 13.0729 | 13.0729 | 13.0729 | 33.2729 | 33.2502 | 33.2268 | 33.2024 | 33.177 | 33.1385 | 33.1332 | 33.1149 | 33.0875 | 33.002 | 32.5723 | 9.6158 | 9.6147 | 9.6135 | 29.7108 | 29.6855 | 29.6595 | 29.6292 | 29.5981 | 29.5539 | 29.5425 | 29.5061 | 29.4106 | 28.828 | 28.3032 | 12.0602 | 12.0591 | 12.0578 | 29.8552 | 29.8299 | 29.8038 | 29.7735 | 29.7424 | 29.6982 | 29.6867 | 29.6503 | 29.2331 | 28.6738 | 28.1718
|  | SUNBURY CROSS | ST |  |  | 13.0729 | 13.0729 | 13.0729 | 33.2729 | 33.2508 | 33.2283 | 33.2054 | 33.1817 | 33.145 | 33.1326 | 33.0929 | 33.061 | 32.9576 | 32.9245 | 9.6167 | 9.6163 | 9.616 | 29.7154 | 29.6925 | 29.669 | 29.6423 | 29.6149 | 29.5744 | 29.5577 | 29.5058 | 29.4541 | 29.3309 | 29.1138 | 12.0611 | 12.0607 | 12.0604 | 29.8597 | 29.8369 | 29.8134 | 29.7867 | 29.7593 | 29.7187 | 29.7021 | 29.6501 | 29.5983 | 29.2993 | 28.9422
|  | SUNBURY CROSS | SP |  |  | 13.0729 | 13.0729 | 13.0729 | 33.2729 | 33.2729 | 33.2729 | 33.2729 | 33.2729 | 33.2729 | 33.2729 | 33.2729 | 33.2729 | 33.2729 | 33.2729 | 9.6171 | 9.617 | 9.6169 | 29.7169 | 29.7167 | 29.7164 | 29.7151 | 29.7139 | 29.7123 | 29.7107 | 29.7059 | 29.6984 | 29.6912 | 29.6844 | 12.0615 | 12.0614 | 12.0613 | 29.8613 | 29.8611 | 29.8608 | 29.8595 | 29.8583 | 29.8566 | 29.855 | 29.8503 | 29.8427 | 29.8355 | 29.8287
BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL | MINIMUM HEADROOM | SU 93757 67606 | YES | 35.4052 | 35.3992 | 35.3914 | 35.3788 | 35.3491 | 35.3038 | 35.2547 | 35.202 | 35.1258 | 35.0893 | 34.9782 | 34.0445 | 33.1668 | 32.3187 | 33.4219 | 33.3424 | 33.2386 | 33.0699 | 32.8893 | 32.6911 | 32.4371 | 32.1343 | 31.7785 | 31.4526 | 30.5356 | 29.4832 | 28.4695 | 27.444 | 34.1756 | 34.1688 | 34.1599 | 34.097 | 33.9774 | 33.8461 | 33.6779 | 33.4773 | 33.1582 | 32.8176 | 31.8587 | 30.7583 | 29.728 | 28.7324
|  | SUNNINGHILL | CT |  |  | 35.4054 | 35.3996 | 35.392 | 35.3797 | 35.3665 | 35.352 | 35.3368 | 35.314 | 35.2873 | 35.2629 | 35.0471 | 34.1097 | 33.2319 | 32.3843 | 33.4247 | 33.3471 | 33.2457 | 33.0822 | 32.9068 | 32.7136 | 32.5104 | 32.2075 | 31.8517 | 31.5258 | 30.6088 | 29.5564 | 28.5483 | 27.5233 | 34.1758 | 34.1692 | 34.1605 | 34.1051 | 33.989 | 33.861 | 33.7264 | 33.5258 | 33.2348 | 32.8941 | 31.9353 | 30.8348 | 29.8045 | 28.8094
|  | SUNNINGHILL | LW |  |  | 35.4052 | 35.3992 | 35.3914 | 35.3788 | 35.3652 | 35.3503 | 35.3313 | 35.3086 | 35.2818 | 35.2574 | 34.9819 | 34.0445 | 33.1668 | 32.3187 | 33.4219 | 33.3424 | 33.2386 | 33.0699 | 32.8893 | 32.6911 | 32.4371 | 32.1343 | 31.7785 | 31.4526 | 30.5356 | 29.4832 | 28.4695 | 27.444 | 34.1756 | 34.1688 | 34.1599 | 34.097 | 33.9774 | 33.8461 | 33.6779 | 33.4773 | 33.1582 | 32.8176 | 31.8587 | 30.7583 | 29.728 | 28.7324
|  | SUNNINGHILL | ST |  |  | 35.4071 | 35.4032 | 35.3985 | 35.3921 | 35.3491 | 35.3038 | 35.2547 | 35.202 | 35.1258 | 35.0893 | 34.9782 | 34.8717 | 34.1521 | 33.5529 | 33.4479 | 33.3955 | 33.3326 | 33.247 | 33.1071 | 32.9438 | 32.7389 | 32.5005 | 32.2027 | 31.9595 | 31.2557 | 30.4829 | 29.667 | 29.0007 | 34.1778 | 34.1733 | 34.168 | 34.1606 | 34.1098 | 33.9896 | 33.8416 | 33.6709 | 33.454 | 33.2863 | 32.6247 | 31.8191 | 30.9739 | 30.2797
|  | SUNNINGHILL | SP |  |  | 35.4425 | 35.4069 | 35.4047 | 35.4024 | 35.3884 | 35.3742 | 35.359 | 35.3428 | 35.319 | 35.2666 | 35.1021 | 35.0113 | 34.7738 | 34.5728 | 33.9188 | 33.4449 | 33.4156 | 33.3853 | 33.3292 | 33.2668 | 33.1926 | 33.1065 | 32.9937 | 32.8597 | 32.4618 | 32.1069 | 31.6315 | 31.2025 | 34.2181 | 34.1776 | 34.1751 | 34.1725 | 34.158 | 34.1432 | 34.1273 | 34.1071 | 34.0268 | 33.9225 | 33.6098 | 33.3514 | 32.9628 | 32.5889
MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER | MINIMUM HEADROOM | ST 93394 80051 | YES | 55.7632 | 55.689 | 55.5492 | 54.6378 | 54.3447 | 54.0326 | 53.5625 | 53.0631 | 52.6265 | 52.2407 | 51.1211 | 49.0348 | 46.7821 | 44.5089 | 56.8223 | 56.7956 | 56.7526 | 56.0114 | 55.8968 | 55.7775 | 55.5212 | 54.9428 | 54.4385 | 53.988 | 52.6811 | 50.2435 | 47.6018 | 44.9459 | 55.7455 | 55.6603 | 55.498 | 54.5473 | 54.2128 | 53.8561 | 53.3138 | 52.7371 | 52.2341 | 51.785 | 50.4818 | 48.0513 | 45.4174 | 42.7692
|  | SUTTON BENGER | CT |  |  | 55.8327 | 55.7743 | 55.6537 | 55.048 | 54.8077 | 54.5481 | 54.2798 | 53.8027 | 53.3887 | 53.0119 | 51.9192 | 49.453 | 47.0944 | 44.8216 | 56.8801 | 56.8606 | 56.8258 | 56.3666 | 56.2819 | 56.1925 | 56.101 | 55.738 | 55.2563 | 54.8148 | 53.5349 | 50.7173 | 47.9696 | 45.3143 | 55.8177 | 55.7502 | 55.6098 | 54.9702 | 54.6939 | 54.3948 | 54.0856 | 53.5312 | 53.0508 | 52.6106 | 51.3344 | 48.5239 | 45.7841 | 43.1365
|  | SUTTON BENGER | LW |  |  | 55.7632 | 55.689 | 55.5492 | 54.6378 | 54.3447 | 54.0326 | 53.5625 | 53.0631 | 52.6265 | 52.2407 | 51.1211 | 49.0348 | 46.7821 | 44.5089 | 56.8223 | 56.7956 | 56.7526 | 56.0114 | 55.8968 | 55.7775 | 55.5212 | 54.9428 | 54.4385 | 53.988 | 52.6811 | 50.2435 | 47.6018 | 44.9459 | 55.7455 | 55.6603 | 55.498 | 54.5473 | 54.2128 | 53.8561 | 53.3138 | 52.7371 | 52.2341 | 51.785 | 50.4818 | 48.0513 | 45.4174 | 42.7692
|  | SUTTON BENGER | ST |  |  | 55.8723 | 55.8264 | 55.7406 | 55.3448 | 55.171 | 54.9675 | 54.6501 | 54.314 | 54.0249 | 53.7647 | 53.0114 | 51.6158 | 50.1371 | 48.6993 | 56.9102 | 56.8955 | 56.8709 | 56.5667 | 56.5032 | 56.4323 | 56.3332 | 56.2294 | 55.971 | 55.6665 | 54.7855 | 53.1508 | 51.4183 | 49.7347 | 55.8594 | 55.8063 | 55.7063 | 55.2893 | 55.09 | 54.8559 | 54.4879 | 54.098 | 53.7639 | 53.4603 | 52.5819 | 50.952 | 49.2246 | 47.546
|  | SUTTON BENGER | SP |  |  | 55.937 | 55.9225 | 55.8864 | 55.71 | 55.6393 | 55.5612 | 55.4459 | 55.3244 | 55.2024 | 55.0969 | 54.7914 | 54.2301 | 53.6053 | 52.9755 | 56.9464 | 56.9412 | 56.9306 | 56.7838 | 56.7572 | 56.7288 | 56.6911 | 56.652 | 56.6124 | 56.5799 | 56.4845 | 56.1798 | 55.4497 | 54.7151 | 55.9307 | 55.914 | 55.872 | 55.6888 | 55.6079 | 55.5184 | 55.385 | 55.2445 | 55.1033 | 54.981 | 54.6269 | 53.9726 | 53.2447 | 52.5122
IVER 132KV | UPTON BSP | SUTTON LANE | MINIMUM HEADROOM | TQ 02185 78595 | YES | 26.9732 | 26.8922 | 26.7967 | 26.6027 | 26.4141 | 26.2256 | 26.0554 | 25.9903 | 25.9261 | 25.8574 | 25.6518 | 25.262 | 24.8483 | 24.4393 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0443 | 27.0374 | 27.0167 | 26.6684 | 26.1883 | 25.7136 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.1725 | 26.6987
|  | SUTTON LANE | CT |  |  | 26.975 | 26.8952 | 26.8012 | 26.6105 | 26.4249 | 26.2395 | 26.0554 | 25.9903 | 25.9261 | 25.8574 | 25.6518 | 25.262 | 24.8483 | 24.4393 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0443 | 27.0374 | 27.0167 | 26.6684 | 26.1883 | 25.7136 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.1725 | 26.6987
|  | SUTTON LANE | LW |  |  | 26.9732 | 26.8922 | 26.7967 | 26.6027 | 26.4141 | 26.2256 | 26.1595 | 26.0944 | 26.0301 | 25.9615 | 25.7559 | 25.3739 | 24.9602 | 24.5511 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0478 | 27.0272 | 26.7984 | 26.3182 | 25.8433 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.302 | 26.8281
|  | SUTTON LANE | ST |  |  | 27.0214 | 26.9784 | 26.9349 | 26.8646 | 26.7781 | 26.6728 | 26.6023 | 26.5329 | 26.4891 | 26.4423 | 26.3033 | 26.0592 | 25.81 | 25.5581 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0326 | 27.0079 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371
|  | SUTTON LANE | SP |  |  | 27.0576 | 27.0467 | 27.0399 | 27.0343 | 27.0089 | 26.9782 | 26.9529 | 26.928 | 26.8967 | 26.8786 | 26.825 | 26.7307 | 26.6349 | 26.5413 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.0483 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371 | 27.3371
MANNINGTON GSP | WAREHAM | SWANAGE | MINIMUM HEADROOM | SZ 02010 79296 | YES | 9.2327 | 9.2327 | 9.2327 | 8.271 | 8.2692 | 8.2655 | 8.2597 | 8.2517 | 8.2357 | 8.2329 | 8.2188 | 8.1844 | 8.1129 | 7.9489 | 8.4176 | 8.3093 | 8.2837 | 7.2594 | 7.1945 | 7.1278 | 7.0991 | 7.0684 | 7.0299 | 7.003 | 6.9174 | 6.7546 | 6.5103 | 6.3313 | 7.4546 | 7.3053 | 7.27 | 6.2337 | 6.1595 | 6.0835 | 6.0514 | 6.0174 | 5.9756 | 5.9452 | 5.8491 | 5.678 | 5.47 | 5.3267
|  | SWANAGE | CT |  |  | 9.2327 | 9.2327 | 9.2327 | 8.271 | 8.2704 | 8.2694 | 8.2679 | 8.2657 | 8.2609 | 8.26 | 8.2554 | 8.2171 | 8.1744 | 8.0182 | 8.422 | 8.3167 | 8.2953 | 7.2839 | 7.2303 | 7.1765 | 7.1229 | 7.098 | 7.0707 | 7.0456 | 6.9696 | 6.8098 | 6.5901 | 6.4026 | 7.4606 | 7.3156 | 7.286 | 6.2617 | 6.2004 | 6.1389 | 6.0775 | 6.0493 | 6.0187 | 5.9901 | 5.9036 | 5.7287 | 5.5452 | 5.3933
|  | SWANAGE | LW |  |  | 9.2327 | 9.2327 | 9.2327 | 8.271 | 8.2692 | 8.2655 | 8.2597 | 8.2517 | 8.2357 | 8.2329 | 8.2188 | 8.1844 | 8.1129 | 7.9489 | 8.4176 | 8.3093 | 8.2837 | 7.2594 | 7.1945 | 7.1278 | 7.0991 | 7.0684 | 7.0299 | 7.003 | 6.9174 | 6.7546 | 6.5103 | 6.3313 | 7.4546 | 7.3053 | 7.27 | 6.2337 | 6.1595 | 6.0835 | 6.0514 | 6.0174 | 5.9756 | 5.9452 | 5.8491 | 5.678 | 5.47 | 5.3267
|  | SWANAGE | ST |  |  | 9.2327 | 9.2327 | 9.2327 | 9.2327 | 9.2324 | 9.2316 | 9.2305 | 9.2288 | 9.2251 | 9.2233 | 9.2136 | 9.201 | 9.1565 | 9.1404 | 8.4413 | 8.4381 | 8.3469 | 8.3416 | 8.3346 | 8.3256 | 8.3105 | 8.2949 | 8.2784 | 8.2629 | 8.2053 | 8.113 | 7.9892 | 7.8943 | 7.4871 | 7.4828 | 7.3571 | 7.3498 | 7.3403 | 7.3283 | 7.3078 | 7.287 | 7.2657 | 7.245 | 7.18 | 7.0761 | 6.9406 | 6.8341
|  | SWANAGE | SP |  |  | 9.2327 | 9.2327 | 9.2327 | 9.2327 | 9.2327 | 9.2327 | 9.2326 | 9.2326 | 9.2324 | 9.2318 | 9.2283 | 9.2256 | 9.2123 | 9.1994 | 8.4427 | 8.4411 | 8.4399 | 8.4387 | 8.4334 | 8.427 | 8.4219 | 8.4167 | 8.41 | 8.4041 | 8.3851 | 8.3573 | 8.3199 | 8.2839 | 7.4892 | 7.4869 | 7.4852 | 7.4836 | 7.4763 | 7.4675 | 7.4604 | 7.4533 | 7.4443 | 7.4363 | 7.4114 | 7.3742 | 7.3276 | 7.2829
MINETY GSP | SWINDON BSP | SWINDON | MINIMUM HEADROOM | SU 12449 86967 | NO | 24.2683 | 24.2651 | 24.2613 | 24.255 | 24.0062 | 23.7484 | 23.4752 | 23.1923 | 22.7681 | 22.6999 | 22.4682 | 22.0832 | 21.3253 | 21.1766 | 25.3277 | 25.3259 | 25.3239 | 25.3204 | 25.0738 | 24.8187 | 24.5501 | 24.2719 | 23.8523 | 23.789 | 23.5732 | 23.2272 | 22.4851 | 21.4682 | 25.7638 | 25.7613 | 25.7583 | 25.7535 | 25.5057 | 25.2492 | 24.9783 | 24.6978 | 24.2758 | 24.2101 | 23.9862 | 23.6206 | 22.8863 | 22.7615
|  | SWINDON | CT |  |  | 24.2683 | 24.2651 | 24.2613 | 24.255 | 24.2489 | 24.2425 | 24.236 | 24.2258 | 24.2155 | 24.2047 | 24.1695 | 24.0834 | 23.9774 | 23.8708 | 25.3277 | 25.3259 | 25.3239 | 25.3204 | 25.3171 | 25.3136 | 25.31 | 25.3044 | 25.2988 | 25.2928 | 25.2736 | 25.2264 | 25.1394 | 24.1806 | 25.7638 | 25.7613 | 25.7583 | 25.7535 | 25.7487 | 25.7437 | 25.7387 | 25.7308 | 25.7228 | 25.7144 | 25.6871 | 25.6202 | 25.538 | 25.4552
|  | SWINDON | LW |  |  | 24.2685 | 24.2654 | 24.2618 | 24.2559 | 24.0062 | 23.7484 | 23.4752 | 23.1923 | 22.7681 | 22.6999 | 22.4682 | 22.0832 | 21.3253 | 21.1766 | 25.3278 | 25.3261 | 25.3241 | 25.3209 | 25.0738 | 24.8187 | 24.5501 | 24.2719 | 23.8523 | 23.789 | 23.5732 | 23.2272 | 22.4851 | 21.4682 | 25.7639 | 25.7615 | 25.7587 | 25.7541 | 25.5057 | 25.2492 | 24.9783 | 24.6978 | 24.2758 | 24.2101 | 23.9862 | 23.6206 | 22.8863 | 22.7615
|  | SWINDON | ST |  |  | 24.2691 | 24.2666 | 24.2641 | 24.2606 | 24.2385 | 24.2153 | 24.1908 | 24.1656 | 24.129 | 24.1116 | 24.0554 | 23.97 | 23.8154 | 23.7208 | 25.3281 | 25.3268 | 25.3254 | 25.3235 | 25.3033 | 25.2824 | 25.2606 | 25.2381 | 25.2047 | 25.1906 | 25.1454 | 25.0869 | 24.9638 | 24.8999 | 25.7644 | 25.7625 | 25.7605 | 25.7577 | 25.7366 | 25.7145 | 25.6914 | 25.6676 | 25.6325 | 25.6167 | 25.566 | 25.4939 | 25.3549 | 25.2755
|  | SWINDON | SP |  |  | 24.2709 | 24.2699 | 24.2692 | 24.2686 | 24.2654 | 24.262 | 24.2579 | 24.2538 | 24.2481 | 24.2361 | 24.1981 | 24.1599 | 24.0851 | 24.0155 | 25.3291 | 25.3286 | 25.3282 | 25.3279 | 25.3252 | 25.3224 | 25.3192 | 25.316 | 25.3114 | 25.3008 | 25.2669 | 25.2399 | 25.1794 | 25.125 | 25.7657 | 25.765 | 25.7644 | 25.764 | 25.761 | 25.7579 | 25.7543 | 25.7507 | 25.7455 | 25.7342 | 25.6982 | 25.6656 | 25.5978 | 25.5358
BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY | MINIMUM HEADROOM | SU 57753 62717 | YES | 17.3614 | 17.3484 | 17.3349 | 16.6262 | 16.5645 | 16.5028 | 16.4345 | 16.3661 | 16.2977 | 16.2631 | 16.1588 | 15.9622 | 15.235 | 14.4602 | 12.5627 | 12.5502 | 12.5373 | 11.8299 | 11.7694 | 11.709 | 11.644 | 11.579 | 11.514 | 11.4829 | 11.013 | 10.1078 | 9.2694 | 8.3819 | 12.7624 | 12.7508 | 12.7393 | 12.0346 | 11.9768 | 11.919 | 11.8613 | 11.8035 | 11.7458 | 11.7227 | 11.6494 | 11.0087 | 10.187 | 9.3192
|  | TADLEY | CT |  |  | 17.4169 | 17.4085 | 17.3996 | 16.9728 | 16.9342 | 16.8956 | 16.8565 | 16.8112 | 16.7659 | 16.7406 | 16.6639 | 16.1014 | 15.3088 | 14.5343 | 12.6182 | 12.6102 | 12.602 | 12.1764 | 12.1391 | 12.1018 | 12.064 | 12.0221 | 11.9802 | 11.9585 | 11.5963 | 10.3009 | 9.3562 | 8.4689 | 12.8178 | 12.8109 | 12.8039 | 12.3811 | 12.3465 | 12.3118 | 12.2772 | 12.2425 | 12.2079 | 12.194 | 12.1524 | 11.2022 | 10.2715 | 9.4039
|  | TADLEY | LW |  |  | 17.3614 | 17.3484 | 17.3349 | 16.6262 | 16.5645 | 16.5028 | 16.4345 | 16.3661 | 16.2977 | 16.2631 | 16.1588 | 15.9622 | 15.235 | 14.4602 | 12.5627 | 12.5502 | 12.5373 | 11.8299 | 11.7694 | 11.709 | 11.644 | 11.579 | 11.514 | 11.4829 | 11.013 | 10.1078 | 9.2694 | 8.3819 | 12.7624 | 12.7508 | 12.7393 | 12.0346 | 11.9768 | 11.919 | 11.8613 | 11.8035 | 11.7458 | 11.7227 | 11.6494 | 11.0087 | 10.187 | 9.3192
|  | TADLEY | ST |  |  | 17.4453 | 17.4398 | 17.4341 | 17.1504 | 17.1133 | 17.0755 | 17.0345 | 16.993 | 16.9431 | 16.9194 | 16.8468 | 16.7447 | 16.6213 | 16.3238 | 12.6464 | 12.6411 | 12.6358 | 12.3527 | 12.3163 | 12.2793 | 12.2401 | 12.2005 | 12.1529 | 12.1317 | 12.0665 | 11.5618 | 10.9909 | 10.4405 | 12.8455 | 12.8409 | 12.8363 | 12.5544 | 12.5195 | 12.4845 | 12.4491 | 12.4134 | 12.3708 | 12.3549 | 12.306 | 12.2358 | 11.893 | 11.3437
|  | TADLEY | SP |  |  | 17.474 | 17.4715 | 17.4691 | 17.328 | 17.3158 | 17.3036 | 17.2905 | 17.2774 | 17.2638 | 17.2562 | 17.2332 | 17.1955 | 17.1689 | 17.1315 | 12.6748 | 12.6723 | 12.6699 | 12.5289 | 12.5169 | 12.5049 | 12.4923 | 12.4797 | 12.4668 | 12.4601 | 12.44 | 12.4069 | 12.3844 | 12.3508 | 12.8733 | 12.8709 | 12.8686 | 12.7277 | 12.7161 | 12.7046 | 12.693 | 12.6815 | 12.6699 | 12.6653 | 12.6515 | 12.6284 | 12.6145 | 12.5891
IVER 132KV | SLOUGH | TAPLOW | MINIMUM HEADROOM | SU 91721 81234 | YES | 70.9657 | 70.9657 | 70.9657 | 70.9657 | 70.9651 | 70.9636 | 70.9614 | 70.9583 | 70.952 | 70.951 | 70.9455 | 70.9321 | 70.9061 | 69.0605 | 68.4708 | 68.4625 | 68.4568 | 68.4453 | 68.4332 | 68.4204 | 68.3946 | 68.368 | 68.3384 | 68.3122 | 68.231 | 66.4529 | 63.7762 | 61.1323 | 69.1276 | 69.1186 | 69.1126 | 69.1002 | 69.0873 | 69.0737 | 69.0462 | 69.0179 | 68.9867 | 68.9588 | 68.8722 | 67.4019 | 64.8296 | 62.3018
|  | TAPLOW | CT |  |  | 70.9657 | 70.9657 | 70.9657 | 70.9657 | 70.9655 | 70.9651 | 70.9646 | 70.9637 | 70.9618 | 70.9615 | 70.9597 | 70.9448 | 70.9283 | 69.3127 | 68.4711 | 68.463 | 68.4576 | 68.4466 | 68.4357 | 68.4245 | 68.4132 | 68.3888 | 68.3636 | 68.3382 | 68.2607 | 66.7209 | 64.0643 | 61.4181 | 69.1279 | 69.1192 | 69.1134 | 69.1017 | 69.0899 | 69.078 | 69.0659 | 69.0399 | 69.013 | 68.9859 | 68.903 | 67.6686 | 65.106 | 62.5759
|  | TAPLOW | LW |  |  | 70.9657 | 70.9657 | 70.9657 | 70.9657 | 70.9651 | 70.9636 | 70.9614 | 70.9583 | 70.952 | 70.951 | 70.9455 | 70.9321 | 70.9061 | 69.0605 | 68.4708 | 68.4625 | 68.4568 | 68.4453 | 68.4332 | 68.4204 | 68.3946 | 68.368 | 68.3384 | 68.3122 | 68.231 | 66.4529 | 63.7762 | 61.1323 | 69.1276 | 69.1186 | 69.1126 | 69.1002 | 69.0873 | 69.0737 | 69.0462 | 69.0179 | 68.9867 | 68.9588 | 68.8722 | 67.4019 | 64.8296 | 62.3018
|  | TAPLOW | ST |  |  | 70.9657 | 70.9657 | 70.9657 | 70.9657 | 70.9656 | 70.9653 | 70.9649 | 70.9642 | 70.9628 | 70.9621 | 70.9583 | 70.9534 | 70.9362 | 70.9299 | 68.4725 | 68.4696 | 68.4621 | 68.4563 | 68.4491 | 68.4402 | 68.4261 | 68.4119 | 68.3945 | 68.3766 | 68.3216 | 68.2219 | 66.8353 | 65.1537 | 69.1294 | 69.1263 | 69.1182 | 69.112 | 69.1043 | 69.0949 | 69.0797 | 69.0646 | 69.046 | 69.027 | 68.9683 | 68.862 | 67.7824 | 66.1476
|  | TAPLOW | SP |  |  | 70.9657 | 70.9657 | 70.9657 | 70.9657 | 70.9657 | 70.9657 | 70.9657 | 70.9657 | 70.9656 | 70.9654 | 70.964 | 70.963 | 70.9578 | 70.9528 | 68.4756 | 68.4751 | 68.4705 | 68.4699 | 68.468 | 68.4658 | 68.4615 | 68.4571 | 68.4515 | 68.4446 | 68.4234 | 68.3853 | 68.34 | 68.2951 | 69.1327 | 69.1321 | 69.1272 | 69.1266 | 69.1246 | 69.1222 | 69.1175 | 69.1129 | 69.1069 | 69.0995 | 69.0769 | 69.0362 | 68.9881 | 68.9404
MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON | MINIMUM HEADROOM | ST 94510 07307 | YES | 14.6312 | 14.6312 | 14.6312 | 14.6312 | 14.618 | 14.6042 | 14.5898 | 14.5741 | 14.5485 | 14.545 | 14.5321 | 14.4565 | 14.3732 | 14.164 | 13.9413 | 13.9413 | 13.9413 | 13.9413 | 13.9282 | 13.9144 | 13.8999 | 13.8842 | 13.8586 | 13.8551 | 13.8422 | 13.1542 | 12.3263 | 11.5519 | 13.8746 | 13.8728 | 13.8704 | 13.8654 | 13.8498 | 13.8319 | 13.8133 | 13.7898 | 13.7564 | 13.7446 | 13.7068 | 13.5587 | 12.75 | 11.9917
|  | TARRANT RUSHTON | CT |  |  | 14.6312 | 14.6312 | 14.6312 | 14.6312 | 14.618 | 14.6042 | 14.5898 | 14.5741 | 14.5485 | 14.545 | 14.5321 | 14.4565 | 14.3732 | 14.164 | 13.9413 | 13.9413 | 13.9413 | 13.9413 | 13.9282 | 13.9144 | 13.8999 | 13.8842 | 13.8586 | 13.8551 | 13.8422 | 13.1781 | 12.3302 | 11.5519 | 13.875 | 13.8734 | 13.8714 | 13.8671 | 13.8498 | 13.8319 | 13.8133 | 13.7898 | 13.7564 | 13.7446 | 13.7068 | 13.5797 | 12.751 | 11.9917
|  | TARRANT RUSHTON | LW |  |  | 14.6312 | 14.6312 | 14.6312 | 14.6312 | 14.6295 | 14.626 | 14.6206 | 14.6131 | 14.598 | 14.5954 | 14.582 | 14.5496 | 14.4864 | 14.1959 | 13.9413 | 13.9413 | 13.9413 | 13.9413 | 13.9396 | 13.9362 | 13.9307 | 13.9232 | 13.9081 | 13.9055 | 13.8921 | 13.1542 | 12.3263 | 11.5676 | 13.8746 | 13.8728 | 13.8704 | 13.8654 | 13.8589 | 13.8506 | 13.8373 | 13.822 | 13.7991 | 13.7881 | 13.7499 | 13.5587 | 12.75 | 12.0103
|  | TARRANT RUSHTON | ST |  |  | 14.6312 | 14.6312 | 14.6312 | 14.6312 | 14.6308 | 14.6301 | 14.6291 | 14.6275 | 14.624 | 14.6223 | 14.6132 | 14.6013 | 14.5594 | 14.5442 | 13.9413 | 13.9413 | 13.9413 | 13.9413 | 13.9409 | 13.9402 | 13.9392 | 13.9376 | 13.9341 | 13.9324 | 13.9233 | 13.8257 | 13.2901 | 12.7859 | 13.875 | 13.8735 | 13.8717 | 13.8687 | 13.8647 | 13.8595 | 13.8527 | 13.8455 | 13.8367 | 13.8293 | 13.8034 | 13.763 | 13.6914 | 13.1996
|  | TARRANT RUSHTON | SP |  |  | 14.6312 | 14.6312 | 14.6312 | 14.6312 | 14.6288 | 14.6264 | 14.624 | 14.6216 | 14.6177 | 14.6068 | 14.5707 | 14.5524 | 14.4907 | 14.4374 | 13.9413 | 13.9413 | 13.9413 | 13.9413 | 13.9389 | 13.9365 | 13.9341 | 13.9317 | 13.9278 | 13.9169 | 13.8808 | 13.8625 | 13.8008 | 13.7475 | 13.8767 | 13.8765 | 13.8763 | 13.8761 | 13.8729 | 13.8696 | 13.8653 | 13.861 | 13.8548 | 13.8416 | 13.799 | 13.7699 | 13.6973 | 13.6335
MANNINGTON GSP | SALISBURY | TEFFONT | MINIMUM HEADROOM | ST 99837 30994 | YES | 35.6314 | 35.6314 | 35.6314 | 35.6314 | 35.6152 | 35.5986 | 35.5816 | 35.5636 | 35.5352 | 35.5315 | 35.4332 | 35.3221 | 33.976 | 32.6639 | 34.1393 | 34.1393 | 34.1393 | 34.1393 | 34.1232 | 34.1066 | 34.0895 | 34.0715 | 34.0431 | 34.0394 | 33.9411 | 33.6998 | 32.1908 | 30.6997 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6739 | 33.6573 | 33.6403 | 33.6223 | 33.5939 | 33.5902 | 33.4919 | 32.998 | 31.4972 | 30.0151
|  | TEFFONT | CT |  |  | 35.6314 | 35.6314 | 35.6314 | 35.6314 | 35.6152 | 35.5986 | 35.5816 | 35.5636 | 35.5352 | 35.5315 | 35.519 | 35.3366 | 33.976 | 32.6639 | 34.1393 | 34.1393 | 34.1393 | 34.1393 | 34.1232 | 34.1066 | 34.0895 | 34.0715 | 34.0431 | 34.0394 | 34.0269 | 33.73 | 32.1908 | 30.6997 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6739 | 33.6573 | 33.6403 | 33.6223 | 33.5939 | 33.5902 | 33.5777 | 33.0274 | 31.4972 | 30.0151
|  | TEFFONT | LW |  |  | 35.6314 | 35.6314 | 35.6314 | 35.6314 | 35.6251 | 35.618 | 35.6099 | 35.6006 | 35.5851 | 35.5827 | 35.5729 | 35.3221 | 33.9952 | 32.7 | 34.1393 | 34.1393 | 34.1393 | 34.1393 | 34.1331 | 34.126 | 34.1178 | 34.1085 | 34.093 | 34.0907 | 34.0808 | 33.6998 | 32.1943 | 30.7201 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6839 | 33.6767 | 33.6686 | 33.6593 | 33.6438 | 33.6414 | 33.6316 | 32.998 | 31.5015 | 30.0362
|  | TEFFONT | ST |  |  | 35.6314 | 35.6314 | 35.6314 | 35.6314 | 35.6223 | 35.6129 | 35.6033 | 35.5931 | 35.5768 | 35.5711 | 35.5514 | 35.5337 | 35.4744 | 34.6698 | 34.1393 | 34.1393 | 34.1393 | 34.1393 | 34.1302 | 34.1209 | 34.1112 | 34.101 | 34.0848 | 34.0791 | 34.0594 | 34.0417 | 33.9285 | 32.9708 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.681 | 33.6716 | 33.662 | 33.6518 | 33.6355 | 33.6298 | 33.6101 | 33.5924 | 33.2249 | 32.2728
|  | TEFFONT | SP |  |  | 35.6314 | 35.6314 | 35.6314 | 35.6314 | 35.623 | 35.6149 | 35.6067 | 35.5984 | 35.5853 | 35.549 | 35.4332 | 35.3776 | 35.2009 | 35.0524 | 34.1393 | 34.1393 | 34.1393 | 34.1393 | 34.131 | 34.1228 | 34.1146 | 34.1063 | 34.0932 | 34.0569 | 33.9411 | 33.8855 | 33.7088 | 33.5603 | 33.6901 | 33.6901 | 33.6901 | 33.6901 | 33.6817 | 33.6736 | 33.6654 | 33.6571 | 33.644 | 33.6077 | 33.4919 | 33.4363 | 33.2596 | 33.1111
BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM | MINIMUM HEADROOM | SU 84178 83872 | YES | 7.0673 | 7.0652 | 7.0625 | 7.0568 | 7.0513 | 7.0457 | 7.0026 | 6.9551 | 6.903 | 6.8472 | 6.6037 | 6.1482 | 6.0243 | 5.9068 | 6.5691 | 6.5665 | 6.563 | 6.5557 | 6.5485 | 6.5414 | 6.4858 | 6.4248 | 6.3577 | 6.2858 | 5.9724 | 5.4192 | 5.2693 | 5.1273 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3446 | 7.1986 | 7.057
|  | TEMPLE FARM | CT |  |  | 7.0673 | 7.0652 | 7.0625 | 7.0568 | 7.0513 | 7.0457 | 7.0179 | 6.9704 | 6.9183 | 6.8625 | 6.619 | 6.1645 | 6.0406 | 5.9232 | 6.5691 | 6.5665 | 6.563 | 6.5557 | 6.5485 | 6.5414 | 6.5055 | 6.4445 | 6.3774 | 6.3055 | 5.9921 | 5.4389 | 5.289 | 5.1471 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3613 | 7.2182 | 7.0767
|  | TEMPLE FARM | LW |  |  | 7.0673 | 7.0652 | 7.0625 | 7.0568 | 7.0513 | 7.0457 | 7.0026 | 6.9551 | 6.903 | 6.8472 | 6.6037 | 6.1482 | 6.0243 | 5.9068 | 6.5691 | 6.5665 | 6.563 | 6.5557 | 6.5485 | 6.5414 | 6.4858 | 6.4248 | 6.3577 | 6.2858 | 5.9724 | 5.4192 | 5.2693 | 5.1273 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3446 | 7.1986 | 7.057
|  | TEMPLE FARM | ST |  |  | 7.0683 | 7.067 | 7.0655 | 7.0629 | 7.0598 | 7.056 | 7.034 | 7.0091 | 6.974 | 6.9358 | 6.7627 | 6.448 | 6.368 | 6.2917 | 6.5704 | 6.5688 | 6.5668 | 6.5635 | 6.5595 | 6.5546 | 6.5263 | 6.4942 | 6.4491 | 6.3998 | 6.177 | 5.7817 | 5.6849 | 5.5928 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749
|  | TEMPLE FARM | SP |  |  | 7.0697 | 7.0694 | 7.0692 | 7.069 | 7.0682 | 7.0671 | 7.0576 | 7.0472 | 7.0352 | 7.0201 | 6.9515 | 6.8236 | 6.7959 | 6.7709 | 6.5722 | 6.5719 | 6.5716 | 6.5714 | 6.5702 | 6.5689 | 6.5566 | 6.5433 | 6.5278 | 6.5083 | 6.4201 | 6.2554 | 6.2197 | 6.1876 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749 | 7.3749
MELKSHAM GSP | CHIPPENHAM | TETBURY | MINIMUM HEADROOM | ST 89708 93444 | YES | 6.3403 | 6.3369 | 6.3323 | 6.3227 | 6.3134 | 6.3041 | 6.2728 | 6.2407 | 6.209 | 6.1748 | 6.0739 | 5.9082 | 5.7374 | 5.5695 | 3.7806 | 3.7766 | 3.7713 | 3.7601 | 3.7492 | 3.7384 | 3.7018 | 3.6645 | 3.6275 | 3.5876 | 3.4699 | 3.2767 | 3.0775 | 2.8817 | 3.0385 | 3.0344 | 3.0291 | 3.0177 | 3.0067 | 2.9958 | 2.9588 | 2.921 | 2.8836 | 2.8432 | 2.724 | 2.5286 | 2.327 | 2.1289
|  | TETBURY | CT |  |  | 6.3403 | 6.3369 | 6.3323 | 6.3227 | 6.3134 | 6.3041 | 6.2949 | 6.2629 | 6.2312 | 6.197 | 6.0961 | 5.9303 | 5.7596 | 5.5918 | 3.7806 | 3.7766 | 3.7713 | 3.7601 | 3.7492 | 3.7384 | 3.7276 | 3.6904 | 3.6534 | 3.6135 | 3.4958 | 3.3024 | 3.1033 | 2.9076 | 3.0385 | 3.0344 | 3.0291 | 3.0177 | 3.0067 | 2.9958 | 2.9849 | 2.9472 | 2.9097 | 2.8694 | 2.7503 | 2.5546 | 2.3532 | 2.1551
|  | TETBURY | LW |  |  | 6.3404 | 6.3371 | 6.3326 | 6.3233 | 6.3141 | 6.305 | 6.2728 | 6.2407 | 6.209 | 6.1748 | 6.0739 | 5.9082 | 5.7374 | 5.5695 | 3.7808 | 3.7768 | 3.7717 | 3.7607 | 3.7501 | 3.7395 | 3.7018 | 3.6645 | 3.6275 | 3.5876 | 3.4699 | 3.2767 | 3.0775 | 2.8817 | 3.0386 | 3.0347 | 3.0294 | 3.0184 | 3.0076 | 2.9969 | 2.9588 | 2.921 | 2.8836 | 2.8432 | 2.724 | 2.5286 | 2.327 | 2.1289
|  | TETBURY | ST |  |  | 6.342 | 6.3399 | 6.3375 | 6.3332 | 6.328 | 6.3216 | 6.3062 | 6.2909 | 6.2693 | 6.2459 | 6.1779 | 6.0679 | 5.958 | 5.8486 | 3.7827 | 3.7802 | 3.7773 | 3.7723 | 3.7662 | 3.7588 | 3.7408 | 3.723 | 3.6978 | 3.6706 | 3.5913 | 3.4629 | 3.3347 | 3.2072 | 3.0405 | 3.0381 | 3.0351 | 3.0301 | 3.0239 | 3.0164 | 2.9982 | 2.9802 | 2.9546 | 2.9271 | 2.8469 | 2.717 | 2.5873 | 2.4583
|  | TETBURY | SP |  |  | 6.3443 | 6.344 | 6.3436 | 6.3433 | 6.3419 | 6.3402 | 6.3356 | 6.331 | 6.3251 | 6.3161 | 6.2898 | 6.2483 | 6.2086 | 6.1712 | 3.7853 | 3.7849 | 3.7845 | 3.7842 | 3.7825 | 3.7805 | 3.7751 | 3.7697 | 3.7629 | 3.7523 | 3.7218 | 3.6733 | 3.627 | 3.5835 | 3.0432 | 3.0428 | 3.0424 | 3.042 | 3.0404 | 3.0384 | 3.0329 | 3.0274 | 3.0205 | 3.0099 | 2.9789 | 2.9299 | 2.8831 | 2.839
BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM | MINIMUM HEADROOM | SU 52758 66466 | YES | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6936 | 4.6429 | 4.5561 | 4.4643 | 4.3738 | 3.9881 | 3.9795 | 3.9682 | 3.9443 | 3.9211 | 3.8981 | 3.8753 | 3.8591 | 3.843 | 3.8256 | 3.774 | 3.6856 | 3.5923 | 3.5002
|  | THATCHAM | CT |  |  | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6936 | 4.6429 | 4.5561 | 4.4643 | 4.3738 | 3.9881 | 3.9795 | 3.9682 | 3.9443 | 3.9211 | 3.8981 | 3.8753 | 3.8591 | 3.843 | 3.8256 | 3.774 | 3.6856 | 3.5923 | 3.5002
|  | THATCHAM | LW |  |  | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6217 | 4.5299 | 4.4394 | 3.9952 | 3.9917 | 3.987 | 3.9773 | 3.9679 | 3.9584 | 3.9421 | 3.9259 | 3.9098 | 3.8924 | 3.8408 | 3.7524 | 3.6591 | 3.5669
|  | THATCHAM | ST |  |  | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.649 | 4.5902 | 3.998 | 3.9966 | 3.9949 | 3.9921 | 3.9886 | 3.9843 | 3.9708 | 3.9574 | 3.9464 | 3.9346 | 3.8998 | 3.8407 | 3.7803 | 3.7204
|  | THATCHAM | SP |  |  | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.892 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 4.6995 | 3.9995 | 3.9992 | 3.999 | 3.9987 | 3.9978 | 3.9966 | 3.9919 | 3.9872 | 3.9812 | 3.9766 | 3.9632 | 3.9408 | 3.9183 | 3.8965
NORTH HYDE GSP | NORTH HYDE (D) | THE GREEN | MINIMUM HEADROOM | TQ 12414 79503 | YES | 12.4146 | 12.4146 | 12.4146 | 12.4146 | 12.3774 | 12.3384 | 12.297 | 12.2534 | 12.1859 | 12.1763 | 12.142 | 11.9483 | 11.4457 | 11.075 | 9.0639 | 9.061 | 9.0571 | 9.049 | 9.009 | 8.9637 | 8.9155 | 8.8651 | 8.7909 | 8.7033 | 8.4119 | 7.9179 | 7.3329 | 6.8811 | 9.2313 | 9.1953 | 9.1481 | 9.0482 | 8.9513 | 8.8549 | 8.7356 | 8.6093 | 8.4598 | 8.3619 | 8.0661 | 7.5702 | 6.9832 | 6.5294
|  | THE GREEN | CT |  |  | 12.4146 | 12.4146 | 12.4146 | 12.4146 | 12.4144 | 12.414 | 12.4135 | 12.4128 | 12.4111 | 12.4108 | 12.4092 | 12.1872 | 11.8041 | 11.4369 | 9.0639 | 9.061 | 9.0571 | 9.049 | 9.0409 | 9.0327 | 9.0244 | 9.0139 | 8.9339 | 8.8486 | 8.5868 | 8.1399 | 7.6744 | 7.2261 | 9.2313 | 9.1953 | 9.1481 | 9.0482 | 8.9513 | 8.8549 | 8.7593 | 8.6759 | 8.5923 | 8.5036 | 8.2406 | 7.7918 | 7.3242 | 6.874
|  | THE GREEN | LW |  |  | 12.4146 | 12.4146 | 12.4146 | 12.4146 | 12.3774 | 12.3384 | 12.297 | 12.2534 | 12.1859 | 12.1763 | 12.142 | 11.9483 | 11.4457 | 11.075 | 9.0647 | 9.0623 | 9.0592 | 9.0526 | 9.009 | 8.9637 | 8.9155 | 8.8651 | 8.7909 | 8.7033 | 8.4119 | 7.9179 | 7.3329 | 6.8811 | 9.2408 | 9.2117 | 9.1734 | 9.0926 | 8.9771 | 8.8604 | 8.7356 | 8.6093 | 8.4598 | 8.3619 | 8.0661 | 7.5702 | 6.9832 | 6.5294
|  | THE GREEN | ST |  |  | 12.4146 | 12.4146 | 12.4146 | 12.4146 | 12.4144 | 12.4142 | 12.4138 | 12.4132 | 12.4119 | 12.4113 | 12.408 | 12.4036 | 12.3883 | 12.1953 | 9.0661 | 9.0648 | 9.0633 | 9.0606 | 9.0573 | 9.0531 | 9.0485 | 9.0437 | 9.0379 | 9.0323 | 9.0146 | 8.7527 | 8.4468 | 8.1527 | 9.2581 | 9.2421 | 9.2232 | 9.191 | 9.1512 | 9.1031 | 9.0509 | 8.9993 | 8.9421 | 8.8811 | 8.7016 | 8.4074 | 8.1001 | 7.8047
|  | THE GREEN | SP |  |  | 12.4146 | 12.4146 | 12.4146 | 12.4146 | 12.4122 | 12.4098 | 12.4075 | 12.405 | 12.4013 | 12.3907 | 12.3567 | 12.3401 | 12.2863 | 12.2407 | 9.0675 | 9.0672 | 9.067 | 9.0667 | 9.0633 | 9.0597 | 9.056 | 9.0523 | 9.0469 | 9.0345 | 8.9949 | 8.9693 | 8.9067 | 8.8528 | 9.2744 | 9.2713 | 9.2684 | 9.2655 | 9.2501 | 9.2324 | 9.2142 | 9.1962 | 9.1723 | 9.1383 | 9.0363 | 8.9097 | 8.7489 | 8.6018
BRAMLEY (FLEE) | READING TOWN BSP | THE MALL | MINIMUM HEADROOM | SU 71319 73293 | YES | 38.6862 | 38.6728 | 38.6594 | 37.8404 | 37.7703 | 37.6971 | 37.5948 | 37.366 | 37.0327 | 36.979 | 36.5495 | 34.0766 | 31.8284 | 30.1895 | 36.1339 | 36.0996 | 36.0662 | 35.2052 | 34.5772 | 33.6851 | 33.3195 | 32.9444 | 32.3272 | 31.9674 | 30.8902 | 28.187 | 25.699 | 23.8242 | 31.5898 | 31.3825 | 31.185 | 29.9769 | 29.5297 | 29.0829 | 28.8788 | 28.5711 | 28.1125 | 27.9238 | 27.3525 | 25.4941 | 23.8856 | 22.8763
|  | THE MALL | CT |  |  | 38.7507 | 38.7426 | 38.7345 | 38.2432 | 38.0307 | 37.8146 | 37.5948 | 37.366 | 37.0327 | 36.979 | 36.5495 | 34.0766 | 31.8284 | 30.1895 | 36.2016 | 36.175 | 36.1501 | 35.6232 | 35.2596 | 34.3772 | 33.4595 | 32.9444 | 32.3272 | 31.9674 | 30.8902 | 28.187 | 25.699 | 23.8242 | 31.6844 | 31.5042 | 31.3407 | 30.5207 | 29.9899 | 29.4582 | 28.9262 | 28.5711 | 28.1125 | 27.9238 | 27.3525 | 25.4941 | 23.8856 | 22.8763
|  | THE MALL | LW |  |  | 38.6862 | 38.6728 | 38.6594 | 37.8404 | 37.7703 | 37.6971 | 37.6205 | 37.5402 | 37.4465 | 37.4151 | 36.913 | 35.4409 | 33.9153 | 32.4465 | 36.1339 | 36.0996 | 36.0662 | 35.2052 | 34.5772 | 33.6851 | 33.3195 | 32.9528 | 32.5753 | 32.2379 | 31.2285 | 29.526 | 27.7606 | 26.0558 | 31.5898 | 31.3825 | 31.185 | 29.9769 | 29.5297 | 29.0829 | 28.8788 | 28.6721 | 28.4532 | 28.2868 | 27.7835 | 26.9257 | 26.04 | 25.2012
|  | THE MALL | ST |  |  | 38.7829 | 38.7775 | 38.7721 | 38.4446 | 38.4171 | 38.389 | 38.3603 | 38.3307 | 38.2976 | 38.2839 | 38.2358 | 38.0868 | 37.1211 | 36.182 | 36.2338 | 36.216 | 36.1902 | 35.8375 | 35.7792 | 35.216 | 34.936 | 34.6513 | 34.4242 | 34.2016 | 33.5428 | 32.4604 | 31.3401 | 30.2476 | 31.7158 | 31.5953 | 31.4008 | 30.8412 | 30.529 | 30.1578 | 30.0101 | 29.8632 | 29.7445 | 29.6387 | 29.3211 | 28.802 | 28.2488 | 27.7189
|  | THE MALL | SP |  |  | 38.8151 | 38.8124 | 38.8097 | 38.6459 | 38.6325 | 38.619 | 38.6055 | 38.592 | 38.5783 | 38.5719 | 38.5501 | 38.5186 | 38.4806 | 38.4298 | 36.2805 | 36.2762 | 36.2663 | 36.1011 | 36.0809 | 36.0595 | 36.0417 | 36.0239 | 36.0048 | 35.9945 | 35.9614 | 35.9117 | 35.856 | 35.7882 | 31.882 | 31.865 | 31.7949 | 31.6181 | 31.5428 | 31.4559 | 31.4026 | 31.3497 | 31.2852 | 31.2431 | 31.1172 | 30.9168 | 30.7144 | 30.5072
BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE | MINIMUM HEADROOM | SU 64755 71015 | YES | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1094 | 15.101 | 15.0923 | 15.0832 | 15.0676 | 15.0565 | 15.0217 | 14.5889 | 13.6508 | 12.7339 | 14.6683 | 14.6658 | 14.663 | 14.6583 | 14.6422 | 14.6246 | 14.6023 | 14.5522 | 14.4438 | 14.3321 | 13.9897 | 13.2159 | 12.2153 | 11.1521 | 14.7198 | 14.7164 | 14.7127 | 14.7069 | 14.6923 | 14.6765 | 14.655 | 14.6334 | 14.6086 | 14.557 | 14.2066 | 13.2936 | 12.2043 | 11.1373
|  | THEALE | CT |  |  | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1098 | 15.0815 | 14.6905 | 13.7749 | 12.8592 | 14.6683 | 14.6658 | 14.663 | 14.6583 | 14.6503 | 14.641 | 14.6314 | 14.6073 | 14.5325 | 14.4227 | 14.0867 | 13.3228 | 12.3447 | 11.284 | 14.7198 | 14.7164 | 14.7127 | 14.7069 | 14.7004 | 14.693 | 14.6841 | 14.6716 | 14.6605 | 14.6485 | 14.3046 | 13.4081 | 12.3353 | 11.2694
|  | THEALE | LW |  |  | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1094 | 15.101 | 15.0923 | 15.0832 | 15.0676 | 15.0565 | 15.0217 | 14.5889 | 13.6508 | 12.7339 | 14.6683 | 14.6658 | 14.663 | 14.6583 | 14.6422 | 14.6246 | 14.6023 | 14.5522 | 14.4438 | 14.3321 | 13.9897 | 13.2159 | 12.2153 | 11.1521 | 14.7198 | 14.7164 | 14.7127 | 14.7069 | 14.6923 | 14.6765 | 14.655 | 14.6334 | 14.6086 | 14.557 | 14.2066 | 13.2936 | 12.2043 | 11.1373
|  | THEALE | ST |  |  | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1158 | 15.0712 | 14.7303 | 14.1615 | 14.669 | 14.6673 | 14.6654 | 14.663 | 14.66 | 14.6543 | 14.6472 | 14.6408 | 14.6334 | 14.6262 | 14.4933 | 13.9637 | 13.369 | 12.7789 | 14.7208 | 14.7184 | 14.7159 | 14.7127 | 14.7086 | 14.7036 | 14.6979 | 14.6928 | 14.6861 | 14.6789 | 14.6568 | 14.1701 | 13.4631 | 12.7852
|  | THEALE | SP |  |  | 15.1175 | 15.1175 | 15.1175 | 15.1175 | 15.1159 | 15.1144 | 15.1128 | 15.1112 | 15.1088 | 15.102 | 15.0803 | 15.07 | 15.0341 | 14.9834 | 14.6698 | 14.6688 | 14.6679 | 14.6669 | 14.664 | 14.661 | 14.6578 | 14.6548 | 14.651 | 14.6418 | 14.6115 | 14.5805 | 14.3939 | 14.0876 | 14.7218 | 14.7204 | 14.7192 | 14.7179 | 14.7146 | 14.711 | 14.7072 | 14.7038 | 14.6996 | 14.6905 | 14.6619 | 14.6332 | 14.5749 | 14.308
BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON | MINIMUM HEADROOM | SU 29134 45674 | YES | 44.4483 | 44.3568 | 44.2979 | 44.183 | 44.0674 | 43.8525 | 43.6429 | 43.5257 | 43.3993 | 43.265 | 42.7776 | 41.9191 | 40.9249 | 39.9277 | 43.8437 | 43.832 | 43.825 | 43.8114 | 43.7976 | 43.7835 | 43.7709 | 43.7646 | 43.7579 | 43.7507 | 43.7248 | 43.4522 | 42.3204 | 41.1824 | 44.1026 | 44.0876 | 44.0787 | 44.0613 | 44.0438 | 43.9141 | 43.7746 | 43.7056 | 43.6183 | 43.4733 | 42.8975 | 41.903 | 40.7515 | 39.5963
|  | THRUXTON | CT |  |  | 44.4489 | 44.3591 | 44.3014 | 44.189 | 44.0758 | 43.8726 | 43.6429 | 43.5257 | 43.3993 | 43.265 | 42.7776 | 41.9191 | 40.9249 | 39.9277 | 43.8439 | 43.8323 | 43.8254 | 43.8121 | 43.7986 | 43.7848 | 43.7709 | 43.7646 | 43.7579 | 43.7507 | 43.7248 | 43.4522 | 42.3204 | 41.1824 | 44.1028 | 44.088 | 44.0792 | 44.0622 | 44.0451 | 43.9281 | 43.7746 | 43.7056 | 43.6183 | 43.4733 | 42.8975 | 41.903 | 40.7515 | 39.5963
|  | THRUXTON | LW |  |  | 44.4483 | 44.3568 | 44.2979 | 44.183 | 44.0674 | 43.8525 | 43.7608 | 43.6542 | 43.5279 | 43.3937 | 42.9094 | 42.051 | 41.0568 | 40.0595 | 43.8437 | 43.832 | 43.825 | 43.8114 | 43.7976 | 43.7835 | 43.7778 | 43.7715 | 43.7647 | 43.7576 | 43.7317 | 43.6024 | 42.4706 | 41.3346 | 44.1026 | 44.0876 | 44.0787 | 44.0613 | 44.0438 | 43.9141 | 43.8503 | 43.7813 | 43.7068 | 43.6125 | 43.0504 | 42.0559 | 40.9043 | 39.749
|  | THRUXTON | ST |  |  | 44.4645 | 44.458 | 44.4071 | 44.3801 | 44.3465 | 44.3056 | 44.2591 | 44.2103 | 44.172 | 44.1307 | 43.9062 | 43.3552 | 42.7087 | 42.0773 | 43.8483 | 43.8465 | 43.838 | 43.8348 | 43.8308 | 43.8259 | 43.8204 | 43.8146 | 43.8101 | 43.8051 | 43.7869 | 43.7555 | 43.7213 | 43.6324 | 44.1084 | 44.1061 | 44.0953 | 44.0912 | 44.0861 | 44.0799 | 44.0728 | 44.0654 | 44.0596 | 44.0534 | 43.9515 | 43.5731 | 42.8176 | 42.0863
|  | THRUXTON | SP |  |  | 44.4671 | 44.4636 | 44.4303 | 44.422 | 44.4008 | 44.3762 | 44.3574 | 44.338 | 44.3143 | 44.2981 | 44.2378 | 44.1279 | 43.9327 | 43.6522 | 43.849 | 43.8481 | 43.8408 | 43.8398 | 43.8373 | 43.8343 | 43.8321 | 43.8298 | 43.827 | 43.825 | 43.8179 | 43.8048 | 43.7886 | 43.7714 | 44.1094 | 44.1081 | 44.0988 | 44.0975 | 44.0943 | 44.0906 | 44.0877 | 44.0848 | 44.0812 | 44.0788 | 44.0696 | 44.0529 | 43.97 | 43.78
MELKSHAM GSP | WEST GRAFTON | TIDWORTH | MINIMUM HEADROOM | SU 24088 49593 | YES | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0577 | 27.0476 | 27.0373 | 27.0267 | 27.0103 | 27.0047 | 26.9869 | 26.9726 | 26.9256 | 26.9107 | 26.1667 | 26.1651 | 26.1625 | 26.1576 | 26.1493 | 26.1366 | 26.1236 | 26.1102 | 26.0909 | 26.0823 | 26.0559 | 26.0272 | 25.9664 | 25.8608 | 26.3848 | 26.3832 | 26.3805 | 26.3754 | 26.3671 | 26.3544 | 26.3414 | 26.3278 | 26.3085 | 26.2998 | 26.1169 | 25.7939 | 25.4718 | 25.1628
|  | TIDWORTH | CT |  |  | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 26.1667 | 26.1651 | 26.1625 | 26.1576 | 26.1536 | 26.1498 | 26.1475 | 26.1434 | 26.1393 | 26.1348 | 26.1222 | 26.1008 | 26.0794 | 25.8887 | 26.3848 | 26.3832 | 26.3805 | 26.3754 | 26.3713 | 26.3674 | 26.365 | 26.3609 | 26.3565 | 26.3322 | 26.1409 | 25.8178 | 25.4958 | 25.187
|  | TIDWORTH | LW |  |  | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 26.1667 | 26.1651 | 26.1625 | 26.1576 | 26.1536 | 26.1498 | 26.1459 | 26.1419 | 26.1377 | 26.1333 | 26.1206 | 26.0992 | 26.0778 | 25.8608 | 26.3848 | 26.3832 | 26.3805 | 26.3754 | 26.3713 | 26.3674 | 26.3634 | 26.3592 | 26.3549 | 26.3083 | 26.1169 | 25.7939 | 25.4718 | 25.1628
|  | TIDWORTH | ST |  |  | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0577 | 27.0476 | 27.0373 | 27.0267 | 27.0103 | 27.0047 | 26.9869 | 26.9726 | 26.9256 | 26.9107 | 26.1673 | 26.1662 | 26.1645 | 26.1616 | 26.1493 | 26.1366 | 26.1236 | 26.1102 | 26.0909 | 26.0823 | 26.0559 | 26.0272 | 25.9664 | 25.9383 | 26.3854 | 26.3843 | 26.3826 | 26.3796 | 26.3671 | 26.3544 | 26.3414 | 26.3278 | 26.3085 | 26.2998 | 26.2731 | 26.0462 | 25.7908 | 25.576
|  | TIDWORTH | SP |  |  | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 27.0676 | 26.168 | 26.1674 | 26.1666 | 26.1653 | 26.1643 | 26.1633 | 26.1624 | 26.1615 | 26.1602 | 26.1591 | 26.1558 | 26.1502 | 26.145 | 26.1401 | 26.3861 | 26.3856 | 26.3847 | 26.3834 | 26.3823 | 26.3814 | 26.3804 | 26.3794 | 26.3781 | 26.377 | 26.3735 | 26.3678 | 26.3624 | 26.3574
MANNINGTON GSP | SHAFTESBURY BSP | TISBURY | MINIMUM HEADROOM | ST 93438 29127 | YES | 8.7538 | 8.7514 | 8.4325 | 8.4259 | 8.4157 | 8.4014 | 8.3843 | 8.3624 | 8.3233 | 8.3122 | 8.2668 | 8.1681 | 7.9987 | 7.9631 | 5.9229 | 5.9229 | 5.6071 | 5.6071 | 5.6033 | 5.5717 | 5.5118 | 5.4475 | 5.3664 | 5.3101 | 5.1307 | 4.81 | 4.4102 | 4.148 | 6.4987 | 6.4973 | 6.1797 | 6.1758 | 6.1683 | 6.1567 | 6.1415 | 6.1216 | 6.0844 | 6.0453 | 5.8866 | 5.5667 | 5.1677 | 4.9062
|  | TISBURY | CT |  |  | 8.7544 | 8.7524 | 8.434 | 8.4285 | 8.4221 | 8.4146 | 8.4062 | 8.3967 | 8.3815 | 8.3745 | 8.3494 | 8.2424 | 8.1251 | 8.0712 | 5.9229 | 5.9229 | 5.6071 | 5.6071 | 5.606 | 5.6038 | 5.573 | 5.5211 | 5.464 | 5.4117 | 5.2528 | 4.9236 | 4.5761 | 4.2956 | 6.4991 | 6.4979 | 6.1806 | 6.1774 | 6.1731 | 6.1678 | 6.1615 | 6.154 | 6.1409 | 6.132 | 6.0085 | 5.6801 | 5.3334 | 5.0537
|  | TISBURY | LW |  |  | 8.7538 | 8.7514 | 8.4325 | 8.4259 | 8.4157 | 8.4014 | 8.3843 | 8.3624 | 8.3233 | 8.3122 | 8.2668 | 8.1681 | 7.9987 | 7.9631 | 5.9229 | 5.9229 | 5.6071 | 5.6071 | 5.6033 | 5.5717 | 5.5118 | 5.4475 | 5.3664 | 5.3101 | 5.1307 | 4.81 | 4.4102 | 4.148 | 6.4987 | 6.4973 | 6.1797 | 6.1758 | 6.1683 | 6.1567 | 6.1415 | 6.1216 | 6.0844 | 6.0453 | 5.8866 | 5.5667 | 5.1677 | 4.9062
|  | TISBURY | ST |  |  | 8.7553 | 8.754 | 8.7525 | 8.7498 | 8.43 | 8.4246 | 8.4189 | 8.4121 | 8.4009 | 8.3935 | 8.3626 | 8.3188 | 8.2071 | 8.1559 | 5.9229 | 5.9229 | 5.9229 | 5.9229 | 5.6063 | 5.6047 | 5.6023 | 5.5988 | 5.5908 | 5.5693 | 5.4482 | 5.2567 | 4.9966 | 4.798 | 6.4996 | 6.4988 | 6.4979 | 6.4964 | 6.1779 | 6.1741 | 6.1697 | 6.1643 | 6.1544 | 6.1485 | 6.1219 | 6.0123 | 5.7528 | 5.5547
|  | TISBURY | SP |  |  | 8.7566 | 8.7563 | 8.7561 | 8.7558 | 8.7547 | 8.7534 | 8.7522 | 8.4352 | 8.4334 | 8.4308 | 8.4194 | 8.4071 | 8.3726 | 8.3392 | 5.9229 | 5.9229 | 5.9229 | 5.9229 | 5.9229 | 5.9228 | 5.9227 | 5.6068 | 5.6065 | 5.6052 | 5.5977 | 5.5918 | 5.5636 | 5.4854 | 6.5004 | 6.5002 | 6.5001 | 6.4999 | 6.4993 | 6.4985 | 6.4977 | 6.1811 | 6.18 | 6.1779 | 6.1681 | 6.1585 | 6.1266 | 6.0956
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD | MINIMUM HEADROOM | SU 54104 05695 | YES | 23.026 | 23.026 | 23.026 | 23.026 | 23.0131 | 22.9996 | 22.9854 | 22.9702 | 22.8856 | 22.7897 | 22.503 | 22.0165 | 21.4942 | 20.9884 | 12.907 | 12.9016 | 12.8957 | 12.8872 | 12.8778 | 12.8628 | 12.8397 | 12.8155 | 12.7781 | 12.7559 | 12.6845 | 12.0172 | 11.2493 | 10.5655 | 13.1327 | 13.1122 | 13.0897 | 13.0577 | 13.0347 | 13.0138 | 12.94 | 12.8608 | 12.7733 | 12.6965 | 12.4658 | 12.072 | 11.5142 | 10.796
|  | TITCHFIELD | CT |  |  | 23.026 | 23.026 | 23.026 | 23.026 | 23.0215 | 23.0164 | 23.0108 | 23.0042 | 22.9589 | 22.8642 | 22.5853 | 22.0822 | 21.574 | 21.0756 | 12.9071 | 12.9017 | 12.8958 | 12.8874 | 12.8778 | 12.8686 | 12.8585 | 12.8333 | 12.8031 | 12.7818 | 12.7173 | 12.1202 | 11.3665 | 10.6705 | 13.1328 | 13.1124 | 13.09 | 13.0583 | 13.0347 | 13.0138 | 12.9914 | 12.9142 | 12.8324 | 12.7569 | 12.534 | 12.1236 | 11.6368 | 10.9063
|  | TITCHFIELD | LW |  |  | 23.026 | 23.026 | 23.026 | 23.026 | 23.024 | 23.0201 | 23.0138 | 22.9914 | 22.8856 | 22.7897 | 22.503 | 22.0165 | 21.4942 | 20.9884 | 12.907 | 12.9016 | 12.8957 | 12.8872 | 12.8802 | 12.872 | 12.8472 | 12.8199 | 12.784 | 12.7615 | 12.6893 | 12.0172 | 11.2493 | 10.5655 | 13.1327 | 13.1122 | 13.0897 | 13.0577 | 13.0364 | 13.0164 | 12.94 | 12.8608 | 12.7733 | 12.6965 | 12.4658 | 12.072 | 11.5142 | 10.796
|  | TITCHFIELD | ST |  |  | 23.026 | 23.026 | 23.026 | 23.026 | 23.0131 | 22.9996 | 22.9854 | 22.9702 | 22.9454 | 22.9364 | 22.7286 | 22.3968 | 21.9996 | 21.6781 | 12.9082 | 12.9042 | 12.9003 | 12.8953 | 12.8793 | 12.8628 | 12.8397 | 12.8155 | 12.7781 | 12.7559 | 12.6845 | 12.5899 | 12.0828 | 11.6055 | 13.137 | 13.1222 | 13.1071 | 13.0884 | 13.0635 | 13.0387 | 12.9909 | 12.9418 | 12.8692 | 12.8098 | 12.6313 | 12.3614 | 12.024 | 11.7614
|  | TITCHFIELD | SP |  |  | 23.026 | 23.026 | 23.026 | 23.026 | 23.0248 | 23.0236 | 23.0223 | 23.0211 | 23.019 | 23.0132 | 22.993 | 22.9822 | 22.8563 | 22.7225 | 12.9095 | 12.9071 | 12.905 | 12.9029 | 12.9005 | 12.8984 | 12.8944 | 12.8904 | 12.8848 | 12.8738 | 12.8388 | 12.8039 | 12.7426 | 12.6872 | 13.1421 | 13.1329 | 13.125 | 13.117 | 13.1115 | 13.1068 | 13.0951 | 13.0833 | 13.068 | 13.0426 | 12.9661 | 12.8641 | 12.7409 | 12.6275
BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM | MINIMUM HEADROOM | SU 88310 49487 | YES | 11.0998 | 11.0956 | 11.0902 | 11.0786 | 11.0674 | 11.0562 | 11.0077 | 10.9597 | 10.9121 | 10.8608 | 10.7094 | 10.461 | 10.2048 | 9.9529 | 9.0527 | 9.0481 | 9.0422 | 9.0295 | 9.0172 | 9.005 | 8.952 | 8.8994 | 8.8474 | 8.7877 | 8.61 | 8.3182 | 8.0174 | 7.7217 | 9.3105 | 9.3068 | 9.3019 | 9.2915 | 9.2814 | 9.2714 | 9.2279 | 9.1848 | 9.1371 | 9.0855 | 8.9333 | 8.6833 | 8.4256 | 8.1545
|  | TONGHAM | CT |  |  | 11.0998 | 11.0956 | 11.0902 | 11.0786 | 11.0674 | 11.0562 | 11.0451 | 10.9972 | 10.9496 | 10.8982 | 10.7469 | 10.4982 | 10.2422 | 9.9904 | 9.0527 | 9.0481 | 9.0422 | 9.0295 | 9.0172 | 9.005 | 8.9928 | 8.9404 | 8.8884 | 8.8316 | 8.6539 | 8.362 | 8.0614 | 7.7658 | 9.3105 | 9.3068 | 9.3019 | 9.2915 | 9.2814 | 9.2714 | 9.2614 | 9.2184 | 9.1748 | 9.1231 | 8.9709 | 8.7208 | 8.4632 | 8.1985
|  | TONGHAM | LW |  |  | 11.0998 | 11.0956 | 11.0902 | 11.0786 | 11.0674 | 11.0562 | 11.0077 | 10.9597 | 10.9121 | 10.8608 | 10.7094 | 10.461 | 10.2048 | 9.9529 | 9.0527 | 9.0481 | 9.0422 | 9.0295 | 9.0172 | 9.005 | 8.952 | 8.8994 | 8.8474 | 8.7877 | 8.61 | 8.3182 | 8.0174 | 7.7217 | 9.3105 | 9.3068 | 9.3019 | 9.2915 | 9.2814 | 9.2714 | 9.2279 | 9.1848 | 9.1371 | 9.0855 | 8.9333 | 8.6833 | 8.4256 | 8.1545
|  | TONGHAM | ST |  |  | 11.1018 | 11.0993 | 11.0962 | 11.091 | 11.0846 | 11.0769 | 11.0465 | 11.0163 | 10.9838 | 10.9488 | 10.8468 | 10.6815 | 10.5166 | 10.3526 | 9.0549 | 9.0521 | 9.0488 | 9.0431 | 9.0361 | 9.0277 | 8.9943 | 8.9614 | 8.9258 | 8.8875 | 8.7712 | 8.5772 | 8.3835 | 8.191 | 9.3123 | 9.31 | 9.3073 | 9.3026 | 9.2969 | 9.29 | 9.2626 | 9.2356 | 9.2064 | 9.1741 | 9.0714 | 8.9052 | 8.7393 | 8.5743
|  | TONGHAM | SP |  |  | 11.1046 | 11.1042 | 11.1038 | 11.1034 | 11.1016 | 11.0996 | 11.0896 | 11.0798 | 11.0667 | 11.0532 | 11.0138 | 10.9513 | 10.8917 | 10.8356 | 9.0579 | 9.0575 | 9.057 | 9.0566 | 9.0547 | 9.0524 | 9.0415 | 9.0308 | 9.0165 | 9.0017 | 8.9586 | 8.8902 | 8.8239 | 8.758 | 9.3148 | 9.3144 | 9.3141 | 9.3137 | 9.3121 | 9.3103 | 9.3013 | 9.2926 | 9.2808 | 9.2686 | 9.2333 | 9.1765 | 9.1166 | 9.0601
MINETY GSP | TOOTHILL BSP | TOOTHILL | MINIMUM HEADROOM | SU 13215 83986 | NO | 17.9224 | 17.9224 | 17.9224 | 17.9224 | 17.9212 | 17.9189 | 17.9152 | 17.9101 | 17.8998 | 17.898 | 17.3677 | 16.1869 | 15.4486 | 14.7937 | 12.2158 | 12.047 | 11.9105 | 11.7027 | 11.484 | 11.2418 | 10.9467 | 10.6166 | 10.2468 | 9.8566 | 8.4529 | 7.0785 | 6.2151 | 5.4431 | 12.2984 | 12.2984 | 12.2984 | 12.2984 | 12.2973 | 12.295 | 12.23 | 11.8941 | 11.518 | 11.1233 | 9.7223 | 8.3516 | 7.4992 | 6.7375
|  | TOOTHILL | CT |  |  | 17.9224 | 17.9224 | 17.9224 | 17.9224 | 17.922 | 17.9214 | 17.9204 | 17.919 | 17.9159 | 17.9153 | 17.471 | 16.2878 | 15.5651 | 14.9054 | 12.221 | 12.0561 | 11.9245 | 11.7274 | 11.5198 | 11.2894 | 11.0434 | 10.7169 | 10.3543 | 9.9671 | 8.5695 | 7.1935 | 6.346 | 5.5693 | 12.2984 | 12.2984 | 12.2984 | 12.2984 | 12.2981 | 12.2974 | 12.2965 | 11.996 | 11.6271 | 11.2335 | 9.8387 | 8.4655 | 7.6288 | 6.8623
|  | TOOTHILL | LW |  |  | 17.9224 | 17.9224 | 17.9224 | 17.9224 | 17.9212 | 17.9189 | 17.9152 | 17.9101 | 17.8998 | 17.898 | 17.3677 | 16.1869 | 15.4486 | 14.7937 | 12.2158 | 12.047 | 11.9105 | 11.7027 | 11.484 | 11.2418 | 10.9467 | 10.6166 | 10.2468 | 9.8566 | 8.4529 | 7.0785 | 6.2151 | 5.4431 | 12.2984 | 12.2984 | 12.2984 | 12.2984 | 12.2973 | 12.295 | 12.23 | 11.8941 | 11.518 | 11.1233 | 9.7223 | 8.3516 | 7.4992 | 6.7375
|  | TOOTHILL | ST |  |  | 17.9224 | 17.9224 | 17.9224 | 17.9224 | 17.9221 | 17.9217 | 17.9209 | 17.9199 | 17.9175 | 17.9163 | 17.9101 | 17.6446 | 17.1658 | 16.7326 | 12.2504 | 12.1809 | 12.0381 | 11.9342 | 11.8139 | 11.6696 | 11.4557 | 11.2196 | 10.9753 | 10.7093 | 9.7296 | 8.7737 | 8.22 | 7.7164 | 12.2984 | 12.2984 | 12.2984 | 12.2984 | 12.2982 | 12.2977 | 12.297 | 12.2959 | 12.2589 | 11.9883 | 10.9965 | 10.0425 | 9.4899 | 8.9873
|  | TOOTHILL | SP |  |  | 17.9224 | 17.9224 | 17.9224 | 17.9224 | 17.9224 | 17.9224 | 17.9223 | 17.9223 | 17.9222 | 17.9218 | 17.9196 | 17.9178 | 17.9093 | 17.901 | 12.2723 | 12.2297 | 12.1242 | 12.0785 | 12.021 | 11.9571 | 11.8726 | 11.7814 | 11.6731 | 11.568 | 11.1821 | 10.8105 | 10.6062 | 10.4225 | 12.2984 | 12.2984 | 12.2984 | 12.2984 | 12.2984 | 12.2984 | 12.2984 | 12.2983 | 12.2982 | 12.2979 | 12.2956 | 12.0913 | 11.8835 | 11.6968
NURSLING GSP | ROWNHAMS | TOTTON | MINIMUM HEADROOM | SU 35835 13428 | YES | 33.9047 | 33.9047 | 33.9047 | 33.9047 | 33.9041 | 33.9029 | 33.9009 | 33.8983 | 33.8929 | 33.8919 | 33.8872 | 33.8756 | 33.8531 | 32.7334 | 33.057 | 33.0545 | 33.0515 | 33.047 | 33.0415 | 33.0354 | 33.0217 | 33.008 | 32.9918 | 32.9796 | 32.9402 | 32.8567 | 31.3639 | 29.6632 | 33.2033 | 33.2003 | 33.1968 | 33.1915 | 33.1851 | 33.1781 | 33.1622 | 33.1464 | 33.1282 | 33.1139 | 33.0682 | 31.9428 | 30.1815 | 28.4509
|  | TOTTON | CT |  |  | 33.9047 | 33.9047 | 33.9047 | 33.9047 | 33.9045 | 33.9042 | 33.9037 | 33.9029 | 33.9013 | 33.901 | 33.8995 | 33.8866 | 33.8723 | 32.8789 | 33.057 | 33.0546 | 33.0517 | 33.0472 | 33.0422 | 33.0371 | 33.0317 | 33.0199 | 33.0075 | 32.9959 | 32.9597 | 32.8749 | 31.5323 | 29.8293 | 33.2034 | 33.2004 | 33.197 | 33.1917 | 33.1858 | 33.1798 | 33.1735 | 33.1596 | 33.1452 | 33.1316 | 33.089 | 32.1053 | 30.3525 | 28.6197
|  | TOTTON | LW |  |  | 33.9047 | 33.9047 | 33.9047 | 33.9047 | 33.9041 | 33.9029 | 33.9009 | 33.8983 | 33.8929 | 33.8919 | 33.8872 | 33.8756 | 33.8531 | 32.7334 | 33.057 | 33.0545 | 33.0515 | 33.047 | 33.0415 | 33.0354 | 33.0217 | 33.008 | 32.9918 | 32.9796 | 32.9402 | 32.8567 | 31.3639 | 29.6632 | 33.2033 | 33.2003 | 33.1968 | 33.1915 | 33.1851 | 33.1781 | 33.1622 | 33.1464 | 33.1282 | 33.1139 | 33.0682 | 31.9428 | 30.1815 | 28.4509
|  | TOTTON | ST |  |  | 33.9047 | 33.9047 | 33.9047 | 33.9047 | 33.9046 | 33.9043 | 33.9039 | 33.9034 | 33.9021 | 33.9015 | 33.8983 | 33.894 | 33.8791 | 33.8737 | 33.0575 | 33.0557 | 33.0537 | 33.051 | 33.0477 | 33.0439 | 33.0367 | 33.0299 | 33.0213 | 33.013 | 32.9861 | 32.9326 | 32.8634 | 32.0733 | 33.2039 | 33.2017 | 33.1994 | 33.1963 | 33.1923 | 33.1878 | 33.1794 | 33.1714 | 33.1615 | 33.1517 | 33.1205 | 33.0579 | 32.015 | 30.903
|  | TOTTON | SP |  |  | 33.9047 | 33.9047 | 33.9047 | 33.9047 | 33.9047 | 33.9047 | 33.9047 | 33.9046 | 33.9046 | 33.9044 | 33.9032 | 33.9023 | 33.8978 | 33.8935 | 33.0584 | 33.0575 | 33.0566 | 33.0558 | 33.0546 | 33.0533 | 33.051 | 33.0489 | 33.0463 | 33.0431 | 33.0328 | 33.0121 | 32.9844 | 32.9563 | 33.205 | 33.2039 | 33.2028 | 33.2019 | 33.2004 | 33.1989 | 33.1962 | 33.1937 | 33.1907 | 33.1869 | 33.1749 | 33.1506 | 33.1186 | 33.086
BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK | MINIMUM HEADROOM | SU 45156 14783 | YES | 65.472 | 65.4273 | 65.4238 | 65.4187 | 65.3875 | 65.3548 | 65.3213 | 65.2781 | 65.2188 | 65.1992 | 65.143 | 64.9813 | 63.8887 | 62.8172 | 64.411 | 64.3285 | 64.322 | 64.3126 | 64.2768 | 64.2385 | 64.199 | 64.1427 | 64.0695 | 64.0378 | 63.8599 | 62.8902 | 61.5435 | 60.2897 | 64.9044 | 64.6896 | 64.6521 | 64.5981 | 64.5139 | 64.4181 | 64.3127 | 64.125 | 63.9072 | 63.7508 | 63.3225 | 62.4269 | 61.4022 | 60.3903
|  | TOWNHILL PARK | CT |  |  | 65.472 | 65.4274 | 65.4239 | 65.4188 | 65.3875 | 65.3548 | 65.3213 | 65.2781 | 65.2188 | 65.1992 | 65.143 | 64.9813 | 63.8887 | 62.8172 | 64.411 | 64.3287 | 64.3222 | 64.3129 | 64.2768 | 64.2385 | 64.199 | 64.1427 | 64.0695 | 64.0378 | 63.8599 | 62.8902 | 61.5435 | 60.2897 | 64.9045 | 64.6902 | 64.6531 | 64.5998 | 64.5139 | 64.4181 | 64.3171 | 64.125 | 63.9072 | 63.7508 | 63.3225 | 62.4269 | 61.4022 | 60.3903
|  | TOWNHILL PARK | LW |  |  | 65.472 | 65.4273 | 65.4238 | 65.4187 | 65.4129 | 65.4063 | 65.3918 | 65.3762 | 65.3597 | 65.3455 | 65.3067 | 65.2127 | 64.1538 | 63.1059 | 64.411 | 64.3285 | 64.322 | 64.3126 | 64.302 | 64.2897 | 64.2629 | 64.2343 | 64.2038 | 64.1702 | 63.9965 | 63.0353 | 61.7922 | 60.5618 | 64.9044 | 64.6896 | 64.6521 | 64.5981 | 64.5371 | 64.4667 | 64.3127 | 64.1483 | 63.9732 | 63.8222 | 63.4114 | 62.601 | 61.6797 | 60.6624
|  | TOWNHILL PARK | ST |  |  | 65.4847 | 65.4708 | 65.4267 | 65.4239 | 65.4204 | 65.4162 | 65.4076 | 65.3984 | 65.3872 | 65.3775 | 65.3509 | 65.2983 | 65.2413 | 64.678 | 64.4344 | 64.4088 | 64.3273 | 64.3222 | 64.3158 | 64.308 | 64.2922 | 64.2752 | 64.2546 | 64.2365 | 64.1875 | 63.9589 | 63.1938 | 62.4076 | 64.928 | 64.9022 | 64.6827 | 64.6529 | 64.6164 | 64.5716 | 64.4808 | 64.3831 | 64.2647 | 64.1613 | 63.8794 | 63.3225 | 62.7184 | 62.1357
|  | TOWNHILL PARK | SP |  |  | 65.4852 | 65.4768 | 65.4289 | 65.4276 | 65.4259 | 65.424 | 65.4209 | 65.4176 | 65.4137 | 65.4099 | 65.3995 | 65.3783 | 65.3536 | 65.3284 | 64.4354 | 64.4199 | 64.3315 | 64.329 | 64.3259 | 64.3224 | 64.3167 | 64.3107 | 64.3035 | 64.2964 | 64.2773 | 64.2382 | 64.1925 | 64.0936 | 64.9291 | 64.9134 | 64.7063 | 64.6923 | 64.6747 | 64.6546 | 64.6218 | 64.5871 | 64.5455 | 64.505 | 64.3951 | 64.1705 | 63.9084 | 63.6411
MINETY GSP | SWINDON BSP | TRADING ESTATE | MINIMUM HEADROOM | SU 13490 85868 | NO | 24.3683 | 24.3574 | 24.3464 | 23.6771 | 23.6027 | 23.5276 | 23.4517 | 23.375 | 23.2843 | 23.2 | 22.9325 | 22.694 | 22.0069 | 21.7602 | 24.0508 | 23.8489 | 23.8222 | 23.1204 | 23.0141 | 22.9027 | 22.7231 | 22.5313 | 22.3029 | 22.0184 | 20.7887 | 19.0284 | 17.7456 | 16.4773 | 24.7617 | 24.7507 | 24.7397 | 24.0704 | 23.996 | 23.921 | 23.8451 | 23.7684 | 23.6777 | 23.5934 | 23.3259 | 22.1394 | 20.9287 | 19.7164
|  | TRADING ESTATE | CT |  |  | 24.421 | 24.4144 | 24.4078 | 24.0062 | 23.9733 | 23.9404 | 23.9075 | 23.8746 | 23.8417 | 23.8285 | 23.789 | 23.3088 | 23.1394 | 23.0187 | 24.104 | 23.9089 | 23.8882 | 23.4576 | 23.3962 | 23.3301 | 23.259 | 23.1144 | 22.9643 | 22.7399 | 21.5523 | 19.4451 | 18.1182 | 16.8538 | 24.8144 | 24.8078 | 24.8012 | 24.3996 | 24.3667 | 24.3338 | 24.3008 | 24.2679 | 24.235 | 24.2218 | 24.1823 | 22.5466 | 21.2917 | 20.0906
|  | TRADING ESTATE | LW |  |  | 24.3683 | 24.3574 | 24.3464 | 23.6771 | 23.6027 | 23.5276 | 23.4517 | 23.375 | 23.287 | 23.2604 | 23.1789 | 23.0456 | 22.9204 | 22.7963 | 24.0508 | 23.8489 | 23.8222 | 23.1204 | 23.0141 | 22.9027 | 22.7231 | 22.5313 | 22.3029 | 22.0184 | 20.7887 | 19.0284 | 17.7456 | 16.4773 | 24.7617 | 24.7507 | 24.7397 | 24.0704 | 23.996 | 23.921 | 23.8451 | 23.7684 | 23.6803 | 23.6538 | 23.5722 | 22.1394 | 20.9287 | 19.7164
|  | TRADING ESTATE | ST |  |  | 24.4473 | 24.4429 | 24.4386 | 24.1708 | 24.0145 | 23.8561 | 23.6948 | 23.5289 | 23.2843 | 23.2 | 22.9325 | 22.694 | 22.0069 | 21.7602 | 24.1287 | 24.1124 | 23.9079 | 23.6123 | 23.4217 | 23.2188 | 23.0035 | 22.7757 | 22.4513 | 22.271 | 21.2033 | 19.8315 | 18.3935 | 17.4079 | 24.8407 | 24.8363 | 24.8319 | 24.5642 | 24.4079 | 24.2494 | 24.0882 | 23.9223 | 23.6777 | 23.5934 | 23.3259 | 22.8541 | 21.4794 | 20.5397
|  | TRADING ESTATE | SP |  |  | 24.4737 | 24.4715 | 24.4693 | 24.3354 | 24.3244 | 24.3135 | 24.3025 | 24.2915 | 24.2806 | 24.2762 | 24.263 | 24.2411 | 24.2279 | 24.2037 | 24.1601 | 24.1575 | 23.9829 | 23.8475 | 23.8311 | 23.8123 | 23.7865 | 23.7604 | 23.7307 | 23.6966 | 23.533 | 23.2324 | 22.9261 | 22.6145 | 24.867 | 24.8648 | 24.8626 | 24.7288 | 24.7178 | 24.7068 | 24.6959 | 24.6849 | 24.6739 | 24.6695 | 24.6564 | 24.6344 | 24.6212 | 24.5971
BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN | MINIMUM HEADROOM | SU 66254 68745 | YES | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8541 | 36.8527 | 36.8495 | 36.8489 | 36.8453 | 36.8301 | 34.8505 | 32.8535 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5317 | 34.5304 | 34.5272 | 34.5265 | 34.5229 | 32.6243 | 30.2892 | 27.9733 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7363 | 34.735 | 34.7317 | 34.7311 | 34.4558 | 32.4935 | 30.15 | 27.8258
|  | TRASH GREEN | CT |  |  | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8538 | 36.8511 | 36.8507 | 36.8485 | 36.8301 | 35.1538 | 33.1508 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5314 | 34.5288 | 34.5284 | 34.5261 | 32.9846 | 30.6431 | 28.3213 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.736 | 34.7334 | 34.7329 | 34.7307 | 32.8551 | 30.5052 | 28.1751
|  | TRASH GREEN | LW |  |  | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8541 | 36.8527 | 36.8495 | 36.8489 | 36.8453 | 36.8365 | 34.8505 | 32.8535 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5317 | 34.5304 | 34.5272 | 34.5265 | 34.5229 | 32.6243 | 30.2892 | 27.9733 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7363 | 34.735 | 34.7317 | 34.7311 | 34.4558 | 32.4935 | 30.15 | 27.8258
|  | TRASH GREEN | ST |  |  | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8545 | 36.8542 | 36.8532 | 36.8528 | 36.851 | 36.8488 | 36.8405 | 36.0314 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5322 | 34.5318 | 34.5309 | 34.5305 | 34.5287 | 34.5264 | 33.1388 | 31.6556 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7368 | 34.7364 | 34.7354 | 34.735 | 34.7332 | 34.5028 | 33.0098 | 31.5213
|  | TRASH GREEN | SP |  |  | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8547 | 36.8545 | 36.8537 | 36.8532 | 36.8512 | 36.8495 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5324 | 34.5323 | 34.5322 | 34.5314 | 34.5308 | 34.5289 | 34.5272 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7369 | 34.7367 | 34.7359 | 34.7354 | 34.7334 | 34.7317
MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN | MINIMUM HEADROOM | ST 84668 58036 | NO | 25.0761 | 25.0552 | 12.4023 | 11.1992 | 11.0976 | 10.9959 | 10.8904 | 10.7849 | 10.6794 | 10.6324 | 10.4906 | 10.2437 | 9.9965 | 9.452 | 24.534 | 24.513 | 11.86 | 10.6567 | 10.5549 | 10.4531 | 10.3471 | 10.2412 | 10.1353 | 10.0879 | 9.9446 | 9.6946 | 9.4441 | 8.6885 | 24.123 | 24.0951 | 11.4332 | 10.2121 | 10.0926 | 9.9727 | 9.8279 | 9.683 | 9.5381 | 9.4491 | 9.1761 | 8.6521 | 7.7678 | 6.7633
|  | TROWBRIDGE TOWN | CT |  |  | 25.1705 | 25.1575 | 12.5124 | 11.7892 | 11.7213 | 11.6532 | 11.585 | 11.5127 | 11.4371 | 11.4046 | 11.3061 | 10.3773 | 9.9965 | 9.452 | 24.6284 | 24.6153 | 11.9702 | 11.2468 | 11.1787 | 11.1104 | 11.042 | 10.9692 | 10.8932 | 10.8603 | 10.7603 | 9.8285 | 9.4441 | 8.6885 | 24.2174 | 24.1974 | 11.5433 | 10.8022 | 10.7164 | 10.63 | 10.5435 | 10.4318 | 10.3168 | 10.2422 | 10.0126 | 8.8067 | 7.7678 | 6.7633
|  | TROWBRIDGE TOWN | LW |  |  | 25.0761 | 25.0552 | 12.4023 | 11.1992 | 11.0976 | 10.9959 | 10.8904 | 10.7849 | 10.6794 | 10.6324 | 10.4906 | 10.2437 | 10.0669 | 9.494 | 24.534 | 24.513 | 11.86 | 10.6567 | 10.5549 | 10.4531 | 10.3471 | 10.2412 | 10.1353 | 10.0879 | 9.9446 | 9.6946 | 9.512 | 8.7169 | 24.123 | 24.0951 | 11.4332 | 10.2121 | 10.0926 | 9.9727 | 9.8279 | 9.683 | 9.5381 | 9.4491 | 9.1761 | 8.6521 | 7.7911 | 6.7908
|  | TROWBRIDGE TOWN | ST |  |  | 25.2661 | 25.2096 | 25.2008 | 24.7193 | 12.0465 | 12.0049 | 11.9619 | 11.9189 | 11.8747 | 11.8538 | 11.7904 | 11.6774 | 11.5917 | 11.4675 | 24.727 | 24.6675 | 24.6586 | 24.1771 | 11.5042 | 11.4624 | 11.4192 | 11.376 | 11.3315 | 11.3102 | 11.2459 | 11.1308 | 11.0428 | 10.9164 | 24.5796 | 24.2551 | 24.241 | 23.7511 | 11.0679 | 11.0138 | 10.9508 | 10.8877 | 10.8167 | 10.767 | 10.6146 | 10.3123 | 10.0146 | 9.4853
|  | TROWBRIDGE TOWN | SP |  |  | 25.314 | 25.262 | 25.2579 | 25.0177 | 24.9975 | 24.9771 | 24.9564 | 12.3042 | 12.2832 | 12.2733 | 12.2435 | 12.1905 | 12.1505 | 12.0903 | 24.7749 | 24.72 | 24.7159 | 24.4757 | 24.4554 | 24.435 | 24.4143 | 11.7619 | 11.7409 | 11.7309 | 11.7007 | 11.6469 | 11.6059 | 11.5446 | 24.6315 | 24.3147 | 24.3094 | 24.068 | 24.0446 | 24.0205 | 23.9942 | 11.3363 | 11.3084 | 11.2874 | 11.2233 | 11.0951 | 10.9644 | 10.8109
BRAMLEY (FLEE) | READING BSP | TWYFORD | MINIMUM HEADROOM | SU 78430 76339 | YES | 17.71 | 17.71 | 17.71 | 17.71 | 17.6395 | 17.5629 | 17.4789 | 17.3875 | 17.2406 | 17.2191 | 17.1357 | 16.9834 | 16.7043 | 16.2802 | 16.6817 | 16.5678 | 16.4202 | 16.1371 | 15.7833 | 15.4181 | 15.2311 | 15.0394 | 14.7904 | 14.6573 | 14.257 | 13.593 | 12.811 | 12.3128 | 17.2906 | 17.2156 | 17.1183 | 16.9317 | 16.6745 | 16.4077 | 16.2558 | 16.0983 | 15.8841 | 15.7891 | 15.4969 | 14.8509 | 14.0698 | 13.5725
|  | TWYFORD | CT |  |  | 17.71 | 17.71 | 17.71 | 17.71 | 17.7089 | 17.7068 | 17.7036 | 17.6991 | 17.6889 | 17.6871 | 17.6774 | 17.5975 | 17.3604 | 16.9265 | 16.6817 | 16.5678 | 16.4202 | 16.1371 | 15.8285 | 15.531 | 15.2823 | 15.1776 | 15.0653 | 14.9518 | 14.6254 | 14.0336 | 13.4404 | 12.9328 | 17.2906 | 17.2156 | 17.1183 | 16.9317 | 16.728 | 16.5311 | 16.3662 | 16.2956 | 16.2181 | 16.1427 | 15.8826 | 15.2917 | 14.6995 | 14.1929
|  | TWYFORD | LW |  |  | 17.71 | 17.71 | 17.71 | 17.71 | 17.6395 | 17.5629 | 17.4789 | 17.3875 | 17.2406 | 17.2191 | 17.1357 | 16.9834 | 16.7043 | 16.2802 | 16.6854 | 16.5743 | 16.4301 | 16.1542 | 15.7833 | 15.4181 | 15.2311 | 15.0394 | 14.7904 | 14.6573 | 14.257 | 13.593 | 12.811 | 12.3128 | 17.2931 | 17.2199 | 17.1248 | 16.943 | 16.6745 | 16.4077 | 16.2558 | 16.0983 | 15.8841 | 15.7891 | 15.4969 | 14.8509 | 14.0698 | 13.5725
|  | TWYFORD | ST |  |  | 17.71 | 17.71 | 17.71 | 17.71 | 17.7092 | 17.7077 | 17.7053 | 17.7018 | 17.694 | 17.6902 | 17.6701 | 17.6436 | 17.5507 | 17.517 | 16.7401 | 16.6742 | 16.5967 | 16.4767 | 16.3133 | 16.1318 | 16.046 | 15.9615 | 15.8841 | 15.8042 | 15.5689 | 15.1991 | 14.7807 | 14.4347 | 17.3291 | 17.2857 | 17.2346 | 17.1555 | 17.0476 | 16.9274 | 16.8701 | 16.8132 | 16.7595 | 16.7056 | 16.5436 | 16.2909 | 15.9835 | 15.692
|  | TWYFORD | SP |  |  | 17.71 | 17.71 | 17.71 | 17.71 | 17.707 | 17.704 | 17.701 | 17.6978 | 17.6928 | 17.6786 | 17.6301 | 17.6047 | 17.5152 | 17.4365 | 16.7903 | 16.7672 | 16.7438 | 16.7202 | 16.6535 | 16.5854 | 16.552 | 16.5195 | 16.4771 | 16.4332 | 16.3014 | 16.1445 | 15.9345 | 15.7468 | 17.3622 | 17.347 | 17.3316 | 17.316 | 17.271 | 17.2251 | 17.2021 | 17.1796 | 17.15 | 17.1162 | 17.0127 | 16.9007 | 16.7318 | 16.5812
COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET | MINIMUM HEADROOM | SP 52865 05849 | NO | 34.8892 | 34.8537 | 34.8405 | 34.1744 | 34.1136 | 34.0511 | 33.9772 | 33.9012 | 33.8175 | 33.7782 | 33.655 | 33.4381 | 33.2292 | 32.3557 | 30.4673 | 30.4366 | 30.4238 | 29.7587 | 29.6989 | 29.6373 | 29.5661 | 29.4929 | 29.4119 | 29.3754 | 29.2609 | 29.0586 | 27.9342 | 26.7193 | 31.0476 | 31.0368 | 31.026 | 30.3648 | 30.3089 | 30.2511 | 30.1913 | 30.1294 | 30.0596 | 30.0352 | 29.9565 | 29.0723 | 27.898 | 26.7452
|  | UNION STREET | CT |  |  | 34.9414 | 34.9102 | 34.9015 | 34.5001 | 34.4625 | 34.4245 | 34.3859 | 34.3373 | 34.2862 | 34.2573 | 34.1694 | 33.5829 | 33.2954 | 32.5241 | 30.5194 | 30.4931 | 30.4848 | 30.0843 | 30.0476 | 30.0104 | 29.9728 | 29.9269 | 29.8785 | 29.8525 | 29.7732 | 29.2013 | 28.1398 | 26.9169 | 31.0997 | 31.0932 | 31.0867 | 30.69 | 30.6569 | 30.6234 | 30.5895 | 30.5548 | 30.5176 | 30.5037 | 30.4602 | 29.3479 | 28.095 | 26.9343
|  | UNION STREET | LW |  |  | 34.8892 | 34.8537 | 34.8405 | 34.1744 | 34.1136 | 34.0511 | 33.9772 | 33.9012 | 33.8175 | 33.7782 | 33.655 | 33.4381 | 33.2292 | 32.3557 | 30.4673 | 30.4366 | 30.4238 | 29.7587 | 29.6989 | 29.6373 | 29.5661 | 29.4929 | 29.4119 | 29.3754 | 29.2609 | 29.0586 | 27.9342 | 26.7193 | 31.0476 | 31.0368 | 31.026 | 30.3648 | 30.3089 | 30.2511 | 30.1913 | 30.1294 | 30.0596 | 30.0352 | 29.9565 | 29.0723 | 27.898 | 26.7452
|  | UNION STREET | ST |  |  | 34.9679 | 34.9624 | 34.9336 | 34.6667 | 34.6385 | 34.6093 | 34.5757 | 34.5416 | 34.5017 | 34.4794 | 34.4085 | 34.2984 | 34.1659 | 34.0486 | 30.5459 | 30.5406 | 30.5166 | 30.2501 | 30.2226 | 30.1941 | 30.162 | 30.1293 | 30.0913 | 30.0709 | 30.0059 | 29.9055 | 29.7829 | 29.3628 | 31.1257 | 31.1213 | 31.117 | 30.8526 | 30.8275 | 30.802 | 30.776 | 30.7494 | 30.7191 | 30.7069 | 30.6661 | 30.606 | 30.0235 | 29.2892
|  | UNION STREET | SP |  |  | 34.9953 | 34.9929 | 34.9677 | 34.8352 | 34.8236 | 34.8118 | 34.7987 | 34.7855 | 34.7717 | 34.7628 | 34.7348 | 34.6914 | 34.6467 | 34.5923 | 30.573 | 30.5707 | 30.5499 | 30.4175 | 30.406 | 30.3944 | 30.3817 | 30.369 | 30.3557 | 30.3476 | 30.3219 | 30.2822 | 30.2411 | 30.1902 | 31.1517 | 31.1495 | 31.1474 | 31.0151 | 31.0043 | 30.9934 | 30.9825 | 30.9716 | 30.9606 | 30.9557 | 30.9393 | 30.915 | 30.8891 | 30.8527
EAST CLAYDON GSP | BICESTER NORTH | UPPER HEYFORD | MINIMUM HEADROOM | SP 51750 25667 | NO | 19.4411 | 19.4411 | 19.4411 | 19.4411 | 19.44 | 19.4378 | 19.4344 | 19.4297 | 19.4203 | 19.4187 | 19.4103 | 19.3901 | 18.7511 | 18.0314 | 17.7923 | 17.7923 | 17.7923 | 17.7923 | 17.7913 | 17.7891 | 17.571 | 17.4191 | 17.2668 | 17.1052 | 16.6255 | 15.8003 | 14.936 | 14.1018 | 17.54 | 17.5303 | 17.5175 | 17.4905 | 17.464 | 17.4375 | 17.411 | 17.2837 | 17.1407 | 16.9891 | 16.5391 | 15.7489 | 14.8863 | 14.0538
|  | UPPER HEYFORD | CT |  |  | 19.4411 | 19.4411 | 19.4411 | 19.4411 | 19.4407 | 19.4401 | 19.4393 | 19.438 | 19.4351 | 19.4346 | 19.4319 | 19.4094 | 18.7511 | 18.0314 | 17.7923 | 17.7923 | 17.7923 | 17.7923 | 17.792 | 17.7914 | 17.571 | 17.4191 | 17.2668 | 17.1052 | 16.6255 | 15.8003 | 14.936 | 14.1018 | 17.54 | 17.5303 | 17.5175 | 17.4905 | 17.464 | 17.4375 | 17.411 | 17.2837 | 17.1407 | 16.9891 | 16.5391 | 15.7489 | 14.8863 | 14.0538
|  | UPPER HEYFORD | LW |  |  | 19.4411 | 19.4411 | 19.4411 | 19.4411 | 19.44 | 19.4378 | 19.4344 | 19.4297 | 19.4203 | 19.4187 | 19.4103 | 19.3901 | 19.3506 | 18.6629 | 17.7923 | 17.7923 | 17.7923 | 17.7923 | 17.7913 | 17.7891 | 17.7857 | 17.781 | 17.7715 | 17.7699 | 17.3707 | 16.548 | 15.669 | 14.8395 | 17.5433 | 17.536 | 17.5264 | 17.506 | 17.4852 | 17.4635 | 17.4512 | 17.4376 | 17.4194 | 17.4083 | 17.2366 | 16.4638 | 15.6178 | 14.7898
|  | UPPER HEYFORD | ST |  |  | 19.4411 | 19.4411 | 19.4411 | 19.4411 | 19.4408 | 19.4404 | 19.4397 | 19.4387 | 19.4365 | 19.4355 | 19.4298 | 19.4224 | 19.3962 | 19.3867 | 17.7923 | 17.7923 | 17.7923 | 17.7923 | 17.7921 | 17.7916 | 17.791 | 17.79 | 17.7878 | 17.7867 | 17.7811 | 17.6886 | 17.1207 | 16.5738 | 17.5464 | 17.5414 | 17.5355 | 17.5254 | 17.5129 | 17.4975 | 17.4895 | 17.4812 | 17.473 | 17.4654 | 17.4409 | 17.402 | 17.0013 | 16.4879
|  | UPPER HEYFORD | SP |  |  | 19.4411 | 19.4411 | 19.4411 | 19.4411 | 19.441 | 19.441 | 19.441 | 19.441 | 19.4409 | 19.4405 | 19.4385 | 19.4368 | 19.429 | 19.4214 | 17.7923 | 17.7923 | 17.7923 | 17.7923 | 17.7923 | 17.7923 | 17.7923 | 17.7922 | 17.7921 | 17.7918 | 17.7897 | 17.7881 | 17.7803 | 17.7727 | 17.5519 | 17.5512 | 17.5505 | 17.5498 | 17.5467 | 17.543 | 17.5403 | 17.5376 | 17.5342 | 17.5313 | 17.5219 | 17.5083 | 17.4888 | 17.4699
IVER 132KV | UPTON BSP | UPTON | MINIMUM HEADROOM | TQ 00800 79434 | YES | 33.9334 | 33.9184 | 33.9035 | 32.992 | 32.9173 | 32.8426 | 32.7679 | 32.6932 | 32.6069 | 32.4446 | 31.855 | 30.5709 | 29.1567 | 27.6733 | 32.2248 | 32.1856 | 32.1631 | 31.2326 | 31.1061 | 30.9311 | 30.7987 | 30.6651 | 30.4154 | 30.1895 | 29.4728 | 27.9912 | 26.3465 | 24.6335 | 32.5215 | 32.5066 | 32.4916 | 31.5802 | 31.5055 | 31.4308 | 31.356 | 31.2813 | 31.2066 | 31.139 | 30.4306 | 28.9668 | 27.343 | 25.6506
|  | UPTON | CT |  |  | 34.0051 | 33.9961 | 33.9872 | 33.4403 | 33.3955 | 33.3506 | 33.3058 | 33.261 | 33.2162 | 33.1635 | 32.6351 | 30.8534 | 29.2982 | 27.8152 | 32.2979 | 32.2657 | 32.2505 | 31.6873 | 31.6285 | 31.5159 | 31.3886 | 31.285 | 31.1678 | 30.9601 | 30.2843 | 28.2983 | 26.5126 | 24.8001 | 32.5932 | 32.5843 | 32.5753 | 32.0284 | 31.9836 | 31.9388 | 31.894 | 31.8491 | 31.8043 | 31.7864 | 31.2399 | 29.2717 | 27.5068 | 25.815
|  | UPTON | LW |  |  | 33.9334 | 33.9184 | 33.9035 | 32.992 | 32.9173 | 32.8426 | 32.7679 | 32.6932 | 32.6069 | 32.4446 | 31.855 | 30.5709 | 29.1567 | 27.6733 | 32.2248 | 32.1856 | 32.1631 | 31.2326 | 31.1061 | 30.9311 | 30.7987 | 30.6651 | 30.4154 | 30.1895 | 29.4728 | 27.9912 | 26.3465 | 24.6335 | 32.5215 | 32.5066 | 32.4916 | 31.5802 | 31.5055 | 31.4308 | 31.356 | 31.2813 | 31.2066 | 31.139 | 30.4306 | 28.9668 | 27.343 | 25.6506
|  | UPTON | ST |  |  | 34.041 | 34.035 | 34.029 | 33.6644 | 33.6345 | 33.6047 | 33.5748 | 33.5449 | 33.515 | 33.503 | 33.4672 | 33.3728 | 32.5354 | 31.6259 | 32.3393 | 32.3327 | 32.3074 | 31.9393 | 31.9069 | 31.8751 | 31.8384 | 31.8016 | 31.7654 | 31.7468 | 31.6524 | 31.1695 | 30.1197 | 29.0634 | 32.6291 | 32.6231 | 32.6172 | 32.2526 | 32.2227 | 32.1928 | 32.1629 | 32.133 | 32.1031 | 32.0912 | 32.0553 | 31.9956 | 31.0806 | 30.0375
|  | UPTON | SP |  |  | 34.0768 | 34.0738 | 34.0708 | 33.8886 | 33.8736 | 33.8587 | 33.8437 | 33.8288 | 33.8138 | 33.8079 | 33.7899 | 33.7601 | 33.7421 | 33.7092 | 32.3748 | 32.3711 | 32.349 | 32.1647 | 32.1467 | 32.1288 | 32.1113 | 32.0936 | 32.0752 | 32.0667 | 32.0409 | 31.9936 | 31.8562 | 31.6821 | 32.665 | 32.662 | 32.659 | 32.4767 | 32.4618 | 32.4468 | 32.4319 | 32.4169 | 32.402 | 32.396 | 32.3781 | 32.3482 | 32.3303 | 32.2974
NURSLING GSP | VELMORE BSP | VELMORE | MINIMUM HEADROOM | SU 42935 19205 | YES | 47.5988 | 47.5867 | 47.5746 | 46.8373 | 46.7769 | 46.7164 | 46.656 | 46.5956 | 46.5351 | 46.5109 | 46.4384 | 46.3175 | 46.245 | 46.1121 | 36.3366 | 36.3246 | 36.3125 | 35.5751 | 35.5147 | 35.4543 | 35.3938 | 35.3334 | 35.2729 | 35.2488 | 35.1762 | 35.0554 | 34.9829 | 34.8499 | 37.3856 | 37.3406 | 37.3264 | 36.5848 | 36.5201 | 36.4555 | 36.3917 | 36.3278 | 36.264 | 36.2362 | 36.1526 | 36.0096 | 35.9068 | 35.7487
|  | VELMORE | CT |  |  | 47.6568 | 47.6496 | 47.6423 | 47.1999 | 47.1637 | 47.1274 | 47.0911 | 47.0549 | 47.0186 | 47.0041 | 46.9606 | 46.4317 | 46.245 | 46.1121 | 36.3947 | 36.3874 | 36.3802 | 35.9378 | 35.9015 | 35.8652 | 35.829 | 35.7927 | 35.7564 | 35.7419 | 35.6984 | 35.1695 | 34.9829 | 34.8499 | 37.4432 | 37.4028 | 37.3931 | 36.9455 | 36.9043 | 36.863 | 36.8218 | 36.7822 | 36.7425 | 36.7244 | 36.6698 | 36.1187 | 35.9068 | 35.7487
|  | VELMORE | LW |  |  | 47.5988 | 47.5867 | 47.5746 | 46.8373 | 46.7769 | 46.7164 | 46.656 | 46.5956 | 46.5351 | 46.5109 | 46.4384 | 46.3175 | 46.245 | 46.1121 | 36.3366 | 36.3246 | 36.3125 | 35.5751 | 35.5147 | 35.4543 | 35.3938 | 35.3334 | 35.2729 | 35.2488 | 35.1762 | 35.0554 | 34.9829 | 34.8499 | 37.3856 | 37.3406 | 37.3264 | 36.5848 | 36.5201 | 36.4555 | 36.3917 | 36.3278 | 36.264 | 36.2362 | 36.1526 | 36.0096 | 35.9118 | 35.7537
|  | VELMORE | ST |  |  | 47.6858 | 47.681 | 47.6762 | 47.3812 | 47.3571 | 47.3329 | 47.3087 | 47.2845 | 47.2604 | 47.2507 | 47.2217 | 47.1733 | 47.1443 | 47.0911 | 36.4237 | 36.4188 | 36.414 | 36.1191 | 36.0949 | 36.0707 | 36.0465 | 36.0224 | 35.9982 | 35.9885 | 35.9595 | 35.9112 | 35.8822 | 35.829 | 37.4738 | 37.4682 | 37.4311 | 37.1347 | 37.1088 | 37.0824 | 37.0558 | 37.0292 | 37.0028 | 36.9906 | 36.9541 | 36.8907 | 36.8453 | 36.776
|  | VELMORE | SP |  |  | 47.7149 | 47.7124 | 47.71 | 47.5626 | 47.5505 | 47.5384 | 47.5263 | 47.5142 | 47.5021 | 47.4973 | 47.4828 | 47.4586 | 47.4441 | 47.4175 | 36.4527 | 36.4503 | 36.4478 | 36.3004 | 36.2883 | 36.2762 | 36.2641 | 36.252 | 36.2399 | 36.2351 | 36.2206 | 36.1964 | 36.1819 | 36.1553 | 37.5034 | 37.5008 | 37.4669 | 37.3192 | 37.3064 | 37.2935 | 37.2804 | 37.2673 | 37.2539 | 37.2481 | 37.2308 | 37.2007 | 37.1794 | 37.1459
FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR | MINIMUM HEADROOM | SZ 56148 77857 | NO | 15.6719 | 15.6618 | 15.6532 | 15.6382 | 15.6142 | 15.585 | 15.5549 | 15.5271 | 15.4519 | 15.2717 | 14.9944 | 14.6274 | 14.2982 | 14.0349 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.4854 | 11.4649 | 11.4441 | 11.4225 | 11.2405 | 11.0277 | 10.7012 | 10.2746 | 9.8951 | 9.5857 | 10.1808 | 10.17 | 10.1609 | 9.9777 | 9.7686 | 9.5442 | 9.389 | 9.2134 | 9.0029 | 8.7963 | 8.479 | 8.0637 | 7.6936 | 7.3929
|  | VENTNOR | CT |  |  | 15.6727 | 15.6632 | 15.6553 | 15.6419 | 15.6142 | 15.585 | 15.5549 | 15.5271 | 15.4519 | 15.2717 | 14.9944 | 14.6274 | 14.2982 | 14.0349 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.4918 | 11.4779 | 11.4637 | 11.4489 | 11.2405 | 11.0277 | 10.7012 | 10.2746 | 9.8951 | 9.5857 | 10.1816 | 10.1715 | 10.1631 | 10.0259 | 9.8296 | 9.6177 | 9.3978 | 9.2147 | 9.0029 | 8.7963 | 8.479 | 8.0637 | 7.6936 | 7.3929
|  | VENTNOR | LW |  |  | 15.6719 | 15.6618 | 15.6532 | 15.6382 | 15.6161 | 15.5927 | 15.5743 | 15.554 | 15.4664 | 15.2876 | 15.0144 | 14.6825 | 14.3946 | 14.1429 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.499 | 11.4924 | 11.4854 | 11.4558 | 11.2501 | 11.0388 | 10.7163 | 10.3249 | 9.9866 | 9.6889 | 10.1808 | 10.17 | 10.1609 | 9.9777 | 9.7686 | 9.5442 | 9.389 | 9.2134 | 9.0135 | 8.8083 | 8.4951 | 8.1149 | 7.7861 | 7.497
|  | VENTNOR | ST |  |  | 15.6739 | 15.6691 | 15.6601 | 15.652 | 15.6219 | 15.5893 | 15.5603 | 15.5295 | 15.4863 | 15.4643 | 15.4117 | 15.1882 | 14.907 | 14.714 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.4854 | 11.4649 | 11.4441 | 11.4225 | 11.3891 | 11.3778 | 11.2401 | 10.9494 | 10.6356 | 10.4127 | 10.1828 | 10.1778 | 10.1682 | 10.1564 | 10.007 | 9.8291 | 9.7019 | 9.5607 | 9.4006 | 9.2496 | 9 | 8.717 | 8.4093 | 8.192
|  | VENTNOR | SP |  |  | 15.6772 | 15.6753 | 15.6733 | 15.6713 | 15.668 | 15.6642 | 15.6609 | 15.6573 | 15.6531 | 15.6488 | 15.6424 | 15.6348 | 15.6289 | 15.624 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 11.5055 | 10.1864 | 10.1843 | 10.1823 | 10.1801 | 10.1766 | 10.1726 | 10.1691 | 10.1652 | 10.1608 | 10.1152 | 10.0318 | 9.933 | 9.8572 | 9.7927
MANNINGTON GSP | MANNINGTON BSP | VERWOOD | MINIMUM HEADROOM | SU 07716 10226 | YES | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.7957 | 33.7782 | 33.7605 | 33.7426 | 33.7146 | 33.6367 | 33.3896 | 33.2719 | 32.9014 | 32.4359 | 25.7511 | 25.7372 | 25.7319 | 25.7204 | 25.7089 | 25.6972 | 25.6828 | 25.6616 | 25.6229 | 25.5467 | 25.2248 | 24.283 | 22.6414 | 20.9667 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6017 | 26.5841 | 26.5664 | 26.5485 | 26.5205 | 26.4426 | 26.1955 | 26.0778 | 25.6442 | 23.9166
|  | VERWOOD | CT |  |  | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 32.6707 | 25.7525 | 25.7395 | 25.7356 | 25.7269 | 25.7181 | 25.709 | 25.6999 | 25.6868 | 25.6717 | 25.6199 | 25.3425 | 24.5329 | 22.9098 | 21.2353 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 25.9211 | 24.1937
|  | VERWOOD | LW |  |  | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 32.4359 | 25.7511 | 25.7372 | 25.7319 | 25.7204 | 25.7089 | 25.6972 | 25.6843 | 25.6712 | 25.6229 | 25.5618 | 25.2248 | 24.283 | 22.6414 | 20.9667 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 25.6442 | 23.9166
|  | VERWOOD | ST |  |  | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.8092 | 33.8047 | 33.8001 | 33.7953 | 33.7879 | 33.7854 | 33.7774 | 33.7709 | 33.7525 | 33.7471 | 25.7519 | 25.7482 | 25.7347 | 25.7276 | 25.7144 | 25.6992 | 25.6852 | 25.6709 | 25.6532 | 25.6383 | 25.5101 | 25.0619 | 24.3151 | 23.2823 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6152 | 26.6106 | 26.606 | 26.6012 | 26.5938 | 26.5913 | 26.5833 | 26.5769 | 26.5584 | 26.3075
|  | VERWOOD | SP |  |  | 33.8137 | 33.8137 | 33.8137 | 33.8137 | 33.7957 | 33.7782 | 33.7605 | 33.7426 | 33.7146 | 33.6367 | 33.3896 | 33.2719 | 32.9014 | 32.5915 | 25.7557 | 25.7549 | 25.7449 | 25.7441 | 25.7239 | 25.7038 | 25.6828 | 25.6616 | 25.6289 | 25.5467 | 25.287 | 25.1458 | 24.7256 | 24.2988 | 26.6196 | 26.6196 | 26.6196 | 26.6196 | 26.6017 | 26.5841 | 26.5664 | 26.5485 | 26.5205 | 26.4426 | 26.1955 | 26.0778 | 25.7073 | 25.3974
COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD | MINIMUM HEADROOM | SU 59847 89486 | NO | 37.2183 | 37.0438 | 36.8098 | 36.4028 | 35.9488 | 35.4903 | 35.1687 | 34.9387 | 34.6853 | 34.4893 | 33.8836 | 32.5499 | 31.0451 | 29.6596 | 34.4668 | 34.2708 | 34.008 | 33.5508 | 33.0481 | 32.5406 | 32.1822 | 31.9302 | 31.6551 | 31.4362 | 30.7597 | 29.2798 | 27.5563 | 25.9282 | 33.611 | 33.4346 | 33.1981 | 32.7867 | 32.3284 | 31.8657 | 31.5408 | 31.309 | 31.0536 | 30.8557 | 30.2438 | 28.8974 | 27.378 | 25.9779
|  | WALLINGFORD | CT |  |  | 37.2275 | 37.0598 | 36.8347 | 36.4464 | 36.0229 | 35.5957 | 35.1687 | 34.9387 | 34.6853 | 34.4893 | 33.8836 | 32.5499 | 31.0451 | 29.6596 | 34.4772 | 34.2888 | 34.0359 | 33.5998 | 33.1299 | 32.6559 | 32.1822 | 31.9302 | 31.6551 | 31.4362 | 30.7597 | 29.2798 | 27.5563 | 25.9282 | 33.6203 | 33.4508 | 33.2233 | 32.8308 | 32.4032 | 31.972 | 31.5408 | 31.309 | 31.0536 | 30.8557 | 30.2438 | 28.8974 | 27.378 | 25.9779
|  | WALLINGFORD | LW |  |  | 37.2183 | 37.0438 | 36.8098 | 36.4028 | 35.9488 | 35.4903 | 35.2489 | 35.0036 | 34.7281 | 34.5282 | 33.9066 | 32.6487 | 31.1557 | 29.7959 | 34.4668 | 34.2708 | 34.008 | 33.5508 | 33.0481 | 32.5406 | 32.2774 | 32.0099 | 31.7128 | 31.4899 | 30.7976 | 29.3934 | 27.6886 | 26.0862 | 33.611 | 33.4346 | 33.1981 | 32.7867 | 32.3284 | 31.8657 | 31.6224 | 31.3752 | 31.0978 | 30.8958 | 30.2681 | 28.9974 | 27.4899 | 26.1156
|  | WALLINGFORD | ST |  |  | 37.267 | 37.1358 | 36.9767 | 36.753 | 36.4799 | 36.1477 | 36.0086 | 35.8689 | 35.7493 | 35.6222 | 35.2313 | 34.4204 | 33.5354 | 32.6706 | 34.5215 | 34.3741 | 34.1955 | 33.9442 | 33.6375 | 33.2643 | 33.108 | 32.9511 | 32.8167 | 32.674 | 32.2349 | 31.3241 | 30.33 | 29.3545 | 33.6602 | 33.5276 | 33.3668 | 33.1407 | 32.8647 | 32.5289 | 32.3882 | 32.247 | 32.1262 | 31.9977 | 31.6026 | 30.7831 | 29.8885 | 29.0143
|  | WALLINGFORD | SP |  |  | 37.3934 | 37.3613 | 37.3259 | 37.3086 | 37.2407 | 37.1591 | 37.1099 | 37.0606 | 37 | 36.9505 | 36.7987 | 36.4751 | 36.0988 | 35.7138 | 34.6635 | 34.6275 | 34.5877 | 34.5683 | 34.492 | 34.4003 | 34.3451 | 34.2897 | 34.2216 | 34.166 | 33.9955 | 33.6321 | 33.2094 | 32.7769 | 33.788 | 33.7556 | 33.7198 | 33.7023 | 33.6336 | 33.5511 | 33.5014 | 33.4516 | 33.3903 | 33.3403 | 33.1869 | 32.8598 | 32.4795 | 32.0903
COWLEY GSP | DRAYTON BSP | WANTAGE | MINIMUM HEADROOM | SU 41290 88304 | NO | 33.817 | 33.8053 | 33.7914 | 33.7664 | 33.7382 | 33.7033 | 33.6061 | 33.503 | 33.4008 | 33.2906 | 32.9528 | 32.3791 | 31.7846 | 31.1996 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9679 | 31.9675 | 31.9671 | 31.9666 | 31.966 | 31.9642 | 31.9586 | 31.956 | 31.9475 | 31.9405 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1955 | 32.1951 | 32.1947 | 32.1943 | 32.1937 | 32.1919 | 32.1863 | 32.1836 | 31.9199 | 31.2146
|  | WANTAGE | CT |  |  | 33.8194 | 33.809 | 33.7953 | 33.7664 | 33.7382 | 33.7101 | 33.6822 | 33.5791 | 33.4769 | 33.3667 | 33.0339 | 32.4599 | 31.8656 | 31.2809 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.0175 | 31.3127
|  | WANTAGE | LW |  |  | 33.8194 | 33.809 | 33.7953 | 33.7664 | 33.7382 | 33.7101 | 33.6061 | 33.503 | 33.4008 | 33.2906 | 32.9528 | 32.3791 | 31.7846 | 31.1996 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 31.9199 | 31.2146
|  | WANTAGE | ST |  |  | 33.817 | 33.8053 | 33.7914 | 33.7677 | 33.7385 | 33.7033 | 33.6558 | 33.609 | 33.5392 | 33.464 | 33.2445 | 32.8686 | 32.4855 | 32.1052 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1959
|  | WANTAGE | SP |  |  | 33.8314 | 33.8304 | 33.8293 | 33.8283 | 33.8235 | 33.8179 | 33.8068 | 33.7959 | 33.7817 | 33.7508 | 33.6604 | 33.5221 | 33.383 | 33.2519 | 31.9683 | 31.9683 | 31.9683 | 31.9683 | 31.9679 | 31.9675 | 31.9671 | 31.9666 | 31.966 | 31.9642 | 31.9586 | 31.956 | 31.9475 | 31.9405 | 32.1959 | 32.1959 | 32.1959 | 32.1959 | 32.1955 | 32.1951 | 32.1947 | 32.1943 | 32.1937 | 32.1919 | 32.1863 | 32.1836 | 32.1752 | 32.1682
MANNINGTON GSP | WAREHAM | WAREHAM TOWN | MINIMUM HEADROOM | SY 92036 87463 | YES | 15.3355 | 15.3355 | 15.3355 | 15.3355 | 15.1703 | 14.9967 | 14.812 | 14.6171 | 14.3144 | 14.2715 | 14.1165 | 13.4329 | 12.2669 | 11.5638 | 12.1828 | 12.179 | 12.1739 | 12.1639 | 11.9898 | 11.8069 | 11.6073 | 11.2677 | 10.8148 | 10.6104 | 9.966 | 8.8963 | 7.6281 | 6.809 | 12.2317 | 12.2279 | 12.2228 | 12.2128 | 12.0386 | 11.8557 | 11.6626 | 11.4593 | 11.1478 | 11.0955 | 10.5603 | 9.4648 | 8.1802 | 7.3608
|  | WAREHAM TOWN | CT |  |  | 15.3355 | 15.3355 | 15.3355 | 15.3355 | 15.3345 | 15.3328 | 15.3302 | 15.3264 | 15.3181 | 15.3166 | 15.3086 | 14.9416 | 14.1881 | 13.4989 | 12.1837 | 12.1804 | 12.1762 | 12.1679 | 12.1597 | 12.1504 | 12.1405 | 12.1229 | 11.9644 | 11.8014 | 11.3041 | 10.4227 | 9.5716 | 8.7665 | 12.2326 | 12.2293 | 12.2251 | 12.2168 | 12.2085 | 12.1992 | 12.1893 | 12.1771 | 12.16 | 12.1491 | 11.903 | 10.9959 | 10.1237 | 9.3183
|  | WAREHAM TOWN | LW |  |  | 15.3355 | 15.3355 | 15.3355 | 15.3355 | 15.1703 | 14.9967 | 14.812 | 14.6171 | 14.3144 | 14.2715 | 14.1165 | 13.4329 | 12.2669 | 11.5638 | 12.1828 | 12.179 | 12.1739 | 12.1639 | 11.9898 | 11.8069 | 11.6073 | 11.2677 | 10.8148 | 10.6104 | 9.966 | 8.8963 | 7.6281 | 6.809 | 12.2317 | 12.2279 | 12.2228 | 12.2128 | 12.0386 | 11.8557 | 11.6626 | 11.4593 | 11.1478 | 11.0955 | 10.5603 | 9.4648 | 8.1802 | 7.3608
|  | WAREHAM TOWN | ST |  |  | 15.3355 | 15.3355 | 15.3355 | 15.3355 | 15.3348 | 15.3335 | 15.3316 | 15.3287 | 15.3223 | 15.3192 | 15.3026 | 15.2808 | 15.0157 | 14.5547 | 12.1914 | 12.1807 | 12.1772 | 12.1714 | 12.1643 | 12.155 | 12.1462 | 12.1366 | 12.12 | 12.0066 | 11.6576 | 11.0878 | 10.5124 | 9.9914 | 12.2404 | 12.2297 | 12.2261 | 12.2203 | 12.2132 | 12.2038 | 12.1951 | 12.1854 | 12.173 | 12.1635 | 12.1275 | 11.6808 | 11.0896 | 10.553
|  | WAREHAM TOWN | SP |  |  | 15.3355 | 15.3355 | 15.3355 | 15.3355 | 15.3355 | 15.3354 | 15.3353 | 15.3352 | 15.3349 | 15.3339 | 15.3279 | 15.3231 | 15.3003 | 15.2781 | 12.1946 | 12.194 | 12.1857 | 12.1851 | 12.1837 | 12.182 | 12.1798 | 12.1775 | 12.1745 | 12.1709 | 12.1574 | 12.1404 | 12.1069 | 11.9831 | 12.2435 | 12.2429 | 12.2346 | 12.234 | 12.2326 | 12.2309 | 12.2287 | 12.2264 | 12.2234 | 12.2198 | 12.2063 | 12.1892 | 12.1557 | 12.1234
BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD | MINIMUM HEADROOM | SU 86960 71382 | YES | 14.7675 | 14.6744 | 14.2607 | 13.4197 | 13.1974 | 12.9677 | 12.7476 | 12.5225 | 12.2911 | 12.0796 | 11.5202 | 10.5788 | 9.6922 | 8.8824 | 16.4496 | 16.4384 | 16.4272 | 15.7443 | 15.6883 | 15.6323 | 15.5763 | 15.5204 | 15.415 | 15.1812 | 14.5637 | 13.5121 | 12.5414 | 11.6507 | 14.7487 | 14.6413 | 14.1543 | 13.2888 | 13.0374 | 12.7775 | 12.5288 | 12.2742 | 12.0122 | 11.7677 | 11.1224 | 10.0179 | 9.0068 | 8.0772
|  | WARFIELD | CT |  |  | 14.8004 | 14.6965 | 14.2674 | 13.6573 | 13.4165 | 13.1689 | 12.9516 | 12.749 | 12.54 | 12.3373 | 11.8049 | 10.5788 | 9.6922 | 8.8824 | 16.5033 | 16.4966 | 16.4899 | 16.0801 | 16.0465 | 16.0129 | 15.9794 | 15.87 | 15.6404 | 15.4154 | 14.825 | 13.5121 | 12.5414 | 11.6507 | 14.7779 | 14.6571 | 14.1543 | 13.5092 | 13.2323 | 12.9473 | 12.6981 | 12.4659 | 12.2263 | 11.9907 | 11.3724 | 10.0179 | 9.0068 | 8.0772
|  | WARFIELD | LW |  |  | 14.7675 | 14.6744 | 14.2607 | 13.4197 | 13.1974 | 12.9677 | 12.7476 | 12.5225 | 12.2911 | 12.0796 | 11.5202 | 10.6723 | 9.8912 | 9.0809 | 16.4496 | 16.4384 | 16.4272 | 15.7443 | 15.6883 | 15.6323 | 15.5763 | 15.5204 | 15.415 | 15.1812 | 14.5637 | 13.6291 | 12.7638 | 11.8727 | 14.7487 | 14.6413 | 14.1574 | 13.2888 | 13.0374 | 12.7775 | 12.5288 | 12.2742 | 12.0122 | 11.7677 | 11.1224 | 10.1461 | 9.2405 | 8.3104
|  | WARFIELD | ST |  |  | 14.9002 | 14.8579 | 14.8236 | 14.5067 | 14.4294 | 14.3426 | 14.2038 | 14.0622 | 13.9207 | 13.7825 | 13.4203 | 12.8822 | 12.3948 | 11.8983 | 16.5302 | 16.5257 | 16.5212 | 16.2481 | 16.2257 | 16.2033 | 16.1809 | 16.1585 | 16.1361 | 16.1271 | 16.1003 | 16.006 | 15.4644 | 14.9152 | 14.8905 | 14.8416 | 14.8021 | 14.4776 | 14.3906 | 14.2926 | 14.1335 | 13.9711 | 13.8089 | 13.6481 | 13.2274 | 12.6033 | 12.0355 | 11.4611
|  | WARFIELD | SP |  |  | 14.9345 | 14.9065 | 14.887 | 14.73 | 14.6843 | 14.6346 | 14.5797 | 14.5242 | 14.4577 | 14.4027 | 14.2589 | 14.0475 | 13.8653 | 13.6858 | 16.557 | 16.5548 | 16.5526 | 16.416 | 16.4048 | 16.3936 | 16.3824 | 16.3712 | 16.36 | 16.3555 | 16.3421 | 16.3197 | 16.3063 | 16.2816 | 14.9261 | 14.8935 | 14.8711 | 14.7105 | 14.6588 | 14.6024 | 14.5399 | 14.4766 | 14.4005 | 14.3367 | 14.1701 | 13.9257 | 13.7141 | 13.5075
MELKSHAM GSP | FROME BSP | WARMINSTER | MINIMUM HEADROOM | ST 84936 44551 | YES | 21.6376 | 21.6376 | 21.6376 | 21.6376 | 21.6336 | 21.6289 | 21.6231 | 21.6164 | 21.5798 | 21.4376 | 21.0277 | 20.3673 | 19.709 | 19.1117 | 14.781 | 14.6834 | 14.5547 | 14.334 | 14.1003 | 13.8452 | 13.6165 | 13.4432 | 13.2665 | 13.0985 | 12.6147 | 11.8361 | 11.0628 | 10.3562 | 14.7817 | 14.6843 | 14.556 | 14.336 | 14.1031 | 13.8487 | 13.6207 | 13.4479 | 13.2716 | 13.1041 | 12.6218 | 11.8456 | 11.0745 | 10.3701
|  | WARMINSTER | CT |  |  | 21.6376 | 21.6376 | 21.6376 | 21.6376 | 21.6374 | 21.637 | 21.6364 | 21.6355 | 21.5969 | 21.4562 | 21.0527 | 20.3945 | 19.7524 | 19.1526 | 14.781 | 14.6834 | 14.5547 | 14.334 | 14.1019 | 13.8506 | 13.6165 | 13.4484 | 13.2814 | 13.1149 | 12.6376 | 11.8611 | 11.1041 | 10.395 | 14.7817 | 14.6843 | 14.556 | 14.336 | 14.1046 | 13.8541 | 13.6207 | 13.4531 | 13.2866 | 13.1206 | 12.6447 | 11.8706 | 11.1158 | 10.4089
|  | WARMINSTER | LW |  |  | 21.6376 | 21.6376 | 21.6376 | 21.6376 | 21.6336 | 21.6289 | 21.6231 | 21.6164 | 21.5798 | 21.4376 | 21.0277 | 20.3673 | 19.709 | 19.1117 | 14.7813 | 14.684 | 14.5556 | 14.3356 | 14.1003 | 13.8452 | 13.6173 | 13.4432 | 13.2665 | 13.0985 | 12.6147 | 11.8361 | 11.0628 | 10.3562 | 14.782 | 14.685 | 14.557 | 14.3376 | 14.1031 | 13.8487 | 13.6215 | 13.4479 | 13.2716 | 13.1041 | 12.6218 | 11.8456 | 11.0745 | 10.3701
|  | WARMINSTER | ST |  |  | 21.6376 | 21.6376 | 21.6376 | 21.6376 | 21.6374 | 21.6371 | 21.6367 | 21.636 | 21.6346 | 21.6339 | 21.6302 | 21.2604 | 20.8397 | 20.4465 | 14.8135 | 14.7464 | 14.6654 | 14.5491 | 14.4059 | 14.231 | 14.0744 | 13.9547 | 13.841 | 13.7268 | 13.4002 | 12.8846 | 12.3896 | 11.9254 | 14.814 | 14.7472 | 14.6664 | 14.5505 | 14.4077 | 14.2333 | 14.0772 | 13.9579 | 13.8445 | 13.7307 | 13.405 | 12.891 | 12.3975 | 11.9347
|  | WARMINSTER | SP |  |  | 21.6376 | 21.6376 | 21.6376 | 21.6376 | 21.6349 | 21.6322 | 21.6296 | 21.6268 | 21.6226 | 21.6107 | 21.5723 | 21.5536 | 21.493 | 21.4416 | 14.9199 | 14.8277 | 14.7963 | 14.764 | 14.7072 | 14.642 | 14.5806 | 14.5363 | 14.482 | 14.426 | 14.2626 | 14.0479 | 13.8118 | 13.6028 | 14.9201 | 14.8282 | 14.797 | 14.7648 | 14.7081 | 14.6431 | 14.5818 | 14.5377 | 14.4835 | 14.4277 | 14.2646 | 14.0506 | 13.815 | 13.6064
LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE | MINIMUM HEADROOM | SU 67988 09282 | NO | 18.7895 | 18.7682 | 18.747 | 17.4519 | 17.3142 | 17.1722 | 17.025 | 16.8728 | 16.6896 | 16.6354 | 16.4597 | 15.8999 | 15.1051 | 14.379 | 17.4858 | 17.4636 | 17.4411 | 16.1433 | 16.003 | 15.8584 | 15.7047 | 15.546 | 15.3563 | 15.2077 | 14.667 | 13.7586 | 12.8336 | 11.9795 | 17.2178 | 17.1966 | 17.1753 | 15.8802 | 15.7425 | 15.6005 | 15.4534 | 15.3011 | 15.1179 | 15.0638 | 14.888 | 14.5794 | 14.2735 | 14.0284
|  | WATERLOOVILLE | CT |  |  | 18.8914 | 18.8786 | 18.8659 | 18.0888 | 17.9997 | 17.9093 | 17.8177 | 17.7236 | 17.6105 | 17.5783 | 17.4769 | 16.2069 | 15.234 | 14.4769 | 17.5877 | 17.574 | 17.56 | 16.7802 | 16.6885 | 16.5955 | 16.5013 | 16.4007 | 16.2812 | 16.221 | 15.7548 | 14.0805 | 12.9775 | 12.0923 | 17.3197 | 17.307 | 17.2942 | 16.5172 | 16.4281 | 16.3377 | 16.246 | 16.152 | 16.0388 | 16.0066 | 15.9053 | 14.8307 | 14.3466 | 14.0703
|  | WATERLOOVILLE | LW |  |  | 18.7895 | 18.7682 | 18.747 | 17.4519 | 17.3142 | 17.1722 | 17.025 | 16.8728 | 16.6896 | 16.6354 | 16.4597 | 15.8999 | 15.1051 | 14.379 | 17.4858 | 17.4636 | 17.4411 | 16.1433 | 16.003 | 15.8584 | 15.7047 | 15.546 | 15.3563 | 15.2077 | 14.667 | 13.7586 | 12.8336 | 11.9795 | 17.2178 | 17.1966 | 17.1753 | 15.8802 | 15.7425 | 15.6005 | 15.4534 | 15.3011 | 15.1179 | 15.0638 | 14.888 | 14.5794 | 14.2735 | 14.0284
|  | WATERLOOVILLE | ST |  |  | 18.9423 | 18.9338 | 18.9253 | 18.4073 | 18.3378 | 18.2672 | 18.1954 | 18.1216 | 18.0287 | 17.9937 | 17.8779 | 17.7321 | 17.37 | 16.8999 | 17.6391 | 17.63 | 17.6208 | 17.1016 | 17.0306 | 16.9582 | 16.8824 | 16.8049 | 16.7076 | 16.6678 | 16.4603 | 15.9159 | 15.2661 | 14.7127 | 17.3707 | 17.3622 | 17.3537 | 16.8356 | 16.7661 | 16.6955 | 16.6237 | 16.5499 | 16.457 | 16.422 | 16.3063 | 16.1605 | 15.9091 | 15.7517
|  | WATERLOOVILLE | SP |  |  | 18.9933 | 18.989 | 18.9848 | 18.7258 | 18.7024 | 18.6791 | 18.6557 | 18.6323 | 18.6075 | 18.5889 | 18.5284 | 18.4673 | 18.3749 | 18.2688 | 17.6907 | 17.6864 | 17.682 | 17.4229 | 17.3992 | 17.3754 | 17.3509 | 17.3263 | 17.3 | 17.2796 | 17.2138 | 17.1443 | 17.0438 | 16.868 | 17.4216 | 17.4174 | 17.4131 | 17.1541 | 17.1308 | 17.1074 | 17.0841 | 17.0606 | 17.0359 | 17.0172 | 16.9568 | 16.8956 | 16.8032 | 16.6972
COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON | MINIMUM HEADROOM | SU 69106 94287 | YES | 37.4269 | 37.4269 | 37.4269 | 37.4269 | 37.4247 | 37.4201 | 37.4128 | 37.4028 | 37.3827 | 37.3793 | 37.276 | 35.4951 | 34.5131 | 33.6518 | 35.7377 | 35.7377 | 35.7377 | 35.7377 | 35.7355 | 35.7309 | 35.7237 | 35.3062 | 34.7324 | 34.1189 | 32.2452 | 30.1731 | 29.0485 | 28.0449 | 36.16 | 36.16 | 36.16 | 36.16 | 36.1578 | 36.1532 | 36.146 | 36.136 | 36.1158 | 35.7348 | 33.8649 | 31.7968 | 30.6742 | 29.6726
|  | WATLINGTON | CT |  |  | 37.4269 | 37.4269 | 37.4269 | 37.4269 | 37.4262 | 37.4249 | 37.4231 | 37.4203 | 37.4142 | 37.4132 | 37.2786 | 35.4951 | 34.5414 | 33.6701 | 35.7377 | 35.7377 | 35.7377 | 35.7377 | 35.737 | 35.7358 | 35.7339 | 35.3062 | 34.7324 | 34.1189 | 32.2452 | 30.1731 | 29.0697 | 28.0562 | 36.16 | 36.16 | 36.16 | 36.16 | 36.1593 | 36.1581 | 36.1562 | 36.1534 | 36.1474 | 35.7348 | 33.8649 | 31.7968 | 30.6955 | 29.684
|  | WATLINGTON | LW |  |  | 37.4269 | 37.4269 | 37.4269 | 37.4269 | 37.4247 | 37.4201 | 37.4128 | 37.4028 | 37.3827 | 37.3793 | 37.276 | 35.4976 | 34.5131 | 33.6518 | 35.7377 | 35.7377 | 35.7377 | 35.7377 | 35.7355 | 35.7309 | 35.7237 | 35.339 | 34.7513 | 34.1355 | 32.2499 | 30.1828 | 29.0485 | 28.0449 | 36.16 | 36.16 | 36.16 | 36.16 | 36.1578 | 36.1532 | 36.146 | 36.136 | 36.1158 | 35.7513 | 33.8694 | 31.8064 | 30.6742 | 29.6726
|  | WATLINGTON | ST |  |  | 37.4269 | 37.4269 | 37.4269 | 37.4269 | 37.4264 | 37.4255 | 37.4241 | 37.422 | 37.4173 | 37.415 | 37.403 | 37.3871 | 37.3315 | 36.7627 | 35.7377 | 35.7377 | 35.7377 | 35.7377 | 35.7372 | 35.7363 | 35.7349 | 35.7328 | 35.7281 | 35.7259 | 34.5018 | 33.0626 | 32.3281 | 31.6595 | 36.16 | 36.16 | 36.16 | 36.16 | 36.1595 | 36.1586 | 36.1572 | 36.1551 | 36.1504 | 36.1482 | 36.1169 | 34.6805 | 33.9474 | 33.2801
|  | WATLINGTON | SP |  |  | 37.4269 | 37.4269 | 37.4269 | 37.4269 | 37.4269 | 37.4268 | 37.4268 | 37.4267 | 37.4265 | 37.4257 | 37.4214 | 37.4179 | 37.4013 | 37.3852 | 35.7377 | 35.7377 | 35.7377 | 35.7377 | 35.7377 | 35.7377 | 35.7376 | 35.7375 | 35.7373 | 35.7366 | 35.7322 | 35.7287 | 35.7121 | 35.696 | 36.16 | 36.16 | 36.16 | 36.16 | 36.16 | 36.16 | 36.1599 | 36.1598 | 36.1596 | 36.1588 | 36.1545 | 36.151 | 36.1344 | 36.1183
AMERSHAM | LOUDWATER BSP | WELL END | MINIMUM HEADROOM | SU 88511 87957 | YES | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.8522 | 17.4439 | 17.0425 | 16.9647 | 16.9621 | 16.9406 | 16.9343 | 16.8647 | 16.7931 | 16.704 | 16.6152 | 16.5275 | 16.4336 | 16.1564 | 15.6915 | 15.211 | 14.7388 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983
|  | WELL END | CT |  |  | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9291 | 17.5211 | 17.1196 | 16.9652 | 16.963 | 16.942 | 16.9369 | 16.911 | 16.8528 | 16.7946 | 16.7059 | 16.6182 | 16.5242 | 16.2472 | 15.782 | 15.3018 | 14.8295 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983
|  | WELL END | LW |  |  | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.8522 | 17.4439 | 17.0425 | 16.9647 | 16.9621 | 16.9406 | 16.9343 | 16.8647 | 16.7931 | 16.704 | 16.6152 | 16.5275 | 16.4336 | 16.1564 | 15.6915 | 15.211 | 14.7388 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983
|  | WELL END | ST |  |  | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9099 | 16.9649 | 16.9626 | 16.9599 | 16.9558 | 16.951 | 16.9453 | 16.9422 | 16.9391 | 16.9343 | 16.8731 | 16.6859 | 16.3756 | 16.0659 | 15.7594 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983
|  | WELL END | SP |  |  | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 17.9597 | 16.9672 | 16.9667 | 16.9662 | 16.9658 | 16.9648 | 16.9636 | 16.9627 | 16.9618 | 16.9607 | 16.9587 | 16.9529 | 16.9435 | 16.9344 | 16.83 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983 | 16.983
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END | MINIMUM HEADROOM | SU 57216 06147 | YES | 67.2811 | 67.2687 | 67.2563 | 66.4999 | 66.4367 | 66.3722 | 66.3063 | 66.2169 | 66.1072 | 66.0418 | 65.8513 | 64.369 | 62.4478 | 60.5455 | 65.8056 | 65.7858 | 65.7639 | 64.9888 | 64.9047 | 64.8173 | 64.7258 | 64.6295 | 64.527 | 64.4691 | 64.1915 | 62.2196 | 59.9989 | 57.8034 | 65.7611 | 65.7487 | 65.7363 | 64.9799 | 64.9167 | 64.8522 | 64.7862 | 64.7188 | 64.6458 | 64.6174 | 64.4474 | 62.3361 | 60.0905 | 57.8707
|  | WEST END | CT |  |  | 67.3406 | 67.3332 | 67.3258 | 66.8719 | 66.8344 | 66.7965 | 66.7582 | 66.7151 | 66.6378 | 66.5836 | 66.4293 | 64.7199 | 62.6986 | 60.7912 | 65.8662 | 65.8522 | 65.8363 | 65.3661 | 65.3099 | 65.2513 | 65.1918 | 65.1243 | 65.0542 | 65.0075 | 64.8045 | 62.6056 | 60.2848 | 58.0844 | 65.8206 | 65.8131 | 65.8057 | 65.3519 | 65.3143 | 65.2764 | 65.2382 | 65.1995 | 65.159 | 65.1435 | 65.0221 | 62.7251 | 60.3794 | 58.1547
|  | WEST END | LW |  |  | 67.2811 | 67.2687 | 67.2563 | 66.4999 | 66.4367 | 66.3722 | 66.3063 | 66.2169 | 66.1072 | 66.0418 | 65.8513 | 64.369 | 62.4478 | 60.5455 | 65.8056 | 65.7858 | 65.7639 | 64.9888 | 64.9047 | 64.8173 | 64.7258 | 64.6295 | 64.527 | 64.4691 | 64.1915 | 62.2196 | 59.9989 | 57.8034 | 65.7611 | 65.7487 | 65.7363 | 64.9799 | 64.9167 | 64.8522 | 64.7862 | 64.7188 | 64.6458 | 64.6174 | 64.4474 | 62.3361 | 60.0905 | 57.8707
|  | WEST END | ST |  |  | 67.3704 | 67.3654 | 67.3605 | 67.0579 | 67.0329 | 67.0076 | 66.982 | 66.956 | 66.9287 | 66.9079 | 66.7978 | 66.6381 | 66.0784 | 64.8779 | 65.8975 | 65.8876 | 65.8768 | 65.5647 | 65.5267 | 65.4853 | 65.4429 | 65.398 | 65.3507 | 65.3181 | 65.2223 | 65.0163 | 64.071 | 62.6817 | 65.8503 | 65.8454 | 65.8404 | 65.5379 | 65.5128 | 65.4875 | 65.4619 | 65.436 | 65.4086 | 65.3975 | 65.3612 | 65.2305 | 64.1994 | 62.7944
|  | WEST END | SP |  |  | 67.4002 | 67.3977 | 67.3952 | 67.2439 | 67.2309 | 67.2179 | 67.2049 | 67.1918 | 67.1784 | 67.1704 | 67.145 | 67.1144 | 67.0677 | 66.9824 | 65.9314 | 65.9274 | 65.9233 | 65.7701 | 65.7527 | 65.7345 | 65.7154 | 65.6955 | 65.6742 | 65.6578 | 65.609 | 65.5461 | 65.4781 | 65.4004 | 65.8801 | 65.8776 | 65.8751 | 65.7239 | 65.7109 | 65.6979 | 65.6848 | 65.6718 | 65.6584 | 65.6504 | 65.6249 | 65.5943 | 65.5581 | 65.5117
MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE | MINIMUM HEADROOM | SU 24639 60279 | YES | 12.2564 | 12.1184 | 12.0616 | 11.9557 | 11.8104 | 11.6629 | 11.5143 | 11.4041 | 11.2665 | 11.1914 | 10.9643 | 10.4579 | 9.9279 | 9.5571 | 9.0212 | 8.9269 | 8.9215 | 8.9116 | 8.8597 | 8.7704 | 8.6053 | 8.485 | 8.3377 | 8.2522 | 7.9943 | 7.4373 | 6.8563 | 6.4353 | 9.1451 | 9.0554 | 9.0554 | 9.0503 | 9.0011 | 8.9505 | 8.8984 | 8.846 | 8.7652 | 8.7507 | 8.6897 | 8.1284 | 7.5429 | 7.1177
|  | WEST GRAFTON VILLAGE | CT |  |  | 12.2564 | 12.1184 | 12.0616 | 11.9557 | 11.8104 | 11.6629 | 11.5143 | 11.4041 | 11.2665 | 11.1914 | 10.9643 | 10.4579 | 9.9279 | 9.5571 | 9.0212 | 8.9269 | 8.9215 | 8.9116 | 8.8597 | 8.7704 | 8.6053 | 8.485 | 8.3377 | 8.2522 | 7.9943 | 7.4373 | 6.8563 | 6.4353 | 9.1451 | 9.0554 | 9.0554 | 9.0503 | 9.0011 | 8.9505 | 8.8984 | 8.846 | 8.7652 | 8.7507 | 8.6897 | 8.1284 | 7.5429 | 7.1177
|  | WEST GRAFTON VILLAGE | LW |  |  | 12.2639 | 12.1316 | 12.0826 | 11.9925 | 11.9018 | 11.8072 | 11.7351 | 11.6601 | 11.5734 | 11.5039 | 11.2895 | 10.9191 | 10.4926 | 10.173 | 9.022 | 8.9281 | 8.9235 | 8.915 | 8.904 | 8.8897 | 8.8433 | 8.7584 | 8.6619 | 8.582 | 8.3368 | 7.9158 | 7.4382 | 7.0685 | 9.1451 | 9.0554 | 9.0554 | 9.0527 | 9.044 | 9.0322 | 9.0187 | 9.0016 | 8.9716 | 8.9628 | 8.9272 | 8.6083 | 8.1264 | 7.7523
|  | WEST GRAFTON VILLAGE | ST |  |  | 12.2797 | 12.2509 | 12.2217 | 12.1802 | 12.0902 | 11.9873 | 11.8999 | 11.8111 | 11.7026 | 11.6347 | 11.4238 | 11.1405 | 10.709 | 10.4341 | 9.0235 | 9.0207 | 9.0179 | 9.0139 | 8.9716 | 8.9271 | 8.8827 | 8.8362 | 8.7653 | 8.7376 | 8.5177 | 8.2007 | 7.7364 | 7.4288 | 9.1451 | 9.1451 | 9.1451 | 9.1451 | 9.1077 | 9.0652 | 9.0221 | 8.9769 | 8.9071 | 8.8806 | 8.7904 | 8.703 | 8.4315 | 8.1212
|  | WEST GRAFTON VILLAGE | SP |  |  | 12.3031 | 12.2937 | 12.2873 | 12.2842 | 12.2699 | 12.2523 | 12.2361 | 12.2199 | 12.1997 | 12.182 | 12.1263 | 12.0422 | 11.9467 | 11.8561 | 9.0257 | 9.0248 | 9.0242 | 9.0239 | 9.0225 | 9.0208 | 9.0192 | 9.0175 | 9.0153 | 9.0128 | 9.0025 | 8.9905 | 8.9622 | 8.9348 | 9.1451 | 9.1451 | 9.1451 | 9.1451 | 9.1451 | 9.1451 | 9.145 | 9.1449 | 9.1446 | 9.1436 | 9.138 | 9.129 | 9.1026 | 9.0771
AXMINSTER | YEOVIL BSP | WEST HENDFORD | MINIMUM HEADROOM | ST 55000 15442 | YES | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.5176 | 29.4018 | 29.2842 | 29.1567 | 28.9542 | 28.9178 | 28.8058 | 28.33 | 27.2105 | 26.3892 | 27.7298 | 27.7205 | 27.7083 | 27.684 | 27.5468 | 27.4077 | 27.2667 | 27.1327 | 26.9328 | 26.8988 | 26.7936 | 26.1652 | 24.9137 | 23.9638 | 28.765 | 28.765 | 28.765 | 28.765 | 28.6393 | 28.4995 | 28.3577 | 28.2234 | 28.0232 | 27.9889 | 27.5874 | 26.3924 | 25.1407 | 24.1905
|  | WEST HENDFORD | CT |  |  | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.5176 | 29.4018 | 29.2842 | 29.1567 | 28.9542 | 28.9178 | 28.8058 | 28.33 | 27.2105 | 26.3892 | 27.7298 | 27.7205 | 27.7083 | 27.684 | 27.5468 | 27.4077 | 27.2667 | 27.1327 | 26.9328 | 26.8988 | 26.7936 | 26.1652 | 24.9137 | 23.9638 | 28.765 | 28.765 | 28.765 | 28.765 | 28.6393 | 28.4995 | 28.3577 | 28.2234 | 28.0232 | 27.9889 | 27.5874 | 26.3924 | 25.1407 | 24.1905
|  | WEST HENDFORD | LW |  |  | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6152 | 29.5984 | 29.581 | 29.5628 | 29.5353 | 29.5314 | 29.4835 | 29.4053 | 28.9061 | 28.1869 | 27.7311 | 27.7228 | 27.7118 | 27.6902 | 27.6532 | 27.6157 | 27.5876 | 27.5584 | 27.5204 | 27.5066 | 27.4654 | 27.3987 | 26.6748 | 25.8268 | 28.765 | 28.765 | 28.765 | 28.765 | 28.746 | 28.7078 | 28.6794 | 28.6499 | 28.6116 | 28.5974 | 28.5554 | 27.8065 | 26.9019 | 26.0537
|  | WEST HENDFORD | ST |  |  | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6225 | 29.5832 | 29.545 | 27.7341 | 27.7285 | 27.7217 | 27.7107 | 27.6977 | 27.6823 | 27.6734 | 27.6642 | 27.6571 | 27.6502 | 27.6311 | 27.5994 | 27.5678 | 27.5369 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.7568 | 28.7495 | 28.7424 | 28.7227 | 28.69 | 28.5902 | 28.0427
|  | WEST HENDFORD | SP |  |  | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 29.6314 | 27.7394 | 27.7379 | 27.7364 | 27.7347 | 27.7309 | 27.7265 | 27.7232 | 27.7199 | 27.716 | 27.7134 | 27.706 | 27.6937 | 27.6816 | 27.67 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.765 | 28.7628
MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR | MINIMUM HEADROOM | ST 77699 22040 | YES | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 33.9093 | 32.58 | 31.256 | 26.6134 | 26.612 | 26.6097 | 26.6053 | 26.6016 | 26.5971 | 26.5869 | 26.5773 | 26.565 | 26.5455 | 26.4724 | 26.0435 | 25.376 | 24.0432 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5116 | 26.4985 | 26.4848 | 26.4701 | 26.4275 | 26.2455 | 24.7927 | 23.2303
|  | WEST STOUR | CT |  |  | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.0295 | 32.7004 | 31.3767 | 26.6135 | 26.6122 | 26.61 | 26.6059 | 26.6024 | 26.5981 | 26.5932 | 26.5836 | 26.5735 | 26.5568 | 26.5006 | 26.1039 | 25.4364 | 24.1719 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.507 | 26.4934 | 26.4786 | 26.4361 | 26.3392 | 24.9348 | 23.3727
|  | WEST STOUR | LW |  |  | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 33.9093 | 32.58 | 31.256 | 26.6134 | 26.612 | 26.6097 | 26.6053 | 26.6016 | 26.5971 | 26.5869 | 26.5773 | 26.565 | 26.5455 | 26.4724 | 26.0435 | 25.376 | 24.0432 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5116 | 26.4985 | 26.4848 | 26.4701 | 26.4275 | 26.2455 | 24.7927 | 23.2303
|  | WEST STOUR | ST |  |  | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 33.919 | 33.0708 | 26.6138 | 26.6129 | 26.6113 | 26.6089 | 26.6065 | 26.6031 | 26.5951 | 26.5874 | 26.5806 | 26.5732 | 26.5373 | 26.4028 | 26.0484 | 25.6224 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5123 | 26.503 | 26.4929 | 26.4639 | 26.4075 | 26.2531 | 25.3671
|  | WEST STOUR | SP |  |  | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 34.7212 | 26.6148 | 26.6146 | 26.6141 | 26.6135 | 26.6128 | 26.6118 | 26.6092 | 26.6067 | 26.6036 | 26.6007 | 26.5924 | 26.5759 | 26.5458 | 26.5104 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.5133 | 26.4966 | 26.4703 | 26.4434
MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE | MINIMUM HEADROOM | SZ 07642 91485 | YES | 10.674 | 10.674 | 10.674 | 10.674 | 10.6686 | 10.662 | 10.6541 | 10.6449 | 10.6287 | 10.6261 | 10.6149 | 10.5908 | 10.544 | 10.5408 | 8.5161 | 8.485 | 8.4441 | 8.3576 | 8.2734 | 8.1897 | 8.1066 | 8.0465 | 7.9855 | 7.922 | 7.7293 | 7.4014 | 7.0417 | 6.731 | 8.6549 | 8.6549 | 8.6549 | 8.6549 | 8.6495 | 8.5742 | 8.4959 | 8.4374 | 8.3779 | 8.316 | 8.1269 | 7.8069 | 7.4553 | 7.1526
|  | WESTBOURNE | CT |  |  | 10.674 | 10.674 | 10.674 | 10.674 | 10.6737 | 10.6731 | 10.6723 | 10.6711 | 10.6685 | 10.668 | 10.6655 | 10.6447 | 10.6214 | 10.6143 | 8.5161 | 8.485 | 8.4441 | 8.3576 | 8.2734 | 8.1897 | 8.1066 | 8.0465 | 7.9855 | 7.922 | 7.7339 | 7.4093 | 7.0732 | 6.7593 | 8.6549 | 8.6549 | 8.6549 | 8.6549 | 8.6518 | 8.5742 | 8.4959 | 8.4374 | 8.3779 | 8.316 | 8.1327 | 7.816 | 7.488 | 7.182
|  | WESTBOURNE | LW |  |  | 10.674 | 10.674 | 10.674 | 10.674 | 10.6686 | 10.662 | 10.6541 | 10.6449 | 10.6287 | 10.6261 | 10.6149 | 10.5908 | 10.544 | 10.5408 | 8.519 | 8.4898 | 8.4515 | 8.3704 | 8.2864 | 8.202 | 8.1346 | 8.0663 | 7.9917 | 7.9262 | 7.7293 | 7.4014 | 7.0417 | 6.731 | 8.6549 | 8.6549 | 8.6549 | 8.6549 | 8.6495 | 8.5848 | 8.5217 | 8.4559 | 8.3828 | 8.319 | 8.1269 | 7.8069 | 7.4553 | 7.1526
|  | WESTBOURNE | ST |  |  | 10.674 | 10.674 | 10.674 | 10.674 | 10.6738 | 10.6734 | 10.6727 | 10.6718 | 10.6698 | 10.6688 | 10.6636 | 10.6567 | 10.6325 | 10.6237 | 8.5288 | 8.5074 | 8.4823 | 8.4391 | 8.386 | 8.3217 | 8.2863 | 8.2509 | 8.2089 | 8.1649 | 8.0345 | 7.8255 | 7.5999 | 7.3907 | 8.6549 | 8.6549 | 8.6549 | 8.6549 | 8.6547 | 8.6543 | 8.6537 | 8.6308 | 8.5917 | 8.5509 | 8.4255 | 8.2217 | 8.0014 | 7.7974
|  | WESTBOURNE | SP |  |  | 10.674 | 10.674 | 10.674 | 10.674 | 10.674 | 10.6739 | 10.6739 | 10.6739 | 10.6738 | 10.6735 | 10.6716 | 10.6701 | 10.6629 | 10.6558 | 8.5529 | 8.5498 | 8.5469 | 8.5441 | 8.5309 | 8.5152 | 8.5032 | 8.4912 | 8.4758 | 8.4587 | 8.4083 | 8.3301 | 8.2503 | 8.1746 | 8.6549 | 8.6549 | 8.6549 | 8.6549 | 8.6549 | 8.6549 | 8.6548 | 8.6548 | 8.6547 | 8.6544 | 8.6525 | 8.651 | 8.6296 | 8.5589
MELKSHAM GSP | FROME BSP | WESTBURY | MINIMUM HEADROOM | ST 87654 51530 | YES | 67.0326 | 67.0309 | 67.0269 | 67.0195 | 66.9427 | 66.8631 | 66.7777 | 66.6883 | 66.5579 | 66.5271 | 66.4207 | 66.2856 | 65.8421 | 65.2726 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.5959 | 55.5248 | 55.4505 | 55.3736 | 55.2567 | 55.2405 | 55.1849 | 55.1019 | 54.9407 | 54.8028 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.5693 | 59.4982 | 59.4239 | 59.3469 | 59.23 | 59.2138 | 59.1583 | 59.0753 | 58.7809 | 58.1592
|  | WESTBURY | CT |  |  | 67.0328 | 67.0313 | 67.0275 | 67.0205 | 67.013 | 67.005 | 66.9966 | 66.9842 | 66.9707 | 66.9561 | 66.9052 | 66.8532 | 66.623 | 66.0658 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6055 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.5671 | 58.9577
|  | WESTBURY | LW |  |  | 67.0326 | 67.0309 | 67.0269 | 67.0195 | 66.9427 | 66.8631 | 66.7777 | 66.6883 | 66.5579 | 66.5271 | 66.4207 | 66.2856 | 65.8421 | 65.2726 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.5959 | 55.5248 | 55.4505 | 55.3736 | 55.2567 | 55.2405 | 55.1849 | 55.1019 | 54.9407 | 54.8028 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.5693 | 59.4982 | 59.4239 | 59.3469 | 59.23 | 59.2138 | 59.1583 | 59.0753 | 58.7809 | 58.1592
|  | WESTBURY | ST |  |  | 67.033 | 67.0317 | 67.0289 | 67.0243 | 67.0188 | 67.0123 | 67.0047 | 66.9964 | 66.9873 | 66.9773 | 66.9415 | 66.9057 | 66.8749 | 66.8453 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382
|  | WESTBURY | SP |  |  | 67.0344 | 67.0342 | 67.0332 | 67.0318 | 67.0298 | 67.0276 | 67.0248 | 67.0217 | 67.018 | 67.0141 | 67 | 66.9858 | 66.9733 | 66.9613 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 55.6648 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382 | 59.6382
NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE | MINIMUM HEADROOM | SU 41618 12009 | YES | 11.8033 | 11.7432 | 11.7384 | 11.7283 | 11.6423 | 11.5512 | 11.414 | 11.2698 | 11.0684 | 10.9949 | 10.7581 | 10.3563 | 9.7812 | 9.5082 | 8.3592 | 8.2867 | 8.2809 | 8.2687 | 8.1807 | 8.0875 | 7.9405 | 7.7865 | 7.5754 | 7.4914 | 7.2236 | 6.7709 | 6.1431 | 5.8184 | 8.5744 | 8.5123 | 8.5074 | 8.4969 | 8.4106 | 8.3191 | 8.1804 | 8.0347 | 7.8317 | 7.7566 | 7.5148 | 7.105 | 6.5215 | 6.2393
|  | WESTERN ESPLANADE | CT |  |  | 11.8033 | 11.7432 | 11.7384 | 11.7283 | 11.7153 | 11.7016 | 11.6872 | 11.6323 | 11.5701 | 11.5166 | 11.3543 | 11.0178 | 10.6591 | 10.3755 | 8.3592 | 8.2867 | 8.2809 | 8.2687 | 8.2537 | 8.238 | 8.2216 | 8.1568 | 8.0849 | 8.0209 | 7.8277 | 7.4403 | 7.0289 | 6.6935 | 8.5744 | 8.5123 | 8.5074 | 8.4969 | 8.4836 | 8.4696 | 8.4549 | 8.3984 | 8.3347 | 8.2795 | 8.1123 | 7.7678 | 7.4007 | 7.1088
|  | WESTERN ESPLANADE | LW |  |  | 11.8033 | 11.7432 | 11.7384 | 11.7283 | 11.6423 | 11.5512 | 11.414 | 11.2698 | 11.0684 | 10.9949 | 10.7581 | 10.3563 | 9.7812 | 9.5082 | 8.3592 | 8.2867 | 8.2809 | 8.2687 | 8.1807 | 8.0875 | 7.9405 | 7.7865 | 7.5754 | 7.4914 | 7.2236 | 6.7709 | 6.1431 | 5.8184 | 8.5744 | 8.5123 | 8.5074 | 8.4969 | 8.4106 | 8.3191 | 8.1804 | 8.0347 | 7.8317 | 7.7566 | 7.5148 | 7.105 | 6.5215 | 6.2393
|  | WESTERN ESPLANADE | ST |  |  | 11.8051 | 11.8029 | 11.7437 | 11.7392 | 11.7294 | 11.7179 | 11.6861 | 11.6534 | 11.6079 | 11.5677 | 11.4422 | 11.2493 | 10.989 | 10.7909 | 8.3613 | 8.3586 | 8.2873 | 8.2818 | 8.2709 | 8.258 | 8.2209 | 8.1829 | 8.1307 | 8.0834 | 7.937 | 7.7102 | 7.4159 | 7.1842 | 8.5762 | 8.5739 | 8.5128 | 8.5081 | 8.4982 | 8.4864 | 8.4538 | 8.4203 | 8.3737 | 8.3324 | 8.2036 | 8.0053 | 7.7396 | 7.5362
|  | WESTERN ESPLANADE | SP |  |  | 11.8076 | 11.8072 | 11.7504 | 11.75 | 11.747 | 11.7437 | 11.734 | 11.7244 | 11.7113 | 11.6903 | 11.6247 | 11.5476 | 11.4347 | 11.331 | 8.3642 | 8.3638 | 8.2953 | 8.2949 | 8.2915 | 8.2879 | 8.2765 | 8.2652 | 8.25 | 8.2262 | 8.1525 | 8.0626 | 7.9374 | 7.8221 | 8.5787 | 8.5784 | 8.5197 | 8.5193 | 8.5163 | 8.5129 | 8.5029 | 8.4931 | 8.4796 | 8.4582 | 8.3913 | 8.3121 | 8.1973 | 8.0918
BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON | MINIMUM HEADROOM | SU 45207 09912 | YES | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 35.925 | 34.2174 | 32.4815 | 34.0608 | 34.0563 | 34.0505 | 34.0387 | 34.026 | 34.0129 | 34.005 | 33.9969 | 33.9884 | 33.9793 | 33.9513 | 32.49 | 30.5283 | 28.5425 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 33.4089 | 31.4384 | 29.4249
|  | WESTON | CT |  |  | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 35.925 | 34.2174 | 32.4815 | 34.0613 | 34.0572 | 34.0518 | 34.041 | 34.0293 | 34.0172 | 34.005 | 33.9969 | 33.9884 | 33.9793 | 33.9513 | 32.49 | 30.5283 | 28.5425 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 33.4089 | 31.4384 | 29.4249
|  | WESTON | LW |  |  | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 35.9309 | 34.2235 | 32.4877 | 34.0608 | 34.0563 | 34.0505 | 34.0387 | 34.026 | 34.0129 | 34.0053 | 33.9973 | 33.9888 | 33.9797 | 33.9516 | 32.4972 | 30.5353 | 28.5496 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 33.4162 | 31.4454 | 29.4322
|  | WESTON | ST |  |  | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6079 | 35.5874 | 34.4913 | 34.0615 | 34.0578 | 34.0533 | 34.046 | 34.0363 | 34.0246 | 34.015 | 34.0052 | 33.9995 | 33.9933 | 33.9738 | 33.3977 | 32.0956 | 30.8417 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 33.0128 | 31.7532
|  | WESTON | SP |  |  | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 36.6281 | 34.0654 | 34.0647 | 34.064 | 34.0633 | 34.0608 | 34.0579 | 34.0545 | 34.051 | 34.0467 | 34.0443 | 34.0367 | 34.0149 | 33.984 | 33.9508 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413 | 34.2413
CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH | MINIMUM HEADROOM | SY 67443 79096 | YES | 33.944 | 33.883 | 33.8106 | 33.669 | 33.535 | 33.3995 | 33.2033 | 33.0044 | 32.7926 | 32.5921 | 31.9911 | 30.9828 | 29.8958 | 28.9411 | 32.3539 | 32.2841 | 32.2013 | 32.0393 | 31.8864 | 31.7325 | 31.5095 | 31.284 | 31.046 | 30.8173 | 30.1336 | 28.9892 | 27.7464 | 26.6343 | 32.4324 | 32.3657 | 32.2865 | 32.1316 | 31.9853 | 31.8378 | 31.6243 | 31.408 | 31.1791 | 30.9603 | 30.3054 | 29.2086 | 28.0312 | 26.9589
|  | WEYMOUTH | CT |  |  | 33.9642 | 33.9179 | 33.8646 | 33.7637 | 33.6712 | 33.5796 | 33.4874 | 33.2991 | 33.1078 | 32.9109 | 32.3273 | 31.3118 | 30.2696 | 29.2995 | 32.377 | 32.324 | 32.2631 | 32.1476 | 32.042 | 31.9374 | 31.8324 | 31.6175 | 31.4 | 31.1749 | 30.5085 | 29.3569 | 28.165 | 27.0376 | 32.4545 | 32.4038 | 32.3456 | 32.2352 | 32.1342 | 32.0341 | 31.9335 | 31.7279 | 31.5196 | 31.3043 | 30.6669 | 29.5628 | 28.4303 | 27.3575
|  | WEYMOUTH | LW |  |  | 33.944 | 33.883 | 33.8106 | 33.669 | 33.535 | 33.3995 | 33.2033 | 33.0044 | 32.7926 | 32.5921 | 31.9911 | 30.9828 | 29.8958 | 28.9411 | 32.3539 | 32.2841 | 32.2013 | 32.0393 | 31.8864 | 31.7325 | 31.5095 | 31.284 | 31.046 | 30.8173 | 30.1336 | 28.9892 | 27.7464 | 26.6343 | 32.4324 | 32.3657 | 32.2865 | 32.1316 | 31.9853 | 31.8378 | 31.6243 | 31.408 | 31.1791 | 30.9603 | 30.3054 | 29.2086 | 28.0312 | 26.9589
|  | WEYMOUTH | ST |  |  | 34.151 | 33.9154 | 33.8665 | 33.7879 | 33.6973 | 33.5887 | 33.4813 | 33.374 | 33.2425 | 33.1057 | 32.7 | 32.0472 | 31.3452 | 30.7001 | 32.5907 | 32.3212 | 32.2652 | 32.1753 | 32.0717 | 31.9477 | 31.8252 | 31.7029 | 31.5534 | 31.3974 | 30.9358 | 30.1923 | 29.4009 | 28.6658 | 32.6588 | 32.4012 | 32.3476 | 32.2617 | 32.1626 | 32.044 | 31.9267 | 31.8097 | 31.6665 | 31.5172 | 31.0751 | 30.3633 | 29.6031 | 28.9003
|  | WEYMOUTH | SP |  |  | 34.1942 | 34.1823 | 33.9833 | 33.9749 | 33.9552 | 33.9327 | 33.9012 | 33.87 | 33.83 | 33.7772 | 33.6205 | 33.3763 | 33.1265 | 32.8912 | 32.6401 | 32.6265 | 32.3989 | 32.3892 | 32.3667 | 32.341 | 32.3049 | 32.2693 | 32.2236 | 32.1633 | 31.985 | 31.7063 | 31.4241 | 31.1583 | 32.7061 | 32.693 | 32.4754 | 32.4662 | 32.4447 | 32.4201 | 32.3856 | 32.3515 | 32.3078 | 32.2501 | 32.0794 | 31.8127 | 31.5418 | 31.2867
COWLEY GSP | HEADINGTON BSP | WHEATLEY | MINIMUM HEADROOM | SP 60777 05379 | NO | 70.0079 | 69.994 | 69.98 | 69.1312 | 69.0616 | 68.992 | 68.9224 | 68.8528 | 68.7833 | 68.7554 | 68.6719 | 68.5328 | 67.7911 | 66.4553 | 52.096 | 52.0692 | 52.0446 | 51.1755 | 51.0904 | 51.0014 | 50.919 | 50.8363 | 50.7525 | 50.71 | 49.7453 | 48.1682 | 46.5561 | 44.9105 | 52.1191 | 52.1052 | 52.0913 | 51.2424 | 51.1728 | 51.1032 | 51.0337 | 50.9641 | 50.7001 | 50.3679 | 49.3431 | 47.8181 | 46.2614 | 44.6698
|  | WHEATLEY | CT |  |  | 70.0747 | 70.0663 | 70.058 | 69.5486 | 69.5069 | 69.4651 | 69.4234 | 69.3816 | 69.3399 | 69.3232 | 69.2731 | 68.6641 | 67.9364 | 66.6005 | 52.1641 | 52.1437 | 52.1259 | 51.5989 | 51.5441 | 51.4854 | 51.4281 | 51.3733 | 51.3172 | 51.2859 | 50.5298 | 48.4828 | 46.7394 | 45.0938 | 52.1859 | 52.1776 | 52.1692 | 51.6599 | 51.6181 | 51.5764 | 51.5347 | 51.4929 | 51.4252 | 51.1041 | 50.1209 | 48.126 | 46.438 | 44.8465
|  | WHEATLEY | LW |  |  | 70.0079 | 69.994 | 69.98 | 69.1312 | 69.0616 | 68.992 | 68.9224 | 68.8528 | 68.7833 | 68.7554 | 68.6719 | 68.5328 | 67.7911 | 66.4553 | 52.096 | 52.0692 | 52.0446 | 51.1755 | 51.0904 | 51.0014 | 50.919 | 50.8363 | 50.7525 | 50.71 | 49.7453 | 48.1682 | 46.5561 | 44.9105 | 52.1191 | 52.1052 | 52.0913 | 51.2424 | 51.1728 | 51.1032 | 51.0337 | 50.9641 | 50.7001 | 50.3679 | 49.3431 | 47.8181 | 46.2614 | 44.6698
|  | WHEATLEY | ST |  |  | 70.1081 | 70.1025 | 70.0969 | 69.7574 | 69.7295 | 69.7017 | 69.6739 | 69.6461 | 69.6182 | 69.6071 | 69.5737 | 69.518 | 69.4846 | 69.4234 | 52.1981 | 52.1866 | 52.1695 | 51.8185 | 51.7809 | 51.7391 | 51.7005 | 51.6619 | 51.6245 | 51.6033 | 51.5393 | 50.8332 | 49.7941 | 48.7818 | 52.2193 | 52.2138 | 52.2082 | 51.8686 | 51.8408 | 51.813 | 51.7851 | 51.7573 | 51.7295 | 51.7183 | 51.4153 | 50.4222 | 49.4196 | 48.4417
|  | WHEATLEY | SP |  |  | 70.1415 | 70.1387 | 70.1359 | 69.9661 | 69.9522 | 69.9383 | 69.9244 | 69.9105 | 69.8965 | 69.891 | 69.8743 | 69.8464 | 69.8297 | 69.7991 | 52.2346 | 52.2291 | 52.2189 | 52.0453 | 52.0278 | 52.0087 | 51.9906 | 51.9725 | 51.9535 | 51.944 | 51.9153 | 51.8695 | 51.833 | 51.7823 | 52.2527 | 52.2499 | 52.2472 | 52.0774 | 52.0635 | 52.0495 | 52.0356 | 52.0217 | 52.0078 | 52.0022 | 51.9855 | 51.9577 | 51.941 | 51.9104
BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH | MINIMUM HEADROOM | SU 45924 48466 | YES | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.0658 | 28.8403 | 28.6047 | 28.3605 | 27.9897 | 27.9383 | 27.7623 | 27.4989 | 26.6064 | 25.1196 | 21.2683 | 21.2537 | 21.2346 | 21.2039 | 20.962 | 20.703 | 20.3229 | 19.9325 | 19.4144 | 19.2076 | 18.5192 | 16.9396 | 14.8239 | 13.1273 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.6847 | 21.4592 | 21.2236 | 20.9794 | 20.6086 | 20.5572 | 20.3811 | 19.4475 | 17.3243 | 15.6202
|  | WHITCHURCH | CT |  |  | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 28.9379 | 27.4807 | 21.2683 | 21.2537 | 21.2346 | 21.2039 | 21.1711 | 21.1348 | 21.0976 | 20.9514 | 20.804 | 20.6485 | 20.1363 | 18.82 | 17.1674 | 15.5004 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.3283 | 19.6682 | 17.9937
|  | WHITCHURCH | LW |  |  | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.0658 | 28.8403 | 28.6047 | 28.3605 | 27.9897 | 27.9383 | 27.7623 | 27.4989 | 26.6064 | 25.1196 | 21.2698 | 21.2562 | 21.2384 | 21.2106 | 20.962 | 20.703 | 20.3229 | 19.9325 | 19.4144 | 19.2076 | 18.5192 | 16.9396 | 14.8239 | 13.1273 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.6847 | 21.4592 | 21.2236 | 20.9794 | 20.6086 | 20.5572 | 20.3811 | 19.4475 | 17.3243 | 15.6202
|  | WHITCHURCH | ST |  |  | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.1687 | 21.2733 | 21.2638 | 21.2524 | 21.237 | 21.2183 | 21.1957 | 21.1262 | 21.0554 | 20.955 | 20.8488 | 20.4969 | 19.5818 | 18.4901 | 17.4314 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 20.9969 | 19.9334
|  | WHITCHURCH | SP |  |  | 29.2843 | 29.2843 | 29.2843 | 29.2843 | 29.2835 | 29.2787 | 29.2738 | 29.2689 | 29.2613 | 29.2399 | 29.1723 | 29.1401 | 29.0386 | 28.9538 | 21.2776 | 21.2724 | 21.2669 | 21.2611 | 21.2524 | 21.2387 | 21.2136 | 21.1883 | 21.1558 | 21.0929 | 20.8878 | 20.4784 | 19.8725 | 19.2515 | 21.9032 | 21.9032 | 21.9032 | 21.9032 | 21.9024 | 21.8976 | 21.8927 | 21.8878 | 21.8802 | 21.8588 | 21.7912 | 21.759 | 21.6575 | 21.5727
BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY | MINIMUM HEADROOM | SU 52936 08794 | NO | 39.3125 | 67.5125 | 67.5125 | 67.5125 | 67.48 | 67.447 | 67.4133 | 67.3785 | 67.3247 | 67.3064 | 67.2481 | 67.2012 | 67.0474 | 66.1065 | 36.8412 | 62.0386 | 62.0352 | 62.0294 | 61.995 | 61.9551 | 61.9101 | 61.8649 | 61.7982 | 61.7662 | 61.6689 | 60.5334 | 58.3771 | 56.2691 | 36.0987 | 61.2987 | 61.2987 | 61.2987 | 61.2662 | 61.2332 | 61.1995 | 61.1647 | 61.1108 | 61.0925 | 61.0342 | 60.934 | 58.7909 | 56.6835
|  | WHITELEY | CT |  |  | 39.3125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 66.3089 | 36.8412 | 62.0386 | 62.0352 | 62.0294 | 62.0175 | 62.0074 | 61.998 | 61.9787 | 61.9599 | 61.9398 | 61.8827 | 60.7641 | 58.608 | 56.5006 | 36.0987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.1607 | 59.0204 | 56.919
|  | WHITELEY | LW |  |  | 39.3125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 66.1065 | 36.8412 | 62.0386 | 62.0352 | 62.0294 | 62.0175 | 62.0074 | 61.9867 | 61.9674 | 61.9486 | 61.9285 | 61.8714 | 60.5334 | 58.3771 | 56.2691 | 36.0987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 60.934 | 58.7909 | 56.6835
|  | WHITELEY | ST |  |  | 39.3125 | 67.5125 | 67.5125 | 67.5125 | 67.48 | 67.447 | 67.4133 | 67.3785 | 67.3247 | 67.3064 | 67.2481 | 67.2012 | 67.0474 | 66.9996 | 36.8549 | 62.0402 | 62.0381 | 62.0351 | 61.995 | 61.9551 | 61.9101 | 61.8649 | 61.7982 | 61.7662 | 61.6689 | 61.5524 | 60.5962 | 59.1907 | 36.0987 | 61.2987 | 61.2987 | 61.2987 | 61.2662 | 61.2332 | 61.1995 | 61.1647 | 61.1108 | 61.0925 | 61.0342 | 60.9873 | 60.7583 | 59.5964
|  | WHITELEY | SP |  |  | 39.3125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 67.5125 | 36.8559 | 62.0551 | 62.0413 | 62.0404 | 62.0369 | 62.0342 | 62.0303 | 62.0269 | 62.023 | 62.0177 | 62.0026 | 61.9751 | 61.9474 | 61.9202 | 36.0987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987 | 61.2987
BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITELEY WOOD | MINIMUM HEADROOM | SU 52936 08794 | NO | 14.9272 | 14.8624 | 14.7783 | 14.6196 | 14.4469 | 14.2574 | 14.1398 | 14.0045 | 13.8187 | 13.7086 | 13.3312 | 12.8131 | 11.9865 | 11.5359 | 13.6819 | 13.6629 | 13.6383 | 13.5917 | 13.5169 | 13.3868 | 13.2695 | 13.1449 | 12.9567 | 12.8788 | 12.6173 | 12.0284 | 11.1262 | 10.5807 | 14.0423 | 14.0369 | 14.0298 | 14.0164 | 13.9294 | 13.8235 | 13.7179 | 13.6052 | 13.4279 | 13.362 | 13.1348 | 12.9167 | 12.0559 | 11.55
|  | WHITELEY WOOD | CT |  |  | 14.9376 | 14.8802 | 14.8059 | 14.6677 | 14.5125 | 14.3503 | 14.2164 | 14.1109 | 13.9808 | 13.8887 | 13.612 | 12.9761 | 12.3142 | 11.865 | 13.685 | 13.6681 | 13.6463 | 13.6058 | 13.5495 | 13.4886 | 13.4334 | 13.382 | 13.3066 | 13.274 | 13.0052 | 12.2123 | 11.3945 | 10.7956 | 14.0432 | 14.0384 | 14.0321 | 14.0205 | 13.9934 | 13.9625 | 13.9305 | 13.8951 | 13.8359 | 13.8209 | 13.7658 | 13.0951 | 12.3186 | 11.7594
|  | WHITELEY WOOD | LW |  |  | 14.9272 | 14.8624 | 14.7783 | 14.6196 | 14.4469 | 14.2574 | 14.1398 | 14.0045 | 13.8187 | 13.717 | 13.3916 | 12.8131 | 12.0669 | 11.6711 | 13.6819 | 13.6629 | 13.6383 | 13.5917 | 13.532 | 13.4578 | 13.3936 | 13.3124 | 13.1814 | 13.1391 | 12.7638 | 12.0284 | 11.1262 | 10.5807 | 14.0423 | 14.0369 | 14.0298 | 14.0164 | 13.9902 | 13.9501 | 13.9016 | 13.8365 | 13.7216 | 13.6969 | 13.5932 | 12.9167 | 12.0559 | 11.55
|  | WHITELEY WOOD | ST |  |  | 14.9502 | 14.9065 | 14.8552 | 14.7756 | 14.5862 | 14.3741 | 14.2171 | 14.0526 | 13.827 | 13.7086 | 13.3312 | 12.8754 | 11.9865 | 11.5359 | 13.6887 | 13.6759 | 13.6608 | 13.6375 | 13.5169 | 13.3868 | 13.2695 | 13.1449 | 12.9567 | 12.8788 | 12.6173 | 12.3173 | 11.3279 | 10.7797 | 14.0443 | 14.0406 | 14.0363 | 14.0296 | 13.9294 | 13.8235 | 13.7179 | 13.6052 | 13.4279 | 13.362 | 13.1348 | 12.9183 | 12.1827 | 11.6604
|  | WHITELEY WOOD | SP |  |  | 14.9874 | 14.9743 | 14.961 | 14.9474 | 14.9199 | 14.8887 | 14.8694 | 14.8496 | 14.8234 | 14.7957 | 14.7012 | 14.5769 | 14.369 | 14.1721 | 13.6996 | 13.6958 | 13.6918 | 13.6879 | 13.6797 | 13.6704 | 13.6644 | 13.6582 | 13.6495 | 13.6376 | 13.588 | 13.5342 | 13.3908 | 13.2528 | 14.0474 | 14.0463 | 14.0452 | 14.044 | 14.0416 | 14.0388 | 14.0368 | 14.0345 | 14.031 | 14.0238 | 13.9874 | 13.9545 | 13.8302 | 13.7097
MINETY GSP | CIRENCESTER BSP | WHITEWAY | MINIMUM HEADROOM | SP 02076 03059 | NO | 6.4774 | 6.4398 | 6.3906 | 6.2864 | 6.1822 | 6.0786 | 5.9758 | 5.9255 | 5.8728 | 5.8223 | 5.6723 | 5.4058 | 5.1268 | 4.8699 | 4.9388 | 4.8946 | 4.8366 | 4.7141 | 4.592 | 4.4708 | 4.3505 | 4.292 | 4.2312 | 4.172 | 3.9961 | 3.6865 | 3.3627 | 3.0616 | 5.8879 | 5.8502 | 5.8006 | 5.6958 | 5.591 | 5.4869 | 5.3835 | 5.3329 | 5.2799 | 5.2292 | 5.0783 | 4.8103 | 4.5299 | 4.2715
|  | WHITEWAY | CT |  |  | 6.4774 | 6.4398 | 6.3906 | 6.2864 | 6.1822 | 6.0786 | 5.9758 | 5.9255 | 5.8728 | 5.8223 | 5.6723 | 5.4058 | 5.1268 | 4.8699 | 4.9388 | 4.8946 | 4.8366 | 4.7141 | 4.592 | 4.4708 | 4.3505 | 4.292 | 4.2312 | 4.172 | 3.9961 | 3.6865 | 3.3627 | 3.0616 | 5.8879 | 5.8502 | 5.8006 | 5.6958 | 5.591 | 5.4869 | 5.3835 | 5.3329 | 5.2799 | 5.2292 | 5.0783 | 4.8103 | 4.5299 | 4.2715
|  | WHITEWAY | LW |  |  | 6.4777 | 6.4403 | 6.3912 | 6.2874 | 6.1862 | 6.0853 | 6.0367 | 5.9876 | 5.9363 | 5.8858 | 5.7347 | 5.4791 | 5.2025 | 4.9511 | 4.9392 | 4.8951 | 4.8374 | 4.7153 | 4.5963 | 4.4778 | 4.4209 | 4.3637 | 4.3042 | 4.2451 | 4.068 | 3.7693 | 3.4479 | 3.1523 | 5.8882 | 5.8506 | 5.8012 | 5.6969 | 5.5951 | 5.4936 | 5.4446 | 5.3953 | 5.3437 | 5.293 | 5.141 | 4.8839 | 4.6058 | 4.353
|  | WHITEWAY | ST |  |  | 6.4965 | 6.4736 | 6.4465 | 6.4002 | 6.3433 | 6.2745 | 6.2396 | 6.2049 | 6.1723 | 6.1379 | 6.0359 | 5.8692 | 5.6905 | 5.5226 | 4.9613 | 4.9343 | 4.9025 | 4.848 | 4.7811 | 4.7002 | 4.6592 | 4.6184 | 4.5803 | 4.54 | 4.4205 | 4.2251 | 4.0175 | 3.8209 | 5.9072 | 5.8841 | 5.8569 | 5.8103 | 5.7531 | 5.6839 | 5.6488 | 5.6139 | 5.5811 | 5.5465 | 5.4439 | 5.2762 | 5.0966 | 4.9278
|  | WHITEWAY | SP |  |  | 6.521 | 6.5171 | 6.5133 | 6.5097 | 6.4929 | 6.4729 | 6.461 | 6.4491 | 6.4338 | 6.4205 | 6.3812 | 6.3185 | 6.2541 | 6.1926 | 4.9902 | 4.9855 | 4.9811 | 4.9768 | 4.9571 | 4.9336 | 4.9195 | 4.9056 | 4.8875 | 4.872 | 4.8259 | 4.7523 | 4.6773 | 4.6057 | 5.9318 | 5.9279 | 5.9241 | 5.9205 | 5.9036 | 5.8835 | 5.8714 | 5.8595 | 5.8441 | 5.8307 | 5.7912 | 5.7281 | 5.6633 | 5.6016
BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD | MINIMUM HEADROOM | SU 69235 73304 | YES | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.8364 | 38.6993 | 38.556 | 38.2953 | 37.8416 | 37.5974 | 36.9241 | 35.9514 | 34.9503 | 34.2619 | 36.3654 | 36.3654 | 36.3654 | 36.3654 | 36.2324 | 36.0953 | 35.952 | 35.6381 | 35.0992 | 34.7754 | 33.8905 | 32.6872 | 31.5723 | 30.7766 | 36.2 | 36.2 | 36.2 | 36.1988 | 36.0396 | 35.8751 | 35.715 | 35.2918 | 34.7474 | 34.4185 | 33.5199 | 32.2983 | 31.169 | 30.3596
|  | WILSON ROAD | CT |  |  | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.8695 | 38.7678 | 38.6646 | 38.5184 | 38.1239 | 37.8899 | 37.256 | 36.1444 | 35.0785 | 34.3172 | 36.3654 | 36.3654 | 36.3654 | 36.3654 | 36.2655 | 36.1638 | 36.0605 | 35.8887 | 35.4091 | 35.0954 | 34.2501 | 32.8942 | 31.7145 | 30.8459 | 36.2 | 36.2 | 36.2 | 36.2 | 36.0834 | 35.9576 | 35.8294 | 35.5442 | 35.0591 | 34.7403 | 33.8813 | 32.5071 | 31.3129 | 30.4307
|  | WILSON ROAD | LW |  |  | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.8364 | 38.6993 | 38.556 | 38.2953 | 37.8416 | 37.5974 | 36.9241 | 35.9514 | 34.9503 | 34.2619 | 36.3654 | 36.3654 | 36.3654 | 36.3654 | 36.2324 | 36.0953 | 35.952 | 35.6381 | 35.0992 | 34.7754 | 33.8905 | 32.6872 | 31.5723 | 30.7766 | 36.2 | 36.2 | 36.2 | 36.1988 | 36.0396 | 35.8751 | 35.715 | 35.2918 | 34.7474 | 34.4185 | 33.5199 | 32.2983 | 31.169 | 30.3596
|  | WILSON ROAD | ST |  |  | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9676 | 38.9658 | 38.9639 | 38.962 | 38.9591 | 38.958 | 38.8304 | 38.3033 | 37.9052 | 37.5363 | 36.3654 | 36.3654 | 36.3654 | 36.3654 | 36.3636 | 36.3618 | 36.3599 | 36.358 | 36.355 | 36.354 | 36.1686 | 35.4455 | 34.9014 | 34.3957 | 36.2 | 36.2 | 36.2 | 36.2 | 36.1982 | 36.1873 | 36.1725 | 36.1568 | 36.1417 | 36.1292 | 35.822 | 35.0863 | 34.5328 | 34.0182
|  | WILSON ROAD | SP |  |  | 38.9694 | 38.9694 | 38.9694 | 38.9694 | 38.9689 | 38.9684 | 38.968 | 38.9675 | 38.9667 | 38.9647 | 38.9581 | 38.955 | 38.9451 | 38.9369 | 36.3654 | 36.3654 | 36.3654 | 36.3654 | 36.3649 | 36.3644 | 36.3639 | 36.3635 | 36.3627 | 36.3607 | 36.3541 | 36.351 | 36.3411 | 36.3329 | 36.2 | 36.2 | 36.2 | 36.2 | 36.1995 | 36.1991 | 36.1986 | 36.1981 | 36.1974 | 36.1953 | 36.1888 | 36.1752 | 36.1532 | 36.1339
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE | MINIMUM HEADROOM | SZ 02014 99989 | YES | 29.9652 | 29.9366 | 29.8991 | 29.8063 | 29.7078 | 29.6251 | 29.525 | 29.4111 | 29.2961 | 29.1715 | 28.808 | 28.2102 | 27.5941 | 26.9916 | 37.8149 | 37.7945 | 37.7676 | 37.7014 | 37.6309 | 37.5718 | 37.5003 | 37.4189 | 37.3367 | 37.2477 | 36.9879 | 36.5606 | 36.1204 | 35.6898 | 33.8091 | 33.807 | 33.8042 | 33.7972 | 33.7898 | 33.7836 | 33.776 | 33.7675 | 33.7588 | 33.7495 | 33.7221 | 33.6772 | 33.6309 | 33.5856
|  | WIMBORNE | CT |  |  | 29.9652 | 29.9366 | 29.8991 | 29.8063 | 29.7078 | 29.6251 | 29.5494 | 29.4355 | 29.3205 | 29.1959 | 28.8323 | 28.2345 | 27.6184 | 27.0164 | 37.8149 | 37.7945 | 37.7676 | 37.7014 | 37.6309 | 37.5718 | 37.5177 | 37.4363 | 37.3541 | 37.2651 | 37.0053 | 36.578 | 36.1377 | 35.7075 | 33.8091 | 33.807 | 33.8042 | 33.7972 | 33.7898 | 33.7836 | 33.7779 | 33.7693 | 33.7607 | 33.7513 | 33.724 | 33.679 | 33.6327 | 33.5874
|  | WIMBORNE | LW |  |  | 29.9669 | 29.9395 | 29.9036 | 29.8143 | 29.719 | 29.6395 | 29.525 | 29.4111 | 29.2961 | 29.1715 | 28.808 | 28.2102 | 27.5941 | 26.9916 | 37.8161 | 37.7965 | 37.7708 | 37.707 | 37.639 | 37.5821 | 37.5003 | 37.4189 | 37.3367 | 37.2477 | 36.9879 | 36.5606 | 36.1204 | 35.6898 | 33.8093 | 33.8072 | 33.8045 | 33.7978 | 33.7906 | 33.7846 | 33.776 | 33.7675 | 33.7588 | 33.7495 | 33.7221 | 33.6772 | 33.6309 | 33.5856
|  | WIMBORNE | ST |  |  | 29.973 | 29.9509 | 29.9248 | 29.8713 | 29.8022 | 29.7319 | 29.6611 | 29.591 | 29.5124 | 29.4274 | 29.1822 | 28.7841 | 28.3874 | 27.9958 | 37.8205 | 37.8047 | 37.786 | 37.7478 | 37.6984 | 37.6482 | 37.5976 | 37.5474 | 37.4913 | 37.4306 | 37.2553 | 36.9708 | 36.6873 | 36.4074 | 33.8097 | 33.8081 | 33.8061 | 33.8021 | 33.7969 | 33.7916 | 33.7863 | 33.781 | 33.7751 | 33.7687 | 33.7503 | 33.7203 | 33.6905 | 33.6611
|  | WIMBORNE | SP |  |  | 29.9985 | 29.9956 | 29.9929 | 29.9849 | 29.9651 | 29.9486 | 29.9251 | 29.9016 | 29.8708 | 29.8379 | 29.7432 | 29.5917 | 29.4471 | 29.3114 | 37.8387 | 37.8366 | 37.8347 | 37.829 | 37.8148 | 37.803 | 37.7862 | 37.7695 | 37.7474 | 37.7239 | 37.6562 | 37.548 | 37.4446 | 37.3477 | 33.8116 | 33.8114 | 33.8112 | 33.8106 | 33.8091 | 33.8079 | 33.8061 | 33.8044 | 33.802 | 33.7996 | 33.7924 | 33.7811 | 33.7702 | 33.76
MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES | MINIMUM HEADROOM | SU 03028 12678 | YES | 32.1905 | 32.0523 | 31.8846 | 31.5417 | 31.1214 | 30.6696 | 30.3567 | 30.0502 | 29.684 | 29.4755 | 28.8154 | 27.4369 | 25.6944 | 24.2333 | 32.0373 | 32.0162 | 31.9907 | 31.9385 | 31.7828 | 31.6185 | 31.4702 | 31.3183 | 31.0076 | 30.7729 | 30.0314 | 28.4757 | 26.5251 | 24.8425 | 32.5961 | 32.5866 | 32.5752 | 32.5517 | 32.4221 | 32.2863 | 32.1193 | 31.7957 | 31.4132 | 31.1876 | 30.4745 | 28.8988 | 26.9194 | 25.2219
|  | WIMBORNE ST GILES | CT |  |  | 32.1905 | 32.0523 | 31.8846 | 31.5417 | 31.1997 | 30.8513 | 30.503 | 30.3196 | 30.1416 | 29.9592 | 29.391 | 28.1394 | 26.6713 | 25.2224 | 32.0373 | 32.0162 | 31.9907 | 31.9385 | 31.8862 | 31.8327 | 31.7789 | 31.6408 | 31.4376 | 31.2291 | 30.5794 | 29.1506 | 27.4745 | 25.7999 | 32.5961 | 32.5866 | 32.5752 | 32.5517 | 32.528 | 32.5036 | 32.2477 | 32.0472 | 31.8528 | 31.6534 | 31.0233 | 29.5699 | 27.865 | 26.1798
|  | WIMBORNE ST GILES | LW |  |  | 32.1949 | 32.0599 | 31.8965 | 31.5626 | 31.1214 | 30.6696 | 30.3567 | 30.0502 | 29.684 | 29.4755 | 28.8154 | 27.4369 | 25.6944 | 24.2333 | 32.0379 | 32.0174 | 31.9925 | 31.9417 | 31.7828 | 31.6185 | 31.4702 | 31.3183 | 31.0076 | 30.7729 | 30.0314 | 28.4757 | 26.5251 | 24.8425 | 32.5964 | 32.5872 | 32.576 | 32.5531 | 32.4221 | 32.2863 | 32.1193 | 31.7957 | 31.4132 | 31.1876 | 30.4745 | 28.8988 | 26.9194 | 25.2219
|  | WIMBORNE ST GILES | ST |  |  | 32.2422 | 32.147 | 32.0438 | 31.8713 | 31.6572 | 31.3975 | 31.2621 | 31.1349 | 31.0134 | 30.8881 | 30.4961 | 29.6433 | 28.6704 | 27.74 | 32.0451 | 32.0306 | 32.0149 | 31.9887 | 31.9559 | 31.916 | 31.8949 | 31.8747 | 31.8545 | 31.8345 | 31.7703 | 30.8693 | 29.7598 | 28.6968 | 32.5996 | 32.5931 | 32.5861 | 32.5742 | 32.5594 | 32.5412 | 32.5314 | 32.5218 | 32.5115 | 32.502 | 32.241 | 31.3089 | 30.19 | 29.1085
|  | WIMBORNE ST GILES | SP |  |  | 32.3328 | 32.3088 | 32.2903 | 32.2705 | 32.2107 | 32.14 | 32.0906 | 32.045 | 31.9913 | 31.9424 | 31.79 | 31.4473 | 31.0247 | 30.5888 | 32.0589 | 32.0553 | 32.0525 | 32.0494 | 32.0403 | 32.0296 | 32.022 | 32.015 | 32.0068 | 31.9991 | 31.9742 | 31.9208 | 31.8502 | 31.7778 | 32.6058 | 32.6042 | 32.6029 | 32.6016 | 32.5975 | 32.5926 | 32.5892 | 32.5861 | 32.5823 | 32.5786 | 32.5664 | 32.5415 | 32.5057 | 32.3431
MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON | MINIMUM HEADROOM | ST 71286 27802 | YES | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.1795 | 36.1461 | 36.1111 | 36.0749 | 36.0199 | 36.0123 | 35.9861 | 35.9471 | 35.8776 | 35.0984 | 34.2061 | 34.2032 | 34.1994 | 34.1925 | 34.1564 | 34.1175 | 34.0726 | 34.0264 | 33.9614 | 33.9432 | 33.8838 | 33.6272 | 32.2645 | 30.7475 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.5683 | 34.5348 | 34.4999 | 34.4637 | 34.4086 | 34.401 | 34.3749 | 34.3358 | 33.3648 | 31.8423
|  | WINCANTON | CT |  |  | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 35.4484 | 34.2061 | 34.2032 | 34.1994 | 34.1925 | 34.1864 | 34.1803 | 34.1741 | 34.1641 | 34.1541 | 34.1435 | 34.1103 | 33.8956 | 32.6099 | 31.0989 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 33.7102 | 32.1938
|  | WINCANTON | LW |  |  | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.1795 | 36.1461 | 36.1111 | 36.0749 | 36.0199 | 36.0123 | 35.9861 | 35.9471 | 35.8776 | 35.0984 | 34.2064 | 34.2038 | 34.2004 | 34.1943 | 34.1564 | 34.1175 | 34.0726 | 34.0264 | 33.9614 | 33.9432 | 33.8838 | 33.6272 | 32.2645 | 30.7475 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.5683 | 34.5348 | 34.4999 | 34.4637 | 34.4086 | 34.401 | 34.3749 | 34.3358 | 33.3648 | 31.8423
|  | WINCANTON | ST |  |  | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 34.207 | 34.205 | 34.2026 | 34.199 | 34.1951 | 34.1905 | 34.1835 | 34.1764 | 34.1696 | 34.1624 | 34.1397 | 34.0895 | 33.8713 | 33.0787 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.1808
|  | WINCANTON | SP |  |  | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 36.2119 | 34.2086 | 34.2079 | 34.2072 | 34.2065 | 34.2054 | 34.2042 | 34.2017 | 34.1992 | 34.1959 | 34.1931 | 34.1843 | 34.164 | 34.1392 | 34.1134 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007 | 34.6007
COWLEY GSP | WITNEY BSP | WINDRUSH PARK | MINIMUM HEADROOM | SP 33366 09758 | NO | 25.2726 | 25.2726 | 25.2726 | 30.7726 | 30.7606 | 30.7489 | 30.7371 | 30.7251 | 30.7063 | 30.6539 | 30.4856 | 30.4041 | 30.1423 | 29.9211 | 18.7894 | 18.6671 | 18.4993 | 28.2751 | 28.0897 | 27.9032 | 27.7008 | 27.3857 | 27.0448 | 26.747 | 25.8487 | 24.4607 | 23.2108 | 22.0791 | 23.6275 | 23.6275 | 23.6275 | 29.1275 | 29.1155 | 29.1038 | 29.092 | 29.08 | 29.0612 | 29.0088 | 28.8405 | 28.3914 | 27.1598 | 26.0456
|  | WINDRUSH PARK | CT |  |  | 25.2726 | 25.2726 | 25.2726 | 30.7726 | 30.772 | 30.7708 | 30.769 | 30.7664 | 30.7607 | 30.7596 | 30.7542 | 30.709 | 30.6585 | 30.0194 | 18.7894 | 18.6671 | 18.4993 | 28.2751 | 28.0897 | 27.9032 | 27.7038 | 27.3956 | 27.0679 | 26.7723 | 25.8854 | 24.4926 | 23.2719 | 22.1306 | 23.6275 | 23.6275 | 23.6275 | 29.1275 | 29.1268 | 29.1256 | 29.1239 | 29.1213 | 29.1155 | 29.1124 | 29.0573 | 28.4234 | 27.2209 | 26.0971
|  | WINDRUSH PARK | LW |  |  | 25.2726 | 25.2726 | 25.2726 | 30.7726 | 30.7705 | 30.7661 | 30.7593 | 30.7499 | 30.7309 | 30.7276 | 30.7109 | 30.6703 | 30.591 | 29.967 | 18.8006 | 18.6864 | 18.5293 | 28.3274 | 28.1622 | 27.994 | 27.7008 | 27.3857 | 27.0448 | 26.747 | 25.8487 | 24.4607 | 23.2108 | 22.0791 | 23.6275 | 23.6275 | 23.6275 | 29.1275 | 29.1254 | 29.121 | 29.1142 | 29.1048 | 29.0858 | 29.0808 | 29.0144 | 28.3914 | 27.1598 | 26.0456
|  | WINDRUSH PARK | ST |  |  | 25.2726 | 25.2726 | 25.2726 | 30.7726 | 30.7632 | 30.7533 | 30.7427 | 30.7311 | 30.7119 | 30.7048 | 30.6773 | 30.6495 | 30.5547 | 30.5222 | 18.8268 | 18.7469 | 18.6449 | 28.5333 | 28.4272 | 28.3095 | 28.0842 | 27.8461 | 27.609 | 27.4005 | 26.7668 | 25.8225 | 24.9705 | 24.2072 | 23.6275 | 23.6275 | 23.6275 | 29.1275 | 29.1181 | 29.1082 | 29.0976 | 29.086 | 29.0668 | 29.0597 | 29.0322 | 28.955 | 28.8174 | 28.1396
|  | WINDRUSH PARK | SP |  |  | 25.2726 | 25.2726 | 25.2726 | 30.7726 | 30.7606 | 30.7489 | 30.7371 | 30.7251 | 30.7063 | 30.6539 | 30.4856 | 30.4041 | 30.1423 | 29.9211 | 18.8551 | 18.8082 | 18.7538 | 28.7083 | 28.6594 | 28.6102 | 28.5217 | 28.4296 | 28.3125 | 28.1812 | 27.7763 | 27.3358 | 26.7888 | 26.3031 | 23.6275 | 23.6275 | 23.6275 | 29.1275 | 29.1155 | 29.1038 | 29.092 | 29.08 | 29.0612 | 29.0088 | 28.8405 | 28.759 | 28.4972 | 28.276
COWLEY GSP | DRAYTON BSP | WINSMORE LANE | MINIMUM HEADROOM | SU 49513 96982 | NO | 6.5 | 6.5 | 6.5 | 6.5 | 6.3466 | 6.1906 | 6.032 | 5.8664 | 5.611 | 5.5787 | 5.4748 | 4.9949 | 4.4916 | 4.3694 | 5.2021 | 5.2008 | 5.1991 | 5.1955 | 5.0387 | 4.8792 | 4.7172 | 4.5436 | 4.2804 | 4.2395 | 4.1102 | 3.5871 | 3.0381 | 2.8709 | 4.9988 | 4.998 | 4.9969 | 4.9945 | 4.8389 | 4.6805 | 4.5197 | 4.3488 | 4.0883 | 4.0503 | 3.9296 | 3.4212 | 2.8788 | 2.7128
|  | WINSMORE LANE | CT |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.3466 | 6.1906 | 6.032 | 5.8664 | 5.611 | 5.5787 | 5.4748 | 4.9949 | 4.4916 | 4.3694 | 5.2021 | 5.2008 | 5.1991 | 5.1955 | 5.0387 | 4.8792 | 4.7172 | 4.5436 | 4.2804 | 4.2395 | 4.1102 | 3.5871 | 3.0381 | 2.8709 | 4.9988 | 4.998 | 4.9969 | 4.9945 | 4.8389 | 4.6805 | 4.5197 | 4.3488 | 4.0883 | 4.0503 | 3.9296 | 3.4212 | 2.8788 | 2.7128
|  | WINSMORE LANE | LW |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5.2021 | 5.2008 | 5.1991 | 5.1955 | 5.1921 | 5.1886 | 5.1806 | 5.1727 | 5.1648 | 5.1562 | 5.1309 | 5.0876 | 5.042 | 4.9969 | 4.9988 | 4.998 | 4.9969 | 4.9945 | 4.9923 | 4.99 | 4.9847 | 4.9794 | 4.9742 | 4.9686 | 4.9518 | 4.9233 | 4.8828 | 4.8389
|  | WINSMORE LANE | ST |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 5.2027 | 5.2019 | 5.2009 | 5.1993 | 5.1974 | 5.195 | 5.1906 | 5.1863 | 5.1809 | 5.1751 | 5.158 | 5.1291 | 5.0996 | 5.0703 | 4.9993 | 4.9987 | 4.9981 | 4.997 | 4.9957 | 4.9942 | 4.9913 | 4.9884 | 4.9849 | 4.981 | 4.9698 | 4.9506 | 4.9311 | 4.9104
|  | WINSMORE LANE | SP |  |  | 6.5 | 6.5 | 6.5 | 6.5 | 6.4957 | 6.4914 | 6.4871 | 6.4828 | 6.476 | 6.4572 | 6.3974 | 6.369 | 6.2793 | 6.2044 | 5.2035 | 5.2034 | 5.2032 | 5.2031 | 5.1982 | 5.1933 | 5.1871 | 5.1807 | 5.1713 | 5.1502 | 5.0839 | 5.0444 | 4.9439 | 4.8584 | 4.9998 | 4.9997 | 4.9996 | 4.9995 | 4.9948 | 4.9901 | 4.9846 | 4.9789 | 4.9704 | 4.95 | 4.8859 | 4.8503 | 4.7534 | 4.6715
MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON | MINIMUM HEADROOM | SY 84631 98138 | YES | 14.4916 | 14.4855 | 14.4686 | 14.4374 | 14.4038 | 14.3673 | 14.2721 | 14.1875 | 14.1081 | 14.0255 | 13.7866 | 13.3994 | 13.0042 | 12.6205 | 12.2511 | 12.244 | 12.2242 | 12.1877 | 12.1484 | 12.1058 | 11.9944 | 11.8955 | 11.8026 | 11.706 | 11.4267 | 10.9739 | 10.5117 | 10.063 | 12.7489 | 12.7424 | 12.7241 | 12.6904 | 12.6541 | 12.6148 | 12.5121 | 12.4208 | 12.335 | 12.2459 | 11.9881 | 11.5703 | 11.1437 | 10.7297
|  | WINTERBOURNE KINGSTON | CT |  |  | 14.4916 | 14.4855 | 14.4686 | 14.4374 | 14.4038 | 14.3673 | 14.3291 | 14.2446 | 14.1651 | 14.0825 | 13.8437 | 13.4565 | 13.0614 | 12.6781 | 12.2511 | 12.244 | 12.2242 | 12.1877 | 12.1484 | 12.1058 | 12.0611 | 11.9622 | 11.8693 | 11.7727 | 11.4934 | 11.0406 | 10.5786 | 10.1304 | 12.7489 | 12.7424 | 12.7241 | 12.6904 | 12.6541 | 12.6148 | 12.5736 | 12.4824 | 12.3966 | 12.3075 | 12.0497 | 11.6319 | 11.2055 | 10.7919
|  | WINTERBOURNE KINGSTON | LW |  |  | 14.4916 | 14.4855 | 14.4686 | 14.4374 | 14.4038 | 14.3673 | 14.2721 | 14.1875 | 14.1081 | 14.0255 | 13.7866 | 13.3994 | 13.0042 | 12.6205 | 12.2511 | 12.244 | 12.2242 | 12.1877 | 12.1484 | 12.1058 | 11.9944 | 11.8955 | 11.8026 | 11.706 | 11.4267 | 10.9739 | 10.5117 | 10.063 | 12.7489 | 12.7424 | 12.7241 | 12.6904 | 12.6541 | 12.6148 | 12.5121 | 12.4208 | 12.335 | 12.2459 | 11.9881 | 11.5703 | 11.1437 | 10.7297
|  | WINTERBOURNE KINGSTON | ST |  |  | 14.4946 | 14.4908 | 14.4801 | 14.4629 | 14.4421 | 14.4175 | 14.3563 | 14.3022 | 14.2481 | 14.1917 | 14.0303 | 13.7721 | 13.5172 | 13.2675 | 12.2546 | 12.2502 | 12.2377 | 12.2176 | 12.1933 | 12.1644 | 12.0929 | 12.0297 | 11.9663 | 11.9004 | 11.7116 | 11.4097 | 11.1117 | 10.8196 | 12.7521 | 12.7481 | 12.7365 | 12.718 | 12.6956 | 12.6689 | 12.6029 | 12.5446 | 12.4861 | 12.4253 | 12.2511 | 11.9725 | 11.6974 | 11.4279
|  | WINTERBOURNE KINGSTON | SP |  |  | 14.5525 | 14.498 | 14.4932 | 14.4869 | 14.4782 | 14.4687 | 14.4486 | 14.4322 | 14.4127 | 14.3907 | 14.3283 | 14.2301 | 14.1373 | 14.0513 | 12.3223 | 12.2586 | 12.253 | 12.2457 | 12.2355 | 12.2243 | 12.2009 | 12.1816 | 12.1588 | 12.1332 | 12.0601 | 11.9453 | 11.8368 | 11.7362 | 12.8095 | 12.7558 | 12.7507 | 12.7439 | 12.7345 | 12.7242 | 12.7026 | 12.6848 | 12.6637 | 12.6401 | 12.5727 | 12.4667 | 12.3666 | 12.2737
MANNINGTON GSP | REDHILL BSP | WINTON | MINIMUM HEADROOM | SZ 09349 93822 | YES | 34.0149 | 34.0141 | 34.0116 | 34.0066 | 34.0008 | 33.9937 | 33.9843 | 33.9742 | 33.9611 | 33.9528 | 33.9256 | 33.874 | 33.4527 | 32.9985 | 33.4229 | 33.42 | 33.4181 | 33.4142 | 33.4095 | 33.4037 | 33.396 | 33.3874 | 33.3758 | 33.3692 | 33.2324 | 32.6984 | 32.1343 | 31.6008 | 33.6477 | 33.6477 | 33.6477 | 33.6477 | 33.6469 | 33.6455 | 33.6432 | 33.64 | 33.6337 | 33.6326 | 33.627 | 33.4573 | 32.9474 | 32.4126
|  | WINTON | CT |  |  | 34.0149 | 34.0147 | 34.0127 | 34.0084 | 34.0038 | 33.9985 | 33.9932 | 33.9854 | 33.9767 | 33.9692 | 33.9458 | 33.8926 | 33.5408 | 33.0834 | 33.4232 | 33.4205 | 33.4189 | 33.4156 | 33.412 | 33.4078 | 33.4036 | 33.3973 | 33.3902 | 33.3843 | 33.3239 | 32.7883 | 32.2338 | 31.6973 | 33.6477 | 33.6477 | 33.6477 | 33.6477 | 33.6474 | 33.647 | 33.6464 | 33.6456 | 33.6436 | 33.6433 | 33.6415 | 33.5359 | 33.0411 | 32.5093
|  | WINTON | LW |  |  | 34.0149 | 34.0141 | 34.0116 | 34.0066 | 34.0008 | 33.9937 | 33.9843 | 33.9742 | 33.9611 | 33.9528 | 33.9256 | 33.874 | 33.4527 | 32.9985 | 33.4229 | 33.42 | 33.4181 | 33.4142 | 33.4095 | 33.4037 | 33.396 | 33.3874 | 33.3758 | 33.3692 | 33.2324 | 32.6984 | 32.1343 | 31.6008 | 33.6477 | 33.6477 | 33.6477 | 33.6477 | 33.6469 | 33.6455 | 33.6432 | 33.64 | 33.6337 | 33.6326 | 33.627 | 33.4573 | 32.9474 | 32.4126
|  | WINTON | ST |  |  | 34.0149 | 34.0149 | 34.0145 | 34.0117 | 34.008 | 34.0031 | 33.998 | 33.9929 | 33.9868 | 33.9812 | 33.9628 | 33.9322 | 33.8891 | 33.7705 | 33.433 | 33.4216 | 33.4203 | 33.4182 | 33.4153 | 33.4114 | 33.4074 | 33.4033 | 33.3982 | 33.3937 | 33.3786 | 33.2192 | 32.8534 | 32.5034 | 33.6477 | 33.6477 | 33.6477 | 33.6477 | 33.6475 | 33.6472 | 33.6468 | 33.6461 | 33.6446 | 33.6439 | 33.6401 | 33.6351 | 33.5901 | 33.29
|  | WINTON | SP |  |  | 34.0149 | 34.0149 | 34.0149 | 34.0149 | 34.0149 | 34.0148 | 34.0148 | 34.014 | 34.0121 | 34.0099 | 34.0029 | 33.9919 | 33.9768 | 33.9621 | 33.4346 | 33.4244 | 33.4242 | 33.424 | 33.4233 | 33.4224 | 33.4211 | 33.4199 | 33.4184 | 33.4167 | 33.4109 | 33.4022 | 33.3893 | 33.3768 | 33.6477 | 33.6477 | 33.6477 | 33.6477 | 33.6476 | 33.6476 | 33.6476 | 33.6476 | 33.6475 | 33.6473 | 33.6459 | 33.6448 | 33.6396 | 33.6344
COWLEY GSP | WITNEY BSP | WITNEY TOWN | MINIMUM HEADROOM | SP 35844 09625 | NO | 32.967 | 32.967 | 32.967 | 32.967 | 32.8733 | 32.7778 | 32.6804 | 32.5782 | 32.4198 | 32.3996 | 32.3335 | 32.0173 | 30.8878 | 29.9666 | 24.5402 | 24.5196 | 24.509 | 24.4868 | 24.3736 | 24.2573 | 24.1393 | 24.0289 | 23.8623 | 23.8332 | 23.3189 | 22.0524 | 20.7088 | 19.6378 | 25.3734 | 25.3734 | 25.3734 | 25.3734 | 25.2797 | 25.1841 | 24.914 | 24.6425 | 24.3162 | 24.1149 | 23.5104 | 22.2717 | 20.9575 | 19.9155
|  | WITNEY TOWN | CT |  |  | 32.967 | 32.967 | 32.967 | 32.967 | 32.8733 | 32.7778 | 32.6804 | 32.5782 | 32.4198 | 32.3996 | 32.3335 | 32.0173 | 30.8878 | 29.9666 | 24.5405 | 24.5201 | 24.5098 | 24.4882 | 24.3736 | 24.2573 | 24.1393 | 24.0289 | 23.8623 | 23.8332 | 23.3189 | 22.0524 | 20.7088 | 19.6378 | 25.3734 | 25.3734 | 25.3734 | 25.3734 | 25.2797 | 25.1841 | 24.914 | 24.6425 | 24.3162 | 24.1149 | 23.5104 | 22.2717 | 20.9575 | 19.9155
|  | WITNEY TOWN | LW |  |  | 32.967 | 32.967 | 32.967 | 32.967 | 32.9659 | 32.9635 | 32.9599 | 32.9548 | 32.9446 | 32.9428 | 32.9339 | 32.912 | 32.2501 | 31.4057 | 24.5402 | 24.5196 | 24.509 | 24.4868 | 24.4641 | 24.4404 | 24.4284 | 24.415 | 24.3966 | 24.386 | 24.1209 | 23.1488 | 22.1016 | 21.1074 | 25.3734 | 25.3734 | 25.3734 | 25.3734 | 25.3722 | 25.3699 | 25.3662 | 25.215 | 25.0367 | 24.854 | 24.3066 | 23.3623 | 22.3444 | 21.3791
|  | WITNEY TOWN | ST |  |  | 32.967 | 32.967 | 32.967 | 32.967 | 32.9288 | 32.8898 | 32.8497 | 32.808 | 32.7428 | 32.7203 | 32.6461 | 32.5833 | 32.3749 | 32.3079 | 24.5421 | 24.5357 | 24.5156 | 24.5027 | 24.4487 | 24.3906 | 24.3429 | 24.2937 | 24.2229 | 24.1943 | 24.1023 | 23.9658 | 23.1085 | 22.399 | 25.3734 | 25.3734 | 25.3734 | 25.3734 | 25.3352 | 25.2962 | 25.2561 | 25.2144 | 25.1491 | 25.1267 | 24.8253 | 24.1458 | 23.3075 | 22.6168
|  | WITNEY TOWN | SP |  |  | 32.967 | 32.967 | 32.967 | 32.967 | 32.9667 | 32.9665 | 32.9662 | 32.9659 | 32.9655 | 32.9641 | 32.9586 | 32.9552 | 32.9419 | 32.9296 | 24.5495 | 24.5486 | 24.5352 | 24.5345 | 24.5307 | 24.5262 | 24.5233 | 24.5204 | 24.5165 | 24.5128 | 24.5004 | 24.4855 | 24.4606 | 24.4371 | 25.3734 | 25.3734 | 25.3734 | 25.3734 | 25.3731 | 25.3729 | 25.3726 | 25.3723 | 25.3718 | 25.3704 | 25.3649 | 25.3616 | 25.3483 | 25.336
BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM | MINIMUM HEADROOM | SU 79589 67665 | YES | 9.8442 | 9.8429 | 9.8413 | 9.8378 | 9.7931 | 9.7386 | 9.6499 | 9.512 | 9.2735 | 9.2242 | 9.0191 | 8.5913 | 7.8306 | 7.7212 | 8.9128 | 8.9121 | 8.9112 | 8.9092 | 8.864 | 8.8106 | 8.7298 | 8.5972 | 8.364 | 8.3204 | 8.0813 | 7.3508 | 6.2773 | 5.8601 | 9.4271 | 9.4266 | 9.4259 | 9.4244 | 9.379 | 9.3259 | 9.2475 | 9.1166 | 8.8419 | 8.715 | 8.2806 | 7.4751 | 6.324 | 5.8305
|  | WOKINGHAM | CT |  |  | 9.8442 | 9.843 | 9.8414 | 9.8381 | 9.8008 | 9.7563 | 9.7041 | 9.6265 | 9.497 | 9.4668 | 9.3555 | 8.7942 | 8.1684 | 7.9496 | 8.9128 | 8.9122 | 8.9113 | 8.9094 | 8.8736 | 8.8305 | 8.7798 | 8.7075 | 8.5833 | 8.5588 | 8.4632 | 7.5991 | 6.6605 | 6.1343 | 9.4272 | 9.4267 | 9.426 | 9.4246 | 9.3892 | 9.3466 | 9.2962 | 9.2257 | 9.103 | 9.0142 | 8.6737 | 7.7346 | 6.7184 | 6.116
|  | WOKINGHAM | LW |  |  | 9.8442 | 9.8429 | 9.8413 | 9.8378 | 9.8083 | 9.7508 | 9.6499 | 9.512 | 9.2735 | 9.2242 | 9.0191 | 8.5913 | 7.8306 | 7.7212 | 8.9128 | 8.9121 | 8.9112 | 8.9092 | 8.8812 | 8.8253 | 8.7298 | 8.5972 | 8.364 | 8.3204 | 8.0813 | 7.3508 | 6.2773 | 5.8601 | 9.4271 | 9.4266 | 9.4259 | 9.4244 | 9.3969 | 9.3414 | 9.2475 | 9.1166 | 8.8419 | 8.715 | 8.2806 | 7.4751 | 6.324 | 5.8305
|  | WOKINGHAM | ST |  |  | 9.8447 | 9.8439 | 9.8429 | 9.8412 | 9.7931 | 9.7386 | 9.672 | 9.5949 | 9.4674 | 9.4139 | 9.2139 | 8.9917 | 8.3454 | 8.1096 | 8.9131 | 8.9126 | 8.9121 | 8.9111 | 8.864 | 8.8106 | 8.747 | 8.673 | 8.5492 | 8.4995 | 8.3109 | 8.0277 | 7.1802 | 6.7443 | 9.4274 | 9.427 | 9.4266 | 9.4259 | 9.379 | 9.3259 | 9.2633 | 9.1902 | 9.0675 | 9.0191 | 8.6936 | 8.2205 | 7.3231 | 6.8377
|  | WOKINGHAM | SP |  |  | 9.8456 | 9.8455 | 9.8454 | 9.8453 | 9.8445 | 9.8434 | 9.8403 | 9.8367 | 9.8308 | 9.816 | 9.7412 | 9.6743 | 9.4192 | 9.172 | 8.9136 | 8.9135 | 8.9135 | 8.9134 | 8.9129 | 8.9121 | 8.91 | 8.9074 | 8.9028 | 8.8895 | 8.8191 | 8.7592 | 8.5108 | 8.2699 | 9.4278 | 9.4277 | 9.4276 | 9.4276 | 9.4271 | 9.4264 | 9.4246 | 9.4224 | 9.4182 | 9.4053 | 9.3363 | 9.2785 | 8.9722 | 8.6387
BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE | MINIMUM HEADROOM | SU 64425 81624 | YES | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.752 | 34.6787 | 34.6043 | 34.5265 | 34.4065 | 34.3913 | 34.3425 | 34.1171 | 33.8601 | 33.3715 | 26.8325 | 26.8166 | 26.8144 | 26.8103 | 26.7341 | 26.6565 | 26.5777 | 26.4902 | 26.3605 | 26.3349 | 26.2532 | 25.8817 | 23.703 | 21.6937 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.1477 | 27.0744 | 26.9999 | 26.9221 | 26.8021 | 26.787 | 26.7382 | 26.5128 | 25.3939 | 23.3917
|  | WOODCOTE | CT |  |  | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.752 | 34.6787 | 34.6043 | 34.5265 | 34.4065 | 34.3913 | 34.3425 | 34.1171 | 33.8601 | 33.3715 | 26.8325 | 26.8166 | 26.8144 | 26.8103 | 26.7341 | 26.6565 | 26.5777 | 26.4902 | 26.3605 | 26.3349 | 26.2532 | 25.8817 | 23.703 | 21.6937 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.1477 | 27.0744 | 26.9999 | 26.9221 | 26.8021 | 26.787 | 26.7382 | 26.5128 | 25.3939 | 23.3917
|  | WOODCOTE | LW |  |  | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.3561 | 26.8328 | 26.8172 | 26.8154 | 26.8119 | 26.8085 | 26.8048 | 26.7951 | 26.7854 | 26.7756 | 26.7653 | 26.7324 | 26.5366 | 24.615 | 22.6701 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 26.3057 | 24.3696
|  | WOODCOTE | ST |  |  | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 26.8335 | 26.8328 | 26.8176 | 26.8162 | 26.8144 | 26.8123 | 26.8046 | 26.797 | 26.7903 | 26.7832 | 26.7609 | 26.7104 | 26.4003 | 25.1697 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 26.8629
|  | WOODCOTE | SP |  |  | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 34.8241 | 26.834 | 26.8337 | 26.8191 | 26.8187 | 26.8178 | 26.8168 | 26.8144 | 26.812 | 26.809 | 26.8063 | 26.7976 | 26.7772 | 26.7519 | 26.7255 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197 | 27.2197
NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE | MINIMUM HEADROOM | SU 43733 15470 | YES | 30.3736 | 30.3573 | 30.341 | 29.3452 | 29.2607 | 29.1732 | 29.0824 | 28.988 | 28.8807 | 28.8436 | 28.7231 | 28.5049 | 27.9544 | 26.6546 | 19.6661 | 19.6461 | 19.6227 | 18.6143 | 18.5169 | 18.4156 | 18.3035 | 18.1863 | 18.0546 | 17.9919 | 17.3375 | 15.6728 | 14.0696 | 12.5416 | 19.9543 | 19.9379 | 19.9216 | 18.9258 | 18.8413 | 18.7416 | 18.6295 | 18.5122 | 18.3804 | 18.3177 | 17.8648 | 16.2376 | 14.6707 | 13.1774
|  | WOODMILL LANE | CT |  |  | 30.452 | 30.4422 | 30.4324 | 29.8349 | 29.7851 | 29.7345 | 29.6831 | 29.6306 | 29.5739 | 29.5529 | 29.4868 | 28.7113 | 28.0349 | 26.7215 | 19.7436 | 19.7296 | 19.712 | 19.1003 | 19.0361 | 18.9701 | 18.9035 | 18.8282 | 18.747 | 18.7005 | 18.0884 | 15.8658 | 14.1479 | 12.6062 | 20.0326 | 20.0228 | 20.013 | 19.4156 | 19.3621 | 19.2962 | 19.2295 | 19.1541 | 19.0728 | 19.0262 | 18.616 | 16.4309 | 14.7493 | 13.2424
|  | WOODMILL LANE | LW |  |  | 30.3736 | 30.3573 | 30.341 | 29.3452 | 29.2607 | 29.1732 | 29.0824 | 28.988 | 28.8807 | 28.8436 | 28.7231 | 28.5049 | 27.9544 | 26.6546 | 19.6661 | 19.6461 | 19.6227 | 18.6143 | 18.5169 | 18.4156 | 18.3035 | 18.1863 | 18.0546 | 17.9919 | 17.3375 | 15.6728 | 14.0696 | 12.5416 | 19.9543 | 19.9379 | 19.9216 | 18.9258 | 18.8413 | 18.7416 | 18.6295 | 18.5122 | 18.3804 | 18.3177 | 17.8648 | 16.2376 | 14.6707 | 13.1774
|  | WOODMILL LANE | ST |  |  | 30.4912 | 30.4846 | 30.4781 | 30.0798 | 29.9262 | 29.7701 | 29.6108 | 29.4465 | 29.2085 | 29.1249 | 28.8543 | 28.5952 | 27.9653 | 27.7129 | 19.7851 | 19.7763 | 19.7655 | 19.3606 | 19.1994 | 19.0343 | 18.861 | 18.6816 | 18.4269 | 18.3258 | 18.014 | 17.5057 | 15.9797 | 14.856 | 20.0718 | 20.0653 | 20.0587 | 19.6604 | 19.5068 | 19.3507 | 19.187 | 19.0076 | 18.7529 | 18.6517 | 18.3398 | 18.0259 | 16.5225 | 15.4215
|  | WOODMILL LANE | SP |  |  | 30.5303 | 30.5271 | 30.5238 | 30.3246 | 30.3083 | 30.2919 | 30.2755 | 30.2591 | 30.2425 | 30.235 | 30.2099 | 30.1728 | 30.132 | 30.0755 | 19.8259 | 19.8218 | 19.8167 | 19.6151 | 19.5957 | 19.576 | 19.5545 | 19.5326 | 19.5093 | 19.4949 | 19.4537 | 19.3957 | 19.3363 | 19.2628 | 20.111 | 20.1077 | 20.1045 | 19.9053 | 19.8889 | 19.8726 | 19.8562 | 19.8397 | 19.8232 | 19.8157 | 19.7798 | 19.7216 | 19.6622 | 19.5886
COWLEY GSP | YARNTON BSP | WOODSTOCK | MINIMUM HEADROOM | SP 44795 17462 | NO | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 32.9426 | 32.0625 | 31.0421 | 30.2332 | 29.4483 | 32.3603 | 32.3501 | 32.3349 | 32.3038 | 32.273 | 31.6634 | 31.0167 | 30.7638 | 30.4886 | 30.1909 | 29.1644 | 27.9743 | 27.0308 | 26.1182 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.3207 | 31.6664 | 31.4105 | 31.132 | 30.8307 | 29.7921 | 28.5879 | 27.6332 | 26.7098
|  | WOODSTOCK | CT |  |  | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 32.9426 | 32.0625 | 31.0421 | 30.2332 | 29.4483 | 32.3603 | 32.3501 | 32.3349 | 32.3038 | 32.273 | 31.6634 | 31.0167 | 30.7638 | 30.4886 | 30.1909 | 29.1644 | 27.9743 | 27.0308 | 26.1182 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.3207 | 31.6664 | 31.4105 | 31.132 | 30.8307 | 29.7921 | 28.5879 | 27.6332 | 26.7098
|  | WOODSTOCK | LW |  |  | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 32.4471 | 31.4268 | 30.6178 | 29.8344 | 32.3605 | 32.3504 | 32.3354 | 32.3047 | 32.2743 | 31.6965 | 31.4654 | 31.2124 | 30.9372 | 30.6395 | 29.613 | 28.423 | 27.4794 | 26.5663 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.3542 | 32.1203 | 31.8643 | 31.5858 | 31.2847 | 30.2459 | 29.0419 | 28.0871 | 27.1632
|  | WOODSTOCK | ST |  |  | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 32.8285 | 32.3234 | 32.3667 | 32.3612 | 32.3536 | 32.3409 | 32.3252 | 32.3065 | 32.2973 | 32.2874 | 32.2785 | 32.2172 | 31.4963 | 30.6712 | 30.0578 | 29.4687 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.1516 | 31.3167 | 30.6961 | 30.1
|  | WOODSTOCK | SP |  |  | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 33.0323 | 32.3722 | 32.3712 | 32.3694 | 32.3673 | 32.3617 | 32.3552 | 32.3517 | 32.348 | 32.3434 | 32.3395 | 32.3258 | 32.31 | 32.2983 | 32.287 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868 | 32.4868
BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON | MINIMUM HEADROOM | SU 44145 11242 | YES | 8.9349 | 8.9342 | 8.9332 | 8.9311 | 8.9292 | 8.9272 | 8.9252 | 8.9229 | 8.9206 | 8.9181 | 8.9108 | 8.8985 | 8.8855 | 8.8291 | 8.119 | 8.1084 | 8.0945 | 8.0652 | 8.0368 | 8.0086 | 7.9806 | 7.9474 | 7.9145 | 7.879 | 7.7738 | 7.5967 | 7.4116 | 7.2291 | 7.4853 | 7.4748 | 7.4609 | 7.4316 | 7.4032 | 7.3751 | 7.3471 | 7.314 | 7.2811 | 7.2457 | 7.1408 | 6.964 | 6.7792 | 6.5971
|  | WOOLSTON | CT |  |  | 8.9349 | 8.9342 | 8.9332 | 8.9311 | 8.9292 | 8.9272 | 8.9252 | 8.9229 | 8.9206 | 8.9181 | 8.9108 | 8.8985 | 8.8855 | 8.8291 | 8.119 | 8.1084 | 8.0945 | 8.0652 | 8.0368 | 8.0086 | 7.9806 | 7.9474 | 7.9145 | 7.879 | 7.7738 | 7.5967 | 7.4116 | 7.2291 | 7.4853 | 7.4748 | 7.4609 | 7.4316 | 7.4032 | 7.3751 | 7.3471 | 7.314 | 7.2811 | 7.2457 | 7.1408 | 6.964 | 6.7792 | 6.5971
|  | WOOLSTON | LW |  |  | 8.9357 | 8.9355 | 8.9352 | 8.9347 | 8.9343 | 8.9338 | 8.9314 | 8.9291 | 8.9268 | 8.9243 | 8.917 | 8.9047 | 8.8917 | 8.879 | 8.1302 | 8.1275 | 8.1241 | 8.1169 | 8.1099 | 8.1028 | 8.0693 | 8.0361 | 8.0032 | 7.9677 | 7.8625 | 7.6855 | 7.5003 | 7.3179 | 7.4964 | 7.4938 | 7.4904 | 7.4832 | 7.4762 | 7.4692 | 7.4357 | 7.4026 | 7.3697 | 7.3343 | 7.2293 | 7.0526 | 6.8678 | 6.6857
|  | WOOLSTON | ST |  |  | 8.9358 | 8.9356 | 8.9355 | 8.9353 | 8.935 | 8.9347 | 8.933 | 8.9313 | 8.9297 | 8.928 | 8.9231 | 8.9148 | 8.9065 | 8.8983 | 8.1314 | 8.1298 | 8.1279 | 8.1246 | 8.1206 | 8.1157 | 8.0914 | 8.0674 | 8.0449 | 8.0207 | 7.9497 | 7.8317 | 7.7122 | 7.5939 | 7.4977 | 7.4961 | 7.4941 | 7.4909 | 7.4869 | 7.482 | 7.4578 | 7.4338 | 7.4113 | 7.3872 | 7.3163 | 7.1985 | 7.0793 | 6.9612
|  | WOOLSTON | SP |  |  | 8.9359 | 8.9359 | 8.9358 | 8.9358 | 8.9357 | 8.9356 | 8.9351 | 8.9345 | 8.9338 | 8.9331 | 8.9312 | 8.928 | 8.925 | 8.922 | 8.1331 | 8.1328 | 8.1325 | 8.1322 | 8.1311 | 8.1298 | 8.1215 | 8.1133 | 8.1027 | 8.0933 | 8.066 | 8.0209 | 7.9766 | 7.9345 | 7.4994 | 7.4991 | 7.4988 | 7.4985 | 7.4974 | 7.4961 | 7.4878 | 7.4796 | 7.469 | 7.4596 | 7.4324 | 7.3874 | 7.3432 | 7.3012
MINETY GSP | SWINDON BSP | WOOTTON BASSETT | MINIMUM HEADROOM | SU 07587 81123 | NO | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6944 | 16.6933 | 16.6921 | 16.6909 | 16.689 | 16.6839 | 16.6674 | 16.54 | 15.2874 | 14.0231 | 26.4556 | 26.4543 | 26.4526 | 26.4496 | 26.4465 | 26.4432 | 26.4332 | 26.423 | 26.4127 | 26.4019 | 26.3661 | 25.5517 | 24.0739 | 22.5824 | 26.7366 | 26.7357 | 26.7344 | 26.7323 | 26.73 | 26.7276 | 26.7202 | 26.7128 | 26.7053 | 26.6975 | 26.6713 | 25.923 | 24.5276 | 23.0355
|  | WOOTTON BASSETT | CT |  |  | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6105 | 15.3579 | 14.0939 | 26.4556 | 26.4543 | 26.4526 | 26.4496 | 26.4465 | 26.4432 | 26.4398 | 26.4296 | 26.4194 | 26.4086 | 26.3727 | 25.6349 | 24.1572 | 22.666 | 26.7366 | 26.7357 | 26.7344 | 26.7323 | 26.73 | 26.7276 | 26.7251 | 26.7177 | 26.7102 | 26.7023 | 26.6762 | 25.9995 | 24.6108 | 23.1191
|  | WOOTTON BASSETT | LW |  |  | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.54 | 15.2874 | 14.0231 | 26.4556 | 26.4543 | 26.4526 | 26.4496 | 26.4465 | 26.4432 | 26.4332 | 26.423 | 26.4127 | 26.4019 | 26.3661 | 25.5517 | 24.0739 | 22.5824 | 26.7366 | 26.7357 | 26.7344 | 26.7323 | 26.73 | 26.7276 | 26.7202 | 26.7128 | 26.7053 | 26.6975 | 26.6713 | 25.923 | 24.5276 | 23.0355
|  | WOOTTON BASSETT | ST |  |  | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.3723 | 15.5701 | 26.456 | 26.4551 | 26.4541 | 26.4525 | 26.4507 | 26.4484 | 26.4435 | 26.4386 | 26.4316 | 26.4242 | 26.3996 | 26.2967 | 25.3539 | 24.4075 | 26.7369 | 26.7363 | 26.7355 | 26.7344 | 26.733 | 26.7314 | 26.7278 | 26.7242 | 26.7191 | 26.7137 | 26.6958 | 26.5715 | 25.7411 | 24.8613
|  | WOOTTON BASSETT | SP |  |  | 16.6956 | 16.6956 | 16.6956 | 16.6956 | 16.6944 | 16.6933 | 16.6921 | 16.6909 | 16.689 | 16.6839 | 16.6674 | 16.6596 | 16.635 | 16.6144 | 26.4566 | 26.4562 | 26.4557 | 26.4553 | 26.4534 | 26.4514 | 26.4485 | 26.4455 | 26.4414 | 26.4334 | 26.4074 | 26.3728 | 26.3121 | 26.2131 | 26.7373 | 26.737 | 26.7367 | 26.7364 | 26.7347 | 26.7329 | 26.7305 | 26.728 | 26.7245 | 26.7172 | 26.6938 | 26.6665 | 26.6156 | 26.4875
COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD | MINIMUM HEADROOM | SU 49244 98269 | YES | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 17.9386 | 17.8348 | 17.7265 | 17.6142 | 17.4437 | 17.42 | 17.3391 | 17.216 | 16.9488 | 16.9311 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 16.9353 | 16.8316 | 16.7233 | 16.611 | 16.4404 | 16.4168 | 16.3358 | 16.1742 | 15.4506 | 14.9921 | 16.9326 | 16.929 | 16.9252 | 16.9189 | 16.8157 | 16.7071 | 16.5926 | 16.4745 | 16.2982 | 16.2685 | 16.1547 | 15.5857 | 14.8754 | 14.4298
|  | WOOTTON ROAD | CT |  |  | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 16.9682 | 16.512 | 16.0715 | 16.9326 | 16.929 | 16.9252 | 16.9189 | 16.9137 | 16.908 | 16.9034 | 16.8976 | 16.8917 | 16.8857 | 16.8267 | 16.3805 | 15.9377 | 15.51
|  | WOOTTON ROAD | LW |  |  | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 17.9386 | 17.8348 | 17.7265 | 17.6142 | 17.4437 | 17.42 | 17.3391 | 17.216 | 16.9488 | 16.9311 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 16.9353 | 16.8316 | 16.7233 | 16.611 | 16.4404 | 16.4168 | 16.3358 | 16.1742 | 15.4506 | 14.9921 | 16.933 | 16.9297 | 16.9262 | 16.9207 | 16.8157 | 16.7071 | 16.5926 | 16.4745 | 16.2982 | 16.2685 | 16.1547 | 15.5857 | 14.8754 | 14.4298
|  | WOOTTON ROAD | ST |  |  | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 16.889 | 16.9336 | 16.9313 | 16.929 | 16.9259 | 16.9231 | 16.9196 | 16.9149 | 16.9105 | 16.9065 | 16.9024 | 16.8905 | 16.8675 | 16.5812 | 16.3036
|  | WOOTTON ROAD | SP |  |  | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 18.0391 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 17.0358 | 16.9346 | 16.9332 | 16.9322 | 16.9311 | 16.9301 | 16.9288 | 16.9271 | 16.9255 | 16.9235 | 16.9219 | 16.9173 | 16.9097 | 16.9026 | 16.8961
BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM | MINIMUM HEADROOM | SU 82093 44312 | YES | 32.9003 | 32.8592 | 32.8235 | 32.8013 | 32.7773 | 32.7484 | 32.6337 | 32.5189 | 32.4061 | 32.2874 | 31.9123 | 31.0678 | 30.072 | 28.7342 | 34.2543 | 34.2333 | 34.2152 | 34.2039 | 34.1917 | 34.1769 | 34.1186 | 34.0602 | 34.0027 | 33.9423 | 33.7515 | 32.418 | 30.7952 | 29.1684 | 34.632 | 34.6169 | 34.6038 | 34.5957 | 34.5869 | 34.5763 | 34.5342 | 34.4921 | 34.4507 | 34.4071 | 34.1587 | 32.7867 | 31.1688 | 29.547
|  | WRECCLESHAM | CT |  |  | 32.9003 | 32.8592 | 32.8235 | 32.8013 | 32.7773 | 32.7484 | 32.7163 | 32.6016 | 32.4888 | 32.3701 | 31.9951 | 31.1504 | 30.1546 | 28.8484 | 34.2543 | 34.2333 | 34.2152 | 34.2039 | 34.1917 | 34.1769 | 34.1606 | 34.1022 | 34.0448 | 33.9844 | 33.7936 | 32.5525 | 30.9299 | 29.303 | 34.632 | 34.6169 | 34.6038 | 34.5957 | 34.5869 | 34.5763 | 34.5645 | 34.5224 | 34.481 | 34.4375 | 34.2933 | 32.9208 | 31.3031 | 29.6811
|  | WRECCLESHAM | LW |  |  | 32.9003 | 32.8592 | 32.8235 | 32.8013 | 32.7773 | 32.7484 | 32.6337 | 32.5189 | 32.4061 | 32.2874 | 31.9123 | 31.0678 | 30.072 | 28.7342 | 34.2543 | 34.2333 | 34.2152 | 34.2039 | 34.1917 | 34.1769 | 34.1186 | 34.0602 | 34.0027 | 33.9423 | 33.7515 | 32.418 | 30.7952 | 29.1684 | 34.632 | 34.6169 | 34.6038 | 34.5957 | 34.5869 | 34.5763 | 34.5342 | 34.4921 | 34.4507 | 34.4071 | 34.1587 | 32.7867 | 31.1688 | 29.547
|  | WRECCLESHAM | ST |  |  | 32.906 | 32.8759 | 32.852 | 32.8407 | 32.8262 | 32.8066 | 32.742 | 32.6774 | 32.6006 | 32.5194 | 32.263 | 31.6816 | 31.0274 | 30.3907 | 34.2572 | 34.2419 | 34.2297 | 34.2239 | 34.2166 | 34.2066 | 34.1737 | 34.1408 | 34.1017 | 34.0604 | 33.9299 | 33.4182 | 32.3521 | 31.3145 | 34.6341 | 34.6231 | 34.6143 | 34.6101 | 34.6048 | 34.5976 | 34.5739 | 34.5502 | 34.522 | 34.4922 | 34.3982 | 33.7838 | 32.721 | 31.6866
|  | WRECCLESHAM | SP |  |  | 32.9122 | 32.8921 | 32.8786 | 32.8755 | 32.8701 | 32.8628 | 32.8436 | 32.8246 | 32.8019 | 32.7703 | 32.6705 | 32.4349 | 32.1455 | 31.8444 | 34.2603 | 34.2501 | 34.2432 | 34.2417 | 34.2389 | 34.2352 | 34.2254 | 34.2158 | 34.2042 | 34.1881 | 34.1373 | 34.0174 | 33.8701 | 33.6835 | 34.6364 | 34.629 | 34.624 | 34.6229 | 34.6209 | 34.6183 | 34.6112 | 34.6042 | 34.5959 | 34.5843 | 34.5477 | 34.4612 | 34.3551 | 34.0484
MINETY GSP | TOOTHILL BSP | WROUGHTON | MINIMUM HEADROOM | SU 14446 81504 | NO | 27.1369 | 27.0938 | 27.0371 | 26.9174 | 26.7186 | 26.4836 | 26.2046 | 25.9188 | 25.5513 | 25.3722 | 24.8212 | 23.9139 | 22.8318 | 22.0889 | 25.222 | 25.1673 | 25.0955 | 24.9436 | 24.7252 | 24.4627 | 24.1466 | 23.824 | 23.4202 | 23.2019 | 22.5351 | 21.4374 | 20.1589 | 19.2229 | 25.5898 | 25.5518 | 25.4875 | 25.3451 | 25.1324 | 24.878 | 24.5729 | 24.2611 | 23.868 | 23.6612 | 23.0284 | 21.9868 | 20.7661 | 19.8869
|  | WROUGHTON | CT |  |  | 27.1369 | 27.0938 | 27.0371 | 26.9174 | 26.8004 | 26.6838 | 26.5674 | 26.4275 | 26.2849 | 26.1374 | 25.6994 | 24.9345 | 24.1408 | 23.402 | 25.222 | 25.1673 | 25.0955 | 24.9436 | 24.7955 | 24.648 | 24.501 | 24.3243 | 24.1454 | 23.9587 | 23.4049 | 22.4496 | 21.4596 | 20.5277 | 25.5898 | 25.5518 | 25.4875 | 25.3451 | 25.2062 | 25.0677 | 24.9297 | 24.7639 | 24.5957 | 24.4204 | 23.9008 | 23.0015 | 22.0692 | 21.1941
|  | WROUGHTON | LW |  |  | 27.1433 | 27.1049 | 27.0545 | 26.9477 | 26.7186 | 26.4836 | 26.2046 | 25.9188 | 25.5513 | 25.3722 | 24.8212 | 23.9139 | 22.8318 | 22.0889 | 25.2302 | 25.1815 | 25.1175 | 24.9821 | 24.7252 | 24.4627 | 24.1466 | 23.824 | 23.4202 | 23.2019 | 22.5351 | 21.4374 | 20.1589 | 19.2229 | 25.5953 | 25.5627 | 25.5082 | 25.3812 | 25.1324 | 24.878 | 24.5729 | 24.2611 | 23.868 | 23.6612 | 23.0284 | 21.9868 | 20.7661 | 19.8869
|  | WROUGHTON | ST |  |  | 27.1507 | 27.1187 | 27.081 | 27.0165 | 26.9367 | 26.8402 | 26.7448 | 26.6498 | 26.5517 | 26.4493 | 26.1447 | 25.6542 | 25.1186 | 24.6269 | 25.2395 | 25.199 | 25.1512 | 25.0693 | 24.9683 | 24.8461 | 24.7256 | 24.6058 | 24.4828 | 24.3537 | 23.971 | 23.3539 | 22.6918 | 22.0744 | 25.6015 | 25.5744 | 25.5394 | 25.463 | 25.3682 | 25.2536 | 25.1405 | 25.0279 | 24.9122 | 24.791 | 24.4313 | 23.8515 | 23.2265 | 22.6462
|  | WROUGHTON | SP |  |  | 27.1879 | 27.1839 | 27.18 | 27.1764 | 27.1589 | 27.1381 | 27.1086 | 27.0793 | 27.0414 | 27.0004 | 26.8788 | 26.6942 | 26.4977 | 26.3123 | 25.2867 | 25.2816 | 25.2767 | 25.2721 | 25.25 | 25.2238 | 25.1865 | 25.1493 | 25.1015 | 25.0502 | 24.8984 | 24.666 | 24.4237 | 24.1951 | 25.633 | 25.6296 | 25.6263 | 25.6233 | 25.6084 | 25.5908 | 25.5657 | 25.5376 | 25.493 | 25.4447 | 25.3018 | 25.0835 | 24.8546 | 24.6388
AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH | MINIMUM HEADROOM | SU 88582 91845 | YES | 22.4195 | 22.4195 | 22.4195 | 22.4195 | 22.3568 | 22.2929 | 22.2275 | 22.1596 | 22.054 | 22.0179 | 21.9004 | 21.8033 | 21.2496 | 20.2632 | 16.9926 | 16.984 | 16.9758 | 16.9612 | 16.9153 | 16.8436 | 16.7654 | 16.3675 | 15.9542 | 15.6625 | 14.8847 | 13.6682 | 12.3988 | 11.2496 | 17.3692 | 17.3692 | 17.3692 | 17.3692 | 17.3065 | 17.2426 | 17.1772 | 16.9949 | 16.6071 | 16.3335 | 15.604 | 14.4619 | 13.2505 | 12.1723
|  | WYCOMBE MARSH | CT |  |  | 22.4195 | 22.4195 | 22.4195 | 22.4195 | 22.4192 | 22.4187 | 22.4178 | 22.4166 | 22.414 | 22.4135 | 22.4109 | 22.3862 | 21.3393 | 20.353 | 16.9926 | 16.984 | 16.9758 | 16.9612 | 16.9439 | 16.9251 | 16.7833 | 16.3675 | 15.9542 | 15.6625 | 14.8847 | 13.6682 | 12.4511 | 11.302 | 17.3692 | 17.3692 | 17.3692 | 17.3692 | 17.3689 | 17.3683 | 17.3675 | 16.9949 | 16.6071 | 16.3335 | 15.604 | 14.4619 | 13.3191 | 12.2411
|  | WYCOMBE MARSH | LW |  |  | 22.4195 | 22.4195 | 22.4195 | 22.4195 | 22.3928 | 22.3641 | 22.3332 | 22.3 | 22.2474 | 22.2399 | 22.2113 | 22.1576 | 21.2496 | 20.2632 | 16.994 | 16.9864 | 16.9795 | 16.9677 | 16.9267 | 16.8825 | 16.8333 | 16.5132 | 16.0499 | 15.7512 | 14.9473 | 13.6984 | 12.3988 | 11.2496 | 17.3692 | 17.3692 | 17.3692 | 17.3692 | 17.3424 | 17.3138 | 17.2829 | 17.1242 | 16.6865 | 16.4059 | 15.6503 | 14.4758 | 13.2505 | 12.1723
|  | WYCOMBE MARSH | ST |  |  | 22.4195 | 22.4195 | 22.4195 | 22.4195 | 22.3568 | 22.2929 | 22.2275 | 22.1596 | 22.054 | 22.0179 | 21.9004 | 21.8033 | 21.5204 | 21.4367 | 16.997 | 16.9943 | 16.9888 | 16.9845 | 16.9153 | 16.8436 | 16.7654 | 16.6836 | 16.5646 | 16.5188 | 16.0139 | 15.1085 | 14.0514 | 13.2281 | 17.3692 | 17.3692 | 17.3692 | 17.3692 | 17.3065 | 17.2426 | 17.1772 | 17.1093 | 17.0037 | 16.9676 | 16.6311 | 15.7761 | 14.7672 | 13.9899
|  | WYCOMBE MARSH | SP |  |  | 22.4195 | 22.4195 | 22.4195 | 22.4195 | 22.4144 | 22.4095 | 22.4044 | 22.3993 | 22.3913 | 22.369 | 22.2973 | 22.2626 | 22.1507 | 22.056 | 16.9978 | 16.9963 | 16.9946 | 16.9928 | 16.9844 | 16.9757 | 16.9657 | 16.9553 | 16.9415 | 16.9154 | 16.8337 | 16.7837 | 16.6573 | 16.5382 | 17.3692 | 17.3692 | 17.3692 | 17.3692 | 17.3641 | 17.3591 | 17.3541 | 17.349 | 17.341 | 17.3187 | 17.247 | 17.2123 | 17.1003 | 17.0057
LOVEDEAN GSP | WYMERING BSP | WYMERING | MINIMUM HEADROOM | SU 64974 05375 | NO | 35.1725 | 35.1725 | 35.1725 | 35.1725 | 35.1614 | 35.1497 | 35.1373 | 35.1239 | 35.102 | 35.0939 | 35.0399 | 35.0014 | 34.875 | 34.3279 | 32.9092 | 32.8968 | 32.8805 | 32.8461 | 32.8121 | 32.7779 | 32.6061 | 32.4674 | 32.327 | 32.1805 | 31.7439 | 30.9714 | 30.1586 | 29.3903 | 34.1319 | 34.1219 | 34.1088 | 34.0811 | 34.0536 | 34.0259 | 33.6373 | 33.4939 | 33.3488 | 33.1973 | 32.7458 | 31.948 | 31.1088 | 30.3145
|  | WYMERING | CT |  |  | 35.1725 | 35.1725 | 35.1725 | 35.1725 | 35.1719 | 35.1708 | 35.1691 | 35.1666 | 35.1612 | 35.1602 | 35.155 | 35.0798 | 34.9745 | 34.3279 | 32.9092 | 32.8968 | 32.8805 | 32.8461 | 32.8121 | 32.7779 | 32.6061 | 32.4674 | 32.327 | 32.1805 | 31.7439 | 30.9714 | 30.1586 | 29.3903 | 34.1319 | 34.1219 | 34.1088 | 34.0811 | 34.0536 | 34.0259 | 33.6373 | 33.4939 | 33.3488 | 33.1973 | 32.7458 | 31.948 | 31.1088 | 30.3145
|  | WYMERING | LW |  |  | 35.1725 | 35.1725 | 35.1725 | 35.1725 | 35.1705 | 35.1664 | 35.1599 | 35.1509 | 35.1329 | 35.1298 | 35.1139 | 35.0753 | 34.9463 | 34.7106 | 32.9116 | 32.9008 | 32.8867 | 32.857 | 32.8261 | 32.7934 | 32.7752 | 32.7546 | 32.7251 | 32.6292 | 32.1817 | 31.4137 | 30.5732 | 29.814 | 34.1338 | 34.1251 | 34.1138 | 34.0899 | 34.0647 | 34.0375 | 34.0216 | 33.974 | 33.8162 | 33.6626 | 33.2002 | 32.4069 | 31.5399 | 30.7547
|  | WYMERING | ST |  |  | 35.1725 | 35.1725 | 35.1725 | 35.1725 | 35.1614 | 35.1497 | 35.1373 | 35.1239 | 35.102 | 35.0939 | 35.0639 | 35.0342 | 34.9289 | 34.8948 | 32.915 | 32.9071 | 32.8978 | 32.8817 | 32.851 | 32.8156 | 32.7929 | 32.7694 | 32.7395 | 32.723 | 32.6681 | 32.3336 | 31.7342 | 31.2102 | 34.1366 | 34.1302 | 34.1227 | 34.1098 | 34.0828 | 34.0521 | 34.0314 | 34.0099 | 33.9816 | 33.9667 | 33.8933 | 33.36 | 32.7436 | 32.2027
|  | WYMERING | SP |  |  | 35.1725 | 35.1725 | 35.1725 | 35.1725 | 35.1671 | 35.1618 | 35.1564 | 35.1509 | 35.1423 | 35.1182 | 35.0399 | 35.0014 | 34.875 | 34.7672 | 32.924 | 32.9229 | 32.9219 | 32.9209 | 32.9108 | 32.8999 | 32.8909 | 32.8819 | 32.8686 | 32.8412 | 32.7533 | 32.6989 | 32.5568 | 32.4341 | 34.1438 | 34.1429 | 34.1421 | 34.1413 | 34.1321 | 34.1223 | 34.114 | 34.1057 | 34.0933 | 34.0666 | 33.9805 | 33.9292 | 33.7902 | 33.6704
COWLEY GSP | YARNTON BSP | YARNTON | MINIMUM HEADROOM | SP 48277 12108 | NO | 26.3544 | 26.3496 | 26.3421 | 26.3286 | 26.1891 | 26.0428 | 25.8914 | 25.7325 | 25.4945 | 25.453 | 25.3133 | 24.86 | 24.0928 | 23.6492 | 9.0384 | 9.0346 | 9.0286 | 9.0182 | 8.8819 | 8.6023 | 8.2986 | 7.984 | 7.6029 | 7.4443 | 6.9937 | 6.2924 | 5.4635 | 4.9611 | 26.0598 | 26.0559 | 26.0499 | 26.0394 | 25.9031 | 25.6109 | 25.3082 | 24.9946 | 24.6145 | 24.4567 | 24.0081 | 23.3099 | 22.4841 | 21.9847
|  | YARNTON | CT |  |  | 26.3553 | 26.3511 | 26.3445 | 26.3328 | 26.3195 | 26.3049 | 26.2893 | 26.2744 | 26.2575 | 26.2471 | 26.2169 | 25.9716 | 25.4804 | 25.0419 | 9.0391 | 9.0357 | 9.0305 | 9.0214 | 9.011 | 8.9578 | 8.7704 | 8.5998 | 8.4398 | 8.3121 | 7.9712 | 7.4137 | 6.8608 | 6.3636 | 26.0605 | 26.0571 | 26.0518 | 26.0426 | 26.0322 | 25.9658 | 25.7795 | 25.6099 | 25.4509 | 25.324 | 24.9851 | 24.4308 | 23.881 | 23.3867
|  | YARNTON | LW |  |  | 26.3544 | 26.3496 | 26.3421 | 26.3286 | 26.1891 | 26.0428 | 25.8914 | 25.7325 | 25.4945 | 25.453 | 25.3133 | 24.86 | 24.0928 | 23.6492 | 9.0384 | 9.0346 | 9.0286 | 9.0182 | 8.8819 | 8.6023 | 8.2986 | 7.984 | 7.6029 | 7.4443 | 6.9937 | 6.2924 | 5.4635 | 4.9611 | 26.0598 | 26.0559 | 26.0499 | 26.0394 | 25.9031 | 25.6109 | 25.3082 | 24.9946 | 24.6145 | 24.4567 | 24.0081 | 23.3099 | 22.4841 | 21.9847
|  | YARNTON | ST |  |  | 26.3824 | 26.3541 | 26.3501 | 26.3443 | 26.3158 | 26.2851 | 26.2547 | 26.223 | 26.1774 | 26.1575 | 26.0933 | 26.0243 | 25.8675 | 25.7471 | 9.0609 | 9.0382 | 9.0349 | 9.0303 | 9.0036 | 8.9749 | 8.9464 | 8.9165 | 8.79 | 8.6901 | 8.4138 | 8.0237 | 7.5639 | 7.2088 | 26.0823 | 26.0595 | 26.0562 | 26.0516 | 26.0249 | 25.9962 | 25.9676 | 25.9377 | 25.7983 | 25.6989 | 25.424 | 25.036 | 24.5782 | 24.2251
|  | YARNTON | SP |  |  | 26.3843 | 26.3578 | 26.3562 | 26.3547 | 26.3516 | 26.348 | 26.3449 | 26.3418 | 26.3385 | 26.3353 | 26.3249 | 26.3118 | 26.2882 | 26.2659 | 9.0625 | 9.0412 | 9.0399 | 9.0386 | 9.0361 | 9.0332 | 9.0308 | 9.0283 | 9.0257 | 9.0231 | 9.0142 | 9.0034 | 8.9819 | 8.8608 | 26.0839 | 26.0625 | 26.0612 | 26.06 | 26.0574 | 26.0546 | 26.0521 | 26.0496 | 26.047 | 26.0444 | 26.0355 | 26.0247 | 25.9945 | 25.8692
BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON | MINIMUM HEADROOM | SU 53699 74307 | YES | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.5836 | 27.5443 | 27.5042 | 27.4628 | 27.3987 | 27.377 | 27.3075 | 27.2518 | 27.0609 | 27.003 | 26.2998 | 26.2959 | 26.2913 | 26.2829 | 26.2437 | 26.1976 | 26.1526 | 26.1064 | 26.0383 | 26.0124 | 25.9308 | 25.8539 | 25.5397 | 24.8793 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.562 | 26.5227 | 26.4826 | 26.4412 | 26.3771 | 26.3554 | 26.2859 | 26.048 | 25.3796 | 24.7187
|  | YATTENDON | CT |  |  | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.2613 | 26.3008 | 26.2977 | 26.294 | 26.2876 | 26.2818 | 26.2766 | 26.2714 | 26.2656 | 26.2598 | 26.2537 | 26.2358 | 26.2044 | 25.7297 | 25.0715 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.227 | 25.5702 | 24.9096
|  | YATTENDON | LW |  |  | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.0972 | 26.2998 | 26.2959 | 26.2913 | 26.2829 | 26.2752 | 26.2679 | 26.2622 | 26.2564 | 26.2506 | 26.2445 | 26.2266 | 26.1499 | 25.5397 | 24.8793 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.048 | 25.3796 | 24.7187
|  | YATTENDON | ST |  |  | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.5836 | 27.5443 | 27.5042 | 27.4628 | 27.3987 | 27.377 | 27.3075 | 27.2518 | 27.0609 | 27.003 | 26.3003 | 26.2972 | 26.2937 | 26.2884 | 26.2437 | 26.1976 | 26.1526 | 26.1064 | 26.0383 | 26.0124 | 25.9308 | 25.8539 | 25.642 | 25.3347 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.562 | 26.5227 | 26.4826 | 26.4412 | 26.3771 | 26.3554 | 26.2859 | 26.2302 | 25.6462 | 25.176
|  | YATTENDON | SP |  |  | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 27.6223 | 26.3029 | 26.3018 | 26.3009 | 26.3001 | 26.2983 | 26.2965 | 26.2948 | 26.2932 | 26.2912 | 26.2896 | 26.2848 | 26.2767 | 26.2685 | 26.2607 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007 | 26.6007
MELKSHAM GSP | CHIPPENHAM | YATTON KEYNALL | MINIMUM HEADROOM | ST 87300 75782 | YES | 74.6668 | 74.6261 | 74.6035 | 73.6946 | 73.36 | 73.0171 | 72.6573 | 72.288 | 71.779 | 71.6668 | 71.3052 | 70.7341 | 68.9424 | 67.1563 | 73.9844 | 73.94 | 73.9164 | 73.0052 | 72.668 | 72.3153 | 71.8672 | 71.4095 | 70.8148 | 70.6119 | 69.977 | 68.1965 | 65.7696 | 63.7602 | 73.5337 | 73.5191 | 73.5045 | 72.6121 | 72.2966 | 71.9733 | 71.6389 | 71.295 | 70.8107 | 70.7245 | 70.4414 | 70.0032 | 69.4247 | 69.2354
|  | YATTON KEYNALL | CT |  |  | 74.738 | 74.7037 | 74.6879 | 74.1378 | 74.0766 | 74.0147 | 73.9537 | 73.8844 | 73.816 | 73.7724 | 73.6412 | 72.8681 | 71.5957 | 69.8381 | 74.0557 | 74.0179 | 74.0011 | 73.449 | 73.3854 | 73.321 | 73.2198 | 73.062 | 72.9079 | 72.7736 | 72.3692 | 70.5224 | 68.4485 | 66.4676 | 73.604 | 73.5952 | 73.5864 | 73.051 | 73.0071 | 72.9632 | 72.9193 | 72.8754 | 72.8315 | 72.8139 | 72.7613 | 72.1211 | 71.8952 | 71.7343
|  | YATTON KEYNALL | LW |  |  | 74.6668 | 74.6261 | 74.6035 | 73.6946 | 73.36 | 73.0171 | 72.6573 | 72.288 | 71.779 | 71.6668 | 71.3052 | 70.7341 | 68.9424 | 67.1563 | 73.9844 | 73.94 | 73.9164 | 73.0052 | 72.668 | 72.3153 | 71.8672 | 71.4095 | 70.8148 | 70.6119 | 69.977 | 68.1965 | 65.7696 | 63.7602 | 73.5337 | 73.5191 | 73.5045 | 72.6121 | 72.2966 | 71.9733 | 71.6389 | 71.295 | 70.8107 | 70.7245 | 70.4414 | 70.0032 | 69.4247 | 69.2354
|  | YATTON KEYNALL | ST |  |  | 74.8326 | 74.7651 | 74.7346 | 74.3696 | 74.3114 | 74.2511 | 74.1897 | 74.1276 | 74.0521 | 74.0125 | 73.8914 | 73.7163 | 73.5085 | 73.2575 | 74.1585 | 74.0825 | 74.0486 | 73.6825 | 73.6228 | 73.5607 | 73.4974 | 73.4334 | 73.3067 | 73.2051 | 72.8962 | 72.4048 | 71.4973 | 70.2382 | 73.6391 | 73.6332 | 73.6274 | 73.2704 | 73.2233 | 73.1759 | 73.1281 | 73.0797 | 73.0209 | 72.9991 | 72.932 | 72.8477 | 72.7334 | 72.6423
|  | YATTON KEYNALL | SP |  |  | 74.8703 | 74.8113 | 74.7836 | 74.6029 | 74.5675 | 74.5322 | 74.497 | 74.4615 | 74.4166 | 74.334 | 74.0741 | 73.9034 | 73.5148 | 73.1659 | 74.1966 | 74.1298 | 74.0987 | 73.9177 | 73.8817 | 73.8457 | 73.8098 | 73.7737 | 73.7281 | 73.6445 | 73.3817 | 73.1352 | 72.6104 | 72.1253 | 73.6742 | 73.6713 | 73.6683 | 73.4898 | 73.4591 | 73.4287 | 73.3983 | 73.3676 | 73.3279 | 73.2523 | 73.0134 | 72.8787 | 72.5293 | 72.2195
AXMINSTER | YEOVIL BSP | YEOVIL | MINIMUM HEADROOM | ST 57690 16833 | YES | 47.3164 | 47.3047 | 47.2929 | 46.5774 | 46.5169 | 46.4544 | 46.3898 | 46.3229 | 46.2477 | 46.2214 | 46.1364 | 45.4337 | 43.8005 | 42.4822 | 45.0503 | 45.0262 | 45.0024 | 44.2682 | 44.1849 | 44.0967 | 43.4669 | 42.7519 | 41.9944 | 41.2977 | 39.9443 | 37.7443 | 35.8454 | 34.3424 | 45.6093 | 45.5976 | 45.5859 | 44.8703 | 44.8098 | 44.7474 | 44.41 | 43.7353 | 43.0203 | 42.3653 | 41.0909 | 38.9841 | 37.1396 | 35.6213
|  | YEOVIL | CT |  |  | 47.3727 | 47.3657 | 47.3586 | 46.9293 | 46.823 | 46.715 | 46.6053 | 46.4917 | 46.334 | 46.3042 | 46.2094 | 45.4337 | 43.8005 | 42.4822 | 45.1066 | 45.0873 | 45.0682 | 44.6202 | 44.4911 | 44.3575 | 43.7734 | 43.0116 | 42.1718 | 41.4715 | 40.1084 | 37.7443 | 35.8454 | 34.3424 | 45.6656 | 45.6586 | 45.6516 | 45.2222 | 45.1159 | 45.0079 | 44.7108 | 43.9894 | 43.192 | 42.5335 | 41.2493 | 38.9841 | 37.1396 | 35.6213
|  | YEOVIL | LW |  |  | 47.3164 | 47.3047 | 47.2929 | 46.5774 | 46.5169 | 46.4544 | 46.3898 | 46.3229 | 46.2477 | 46.2214 | 46.1364 | 45.9702 | 44.6205 | 43.3757 | 45.0503 | 45.0262 | 45.0024 | 44.2682 | 44.1849 | 44.0967 | 43.4669 | 42.7519 | 41.9944 | 41.2977 | 39.9443 | 38.2034 | 36.6524 | 35.2228 | 45.6093 | 45.5976 | 45.5859 | 44.8703 | 44.8098 | 44.7474 | 44.41 | 43.7353 | 43.0203 | 42.3653 | 41.0909 | 39.4488 | 37.9454 | 36.5006
|  | YEOVIL | ST |  |  | 47.4008 | 47.3962 | 47.3915 | 47.1052 | 47.0814 | 47.0572 | 47.0325 | 47.0073 | 46.98 | 46.9688 | 46.9307 | 46.8707 | 46.7967 | 46.7285 | 45.1375 | 45.1273 | 45.1117 | 44.8161 | 44.7793 | 44.7396 | 44.6948 | 44.6485 | 44.1939 | 43.7231 | 42.8079 | 41.6711 | 40.6851 | 39.7751 | 45.6938 | 45.6891 | 45.6844 | 45.3982 | 45.3743 | 45.3501 | 45.3255 | 45.3003 | 45.1285 | 44.6863 | 43.8257 | 42.7559 | 41.8267 | 40.969
|  | YEOVIL | SP |  |  | 47.429 | 47.4267 | 47.4243 | 47.2812 | 47.2695 | 47.2577 | 47.2459 | 47.2341 | 47.2222 | 47.2169 | 47.1992 | 47.1729 | 47.1452 | 47.106 | 45.167 | 45.1611 | 45.151 | 45.0034 | 44.985 | 44.966 | 44.9461 | 44.9263 | 44.9054 | 44.8913 | 44.8571 | 44.7701 | 44.4012 | 44.0701 | 45.7219 | 45.7196 | 45.7172 | 45.5741 | 45.5624 | 45.5506 | 45.5389 | 45.527 | 45.5152 | 45.5098 | 45.4922 | 45.4659 | 45.3332 | 45.0203
AXMINSTER | YEOVIL BSP | YETMINSTER | MINIMUM HEADROOM | ST 60294 10206 | YES | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.3581 | 19.0166 | 18.5645 | 18.1245 | 17.6273 | 17.6245 | 17.6208 | 17.613 | 17.6044 | 17.5958 | 17.5873 | 17.5827 | 17.5782 | 17.5458 | 17.2268 | 16.7098 | 16.179 | 15.6625 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.4181 | 16.9084
|  | YETMINSTER | CT |  |  | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.3581 | 19.0166 | 18.5645 | 18.1245 | 17.6273 | 17.6245 | 17.6208 | 17.613 | 17.6044 | 17.5958 | 17.5873 | 17.5827 | 17.5782 | 17.5458 | 17.2268 | 16.7098 | 16.179 | 15.6625 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.4181 | 16.9084
|  | YETMINSTER | LW |  |  | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.3631 | 19.0758 | 18.6237 | 18.1833 | 17.6273 | 17.6245 | 17.6208 | 17.6131 | 17.6045 | 17.5958 | 17.5904 | 17.5858 | 17.5813 | 17.5764 | 17.2962 | 16.7793 | 16.2485 | 15.7314 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.4866 | 16.9764
|  | YETMINSTER | ST |  |  | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.3786 | 19.3538 | 19.1201 | 17.6287 | 17.627 | 17.625 | 17.6215 | 17.6165 | 17.6106 | 17.6065 | 17.6029 | 17.5998 | 17.5965 | 17.587 | 17.5094 | 17.1676 | 16.8314 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718
|  | YETMINSTER | SP |  |  | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 19.38 | 17.6306 | 17.6303 | 17.63 | 17.6297 | 17.6281 | 17.6262 | 17.6247 | 17.6234 | 17.6217 | 17.6205 | 17.6168 | 17.611 | 17.6055 | 17.6004 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718 | 17.8718
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD | MINIMUM HEADROOM | SU 60592 00043 | YES | 8.0302 | 8.0302 | 8.0302 | 8.0302 | 7.8694 | 7.6998 | 7.5188 | 7.3193 | 6.9769 | 6.8875 | 6.594 | 6.1079 | 5.3891 | 5.1204 | 5.788 | 5.7259 | 5.6443 | 5.4716 | 5.1435 | 4.8082 | 4.5748 | 4.3311 | 3.9808 | 3.8828 | 3.5641 | 3.0363 | 2.2745 | 1.9635 | 6.1148 | 6.0738 | 6.02 | 5.9063 | 5.6146 | 5.2797 | 5.0464 | 4.8027 | 4.4525 | 4.3546 | 4.0362 | 3.5089 | 2.7477 | 2.4372
|  | ZETLAND ROAD | CT |  |  | 8.0302 | 8.0302 | 8.0302 | 8.0302 | 7.9428 | 7.853 | 7.7608 | 7.6267 | 7.4299 | 7.363 | 7.1568 | 6.5823 | 5.9814 | 5.6553 | 5.7952 | 5.7384 | 5.6639 | 5.5063 | 5.266 | 5.0248 | 4.7827 | 4.6332 | 4.4285 | 4.3531 | 4.1216 | 3.5055 | 2.8616 | 2.4932 | 6.1195 | 6.0821 | 6.033 | 5.9291 | 5.737 | 5.4961 | 5.2543 | 5.1049 | 4.9003 | 4.8249 | 4.5938 | 3.9782 | 3.3348 | 2.967
|  | ZETLAND ROAD | LW |  |  | 8.0302 | 8.0302 | 8.0302 | 8.0302 | 7.8694 | 7.6998 | 7.5188 | 7.3193 | 6.9769 | 6.8875 | 6.594 | 6.1079 | 5.3891 | 5.1204 | 5.788 | 5.7259 | 5.6443 | 5.4716 | 5.1435 | 4.8082 | 4.5748 | 4.3311 | 3.9808 | 3.8828 | 3.5641 | 3.0363 | 2.2745 | 1.9635 | 6.1148 | 6.0738 | 6.02 | 5.9063 | 5.6146 | 5.2797 | 5.0464 | 4.8027 | 4.4525 | 4.3546 | 4.0362 | 3.5089 | 2.7477 | 2.4372
|  | ZETLAND ROAD | ST |  |  | 8.0302 | 8.0302 | 8.0302 | 8.0302 | 8.0295 | 8.028 | 8.0257 | 8.0224 | 8.015 | 8.0114 | 7.9922 | 7.8669 | 7.6267 | 7.4436 | 5.8094 | 5.7643 | 5.7112 | 5.62 | 5.5075 | 5.3712 | 5.3258 | 5.2799 | 5.2374 | 5.196 | 5.0664 | 4.8619 | 4.5939 | 4.3833 | 6.1289 | 6.0991 | 6.0642 | 6.004 | 5.9296 | 5.8393 | 5.7968 | 5.7511 | 5.7086 | 5.6673 | 5.5379 | 5.3337 | 5.0661 | 4.8558
|  | ZETLAND ROAD | SP |  |  | 8.0302 | 8.0302 | 8.0302 | 8.0302 | 8.0302 | 8.0302 | 8.0301 | 8.0299 | 8.0296 | 8.0284 | 8.0215 | 8.016 | 7.9896 | 7.9639 | 5.8601 | 5.8536 | 5.8473 | 5.8413 | 5.8135 | 5.7805 | 5.765 | 5.7495 | 5.7296 | 5.7138 | 5.6643 | 5.591 | 5.4996 | 5.4125 | 6.1623 | 6.158 | 6.1538 | 6.1499 | 6.1315 | 6.1098 | 6.0995 | 6.0893 | 6.0761 | 6.0652 | 6.0302 | 5.98 | 5.9109 | 5.8446
[6 empty] | 30.6384 | 30.6372 | 30.6348 | 30.6306 | 30.6079 | 30.5845 | 30.5535 | 30.5163 | 30.468 | 30.4416 | 30.3521 | 30.1853 | 29.5117 | 28.1517 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5329 | 22.5145 | 22.4958 | 22.4762 | 22.4461 | 22.4423 | 22.3199 | 22.0406 | 20.4125 | 18.8268 | 22.4015 | 22.4006 | 22.3987 | 22.3953 | 22.3736 | 22.3512 | 22.3237 | 22.2903 | 22.2462 | 22.2244 | 22.1406 | 21.6634 | 20.0385 | 18.456
[6 empty] | 30.6384 | 30.6372 | 30.6348 | 30.6306 | 30.6079 | 30.5845 | 30.5606 | 30.5219 | 30.4711 | 30.4447 | 30.356 | 30.1853 | 29.5683 | 28.1948 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5329 | 22.5145 | 22.4958 | 22.4762 | 22.4461 | 22.4423 | 22.43 | 22.0969 | 20.4921 | 18.8929 | 22.4015 | 22.4006 | 22.3987 | 22.3953 | 22.3736 | 22.3512 | 22.3284 | 22.2935 | 22.2469 | 22.225 | 22.1518 | 21.7755 | 20.1178 | 18.5218
[6 empty] | 30.6384 | 30.6372 | 30.6348 | 30.6306 | 30.6098 | 30.5881 | 30.5535 | 30.5163 | 30.468 | 30.4416 | 30.3521 | 30.2223 | 29.5117 | 28.1517 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5348 | 22.518 | 22.5005 | 22.4824 | 22.4549 | 22.4511 | 22.4381 | 22.0406 | 20.4125 | 18.8268 | 22.4015 | 22.4006 | 22.3987 | 22.3953 | 22.3754 | 22.3547 | 22.3237 | 22.2903 | 22.2462 | 22.2244 | 22.1503 | 21.6634 | 20.0385 | 18.456
[6 empty] | 30.6436 | 30.638 | 30.6365 | 30.6342 | 30.6313 | 30.6279 | 30.6219 | 30.6145 | 30.6004 | 30.5849 | 30.5318 | 30.4561 | 30.3794 | 30.3047 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5363 | 22.315 | 21.4931 | 22.4057 | 22.4013 | 22.4 | 22.3982 | 22.3959 | 22.3932 | 22.3884 | 22.3825 | 22.3712 | 22.3589 | 22.3165 | 22.2561 | 22.0686 | 21.1173
[6 empty] | 30.6442 | 30.6391 | 30.6384 | 30.6376 | 30.6266 | 30.6157 | 30.6043 | 30.5922 | 30.5739 | 30.5254 | 30.3699 | 30.2755 | 30.0411 | 29.8393 | 22.551 | 22.551 | 22.551 | 22.551 | 22.5412 | 22.5316 | 22.522 | 22.5122 | 22.4969 | 22.4545 | 22.3199 | 22.2558 | 22.0539 | 21.885 | 22.4062 | 22.4021 | 22.4016 | 22.4009 | 22.3902 | 22.3795 | 22.3685 | 22.3568 | 22.3392 | 22.2919 | 22.1406 | 22.0523 | 21.8245 | 21.6294
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3028 | 13.2064 | 13.1045 | 12.9907 | 12.8044 | 12.7791 | 12.6858 | 11.7947 | 10.7815 | 10.2143 | 8.443 | 8.4288 | 8.41 | 8.3702 | 8.2182 | 8.0572 | 7.8891 | 7.6486 | 7.3293 | 7.1586 | 6.5887 | 5.4556 | 4.3665 | 3.7254 | 8.7899 | 8.7759 | 8.7574 | 8.7183 | 8.5673 | 8.4074 | 8.2404 | 8.002 | 7.6849 | 7.5167 | 6.9547 | 5.8315 | 4.7508 | 4.1178
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3028 | 13.2064 | 13.1045 | 12.9907 | 12.8044 | 12.7791 | 12.6858 | 11.7947 | 10.7815 | 10.2143 | 8.443 | 8.4288 | 8.41 | 8.3702 | 8.2182 | 8.0572 | 7.8891 | 7.6486 | 7.3293 | 7.1586 | 6.5887 | 5.4556 | 4.3665 | 3.7254 | 8.7899 | 8.7759 | 8.7574 | 8.7183 | 8.5673 | 8.4074 | 8.2404 | 8.002 | 7.6849 | 7.5167 | 6.9547 | 5.8315 | 4.7508 | 4.1178
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3651 | 13.3201 | 13.2554 | 13.1699 | 13.0152 | 12.9903 | 12.8754 | 12.3066 | 11.3922 | 10.9446 | 8.4542 | 8.4481 | 8.44 | 8.423 | 8.3551 | 8.2672 | 8.0806 | 7.8683 | 7.5807 | 7.4104 | 6.8187 | 5.9736 | 4.9832 | 4.4618 | 8.8009 | 8.7949 | 8.7869 | 8.7702 | 8.7029 | 8.6158 | 8.4312 | 8.221 | 7.9356 | 7.7678 | 7.1841 | 6.3488 | 5.3668 | 4.8535
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3907 | 13.3845 | 13.3746 | 13.3598 | 13.3294 | 13.316 | 13.25 | 13.1678 | 12.7975 | 12.4323 | 8.4572 | 8.4534 | 8.4489 | 8.4413 | 8.4136 | 8.3785 | 8.3048 | 8.2231 | 8.1025 | 7.9898 | 7.5933 | 7.109 | 6.5047 | 6.0912 | 8.8039 | 8.8001 | 8.7957 | 8.7882 | 8.7609 | 8.7263 | 8.6537 | 8.5731 | 8.454 | 8.3429 | 7.9519 | 7.4744 | 6.8755 | 6.4674
[6 empty] | 13.3938 | 13.3938 | 13.3938 | 13.3938 | 13.3937 | 13.3934 | 13.3929 | 13.3922 | 13.3906 | 13.3842 | 13.3478 | 13.3191 | 13.1835 | 13.0518 | 8.4613 | 8.4607 | 8.46 | 8.4595 | 8.4487 | 8.4368 | 8.4149 | 8.3918 | 8.3623 | 8.3169 | 8.151 | 7.9673 | 7.7138 | 7.4724 | 8.8079 | 8.8072 | 8.8066 | 8.8061 | 8.7955 | 8.7838 | 8.7622 | 8.7395 | 8.7104 | 8.6657 | 8.502 | 8.3209 | 8.0693 | 7.8298
[6 empty] | 32.6383 | 32.6236 | 32.6088 | 31.7082 | 31.6344 | 31.5606 | 31.4868 | 31.4129 | 31.3391 | 31.3096 | 31.221 | 30.9675 | 28.9927 | 26.9667 | 24.3028 | 24.2881 | 24.2733 | 23.3727 | 23.2989 | 23.2251 | 23.1513 | 23.0775 | 23.0036 | 22.9741 | 22.8855 | 21.3793 | 19.1328 | 16.8385 | 24.6384 | 24.6215 | 24.6041 | 23.696 | 23.6123 | 23.5269 | 23.4304 | 23.3338 | 23.2345 | 23.1784 | 23.0198 | 22.0147 | 19.7 | 17.3384
[6 empty] | 32.7092 | 32.7003 | 32.6915 | 32.1511 | 32.1068 | 32.0625 | 32.0182 | 31.974 | 31.9297 | 31.9119 | 31.8588 | 31.137 | 29.0231 | 26.9973 | 24.3737 | 24.3648 | 24.356 | 23.8156 | 23.7713 | 23.7271 | 23.6828 | 23.6385 | 23.5942 | 23.5765 | 23.5233 | 21.5531 | 19.1676 | 16.8735 | 24.7083 | 24.6965 | 24.684 | 24.1341 | 24.0779 | 24.02 | 23.9641 | 23.8971 | 23.8273 | 23.7831 | 23.6599 | 22.1896 | 19.7359 | 17.3744
[6 empty] | 32.6383 | 32.6236 | 32.6088 | 31.7082 | 31.6344 | 31.5606 | 31.4868 | 31.4129 | 31.3391 | 31.3096 | 31.221 | 30.9675 | 28.9927 | 26.9667 | 24.3028 | 24.2881 | 24.2733 | 23.3727 | 23.2989 | 23.2251 | 23.1513 | 23.0775 | 23.0036 | 22.9741 | 22.8855 | 21.3793 | 19.1328 | 16.8385 | 24.6384 | 24.6215 | 24.6041 | 23.696 | 23.6123 | 23.5269 | 23.4304 | 23.3338 | 23.2345 | 23.1784 | 23.0198 | 22.0147 | 19.7 | 17.3384
[6 empty] | 32.7446 | 32.7387 | 32.7328 | 32.3726 | 32.343 | 32.3135 | 32.284 | 32.2545 | 32.2249 | 32.2131 | 32.1777 | 32.1186 | 32.0832 | 30.9386 | 24.4091 | 24.4032 | 24.3973 | 24.0371 | 24.0076 | 23.978 | 23.9485 | 23.919 | 23.8895 | 23.8776 | 23.8422 | 23.7832 | 22.6402 | 21.2101 | 24.7454 | 24.738 | 24.7305 | 24.3661 | 24.3302 | 24.2929 | 24.2498 | 24.2068 | 24.16 | 24.13 | 24.0465 | 23.901 | 23.2836 | 21.8103
[6 empty] | 32.78 | 32.7771 | 32.7741 | 32.594 | 32.5769 | 32.5598 | 32.5427 | 32.5255 | 32.507 | 32.4908 | 32.4402 | 32.3951 | 32.3281 | 32.2544 | 24.4446 | 24.4416 | 24.4387 | 24.2585 | 24.2414 | 24.2243 | 24.2072 | 24.19 | 24.1716 | 24.1553 | 24.1047 | 24.0596 | 23.9926 | 23.919 | 24.7817 | 24.7781 | 24.7746 | 24.5928 | 24.5728 | 24.5524 | 24.5307 | 24.509 | 24.4845 | 24.4611 | 24.3918 | 24.312 | 24.2052 | 24.0912

## BSP Headroom Gen
Grid Supply Point | Bulk Supply Point | Scenario | Grid Reference | Upstream Constraint (YES / NO) | Generation Headroom Winter MVA | [13 empty] | Generation Headroom Summer MVA | [13 empty] | Generation Headroom Spring/Autumn MVA
[5 empty] | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2035 | 2040 | 2045 | 2050
WILLESDEN GSP | ACTON LANE | MINIMUM HEADROOM | TQ2080583142 | YES | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2152 | 148.2107 | 148.206 | 148.2013 | 148.1939 | 148.1893 | 148.1346 | 148.008 | 147.8433 | 148.1316 | 128.9188 | 128.8829 | 128.8537 | 128.7984 | 128.7412 | 128.6805 | 128.6003 | 128.5248 | 128.4513 | 128.3751 | 128.13 | 127.5625 | 126.0209 | 124.6133 | 130.4598 | 130.4449 | 130.4328 | 130.4098 | 130.386 | 130.3608 | 130.3039 | 130.2495 | 130.1965 | 130.117 | 129.4793 | 127.9403 | 125.9388 | 125.0277
|  | CT |  |  | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2134 | 148.1964 | 148.1417 | 148.008 | 147.8433 | 148.1387 | 128.92 | 128.885 | 128.857 | 128.8041 | 128.7493 | 128.691 | 128.6322 | 128.5566 | 128.4831 | 128.407 | 128.1618 | 127.5625 | 126.0209 | 124.715 | 130.4603 | 130.4458 | 130.4342 | 130.4122 | 130.3894 | 130.3651 | 130.3269 | 130.2724 | 130.2194 | 130.153 | 129.5656 | 127.9403 | 125.9388 | 125.1256
|  | LW |  |  | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2063 | 148.1893 | 148.1346 | 148.4617 | 148.297 | 148.1316 | 128.9188 | 128.8829 | 128.8537 | 128.7984 | 128.7412 | 128.6805 | 128.6003 | 128.5248 | 128.4513 | 128.3751 | 128.13 | 128.5983 | 126.9782 | 124.6133 | 130.4598 | 130.4449 | 130.4328 | 130.4098 | 130.386 | 130.3608 | 130.3039 | 130.2495 | 130.1965 | 130.117 | 129.4793 | 129.1133 | 127.1118 | 125.0277
|  | ST |  |  | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2152 | 148.2107 | 148.206 | 148.2013 | 148.1939 | 148.1914 | 148.1559 | 148.0568 | 147.9251 | 148.2742 | 128.9265 | 128.9125 | 128.8788 | 128.8497 | 128.8095 | 128.7616 | 128.6989 | 128.6394 | 128.5822 | 128.5277 | 128.3519 | 127.9302 | 127.4205 | 127.6173 | 130.4631 | 130.4572 | 130.4432 | 130.4311 | 130.4118 | 130.3892 | 130.3604 | 130.327 | 130.2836 | 130.2437 | 130.0955 | 129.0106 | 127.6681 | 127.644
|  | SP |  |  | 148.2197 | 148.2197 | 148.2197 | 148.2197 | 148.2187 | 148.2175 | 148.2163 | 148.215 | 148.213 | 148.2076 | 148.1903 | 148.1821 | 148.1173 | 148.5042 | 128.9385 | 128.934 | 128.9129 | 128.9061 | 128.8929 | 128.8775 | 128.8542 | 128.8326 | 128.8065 | 128.7811 | 128.6989 | 128.521 | 128.2733 | 129.0851 | 130.4681 | 130.4662 | 130.4574 | 130.4546 | 130.4485 | 130.4414 | 130.431 | 130.4213 | 130.4093 | 130.3955 | 130.3513 | 130.2362 | 129.9767 | 130.5804
BRAMLEY (FLEE) | ALDERSHOT BSP | MINIMUM HEADROOM | SU8597648834 | YES | 275.6747 | 275.6693 | 275.6633 | 275.6743 | 275.628 | 274.5061 | 273.3551 | 272.1082 | 269.7012 | 269.3143 | 268.053 | 267.4777 | 261.185 | 251.8437 | 211.5047 | 211.4547 | 211.3927 | 211.2716 | 211.0907 | 210.302 | 209.1237 | 207.8496 | 205.4086 | 204.9873 | 196.2565 | 182.0685 | 168.8945 | 158.358 | 240.6849 | 240.6795 | 240.6735 | 240.6845 | 240.6381 | 239.5163 | 238.3653 | 237.1184 | 234.7114 | 234.3245 | 231.3332 | 217.9986 | 205.5786 | 195.5466
|  | CT |  |  | 275.6808 | 275.6791 | 275.6772 | 275.6743 | 275.628 | 275.4905 | 276.3619 | 275.6033 | 274.9982 | 274.5652 | 273.1809 | 270.6061 | 265.3239 | 254.53 | 211.5066 | 211.4572 | 211.3954 | 211.2716 | 211.0907 | 210.829 | 211.5365 | 210.6392 | 209.627 | 207.0635 | 198.976 | 186.1541 | 173.7322 | 161.5072 | 240.691 | 240.6893 | 240.6873 | 240.6845 | 240.6381 | 240.5007 | 241.3503 | 240.4932 | 239.7806 | 239.2259 | 233.8943 | 221.792 | 210.0619 | 198.5628
|  | LW |  |  | 275.6747 | 275.6693 | 275.6633 | 276.6659 | 276.6371 | 276.4983 | 276.0348 | 275.5536 | 275.047 | 274.5818 | 272.717 | 270.6833 | 261.185 | 251.8437 | 211.5047 | 211.4547 | 211.3927 | 212.2828 | 212.1052 | 211.825 | 211.1996 | 210.5489 | 208.7616 | 205.9202 | 196.2565 | 182.0685 | 168.8945 | 158.358 | 240.6849 | 240.6795 | 240.6735 | 241.6761 | 241.6473 | 241.5085 | 241.0163 | 240.4147 | 239.7771 | 239.1762 | 231.3332 | 217.9986 | 205.5786 | 195.5466
|  | ST |  |  | 275.6817 | 275.6816 | 275.6815 | 275.6814 | 275.6585 | 275.5422 | 275.2665 | 275.9805 | 275.6234 | 275.0283 | 273.2146 | 271.0629 | 269.6228 | 268.8071 | 211.5364 | 211.503 | 211.4713 | 211.4186 | 211.3186 | 211.1198 | 210.7711 | 211.4077 | 210.9686 | 210.2541 | 206.7851 | 196.8977 | 188.52 | 180.2773 | 240.6919 | 240.6918 | 240.6917 | 240.6916 | 240.6687 | 240.5524 | 240.2767 | 240.9907 | 240.6336 | 240.0385 | 237.9366 | 231.8132 | 223.9227 | 216.2014
|  | SP |  |  | 275.6816 | 275.6815 | 275.6813 | 275.6812 | 275.6571 | 274.5061 | 273.3551 | 272.1082 | 269.7012 | 269.3143 | 268.053 | 267.4777 | 266.111 | 265.3368 | 211.5594 | 211.5452 | 211.5369 | 211.5271 | 211.4784 | 210.302 | 209.1237 | 207.8496 | 205.4086 | 204.9873 | 203.6076 | 202.8486 | 201.2619 | 200.282 | 240.6918 | 240.6917 | 240.6915 | 240.6914 | 240.6673 | 239.5163 | 238.3653 | 237.1184 | 234.7114 | 234.3245 | 233.0632 | 232.4879 | 231.0825 | 230.1624
BRAMLEY (FLEE) | ALTON | MINIMUM HEADROOM | SU7268539765 | YES | 130.9624 | 130.3408 | 129.7665 | 128.0253 | 123.0696 | 87.3999 | 84.3034 | 81.1418 | 76.0848 | 72.6833 | 57.9956 | 11.998 | -10.4092 | -18.9765 | 57.0663 | 56.3354 | 55.6602 | 53.7296 | 46.7898 | 7.2206 | 3.8074 | 0.33238 | -5.139 | -9.0918 | -25.5204 | -82.6299 | -108.2941 | -117.8404 | 68.648 | 67.9695 | 67.3425 | 65.5026 | 57.5368 | 17.1572 | 13.8957 | 10.5707 | 5.2976 | 1.6087 | -13.7027 | -67.1948 | -92.8662 | -102.4147
|  | CT |  |  | 130.9624 | 130.3408 | 129.7665 | 128.0253 | 123.0696 | 118.8138 | 114.5261 | 108.9977 | 104.555 | 99.3714 | 90.0288 | 66.6887 | 50.0605 | 33.3421 | 57.0663 | 56.3354 | 55.6602 | 53.7296 | 47.9356 | 42.9479 | 37.9243 | 31.55 | 26.4441 | 20.4225 | 12.4131 | -14.2458 | -33.0768 | -52.1929 | 68.648 | 67.9695 | 67.3425 | 65.5026 | 60.1099 | 55.4725 | 50.8011 | 44.8317 | 40.0433 | 34.4228 | 28.8276 | 2.7494 | -15.696 | -34.3926
|  | LW |  |  | 139.0327 | 138.4734 | 137.9792 | 135.9685 | 126.419 | 116.7053 | 106.6167 | 96.4099 | 89.2654 | 82.5633 | 57.9956 | 11.998 | -10.4092 | -18.9765 | 69.4501 | 68.7812 | 68.1907 | 66.0031 | 54.5955 | 43.2164 | 31.5047 | 19.6642 | 11.4627 | 3.6982 | -24.737 | -82.6299 | -108.2941 | -117.8404 | 82.2764 | 81.6545 | 81.1052 | 78.9934 | 68.3819 | 57.8009 | 46.8876 | 35.8508 | 27.9099 | 20.3313 | -7.4271 | -67.1948 | -92.8662 | -102.4147
|  | ST |  |  | 131.2183 | 130.9566 | 130.4655 | 129.5538 | 125.7432 | 121.8897 | 117.935 | 112.9859 | 109.1464 | 104.072 | 95.1251 | 74.7002 | 53.2987 | 39.6326 | 57.36 | 57.0526 | 56.4746 | 55.4811 | 50.9936 | 46.4761 | 41.8656 | 36.0869 | 31.6341 | 25.7726 | 18.2839 | -5.2443 | -32.919 | -48.8119 | 68.9237 | 68.6381 | 68.1017 | 67.1474 | 62.9839 | 58.7842 | 54.4876 | 49.106 | 44.9468 | 39.462 | 34.5174 | 11.5777 | -17.1928 | -32.7042
|  | SP |  |  | 156.9954 | 131.3952 | 131.2564 | 130.9536 | 123.802 | 87.3999 | 84.3034 | 81.1418 | 76.0848 | 72.6833 | 58.5887 | 40.1684 | 26.1614 | 18.94 | 88.6181 | 57.5613 | 57.3982 | 57.0821 | 46.7898 | 7.2206 | 3.8074 | 0.33238 | -5.139 | -9.0918 | -25.5204 | -46.9451 | -63.2386 | -71.6324 | 97.9055 | 69.1132 | 68.9618 | 68.6521 | 57.5368 | 17.1572 | 13.8957 | 10.5707 | 5.2976 | 1.6087 | -13.7027 | -34.1748 | -50.079 | -58.2732
MELKSHAM GSP | AMESBURY | MINIMUM HEADROOM | SU1590542695 | YES | 131.2319 | 131.1397 | 131.0197 | 130.7644 | 128.001 | 125.21 | 122.2506 | 119.2296 | 115.4237 | 111.6769 | 97.8395 | 79.4169 | 68.2444 | 64.8107 | 94.0303 | 93.9334 | 93.8073 | 93.5398 | 90.6356 | 87.3396 | 83.8653 | 80.3692 | 75.9701 | 71.6161 | 55.4582 | 33.9786 | 20.9929 | 16.9973 | 105.0348 | 104.9256 | 104.7833 | 104.4833 | 101.2033 | 97.8929 | 94.4254 | 90.9362 | 86.5457 | 82.2115 | 66.2054 | 44.9257 | 32.0586 | 28.0997
|  | CT |  |  | 131.2498 | 131.1703 | 131.0667 | 130.8465 | 129.541 | 128.3981 | 127.2459 | 125.7128 | 123.551 | 120.7294 | 111.0075 | 99.64 | 91.8806 | 82.0533 | 94.049 | 93.9654 | 93.8565 | 93.6257 | 92.2539 | 91.0533 | 89.763 | 87.9427 | 85.3767 | 82.1059 | 70.8181 | 57.5931 | 48.5762 | 37.114 | 105.0557 | 104.9613 | 104.8382 | 104.5791 | 103.0306 | 101.6762 | 100.3114 | 98.4947 | 95.9337 | 92.6695 | 81.4219 | 68.3184 | 59.3837 | 48.0285
|  | LW |  |  | 131.2319 | 131.1397 | 131.0197 | 130.7644 | 128.001 | 125.21 | 122.2506 | 119.2296 | 115.4237 | 111.6769 | 97.8395 | 79.4169 | 68.2444 | 64.8107 | 94.0303 | 93.9334 | 93.8073 | 93.5398 | 90.6356 | 87.3396 | 83.8653 | 80.3692 | 75.9701 | 71.6161 | 55.4582 | 33.9786 | 20.9929 | 16.9973 | 105.0348 | 104.9256 | 104.7833 | 104.4833 | 101.2033 | 97.8929 | 94.4254 | 90.9362 | 86.5457 | 82.2115 | 66.2054 | 44.9257 | 32.0586 | 28.0997
|  | ST |  |  | 131.2642 | 131.1992 | 131.1226 | 130.988 | 129.8373 | 128.699 | 127.5661 | 126.1451 | 124.0646 | 121.3642 | 111.9523 | 101.4142 | 94.2234 | 85.0379 | 94.0641 | 93.9957 | 93.9151 | 93.7741 | 92.5659 | 91.3709 | 90.1517 | 88.4675 | 86.0027 | 82.8562 | 71.9423 | 59.6441 | 51.3023 | 40.5843 | 105.0727 | 104.9954 | 104.9043 | 104.7459 | 103.3845 | 102.0384 | 100.6992 | 99.0184 | 96.5583 | 93.418 | 82.5344 | 70.3512 | 62.0847 | 51.467
|  | SP |  |  | 131.3289 | 131.3146 | 131.3004 | 131.2837 | 130.9741 | 130.6217 | 130.1159 | 129.6159 | 128.9543 | 127.9877 | 124.0458 | 119.0819 | 114.8031 | 112.3324 | 94.1321 | 94.1171 | 94.1022 | 94.0847 | 93.7605 | 93.3914 | 92.8609 | 92.3365 | 91.6428 | 90.6321 | 86.0509 | 80.2906 | 75.417 | 72.6288 | 105.1497 | 105.1327 | 105.1158 | 105.0964 | 104.7333 | 104.3193 | 103.7229 | 103.1335 | 102.3545 | 101.2261 | 96.6057 | 90.8566 | 85.9916 | 83.208
BRAMLEY (ANDO-THAT) | ANDOVER BSP | MINIMUM HEADROOM | SU3524046643 | YES | 67.4384 | 52.9526 | 51.3801 | 49.699 | 47.6316 | 43.7686 | 38.9326 | 34.0836 | 28.0256 | 22.7705 | 3.7481 | -39.2737 | -78.2893 | -85.957 | 14.4706 | -2.587 | -4.9424 | -6.7208 | -9.1287 | -12.3255 | -17.8458 | -23.3795 | -30.2848 | -36.3956 | -58.5498 | -109.3875 | -154.5359 | -163.1942 | 32.7903 | 16.0169 | 13.4364 | 11.6688 | 9.2985 | 5.9446 | 0.48795 | -5.032 | -11.9202 | -18.0138 | -40.1048 | -91.0608 | -136.0857 | -144.7241
|  | CT |  |  | 97.4567 | 65.9429 | 51.3801 | 49.699 | 47.6316 | 45.4898 | 44.8808 | 42.3185 | 40.3856 | 37.5972 | 24.0992 | -1.864 | -26.0558 | -41.4979 | 49.2728 | 12.1528 | -4.9424 | -6.7208 | -9.1287 | -11.5725 | -12.0024 | -14.9393 | -16.9282 | -19.6293 | -35.3704 | -65.2322 | -93.0768 | -110.8952 | 66.7522 | 30.2517 | 13.4364 | 11.6688 | 9.2985 | 6.8881 | 6.2361 | 3.3406 | 1.1651 | -1.2865 | -16.9825 | -46.7657 | -74.5367 | -92.3072
|  | LW |  |  | 67.4384 | 52.9526 | 52.3093 | 52.8209 | 48.4835 | 43.7686 | 38.9326 | 34.0836 | 28.0256 | 22.7705 | 3.7481 | -39.2737 | -78.2893 | -85.957 | 14.4706 | -2.587 | -3.2815 | -1.9368 | -6.9411 | -12.3255 | -17.8458 | -23.3795 | -30.2848 | -36.3956 | -58.5498 | -109.3875 | -154.5359 | -163.1942 | 32.7903 | 16.0169 | 15.3281 | 16.1856 | 11.255 | 5.9446 | 0.48795 | -5.032 | -11.9202 | -18.0138 | -40.1048 | -91.0608 | -136.0857 | -144.7241
|  | ST |  |  | 97.5709 | 66.3419 | 51.9281 | 50.8358 | 48.8185 | 46.7919 | 46.379 | 44.0761 | 42.4722 | 38.6889 | 22.206 | -3.7425 | -27.3632 | -40.9981 | 49.3939 | 12.6079 | -4.3696 | -5.5223 | -7.831 | -10.1538 | -10.3679 | -13.0151 | -14.6387 | -18.2957 | -36.9033 | -66.5442 | -94.3297 | -110.1147 | 66.8726 | 30.7007 | 14.0065 | 12.8605 | 10.584 | 8.2939 | 7.8555 | 5.2464 | 3.4322 | 0.04221 | -18.5226 | -48.0891 | -75.9746 | -91.7163
|  | SP |  |  | 106.2304 | 106.1825 | 106.0153 | 74.5915 | 60.1827 | 56.0743 | 52.8118 | 48.1921 | 40.0723 | 38.1307 | 30.9984 | 23.6211 | 15.9479 | 11.8915 | 58.0689 | 58.0137 | 57.8177 | 20.8671 | 3.9007 | -0.29135 | -3.6742 | -8.4123 | -16.6883 | -18.8339 | -26.8076 | -34.3607 | -42.9113 | -47.467 | 75.5377 | 75.4833 | 75.2905 | 38.9507 | 22.267 | 18.0842 | 14.7146 | 9.9897 | 1.7309 | -0.39213 | -8.2728 | -16.2017 | -24.7243 | -29.2699
MANNINGTON GSP | ARNEWOOD | MINIMUM HEADROOM | SZ2612997354 | YES | 97.9883 | 97.9626 | 97.9368 | 105.6642 | 105.5185 | 104.3471 | 101.7796 | 99.2121 | 94.1029 | 93.5738 | 91.986 | 89.1332 | 87.2725 | 85.3707 | 63.3149 | 63.1903 | 63.0379 | 83.9756 | 83.3091 | 82.3869 | 79.8271 | 77.0596 | 71.7073 | 70.9059 | 68.466 | 61.4085 | 54.3414 | 48.7331 | 86.7241 | 86.6222 | 86.479 | 89.4378 | 88.8093 | 87.9265 | 85.2041 | 82.4511 | 77.1166 | 76.3351 | 73.9573 | 67.9638 | 61.0208 | 55.461
|  | CT |  |  | 98.1121 | 98.0966 | 98.0812 | 106.4376 | 106.3601 | 106.0807 | 105.8012 | 105.5214 | 105.2408 | 105.0482 | 104.4699 | 98.9703 | 93.5949 | 89.0985 | 63.4294 | 63.3083 | 63.1575 | 84.7059 | 84.1885 | 83.4632 | 82.7185 | 81.5201 | 80.307 | 79.1217 | 75.5878 | 66.1677 | 59.433 | 53.5545 | 86.8478 | 86.7413 | 86.6004 | 90.1712 | 89.686 | 88.9931 | 88.2824 | 87.151 | 86.0058 | 84.8929 | 81.5746 | 72.6225 | 66.0062 | 60.2479
|  | LW |  |  | 97.9883 | 97.9626 | 97.9368 | 105.6642 | 105.5185 | 105.1362 | 104.7526 | 104.3675 | 103.9704 | 103.7258 | 102.9884 | 95.3659 | 89.7249 | 85.3707 | 63.3149 | 63.1903 | 63.0379 | 83.9756 | 83.3091 | 82.3869 | 80.9737 | 79.5732 | 78.1398 | 76.8406 | 72.8705 | 61.4085 | 54.3414 | 48.7331 | 86.7241 | 86.6222 | 86.479 | 89.4378 | 88.8093 | 87.9265 | 86.5884 | 85.2619 | 83.904 | 82.6817 | 78.9474 | 67.9638 | 61.0208 | 55.461
|  | ST |  |  | 98.174 | 98.1637 | 98.1533 | 106.8243 | 106.7726 | 106.5123 | 106.2518 | 105.9911 | 105.7298 | 104.6714 | 101.4949 | 97.2296 | 92.9971 | 89.7165 | 63.5225 | 63.4331 | 63.3317 | 85.3311 | 84.9639 | 84.3393 | 83.4412 | 82.5351 | 81.5987 | 79.8102 | 74.4459 | 65.3656 | 60.2139 | 55.9804 | 86.9097 | 86.8619 | 86.7671 | 90.7791 | 90.4348 | 89.8368 | 88.9852 | 88.1262 | 87.239 | 85.5038 | 80.299 | 71.6159 | 66.6671 | 62.5165
|  | SP |  |  | 98.2358 | 98.2307 | 98.2255 | 106.9403 | 106.9145 | 104.3471 | 101.7796 | 99.2121 | 94.1029 | 93.5738 | 91.986 | 89.1332 | 87.2725 | 86.5683 | 63.6713 | 63.6537 | 63.6377 | 85.3891 | 85.2731 | 82.6019 | 79.8271 | 77.0596 | 71.7073 | 70.9059 | 68.466 | 64.2972 | 61.1982 | 59.415 | 86.9716 | 86.9664 | 86.9613 | 90.7369 | 90.6274 | 87.9638 | 85.2041 | 82.4511 | 77.1166 | 76.3351 | 73.9573 | 69.8845 | 66.8758 | 65.1712
BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | MINIMUM HEADROOM | SU6515552705 | YES | 95.0542 | 94.3093 | 94.1791 | 93.2057 | 92.7198 | 92.0774 | 90.8382 | 89.0524 | 85.5585 | 85.0811 | 83.5785 | 81.0333 | 79.2189 | 74.8209 | 54.3689 | 53.4612 | 53.3171 | 52.3142 | 51.7782 | 51.0856 | 49.9841 | 48.1872 | 44.6789 | 44.1863 | 42.6297 | 40.0055 | 38.1219 | 30.6373 | 64.2035 | 63.3023 | 63.1616 | 62.1661 | 61.6426 | 60.9625 | 59.8267 | 58.0325 | 54.5278 | 54.039 | 52.4959 | 49.8914 | 48.025 | 41.1107
|  | CT |  |  | 95.1111 | 94.3637 | 94.2342 | 93.5418 | 93.1753 | 92.6884 | 92.2043 | 91.688 | 91.1272 | 90.5524 | 88.7452 | 85.1393 | 81.8914 | 84.0385 | 54.421 | 53.5147 | 53.3708 | 52.6481 | 52.2425 | 51.7182 | 51.197 | 50.6399 | 50.0331 | 49.405 | 47.3486 | 43.3828 | 39.8072 | 44.2721 | 64.2558 | 63.356 | 63.2157 | 62.5005 | 62.1047 | 61.5897 | 61.0778 | 60.5309 | 59.9355 | 59.3207 | 57.3859 | 53.5971 | 50.1827 | 55.5901
|  | LW |  |  | 95.0542 | 94.3093 | 94.1791 | 93.2057 | 92.7198 | 92.0774 | 91.4116 | 90.7464 | 90.0268 | 89.3592 | 87.1776 | 88.2389 | 84.6653 | 74.8209 | 54.3689 | 53.4612 | 53.3171 | 52.3142 | 51.7782 | 51.0856 | 50.367 | 49.649 | 48.8687 | 48.1108 | 45.628 | 48.9116 | 44.9697 | 30.6373 | 64.2035 | 63.3023 | 63.1616 | 62.1661 | 61.6426 | 60.9625 | 60.2571 | 59.5523 | 58.7886 | 58.0752 | 55.7406 | 60.0136 | 56.2529 | 41.1107
|  | ST |  |  | 95.1396 | 94.4831 | 94.3915 | 93.9782 | 93.7315 | 93.3183 | 92.8985 | 92.4603 | 91.9897 | 90.9296 | 87.6693 | 83.6864 | 80.9659 | 83.7261 | 54.9263 | 53.7719 | 53.5428 | 53.1149 | 52.8419 | 52.3991 | 51.949 | 51.4782 | 50.9714 | 49.8684 | 46.4473 | 42.1861 | 39.2294 | 44.3965 | 64.7485 | 63.6072 | 63.384 | 62.9597 | 62.6933 | 62.2578 | 61.8153 | 61.3527 | 60.8549 | 59.7626 | 56.3987 | 52.2744 | 49.4339 | 55.4996
|  | SP |  |  | 95.1681 | 94.5139 | 94.5115 | 94.3668 | 94.3549 | 92.6249 | 90.8382 | 89.0524 | 85.5585 | 85.0811 | 83.5785 | 81.0333 | 79.2189 | 83.2445 | 55.0319 | 53.9378 | 53.7818 | 53.6271 | 53.5504 | 51.782 | 49.9841 | 48.1872 | 44.6789 | 44.1863 | 42.6297 | 40.0055 | 38.1219 | 44.7645 | 64.8521 | 63.7696 | 63.6176 | 63.4632 | 63.3881 | 61.6217 | 59.8267 | 58.0325 | 54.5278 | 54.039 | 52.4959 | 49.8914 | 48.025 | 55.4497
BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | MINIMUM HEADROOM | SU6515552705 | YES | 128.4648 | 125.8806 | 109.8702 | 107.9371 | 104.6219 | 101.1331 | 97.777 | 94.4156 | 90.2903 | 86.4624 | 72.6536 | 53.9658 | 35.2276 | 28.0599 | 62.9699 | 59.7989 | 41.2332 | 39.1213 | 35.2998 | 31.2692 | 27.4348 | 23.5982 | 18.8931 | 14.4782 | -1.4294 | -22.9614 | -44.4276 | -52.435 | 108.0294 | 107.8184 | 98.3656 | 96.249 | 92.4293 | 88.4331 | 84.6292 | 80.8228 | 76.1545 | 71.777 | 56.0028 | 34.6517 | 13.359 | 5.405
|  | CT |  |  | 128.545 | 125.9815 | 125.4302 | 108.415 | 106.4343 | 104.4598 | 102.4785 | 100.218 | 97.4986 | 94.4394 | 84.2758 | 70.1766 | 56.4079 | 44.3302 | 63.0545 | 59.9036 | 59.2657 | 39.6097 | 37.3236 | 35.0415 | 32.7475 | 30.2062 | 27.116 | 23.5951 | 11.8897 | -4.0827 | -19.6955 | -33.4817 | 108.0988 | 107.8968 | 107.8488 | 96.7377 | 94.4436 | 92.1771 | 89.903 | 87.3795 | 84.3129 | 80.8214 | 69.214 | 53.3607 | 37.8652 | 24.1876
|  | LW |  |  | 128.4648 | 125.8806 | 109.8702 | 107.9371 | 104.6219 | 101.1331 | 97.777 | 94.4156 | 90.2903 | 86.4624 | 72.6536 | 53.9658 | 35.2276 | 28.0599 | 62.9699 | 59.7989 | 41.2332 | 39.1213 | 35.2998 | 31.2692 | 27.4348 | 23.5982 | 18.8931 | 14.4782 | -1.4294 | -22.9614 | -44.4276 | -52.435 | 108.0294 | 107.8184 | 98.3656 | 96.249 | 92.4293 | 88.4331 | 84.6292 | 80.8228 | 76.1545 | 71.777 | 56.0028 | 34.6517 | 13.359 | 5.405
|  | ST |  |  | 129.0539 | 126.2729 | 125.9214 | 109.5881 | 108.0924 | 106.3704 | 104.8768 | 103.1586 | 100.8881 | 97.7371 | 87.327 | 75.0865 | 63.9608 | 54.3984 | 63.7414 | 60.2358 | 59.8289 | 40.9376 | 39.2109 | 37.2421 | 35.5394 | 33.573 | 30.9699 | 27.3976 | 15.5624 | 1.6471 | -11.0992 | -22.1505 | 108.1714 | 107.9514 | 107.9214 | 98.0696 | 96.3369 | 94.3617 | 92.6698 | 90.7192 | 88.1372 | 84.5917 | 72.8472 | 59.0384 | 46.3951 | 35.4385
|  | SP |  |  | 130.7925 | 129.2705 | 126.7338 | 126.4955 | 126.098 | 124.1104 | 122.059 | 119.959 | 116.1653 | 115.0023 | 110.657 | 104.4895 | 101.9306 | 99.3012 | 73.0067 | 64.0281 | 60.7653 | 60.5148 | 60.0559 | 57.9972 | 55.8646 | 53.6857 | 49.7889 | 48.4968 | 43.6369 | 36.7789 | 33.6639 | 30.6967 | 108.8271 | 108.2162 | 108.0135 | 107.8463 | 107.8055 | 106.231 | 104.6519 | 103.0106 | 99.8162 | 99.4039 | 98.0498 | 93.9355 | 90.806 | 87.83
BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | MINIMUM HEADROOM | SU6515552705 | YES | 133.6423 | 133.6056 | 105.7818 | 105.7169 | 105.5784 | 105.4357 | 105.2636 | 105.0753 | 104.8468 | 104.6203 | 101.2912 | 96.306 | 92.409 | 89.801 | 103.4916 | 103.4179 | 75.5595 | 75.4291 | 75.1522 | 74.8688 | 74.5284 | 74.1575 | 73.7131 | 72.963 | 69.6309 | 63.7618 | 59.1602 | 56.0738 | 117.3384 | 117.2853 | 89.4461 | 89.3521 | 89.1521 | 88.9468 | 88.6999 | 88.4305 | 88.106 | 87.6395 | 83.7898 | 78.1487 | 73.7262 | 70.7615
|  | CT |  |  | 133.6423 | 133.6056 | 105.7818 | 105.7169 | 105.5871 | 105.4694 | 105.3479 | 105.1837 | 104.975 | 104.7726 | 103.2104 | 99.2438 | 95.8194 | 92.2147 | 103.4916 | 103.4179 | 75.5595 | 75.4291 | 75.1898 | 74.9759 | 74.7551 | 74.4501 | 74.0706 | 73.6691 | 71.5079 | 67.2572 | 63.2239 | 58.9775 | 117.3384 | 117.2853 | 89.4461 | 89.3521 | 89.1736 | 89.0132 | 88.8475 | 88.6207 | 88.3361 | 88.0452 | 85.9867 | 81.4905 | 77.6121 | 73.5407
|  | LW |  |  | 133.6444 | 133.6092 | 105.7875 | 105.7268 | 105.5784 | 105.4357 | 105.2636 | 105.0753 | 104.8468 | 104.6203 | 101.2912 | 96.306 | 92.409 | 89.801 | 103.4958 | 103.4251 | 75.5707 | 75.4488 | 75.1522 | 74.8688 | 74.5284 | 74.1575 | 73.7131 | 72.963 | 69.6309 | 63.7618 | 59.1602 | 56.0738 | 117.3415 | 117.2905 | 89.4542 | 89.3663 | 89.1521 | 88.9468 | 88.6999 | 88.4305 | 88.106 | 87.6395 | 83.7898 | 78.1487 | 73.7262 | 70.7615
|  | ST |  |  | 133.6516 | 133.6408 | 133.6032 | 133.5709 | 105.7091 | 105.6396 | 105.5582 | 105.4586 | 105.3237 | 105.1644 | 104.643 | 102.2652 | 99.7476 | 97.0026 | 103.5103 | 103.4886 | 103.413 | 103.3481 | 75.4136 | 75.2747 | 75.1121 | 74.9136 | 74.6459 | 74.3275 | 72.9987 | 70.5851 | 67.8193 | 64.5874 | 117.3519 | 117.3363 | 117.2818 | 117.235 | 89.3408 | 89.2405 | 89.123 | 88.9795 | 88.7855 | 88.5556 | 87.6779 | 84.8947 | 82.0378 | 78.9415
|  | SP |  |  | 133.6589 | 133.6546 | 133.6276 | 133.6149 | 133.5833 | 133.5537 | 133.5156 | 133.4743 | 133.421 | 133.3406 | 133.0618 | 132.7754 | 132.4357 | 132.2044 | 103.5249 | 103.5162 | 103.462 | 103.4365 | 103.3783 | 103.3241 | 103.2528 | 103.1754 | 103.0767 | 102.9388 | 102.4554 | 101.9173 | 101.3571 | 100.8496 | 117.3624 | 117.3562 | 117.3171 | 117.2987 | 117.2553 | 117.2147 | 117.1619 | 117.1046 | 117.0311 | 116.9251 | 116.5554 | 116.1571 | 115.7194 | 115.4443
EAST CLAYDON GSP | BICESTER NORTH | MINIMUM HEADROOM | SP5972023735 | YES | 117 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 90 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 103.3705 | 103.3597 | 61.3041 | 60.909 | 60.8144 | 60.7181 | 60.6201 | 60.5163 | 60.3698 | 60.3419 | 60.2509 | 59.5028 | 59.0189 | 58.813
|  | CT |  |  | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 103.4223 | 103.4158 | 61.3041 | 60.909 | 60.8144 | 60.7181 | 60.6201 | 60.5163 | 60.3698 | 60.3419 | 60.2509 | 59.5028 | 59.0189 | 58.813
|  | LW |  |  | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 103.3705 | 103.3597 | 103.3489 | 102.6905 | 102.6276 | 102.562 | 102.4917 | 102.4163 | 102.3218 | 102.2935 | 102.1962 | 102.0146 | 101.8048 | 101.6758
|  | ST |  |  | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 103.4482 | 103.4439 | 103.4396 | 103.1762 | 103.0962 | 103.0149 | 102.9313 | 102.8446 | 102.7198 | 102.6752 | 102.5284 | 102.3783 | 101.998 | 101.8398
|  | SP |  |  | 117 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 111.8342 | 90 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 86.788 | 103.4741 | 103.4719 | 103.4698 | 103.3381 | 103.3273 | 103.3165 | 103.3056 | 103.2947 | 103.2836 | 103.278 | 103.2583 | 103.2316 | 103.1958 | 103.1503
EALING GSP | BOSTON MANOR ROAD | MINIMUM HEADROOM | TQ1703978105 | NO | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.2631 | 38.2256 | 38.1875 | 38.1477 | 38.0863 | 38.0786 | 38.0536 | 37.9383 | 37.8066 | 37.7724
|  | CT |  |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.2631 | 38.2256 | 38.1875 | 38.1477 | 38.0863 | 38.0786 | 38.0536 | 37.9383 | 37.8066 | 37.7724
|  | LW |  |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
|  | ST |  |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
|  | SP |  |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
BOTLEY WOOD GSP | BOTLEY WOOD BSP | MINIMUM HEADROOM | SU5398809673 | NO | 116.4477 | 116.4477 | 116.4477 | 116.4477 | 116.2935 | 116.4468 | 116.4463 | 116.4459 | 116.4451 | 116.443 | 116.4365 | 129.1553 | 128.4772 | 128.2652 | 80.7622 | 80.7148 | 80.6641 | 80.6031 | 80.4119 | 80.7247 | 80.7052 | 80.685 | 80.6615 | 80.6411 | 80.5805 | 94.9389 | 94.0928 | 93.7186 | 84.1369 | 84.1147 | 84.091 | 84.0625 | 83.9065 | 84.1188 | 84.1095 | 84.0998 | 84.0884 | 84.0777 | 84.0459 | 97.2074 | 96.4508 | 96.163
|  | CT |  |  | 116.4477 | 116.4477 | 116.4477 | 116.4477 | 116.3365 | 130.4088 | 130.2938 | 130.1736 | 129.9884 | 129.9649 | 129.8895 | 129.5414 | 129.1494 | 129.0491 | 80.7692 | 80.7268 | 80.6827 | 80.6031 | 80.4119 | 96.6379 | 96.436 | 96.2475 | 95.9933 | 95.9014 | 95.627 | 94.9916 | 94.3409 | 93.9895 | 84.1401 | 84.1203 | 84.0997 | 84.0625 | 83.9139 | 98.6691 | 98.5135 | 98.3614 | 98.1439 | 98.0885 | 97.9201 | 97.4377 | 96.9249 | 96.7072
|  | LW |  |  | 116.4477 | 116.4477 | 116.4477 | 130.6333 | 130.5004 | 130.3632 | 130.2199 | 130.0714 | 129.8458 | 129.8146 | 129.7075 | 129.5473 | 129.2585 | 129.2417 | 80.7622 | 80.7148 | 80.6641 | 96.9921 | 96.7657 | 96.5327 | 96.3251 | 96.1082 | 95.8136 | 95.714 | 95.4078 | 94.9604 | 94.4129 | 94.1449 | 84.1369 | 84.1147 | 84.091 | 98.9542 | 98.7776 | 98.5956 | 98.4222 | 98.2418 | 97.984 | 97.9208 | 97.7207 | 97.4263 | 97.0166 | 96.8824
|  | ST |  |  | 116.4477 | 116.4477 | 116.4477 | 116.4477 | 116.2935 | 130.3223 | 130.1623 | 129.9971 | 129.7414 | 129.6547 | 129.3778 | 129.1553 | 128.4772 | 128.2652 | 80.7754 | 80.7463 | 80.7078 | 80.6587 | 80.445 | 96.6385 | 96.4276 | 96.2089 | 95.9066 | 95.773 | 95.3583 | 94.9389 | 94.0928 | 93.7186 | 84.143 | 84.1294 | 84.1115 | 84.0885 | 83.9065 | 98.6233 | 98.4395 | 98.2493 | 97.9718 | 97.8632 | 97.5219 | 97.2074 | 96.4508 | 96.163
|  | SP |  |  | 116.4477 | 116.4477 | 116.4477 | 116.4477 | 116.4473 | 116.4468 | 116.4463 | 116.4459 | 116.4451 | 116.443 | 116.4365 | 130.6189 | 130.6091 | 130.6008 | 80.7985 | 80.7886 | 80.7734 | 80.7647 | 80.7461 | 80.7247 | 80.7052 | 80.685 | 80.6615 | 80.6411 | 80.5805 | 96.9213 | 96.8449 | 96.7726 | 84.1538 | 84.1492 | 84.1421 | 84.138 | 84.1291 | 84.1188 | 84.1095 | 84.0998 | 84.0884 | 84.0777 | 84.0459 | 98.9134 | 98.8725 | 98.8343
MANNINGTON GSP | BOURNEMOUTH | MINIMUM HEADROOM | SZ0627892368 | YES | 250.8039 | 227.9891 | 227.9493 | 226.8291 | 226.6757 | 226.405 | 225.0378 | 223.6246 | 222.5596 | 221.564 | 217.508 | 213.7524 | 208.4559 | 197.2307 | 186.9919 | 164.1771 | 164.1372 | 163.0171 | 162.8636 | 162.593 | 161.2257 | 159.8126 | 158.7475 | 157.7519 | 152.6367 | 139.999 | 126.5964 | 113.4385 | 213.9768 | 191.162 | 191.1221 | 190.002 | 189.8485 | 189.5779 | 188.2106 | 186.7974 | 185.7324 | 184.7368 | 180.6808 | 176.9252 | 165.1068 | 151.9012
|  | CT |  |  | 250.9121 | 250.8951 | 250.8774 | 250.2123 | 250.1131 | 249.9205 | 249.7264 | 247.3342 | 246.0622 | 245.1104 | 242.0382 | 236.0123 | 229.8951 | 218.7069 | 187.1 | 187.0831 | 187.0653 | 186.4002 | 186.301 | 186.1085 | 185.9144 | 183.5222 | 182.2501 | 181.2983 | 176.7919 | 161.884 | 147.9671 | 134.8464 | 214.0849 | 214.068 | 214.0502 | 213.3851 | 213.2859 | 213.0934 | 212.8993 | 210.5071 | 209.235 | 208.2832 | 205.211 | 199.1852 | 186.4758 | 173.3074
|  | LW |  |  | 250.8039 | 227.9891 | 227.9493 | 226.8291 | 226.6757 | 226.405 | 225.0378 | 223.6246 | 222.5596 | 221.564 | 217.508 | 213.7524 | 208.4559 | 197.2307 | 186.9919 | 164.1771 | 164.1372 | 163.0171 | 162.8636 | 162.593 | 161.2257 | 159.8126 | 158.7475 | 157.7519 | 152.6367 | 139.999 | 126.5964 | 113.4385 | 213.9768 | 191.162 | 191.1221 | 190.002 | 189.8485 | 189.5779 | 188.2106 | 186.7974 | 185.7324 | 184.7368 | 180.6808 | 176.9252 | 165.1068 | 151.9012
|  | ST |  |  | 250.9584 | 250.951 | 250.9435 | 250.5067 | 250.4539 | 250.306 | 249.618 | 248.8632 | 247.9082 | 246.9827 | 244.1318 | 241.1831 | 239.2175 | 238.0513 | 187.1464 | 187.1389 | 187.1314 | 186.6946 | 186.6419 | 186.4939 | 185.8059 | 185.0511 | 184.0961 | 183.1706 | 180.3198 | 174.7019 | 165.7899 | 158.0767 | 214.1313 | 214.1238 | 214.1163 | 213.6795 | 213.6267 | 213.4788 | 212.7908 | 212.036 | 211.081 | 210.1555 | 207.3047 | 204.3559 | 202.3903 | 196.6058
|  | SP |  |  | 251.001 | 250.997 | 250.9929 | 250.7742 | 250.754 | 249.5779 | 248.4017 | 246.9 | 244.176 | 243.7476 | 242.1872 | 240.2422 | 239.2519 | 238.7583 | 187.189 | 187.1849 | 187.1808 | 186.9621 | 186.942 | 185.7658 | 184.5896 | 183.0879 | 180.3639 | 179.9355 | 178.3752 | 176.4302 | 175.4398 | 174.9463 | 214.1739 | 214.1698 | 214.1657 | 213.947 | 213.9268 | 212.7507 | 211.5745 | 210.0728 | 207.3488 | 206.9204 | 205.36 | 203.4151 | 202.4247 | 201.9312
BRAMLEY (FLEE) | BRACKNELL MAIN | MINIMUM HEADROOM | SU8607569397 | YES | 145.0939 | 145.0303 | 144.9708 | 144.8738 | 144.569 | 144.2609 | 145.0018 | 144.9664 | 144.9222 | 144.8731 | 144.6899 | 150.2832 | 145.2361 | 134.3479 | 103.971 | 103.1901 | 102.4599 | 101.269 | 99.2655 | 97.259 | 102.8423 | 102.4084 | 101.8684 | 101.2761 | 97.18 | 91.9077 | 86.0622 | 71.9223 | 122.1515 | 122.1515 | 122.1515 | 122.1515 | 121.9973 | 121.8398 | 122.1514 | 122.1512 | 122.151 | 122.15 | 122.1446 | 125.7545 | 119.9073 | 105.0629
|  | CT |  |  | 145.0992 | 145.0394 | 144.9849 | 144.8738 | 144.569 | 144.2609 | 158.91 | 158.741 | 158.4782 | 158.4445 | 157.5067 | 150.2832 | 145.2361 | 146.5299 | 104.0358 | 103.3016 | 102.633 | 101.269 | 99.2655 | 97.259 | 112.76 | 111.1735 | 109.1867 | 107.115 | 100.3325 | 91.9077 | 86.0622 | 89.5726 | 122.1515 | 122.1515 | 122.1515 | 122.1515 | 121.9973 | 121.8398 | 140.324 | 140.155 | 139.8922 | 139.8585 | 134.1819 | 125.7545 | 119.9073 | 124.8174
|  | LW |  |  | 145.0939 | 145.0303 | 144.9708 | 159.3825 | 159.3635 | 159.341 | 159.3145 | 159.2838 | 159.231 | 159.2228 | 154.9646 | 152.677 | 147.1849 | 134.3479 | 103.971 | 103.1901 | 102.4599 | 118.4299 | 115.9952 | 113.4989 | 111.7211 | 109.8142 | 107.5336 | 105.1938 | 97.18 | 96.451 | 89.9996 | 71.9223 | 122.1515 | 122.1515 | 122.1515 | 140.7966 | 140.7776 | 140.755 | 140.7285 | 140.6978 | 140.645 | 138.9924 | 131.0281 | 131.6975 | 125.244 | 105.0629
|  | ST |  |  | 145.1178 | 145.0816 | 145.032 | 144.9733 | 144.8533 | 144.7176 | 159.3346 | 159.3164 | 159.2864 | 159.2755 | 159.2342 | 157.3581 | 153.7956 | 156.1836 | 104.2642 | 103.8199 | 103.211 | 102.4902 | 101.1876 | 99.701 | 116.1672 | 114.988 | 113.6102 | 111.9747 | 106.4412 | 100.0027 | 95.8243 | 100.6063 | 122.1515 | 122.1515 | 122.1515 | 122.1515 | 122.1364 | 122.1204 | 140.7486 | 140.7304 | 140.7005 | 140.6895 | 140.2232 | 133.8517 | 129.672 | 135.8542
|  | SP |  |  | 145.1458 | 145.1365 | 145.1146 | 145.1058 | 145.0731 | 145.0354 | 145.0018 | 144.9664 | 144.9222 | 144.8731 | 144.6899 | 159.3713 | 159.3504 | 163.4625 | 104.6077 | 104.494 | 104.2257 | 104.1172 | 103.7162 | 103.2537 | 102.8423 | 102.4084 | 101.8684 | 101.2761 | 99.089 | 113.8296 | 111.8967 | 120.4796 | 122.1515 | 122.1515 | 122.1515 | 122.1515 | 122.1515 | 122.1514 | 122.1514 | 122.1512 | 122.151 | 122.15 | 122.1446 | 140.7853 | 140.7644 | 148.7569
BRAMLEY (FLEE) | BRACKNELL RESERVE | MINIMUM HEADROOM | SU8607569397 | YES | 128.6379 | 128.6243 | 128.583 | 128.5736 | 128.5115 | 127.5247 | 125.7705 | 123.9988 | 121.8869 | 119.9414 | 113.1362 | 102.4123 | 95.1551 | 91.035 | 94.0526 | 94.0526 | 94.0526 | 94.0526 | 93.3153 | 91.2514 | 89.2685 | 87.2669 | 84.8871 | 82.6759 | 74.9419 | 62.6073 | 54.2351 | 49.4563 | 104.4743 | 104.4534 | 104.3901 | 104.3757 | 104.2835 | 104.1763 | 103.7441 | 102.4593 | 100.5988 | 98.9029 | 92.9694 | 83.6165 | 77.2614 | 73.6741
|  | CT |  |  | 130.9662 | 130.8862 | 130.7906 | 130.5972 | 129.8626 | 128.5536 | 127.2117 | 125.8405 | 124.0977 | 122.4751 | 117.1474 | 109.0049 | 102.451 | 95.714 | 96.4947 | 96.4947 | 96.2467 | 95.434 | 93.9192 | 92.461 | 90.9661 | 89.4395 | 87.5088 | 85.6685 | 79.6256 | 70.4654 | 63.0252 | 55.2433 | 106.7417 | 106.6191 | 106.4725 | 106.1758 | 105.4788 | 104.7992 | 104.1032 | 103.3882 | 102.4239 | 101.0058 | 96.3493 | 89.1623 | 83.3484 | 77.4569
|  | LW |  |  | 130.962 | 130.8791 | 130.7796 | 130.5779 | 129.3491 | 127.5247 | 125.7705 | 123.9988 | 121.8869 | 119.9414 | 113.1362 | 102.4123 | 95.1551 | 91.035 | 96.4947 | 96.4947 | 96.2004 | 95.3528 | 93.3153 | 91.2514 | 89.2685 | 87.2669 | 84.8871 | 82.6759 | 74.9419 | 62.6073 | 54.2351 | 49.4563 | 106.7354 | 106.6082 | 106.4556 | 106.1462 | 105.3467 | 104.5333 | 103.7441 | 102.4593 | 100.5988 | 98.9029 | 92.9694 | 83.6165 | 77.2614 | 73.6741
|  | ST |  |  | 131.0396 | 130.9616 | 130.9129 | 130.8335 | 130.6141 | 130.3533 | 129.6625 | 128.6981 | 127.5145 | 126.1326 | 121.528 | 115.2136 | 110.5813 | 105.251 | 96.4947 | 96.4947 | 96.4947 | 96.4266 | 95.5658 | 94.6333 | 93.6683 | 92.5736 | 91.2314 | 89.6602 | 84.4255 | 77.2443 | 71.9963 | 65.841 | 106.8544 | 106.7347 | 106.6601 | 106.5382 | 106.2119 | 105.8586 | 105.4928 | 105.0785 | 104.5641 | 103.9815 | 100.3364 | 94.8357 | 90.7813 | 86.1358
|  | SP |  |  | 128.6379 | 128.6243 | 128.583 | 128.5736 | 128.5115 | 128.4395 | 130.7866 | 130.6921 | 130.5702 | 130.416 | 128.8297 | 126.2583 | 123.9663 | 122.3634 | 94.0526 | 94.0526 | 94.0526 | 94.0526 | 94.0466 | 94.0408 | 96.2862 | 95.9085 | 95.4268 | 94.865 | 92.7325 | 89.8111 | 87.2227 | 85.4159 | 104.4743 | 104.4534 | 104.3901 | 104.3757 | 104.2835 | 104.1763 | 106.4757 | 106.334 | 106.1521 | 105.9299 | 105.0951 | 104.0002 | 102.4378 | 101.0263
EALING GSP | BRIDGE ROAD | MINIMUM HEADROOM | TQ1484575785 | NO | 108.569 | 108.5451 | 108.5212 | 107.0629 | 106.9433 | 106.8238 | 106.6282 | 106.4194 | 106.2257 | 105.8949 | 103.3401 | 98.1291 | 92.2487 | 86.3158 | 86.6664 | 86.5953 | 86.5341 | 85.0049 | 84.8132 | 84.407 | 83.7879 | 82.8014 | 81.6187 | 80.5943 | 77.5997 | 71.482 | 64.5555 | 57.5885 | 94.7432 | 94.7193 | 94.6954 | 93.2371 | 93.1175 | 92.9878 | 92.8002 | 91.5735 | 90.4073 | 89.3982 | 86.4479 | 80.4217 | 73.6008 | 66.677
|  | CT |  |  | 108.6838 | 108.6694 | 108.6551 | 107.7801 | 107.7084 | 107.6366 | 107.5072 | 107.3463 | 107.2004 | 107.0932 | 104.5958 | 98.577 | 92.4711 | 86.5385 | 86.7844 | 86.7251 | 86.6765 | 85.737 | 85.5993 | 85.4584 | 84.7602 | 83.9704 | 82.8384 | 81.8332 | 78.8961 | 71.9704 | 64.8184 | 57.8519 | 94.858 | 94.8436 | 94.8293 | 93.9543 | 93.8826 | 93.8108 | 93.676 | 92.7415 | 91.6229 | 90.633 | 87.7402 | 80.9061 | 73.8596 | 66.9399
|  | LW |  |  | 108.569 | 108.5451 | 108.5212 | 107.0629 | 106.9433 | 106.8238 | 106.6282 | 106.4194 | 106.2257 | 105.8949 | 103.3401 | 98.1291 | 92.2487 | 86.3158 | 86.6664 | 86.5953 | 86.5341 | 85.0049 | 84.8132 | 84.407 | 83.7879 | 82.8014 | 81.6187 | 80.5943 | 77.5997 | 71.482 | 64.5555 | 57.5885 | 94.7432 | 94.7193 | 94.6954 | 93.2371 | 93.1175 | 92.9878 | 92.8002 | 91.5735 | 90.4073 | 89.3982 | 86.4479 | 80.4217 | 73.6008 | 66.677
|  | ST |  |  | 108.7412 | 108.7316 | 108.722 | 108.1387 | 108.0909 | 108.0431 | 107.9952 | 107.9474 | 107.8996 | 107.8707 | 107.677 | 105.7418 | 101.9181 | 98.192 | 86.8526 | 86.8288 | 86.778 | 86.1642 | 86.0792 | 85.9866 | 85.8935 | 85.7973 | 85.6705 | 85.3675 | 84.3118 | 80.1743 | 75.6638 | 71.2774 | 94.9154 | 94.9058 | 94.8962 | 94.3129 | 94.2651 | 94.2173 | 94.1694 | 94.1216 | 94.0738 | 94.0314 | 93.0828 | 89.0051 | 84.5639 | 80.2442
|  | SP |  |  | 108.7985 | 108.7937 | 108.789 | 108.4973 | 108.4734 | 108.4495 | 108.4256 | 108.4017 | 108.3778 | 108.3682 | 108.3395 | 108.2917 | 118.0314 | 117.8499 | 86.9208 | 86.9111 | 86.8995 | 86.6002 | 86.5612 | 86.5199 | 86.4786 | 86.4364 | 86.3943 | 86.3723 | 86.3075 | 86.1819 | 95.6392 | 94.7078 | 94.9727 | 94.9679 | 94.9632 | 94.6715 | 94.6476 | 94.6237 | 94.5998 | 94.5759 | 94.552 | 94.5424 | 94.5137 | 94.4659 | 104.1988 | 103.4814
BRAMLEY (FLEE) | BURGHFIELD MAIN | MINIMUM HEADROOM | SU6942870520 | YES | 108.8748 | 108.854 | 108.1316 | 108.1269 | 108.1143 | 108.1015 | 108.0772 | 108.053 | 106.2307 | 106.107 | 105.7197 | 104.9753 | 104.0588 | 103.3178 | 77.7469 | 77.6684 | 77.036 | 77.0183 | 76.9803 | 76.9019 | 76.4498 | 75.994 | 73.7971 | 73.3869 | 72.1206 | 69.6033 | 65.7217 | 60.7131 | 103.0654 | 103.0304 | 102.2879 | 102.28 | 102.2612 | 102.2419 | 102.2033 | 102.0955 | 100.1012 | 99.9072 | 99.3044 | 98.1254 | 96.7125 | 95.477
|  | CT |  |  | 108.8748 | 108.854 | 108.8274 | 108.7767 | 108.6933 | 108.6114 | 108.5299 | 108.3963 | 106.5516 | 106.4402 | 106.0971 | 105.3377 | 104.467 | 103.7056 | 77.7469 | 77.6684 | 77.5682 | 77.3769 | 77.1563 | 76.943 | 76.7326 | 76.3305 | 74.2175 | 73.8196 | 72.5976 | 70.065 | 66.3213 | 61.3139 | 103.0654 | 103.0304 | 102.9858 | 102.9006 | 102.7836 | 102.6695 | 102.5563 | 102.357 | 100.4465 | 100.2648 | 99.7063 | 98.5121 | 97.1451 | 95.8895
|  | LW |  |  | 108.8765 | 108.8569 | 108.832 | 108.7847 | 108.6577 | 108.5302 | 108.3464 | 108.1593 | 106.2307 | 106.107 | 105.7197 | 104.9753 | 104.0588 | 103.3178 | 77.7533 | 77.6794 | 77.5852 | 77.4068 | 77.1518 | 76.9019 | 76.4498 | 75.994 | 73.7971 | 73.3869 | 72.1206 | 69.6033 | 65.7217 | 60.7131 | 103.0682 | 103.0353 | 102.9934 | 102.914 | 102.7556 | 102.5981 | 102.3485 | 102.0955 | 100.1012 | 99.9072 | 99.3044 | 98.1254 | 96.7125 | 95.477
|  | ST |  |  | 108.9082 | 108.868 | 108.8515 | 108.8256 | 108.7831 | 108.7364 | 108.6617 | 108.5868 | 107.6561 | 107.5778 | 107.3378 | 106.882 | 109.203 | 108.7172 | 77.8728 | 77.721 | 77.6589 | 77.561 | 77.4337 | 77.291 | 77.0437 | 76.7963 | 75.6825 | 75.4084 | 74.5708 | 72.9077 | 73.9063 | 71.8026 | 103.1215 | 103.0539 | 103.0262 | 102.9826 | 102.9193 | 102.8491 | 102.7321 | 102.6149 | 101.6393 | 101.5131 | 101.1265 | 100.3747 | 102.3715 | 101.5685
|  | SP |  |  | 108.9202 | 108.9157 | 108.1316 | 108.1269 | 108.1143 | 108.1015 | 108.0772 | 108.053 | 110.8844 | 110.8423 | 111.4661 | 111.271 | 111.0013 | 110.7397 | 77.9179 | 77.9008 | 77.036 | 77.0183 | 76.9803 | 76.941 | 76.8586 | 76.7764 | 79.5343 | 79.416 | 79.8041 | 79.1294 | 78.3044 | 77.4781 | 103.1416 | 103.134 | 102.2879 | 102.28 | 102.2612 | 102.2419 | 102.2033 | 102.1649 | 104.9782 | 104.9175 | 105.5257 | 105.213 | 104.8072 | 104.4071
BRAMLEY (FLEE) | BURGHFIELD RESERVE | MINIMUM HEADROOM | SU6942870520 | YES | 134.462 | 134.4619 | 134.4619 | 134.4619 | 134.45 | 134.436 | 133.6308 | 130.6929 | 126.9976 | 123.4644 | 110.3252 | 91.1587 | 65.9118 | 60.4894 | 94.7072 | 94.5076 | 94.1469 | 93.7685 | 92.3195 | 90.845 | 88.7265 | 85.4455 | 81.3255 | 77.3633 | 62.8432 | 41.9082 | 13.5088 | 7.1776 | 114.686 | 114.686 | 114.6859 | 114.4601 | 113.4292 | 111.9076 | 109.4387 | 106.0144 | 101.7172 | 97.576 | 82.4006 | 60.5246 | 31.7336 | 25.541
|  | CT |  |  | 140.3564 | 140.3558 | 140.3551 | 140.354 | 140.2683 | 138.8636 | 137.2183 | 135.565 | 133.2788 | 130.5606 | 121.2415 | 108.674 | 92.6764 | 81.3929 | 100.4122 | 99.9387 | 99.4757 | 98.5689 | 96.4813 | 94.5795 | 92.7438 | 90.9002 | 88.3534 | 85.3047 | 74.853 | 61.0587 | 43.6185 | 31.2969 | 120.5804 | 120.5499 | 120.2214 | 119.5781 | 117.535 | 115.5505 | 113.6353 | 111.7122 | 109.0568 | 105.8702 | 94.9458 | 80.5452 | 62.3372 | 49.4632
|  | LW |  |  | 140.3542 | 140.3523 | 140.3502 | 140.3473 | 139.6188 | 136.5496 | 133.6308 | 130.6929 | 126.9976 | 123.4644 | 110.3252 | 91.1587 | 65.9118 | 60.4894 | 100.4695 | 100.0376 | 99.6298 | 98.8408 | 95.4191 | 91.9873 | 88.7265 | 85.4455 | 81.3255 | 77.3633 | 62.8432 | 41.9082 | 13.5088 | 7.1776 | 120.5782 | 120.5763 | 120.3292 | 119.7689 | 116.4253 | 112.8423 | 109.4387 | 106.0144 | 101.7172 | 97.576 | 82.4006 | 60.5246 | 31.7336 | 25.541
|  | ST |  |  | 134.462 | 134.4619 | 134.4619 | 134.4619 | 134.45 | 134.436 | 133.6922 | 132.2179 | 130.2235 | 127.6899 | 118.9283 | 107.9718 | 93.6715 | 83.9041 | 94.7072 | 94.5076 | 94.1469 | 93.7685 | 92.3195 | 90.845 | 89.4801 | 87.8273 | 85.5927 | 82.7501 | 72.922 | 60.7604 | 45.1461 | 34.4728 | 114.686 | 114.686 | 114.6859 | 114.4601 | 113.4292 | 111.9076 | 110.4812 | 108.7539 | 106.419 | 103.4475 | 93.1743 | 80.4618 | 64.1483 | 52.9928
|  | SP |  |  | 140.3567 | 140.3566 | 140.3566 | 139.1388 | 139.1168 | 139.0952 | 139.0734 | 139.0511 | 139.0162 | 138.6368 | 134.8758 | 129.9563 | 125.4832 | 122.5659 | 100.7742 | 100.7148 | 100.5809 | 97.4018 | 96.9827 | 96.5155 | 95.9166 | 95.3248 | 94.5408 | 93.505 | 89.3217 | 83.8181 | 78.8601 | 75.6395 | 120.5807 | 120.5807 | 120.5806 | 117.4437 | 117.1402 | 116.8027 | 116.3717 | 115.9456 | 115.1743 | 114.0957 | 109.7362 | 103.9888 | 98.8286 | 95.4814
BRAMLEY (FLEE) | CAMBERLEY MAIN | MINIMUM HEADROOM | SU8607569397 | YES | 146.2567 | 146.189 | 146.1002 | 144.3259 | 143.9737 | 142.4597 | 139.1359 | 135.813 | 129.2246 | 128.4744 | 126.5443 | 119.8746 | 108.1323 | 100.8287 | 88.8616 | 87.9077 | 87.2199 | 84.256 | 81.8451 | 79.0955 | 76.807 | 74.527 | 69.6534 | 68.4321 | 61.2773 | 48.2611 | 37.5563 | 30.9107 | 102.0865 | 100.8191 | 99.9079 | 96.5002 | 93.3212 | 89.7924 | 86.8824 | 83.9856 | 80.6954 | 77.5792 | 66.8293 | 50.2974 | 36.9729 | 28.6659
|  | CT |  |  | 146.4389 | 146.3405 | 146.2683 | 145.1671 | 144.7222 | 144.0158 | 143.2979 | 142.5975 | 141.7427 | 141.2854 | 138.9112 | 126.8119 | 116.4152 | 106.5119 | 89.0576 | 88.1624 | 87.5483 | 85.378 | 83.4855 | 81.3665 | 79.2132 | 77.3469 | 75.11 | 73.0638 | 66.3706 | 54.7366 | 44.7316 | 35.7288 | 102.3048 | 101.1123 | 100.296 | 97.727 | 95.2944 | 92.6476 | 89.9566 | 87.6535 | 84.8988 | 82.2573 | 73.5956 | 59.3445 | 47.1364 | 35.6685
|  | LW |  |  | 146.3028 | 146.189 | 146.1002 | 144.3259 | 143.9737 | 143.3042 | 142.6746 | 142.0409 | 141.3602 | 140.8536 | 133.5204 | 119.8746 | 108.1323 | 100.8287 | 88.8616 | 87.9077 | 87.2199 | 84.256 | 81.8451 | 79.0955 | 76.807 | 74.527 | 71.9479 | 69.543 | 61.2773 | 48.2611 | 37.5563 | 30.9107 | 102.0865 | 100.8191 | 99.9079 | 96.5002 | 93.3212 | 89.7924 | 86.8824 | 83.9856 | 80.6954 | 77.5792 | 66.8293 | 50.2974 | 36.9729 | 28.6659
|  | ST |  |  | 146.5344 | 146.4827 | 146.3995 | 145.6856 | 145.5245 | 145.0832 | 144.6566 | 144.2174 | 143.7553 | 142.2536 | 137.6864 | 129.3326 | 121.3046 | 113.8602 | 89.4488 | 89.0007 | 88.2157 | 86.9857 | 85.8513 | 84.3167 | 82.9496 | 81.4869 | 79.8871 | 77.038 | 67.955 | 56.9256 | 49.1969 | 42.0986 | 102.8064 | 102.2103 | 101.1636 | 99.741 | 98.2435 | 96.301 | 94.5831 | 92.7376 | 90.7116 | 87.3577 | 76.5828 | 63.3994 | 53.9873 | 44.942
|  | SP |  |  | 146.2567 | 146.2309 | 146.1819 | 145.8438 | 145.7806 | 142.4597 | 139.1359 | 135.813 | 129.2246 | 128.4744 | 126.5443 | 122.5933 | 119.8392 | 118.6559 | 89.2032 | 88.9789 | 88.508 | 88.0944 | 87.7383 | 84.0743 | 80.379 | 76.6951 | 69.6534 | 68.4321 | 64.9235 | 58.4634 | 53.5657 | 50.8335 | 102.7404 | 102.4488 | 101.8204 | 101.3787 | 100.9134 | 97.1213 | 93.2874 | 89.4688 | 82.258 | 80.8609 | 76.589 | 69.1899 | 63.4891 | 60.1765
BRAMLEY (FLEE) | CAMBERLEY RESERVE | MINIMUM HEADROOM | SU8658459452 | YES | 138.0923 | 137.5704 | 120.3874 | 120.3874 | 120.2797 | 120.1686 | 120.0525 | 119.9322 | 119.7494 | 119.7241 | 119.884 | 119.7305 | 115.7354 | 104.9557 | 104.9909 | 104.4689 | 87.2859 | 87.2859 | 87.1782 | 87.0671 | 86.8136 | 86.5454 | 86.2077 | 86.022 | 84.0413 | 79.923 | 75.5296 | 60.8691 | 118.1427 | 117.6208 | 100.4378 | 100.4378 | 100.3301 | 100.219 | 100.1029 | 99.9826 | 99.7998 | 99.7745 | 99.8413 | 95.834 | 91.5734 | 76.1875
|  | CT |  |  | 138.0923 | 137.6858 | 137.4005 | 137.4005 | 137.3891 | 120.5355 | 120.5237 | 120.5114 | 120.4925 | 120.4901 | 120.4824 | 119.7305 | 115.7354 | 121.3048 | 104.9909 | 104.5844 | 104.2991 | 104.2991 | 104.2877 | 87.434 | 87.3422 | 87.182 | 87.0081 | 86.8453 | 84.6781 | 79.923 | 75.5296 | 85.5807 | 118.1427 | 117.7362 | 117.4509 | 117.4509 | 117.4395 | 100.5858 | 100.5741 | 100.5618 | 100.5429 | 100.5405 | 100.3817 | 95.834 | 91.5734 | 103.8143
|  | LW |  |  | 138.0923 | 137.5704 | 120.3874 | 120.3874 | 120.2797 | 120.1686 | 120.0525 | 119.9322 | 119.7494 | 119.7241 | 119.884 | 125.5152 | 124.0707 | 104.9557 | 104.9909 | 104.4689 | 87.2859 | 87.2859 | 87.1782 | 87.0671 | 86.8136 | 86.5454 | 86.2077 | 86.022 | 84.0413 | 92.2553 | 88.8883 | 60.8691 | 118.1427 | 117.6208 | 100.4378 | 100.4378 | 100.3301 | 100.219 | 100.1029 | 99.9826 | 99.7998 | 99.7745 | 99.8413 | 106.8296 | 106.5727 | 76.1875
|  | ST |  |  | 138.0923 | 137.7891 | 137.5965 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 120.7544 | 121.0011 | 126.762 | 104.9909 | 104.6876 | 104.4951 | 87.653 | 87.653 | 87.653 | 87.653 | 87.653 | 87.561 | 87.4512 | 87.1771 | 85.228 | 82.6142 | 93.5021 | 118.1427 | 117.8395 | 117.6469 | 100.8048 | 100.8048 | 100.8048 | 100.8048 | 100.8048 | 100.8048 | 100.8048 | 100.8048 | 100.8048 | 98.5261 | 108.0764
|  | SP |  |  | 138.2142 | 138.09 | 138.031 | 138.031 | 134.2613 | 134.2613 | 134.2613 | 134.2613 | 134.2613 | 134.2613 | 134.2613 | 134.2613 | 134.5331 | 140.618 | 105.1127 | 104.9885 | 104.9295 | 104.9295 | 98.2258 | 98.1515 | 98.0584 | 97.9641 | 97.8522 | 97.7182 | 97.3649 | 96.8029 | 96.94 | 107.4483 | 118.2646 | 118.1404 | 118.0814 | 118.0814 | 113.801 | 113.801 | 113.801 | 113.801 | 113.6571 | 113.5097 | 113.1435 | 112.5612 | 113.0019 | 121.2127
IVER 132KV | CHALVEY BSP | MINIMUM HEADROOM | SU9666979364 | NO | 140.0345 | 139.9929 | 139.9475 | 139.213 | 139.0793 | 138.7266 | 137.5006 | 136.2737 | 133.8499 | 133.5654 | 132.7175 | 131.2574 | 128.8614 | 124.196 | 100.9381 | 100.8923 | 100.8422 | 100.1005 | 99.9573 | 99.6227 | 98.3939 | 97.1641 | 94.737 | 94.4492 | 92.8067 | 86.4579 | 80.1606 | 74.8758 | 116.4316 | 116.3958 | 116.357 | 115.6324 | 115.5119 | 115.1341 | 113.912 | 112.6891 | 110.2699 | 109.9901 | 109.1544 | 107.7144 | 106.6673 | 103.1091
|  | CT |  |  | 140.089 | 140.0524 | 140.0122 | 139.5523 | 139.4576 | 139.2654 | 139.0742 | 138.8606 | 138.6395 | 138.463 | 137.9751 | 136.2067 | 130.8421 | 125.9108 | 100.9927 | 100.9519 | 100.9071 | 100.4403 | 100.3372 | 100.1361 | 99.9363 | 99.711 | 99.2342 | 97.9199 | 94.5693 | 88.4091 | 82.3735 | 76.7703 | 116.4859 | 116.4551 | 116.4213 | 115.971 | 115.8881 | 115.7081 | 115.5289 | 115.3315 | 115.128 | 114.9683 | 114.5224 | 112.3983 | 108.2331 | 104.5025
|  | LW |  |  | 140.0345 | 139.9929 | 139.9475 | 139.213 | 139.0793 | 138.8306 | 138.5678 | 138.2986 | 138.0148 | 137.8102 | 137.2298 | 134.4604 | 128.8614 | 124.196 | 100.9381 | 100.8923 | 100.8422 | 100.1005 | 99.9573 | 99.6987 | 99.424 | 99.1422 | 97.8788 | 96.4839 | 92.8067 | 86.4579 | 80.1606 | 74.8758 | 116.4316 | 116.3958 | 116.357 | 115.6324 | 115.5119 | 115.2772 | 115.0308 | 114.779 | 114.5141 | 114.3269 | 113.7921 | 111.0183 | 106.6673 | 103.1091
|  | ST |  |  | 140.123 | 140.1039 | 140.0713 | 139.772 | 139.6495 | 139.4235 | 139.1868 | 138.9431 | 138.653 | 138.0586 | 136.2939 | 134.2448 | 132.7428 | 130.1687 | 101.0277 | 101.0066 | 100.9701 | 100.6672 | 100.5396 | 100.3078 | 100.0641 | 99.8127 | 99.5137 | 98.9107 | 96.1118 | 90.7438 | 86.0766 | 82.1088 | 116.5186 | 116.5023 | 116.4751 | 116.1808 | 116.0654 | 115.8473 | 115.6205 | 115.3874 | 115.1096 | 114.5273 | 112.7938 | 110.7935 | 109.338 | 106.8291
|  | SP |  |  | 140.1554 | 140.1449 | 140.128 | 139.9805 | 139.95 | 138.7266 | 137.5006 | 136.2737 | 133.8499 | 133.5654 | 132.7175 | 131.2574 | 131.2278 | 130.7496 | 101.0609 | 101.0492 | 101.0303 | 100.8813 | 100.8485 | 99.6227 | 98.3939 | 97.1641 | 94.737 | 94.4492 | 93.5925 | 92.1178 | 92.0735 | 90.8203 | 116.5499 | 116.541 | 116.527 | 116.3815 | 116.3542 | 115.1341 | 113.912 | 112.6891 | 110.2699 | 109.9901 | 109.1544 | 107.7144 | 107.7053 | 107.2458
LOVEDEAN GSP | CHICHESTER & HUNSTON | MINIMUM HEADROOM | SU9219807420 | NO | 342.7183 | 334.2088 | 332.6168 | 329.0421 | 305.6368 | 303.6608 | 301.4971 | 299.1926 | 296.6136 | 293.1487 | 282.108 | 262.2936 | 229.4264 | 212.0566 | 223.6969 | 214.8384 | 213.0399 | 209.1777 | 185.8098 | 183.5512 | 181.0735 | 178.4314 | 175.4734 | 171.5916 | 159.1902 | 136.6036 | 96.3102 | 73.5175 | 256.2024 | 247.3335 | 245.5289 | 241.6583 | 218.2915 | 216.0246 | 213.5375 | 210.8854 | 207.9162 | 204.0221 | 191.5805 | 168.9121 | 128.463 | 105.4144
|  | CT |  |  | 357.2652 | 334.5719 | 333.0962 | 330.3675 | 328.1592 | 325.7018 | 323.2341 | 319.9187 | 316.3297 | 312.7686 | 301.3833 | 277.9495 | 252.4476 | 241.8267 | 240.6833 | 215.2161 | 213.5419 | 210.5425 | 207.9983 | 205.1946 | 202.3794 | 198.5743 | 194.461 | 190.336 | 177.1409 | 150.3023 | 120.9222 | 110.5653 | 273.1229 | 247.7117 | 246.0316 | 243.0242 | 240.4701 | 237.6562 | 234.8307 | 231.0112 | 226.8823 | 222.7407 | 209.4921 | 182.5529 | 153.0582 | 142.7729
|  | LW |  |  | 342.7183 | 334.2088 | 332.6168 | 329.0421 | 326.1308 | 322.8868 | 319.0379 | 315.0677 | 310.6776 | 306.7979 | 294.1067 | 266.9009 | 229.4264 | 212.0566 | 223.6969 | 214.8384 | 213.0399 | 209.1777 | 205.8549 | 202.1816 | 197.8039 | 193.2862 | 188.3097 | 183.8292 | 169.1625 | 139.602 | 96.3102 | 73.5175 | 256.2024 | 247.3335 | 245.5289 | 241.6583 | 238.3233 | 234.6374 | 230.244 | 225.7101 | 220.7163 | 216.218 | 201.493 | 171.9266 | 128.463 | 105.4144
|  | ST |  |  | 357.4714 | 336.3666 | 334.1917 | 332.4663 | 305.6368 | 303.6608 | 301.4971 | 299.1926 | 296.6136 | 293.1487 | 282.108 | 262.2936 | 241.0335 | 234.4975 | 240.9121 | 217.2837 | 214.775 | 212.8849 | 185.8098 | 183.5512 | 181.0735 | 178.4314 | 175.4734 | 171.5916 | 159.1902 | 136.6036 | 112.1123 | 106.4735 | 273.3409 | 249.7874 | 247.2688 | 245.3738 | 218.2915 | 216.0246 | 213.5375 | 210.8854 | 207.9162 | 204.0221 | 191.5805 | 168.9121 | 144.3252 | 138.7767
|  | SP |  |  | 358.0454 | 351.8016 | 350.5027 | 335.5273 | 330.7893 | 327.9094 | 324.903 | 321.882 | 316.4264 | 315.0128 | 310.3874 | 300.6457 | 295.3586 | 294.9121 | 241.5503 | 235.2694 | 233.7614 | 216.3123 | 208.4239 | 205.4525 | 202.3331 | 199.1967 | 193.6037 | 192.0338 | 186.8739 | 174.292 | 168.404 | 169.8233 | 273.9484 | 267.6853 | 266.2772 | 248.8121 | 240.7482 | 237.7742 | 234.6514 | 231.5116 | 225.9145 | 224.34 | 219.1643 | 206.4413 | 200.5356 | 202.0738
CHICKERELL GSP | CHICKERELL BSP | MINIMUM HEADROOM | SY6547980511 | NO | 121.4647 | 121.3801 | 110.5533 | 107.4049 | 94.5631 | 93.063 | 91.557 | 88.6614 | 85.4371 | 82.0845 | 71.0623 | 49.1074 | 20.3495 | 10.1721 | 58.5743 | 58.4698 | 48.9154 | 45.6319 | 32.4864 | 30.709 | 28.9251 | 25.553 | 21.7262 | 17.6687 | 4.0971 | -24.5403 | -59.5026 | -71.4379 | 84.1462 | 84.1043 | 83.9362 | 83.2929 | 72.4761 | 71.572 | 70.6634 | 68.7916 | 63.6982 | 62.6051 | 58.522 | 34.559 | -0.79094 | -12.8751
|  | CT |  |  | 136.9568 | 136.5593 | 110.7981 | 108.6907 | 94.5631 | 93.063 | 91.557 | 88.6614 | 85.4371 | 82.0845 | 71.0623 | 50.9624 | 30.676 | 30.2309 | 79.21 | 78.7157 | 49.1582 | 46.9141 | 32.4864 | 30.709 | 28.9251 | 25.553 | 21.7262 | 17.6687 | 4.3031 | -19.5008 | -43.8461 | -46.9068 | 105.5641 | 105.3745 | 87.7724 | 85.9586 | 72.4761 | 71.572 | 70.6634 | 68.7916 | 66.8624 | 65.0247 | 59.039 | 39.4573 | 15.2919 | 12.0347
|  | LW |  |  | 136.7492 | 122.1371 | 110.5533 | 107.4049 | 105.0565 | 102.3856 | 98.7416 | 95.0457 | 90.6628 | 86.6941 | 72.7267 | 49.1074 | 20.3495 | 10.1721 | 79.0031 | 60.5867 | 48.9154 | 45.6319 | 42.7877 | 39.6186 | 35.3118 | 30.9475 | 25.7555 | 20.9583 | 4.0971 | -24.5403 | -59.5026 | -71.4379 | 105.3549 | 98.919 | 87.5233 | 84.6654 | 83.3824 | 81.7823 | 79.5627 | 77.3035 | 74.6592 | 72.4713 | 62.9738 | 34.559 | -0.79094 | -12.8751
|  | ST |  |  | 137.3217 | 136.9073 | 122.3346 | 120.9732 | 95.926 | 94.5842 | 92.8321 | 90.8968 | 88.3556 | 84.6018 | 72.4856 | 55.4992 | 38.7453 | 41.7874 | 79.6432 | 79.125 | 60.7503 | 59.3084 | 34.0249 | 32.439 | 30.3785 | 28.0929 | 25.0633 | 20.7232 | 6.6292 | -13.4076 | -33.6608 | -32.6895 | 105.7821 | 105.5907 | 99.1895 | 98.001 | 73.4619 | 72.6445 | 71.5552 | 70.3728 | 68.8813 | 66.3877 | 58.522 | 45.4815 | 25.3834 | 26.4465
|  | SP |  |  | 121.4647 | 121.3801 | 121.008 | 120.3776 | 120.0645 | 119.8075 | 116.1011 | 101.0996 | 93.9162 | 92.3797 | 87.0721 | 78.7446 | 72.9803 | 69.622 | 58.5743 | 58.4698 | 58.0028 | 57.3284 | 56.9468 | 61.8594 | 58.0346 | 42.9155 | 35.5729 | 33.83 | 27.7421 | 18.2441 | 11.6336 | 7.6795 | 84.1462 | 84.1043 | 83.9362 | 83.2929 | 83.1269 | 88.7401 | 85.288 | 70.5393 | 63.6982 | 62.6051 | 58.9745 | 53.1629 | 49.2171 | 47.1394
MELKSHAM GSP | CHIPPENHAM | MINIMUM HEADROOM | ST9275574305 | NO | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6938 | 100.321 | 51.9287 | 17.2563 | -5.8871 | -25.0174 | -28.4514 | -33.3208 | -38.213 | -47.8696 | -59.2127 | -65.2757 | -105.9746 | -197.5831 | -233.397 | -249.3776 | 75.9571 | 41.145 | 15.8084 | -1.2686 | -4.7219 | -9.6083 | -15.0173 | -26.1505 | -37.5307 | -43.5471 | -83.8783 | -174.937 | -210.7055 | -226.83
|  | CT |  |  | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 117 | 117 | 117.0126 | 117.0126 | 51.9287 | 51.127 | 11.6 | -25.0174 | -28.4514 | -33.3208 | -38.213 | -30.0805 | -36.974 | -45.2714 | -63.6969 | -115.484 | -140.8027 | -167.5489 | 75.9571 | 75.1526 | 35.4833 | -1.2686 | -4.7219 | -9.6083 | -14.5174 | -8.4626 | -15.378 | -23.7036 | -41.9838 | -93.3151 | -118.4243 | -144.9404
|  | LW |  |  | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 117 | 117 | 117 | 117 | 117 | 117.0126 | 108.3773 | 108.3773 | 100.321 | 53.9635 | 17.2563 | -5.8871 | -9.0979 | -20.0206 | -25.7691 | -36.7736 | -47.8696 | -59.2127 | -65.2757 | -105.9746 | -197.5831 | -233.397 | -249.3776 | 77.9918 | 41.145 | 15.8084 | 12.592 | 1.6312 | -3.9757 | -15.0173 | -26.1505 | -37.5307 | -43.5471 | -83.8783 | -174.937 | -210.7055 | -226.83
|  | ST |  |  | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 117 | 117 | 107.6938 | 107.6938 | 52.2794 | 51.8314 | 13.1595 | -23.7193 | -26.0657 | -28.389 | -32.6596 | -23.7718 | -29.8318 | -37.4648 | -58.6676 | -100.8513 | -126.9422 | -150.0634 | 76.3086 | 75.859 | 37.0478 | 0.037264 | -2.325 | -4.6641 | -8.9494 | -2.1387 | -8.2194 | -15.8793 | -36.9954 | -78.7571 | -104.9298 | -127.839
|  | SP |  |  | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6254 | 107.6938 | 107.6938 | 53.187 | 52.572 | 52.449 | 52.2018 | 12.9601 | 11.5441 | 9.5558 | 7.5106 | 4.8095 | 1.2683 | 4.8069 | -14.2053 | -24.2955 | -32.4571 | 77.2176 | 76.6022 | 76.4788 | 76.2311 | 36.8483 | 35.4273 | 33.4319 | 31.3798 | 28.6695 | 25.1161 | 26.5444 | 7.4651 | -2.6752 | -10.8638
MANNINGTON GSP | CHRISTCHURCH BSP | MINIMUM HEADROOM | SZ1569893141 | YES | 140.5268 | 140.499 | 140.6268 | 139.4809 | 138.6828 | 137.769 | 136.5342 | 135.277 | 133.4855 | 132.8435 | 129.1479 | 121.8704 | 105.6649 | 98.9382 | 102.756 | 102.7055 | 102.8215 | 101.7814 | 101.659 | 101.2662 | 99.91 | 98.5534 | 95.8824 | 95.5496 | 92.7988 | 85.0333 | 66.4258 | 58.649 | 111.5273 | 111.0069 | 110.8761 | 109.3572 | 108.579 | 107.5804 | 106.2171 | 104.8287 | 103.3097 | 102.1278 | 97.9929 | 89.8882 | 71.6441 | 64.117
|  | CT |  |  | 140.6602 | 140.6435 | 140.6268 | 139.5142 | 139.6382 | 138.8405 | 138.0308 | 136.8575 | 135.6253 | 134.5504 | 131.1869 | 123.2524 | 111.1166 | 103.9568 | 102.8898 | 102.8507 | 102.8215 | 101.7814 | 102.4758 | 102.1476 | 101.8168 | 100.6833 | 99.426 | 98.3237 | 94.8739 | 86.6248 | 72.9888 | 64.7035 | 111.6694 | 111.1663 | 110.8761 | 109.3572 | 109.5545 | 108.6888 | 107.8099 | 106.5183 | 105.169 | 103.966 | 100.2002 | 91.503 | 77.9429 | 69.9252
|  | LW |  |  | 140.5268 | 140.499 | 141.1759 | 139.4809 | 138.6828 | 137.769 | 136.5342 | 135.277 | 133.9994 | 132.8435 | 129.1479 | 121.8704 | 105.6649 | 98.9382 | 102.756 | 102.7055 | 103.5827 | 101.8638 | 101.659 | 101.3318 | 100.3648 | 99.0794 | 97.7737 | 96.5886 | 92.7988 | 85.0333 | 66.4258 | 58.649 | 111.5273 | 111.0069 | 111.6769 | 109.4629 | 108.579 | 107.5804 | 106.2171 | 104.8287 | 103.42 | 102.1278 | 97.9929 | 89.8882 | 71.6441 | 64.117
|  | ST |  |  | 140.7268 | 140.7157 | 140.7046 | 140.0266 | 140.5149 | 139.8319 | 138.7916 | 137.7172 | 136.6654 | 135.3298 | 131.1902 | 125.0264 | 114.6935 | 109.6579 | 102.9588 | 102.9412 | 102.9081 | 102.2172 | 102.8999 | 102.5528 | 102.1858 | 101.5588 | 100.4888 | 99.133 | 94.9293 | 88.6479 | 77.4406 | 71.7324 | 111.7861 | 111.6354 | 111.1465 | 110.1882 | 110.5428 | 109.7649 | 108.6274 | 107.4517 | 106.3149 | 104.8848 | 100.4464 | 93.7343 | 82.2491 | 76.6384
|  | SP |  |  | 140.7935 | 140.788 | 140.7824 | 140.4434 | 140.4061 | 139.0622 | 137.7183 | 136.3742 | 133.4855 | 132.9097 | 131.9285 | 128.7257 | 126.6046 | 124.281 | 103.071 | 103.0231 | 103.0014 | 102.6596 | 102.6164 | 101.2662 | 99.91 | 98.5534 | 95.8824 | 95.5496 | 95.4571 | 92.5366 | 90.3616 | 87.9862 | 112.8429 | 111.9168 | 111.5594 | 111.16 | 110.9953 | 109.5155 | 107.9035 | 106.2887 | 103.3097 | 102.6988 | 101.7448 | 98.3168 | 95.9444 | 93.3794
IVER 132KV | CIPPENHAM | MINIMUM HEADROOM | SU9626679634 | NO | 127.9697 | 127.9588 | 127.9479 | 127.2605 | 127.1135 | 126.9397 | 126.8091 | 121.0226 | 121.0042 | 120.9788 | 120.8984 | 120.8439 | 120.7258 | 119.571 | 97.9999 | 97.9734 | 97.9416 | 97.2101 | 97.0079 | 96.7782 | 96.6174 | 90.9199 | 90.7659 | 90.6172 | 90.1126 | 89.0511 | 86.0137 | 83.8294 | 110.1415 | 110.1115 | 110.0752 | 109.3342 | 109.12 | 108.8781 | 108.7108 | 100.6813 | 100.6355 | 100.5853 | 100.4193 | 100.2473 | 99.8759 | 97.755
|  | CT |  |  | 128.0219 | 128.0154 | 128.0089 | 127.5869 | 127.5304 | 127.4501 | 127.4167 | 127.3357 | 127.3006 | 127.2635 | 127.1748 | 126.0963 | 123.8146 | 121.3729 | 98.0526 | 98.0306 | 98.0035 | 97.5384 | 97.4344 | 97.3068 | 97.2259 | 97.1212 | 97.0588 | 96.7123 | 94.586 | 91.2631 | 88.6271 | 85.8092 | 110.1942 | 110.1689 | 110.1374 | 109.6628 | 109.5486 | 109.4107 | 109.3194 | 109.2096 | 109.1412 | 109.0655 | 108.2221 | 104.9869 | 102.4288 | 99.695
|  | LW |  |  | 127.9697 | 127.9588 | 127.9479 | 127.2605 | 127.1135 | 126.9397 | 126.8091 | 126.6274 | 126.4495 | 126.3867 | 126.2123 | 124.1135 | 121.472 | 119.571 | 97.9999 | 97.9734 | 97.9416 | 97.2101 | 97.0079 | 96.7782 | 96.6174 | 96.4052 | 96.1925 | 95.4275 | 92.8038 | 89.0511 | 86.0137 | 83.8294 | 110.1415 | 110.1115 | 110.0752 | 109.3342 | 109.12 | 108.8781 | 108.7108 | 108.4919 | 108.2716 | 108.1649 | 106.4664 | 102.8248 | 99.8759 | 97.755
|  | ST |  |  | 128.0481 | 128.0437 | 128.0394 | 127.7502 | 127.7046 | 127.6825 | 127.613 | 127.5904 | 127.5667 | 127.5335 | 127.5026 | 127.4056 | 127.3337 | 126.977 | 98.0896 | 98.0779 | 98.0648 | 97.7606 | 97.6919 | 97.6423 | 97.5527 | 97.5083 | 97.4633 | 97.4047 | 97.2941 | 96.0878 | 94.2627 | 92.2173 | 110.2336 | 110.2204 | 110.2053 | 109.8979 | 109.8241 | 109.7686 | 109.6746 | 109.6255 | 109.5758 | 109.5116 | 109.3837 | 109.1629 | 107.9144 | 105.9327
|  | SP |  |  | 128.0742 | 128.072 | 128.0698 | 127.9371 | 127.9214 | 127.9058 | 127.8902 | 121.0226 | 121.0042 | 120.9788 | 120.8984 | 120.8439 | 120.7258 | 120.6131 | 98.1228 | 98.119 | 98.1152 | 97.9807 | 97.9569 | 97.9314 | 97.9081 | 90.9199 | 90.7659 | 90.6172 | 90.1126 | 89.4753 | 88.8532 | 88.3605 | 110.2683 | 110.2642 | 110.26 | 110.1252 | 110.0997 | 110.072 | 110.0469 | 100.6813 | 100.6355 | 100.5853 | 100.4193 | 100.2473 | 100.0275 | 99.8381
MINETY GSP | CIRENCESTER BSP | MINIMUM HEADROOM | SP0268900364 | YES | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | -108.8883 | -238.9661 | -295.2468 | -296.3619 | -305.5516 | -314.8429 | -323.9572 | -333.1534 | -341.7668 | -349.6765 | -378.875 | -425.2768 | -488.9673 | -496.1359 | -106.5133 | -234.7106 | -290.9557 | -292.0314 | -300.9052 | -309.8783 | -318.6827 | -327.5674 | -335.9028 | -343.5319 | -371.6469 | -417.477 | -480.9788 | -488.1261
|  | CT |  |  | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | -93.1465 | -160.3408 | -235.7033 | -236.791 | -241.3544 | -245.431 | -249.5376 | -254.1459 | -259.0807 | -265.0534 | -285.6522 | -313.813 | -350.056 | -367.5889 | -90.8789 | -157.9564 | -231.4132 | -232.4623 | -236.8668 | -240.8026 | -244.7678 | -249.217 | -253.9852 | -259.7442 | -279.6056 | -306.752 | -342.3001 | -359.7807
|  | LW |  |  | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | -108.8883 | -238.9661 | -295.2468 | -296.3619 | -305.5516 | -314.8429 | -323.9572 | -333.1534 | -341.7668 | -349.6765 | -378.875 | -425.2768 | -488.9673 | -496.1359 | -106.5133 | -234.7106 | -290.9557 | -292.0314 | -300.9052 | -309.8783 | -318.6827 | -327.5674 | -335.9028 | -343.5319 | -371.6469 | -417.477 | -480.9788 | -488.1261
|  | ST |  |  | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 23.5065 | 11.6843 | -179.6385 | -235.5697 | -239.5193 | -243.4971 | -247.1064 | -251.6013 | -256.3265 | -262.0737 | -282.0099 | -308.1029 | -343.1581 | -359.2532 | 25.7736 | 14.0645 | -175.3763 | -231.2847 | -235.0997 | -238.9421 | -242.4298 | -246.7715 | -251.3406 | -256.8853 | -276.118 | -301.2689 | -335.4245 | -351.4721
|  | SP |  |  | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 23.8279 | 23.7718 | 23.7138 | 12.1326 | -36.2875 | -37.4837 | -39.1429 | -40.7807 | -42.9454 | -45.8688 | -58.2112 | -74.1803 | -86.8169 | -93.6631 | 26.0799 | 26.0268 | 25.9717 | 14.5014 | -32.703 | -33.8696 | -35.4874 | -37.0845 | -39.1954 | -42.0468 | -54.0843 | -69.5329 | -81.7276 | -88.3402
EALING GSP | COPLEY DENE | MINIMUM HEADROOM | TQ1745580805 | NO | 60.3331 | 59.9275 | 59.9097 | 59.9051 | 59.8737 | 59.5783 | 57.6899 | 57.2793 | 56.8716 | 56.4382 | 55.0817 | 52.1876 | 48.8195 | 45.4477 | 46.3733 | 45.8022 | 45.7878 | 45.784 | 44.6375 | 42.3952 | 40.1762 | 39.6938 | 39.2147 | 38.7054 | 37.1114 | 33.7105 | 29.7527 | 25.7906 | 54.3636 | 53.8071 | 53.7868 | 53.0956 | 51.0228 | 48.9535 | 46.9058 | 46.4606 | 46.0185 | 45.5485 | 44.0493 | 40.6807 | 36.7603 | 32.8357
|  | CT |  |  | 60.3331 | 60.2711 | 60.1934 | 60.0313 | 59.8737 | 59.5783 | 57.6899 | 57.2793 | 56.8716 | 56.4382 | 55.0817 | 52.1876 | 48.8195 | 45.4477 | 46.3733 | 46.3234 | 46.2608 | 46.1303 | 44.6375 | 42.3952 | 40.1762 | 39.6938 | 39.2147 | 38.7054 | 37.1114 | 33.7105 | 29.7527 | 25.7906 | 54.3636 | 54.2928 | 54.2042 | 53.0956 | 51.0228 | 48.9535 | 46.9058 | 46.4606 | 46.0185 | 45.5485 | 44.0493 | 40.6807 | 36.7603 | 32.8357
|  | LW |  |  | 60.3435 | 60.2891 | 60.2214 | 60.0804 | 59.9431 | 59.8059 | 59.772 | 59.7381 | 59.4357 | 59.0024 | 57.646 | 54.7518 | 51.3835 | 48.0117 | 46.3818 | 46.3379 | 46.2834 | 46.1699 | 45.627 | 43.6722 | 43.1885 | 42.7066 | 42.2277 | 41.7186 | 40.1247 | 36.7237 | 32.7657 | 28.8035 | 54.3755 | 54.3134 | 54.2362 | 53.6796 | 51.9359 | 50.1319 | 49.6856 | 49.2408 | 48.7989 | 48.3291 | 46.8582 | 43.6653 | 39.7447 | 35.8201
|  | ST |  |  | 60.4038 | 60.3718 | 60.3516 | 60.3181 | 60.2768 | 60.2264 | 60.1809 | 60.1359 | 60.113 | 60.0886 | 60.0125 | 59.849 | 58.9817 | 56.8267 | 46.4303 | 46.4046 | 46.3883 | 46.3613 | 46.328 | 46.2874 | 46.2508 | 46.2145 | 46.1961 | 46.1764 | 46.1151 | 44.2864 | 41.6942 | 39.1619 | 54.4443 | 54.4078 | 54.3847 | 54.3465 | 54.2993 | 54.2419 | 54.19 | 54.1386 | 54.0244 | 53.7657 | 52.8475 | 50.6987 | 48.3066 | 45.9697
|  | SP |  |  | 60.4182 | 59.9275 | 59.9097 | 59.9051 | 59.8791 | 59.8492 | 59.8258 | 59.8025 | 59.7712 | 59.7359 | 60.1082 | 60.0038 | 59.8024 | 59.6185 | 46.4419 | 45.8022 | 45.7878 | 45.784 | 45.7619 | 45.7368 | 45.7168 | 45.6969 | 45.6698 | 45.6363 | 46.1648 | 46.0731 | 45.8869 | 45.7188 | 54.4607 | 53.8071 | 53.7868 | 53.7815 | 53.7527 | 53.7195 | 53.6936 | 53.6678 | 53.6334 | 53.5968 | 54.1269 | 54.0133 | 53.6417 | 52.6009
FAWLEY GSP | COWES & WOOTTON COMMON BSP | MINIMUM HEADROOM | SZ5053594332 | YES | 241.9915 | 241.806 | 208.4107 | 109.5287 | 79.8313 | 77.6097 | 70.3437 | 67.3596 | 63.9014 | 60.9406 | 51.7264 | 19.4331 | -7.6441 | -31.8285 | 162.4598 | 162.2343 | 122.2539 | 12.6036 | -22.358 | -24.8515 | -32.5346 | -35.927 | -39.8454 | -43.2778 | -53.7428 | -85.8484 | -115.6764 | -148.7601 | 192.4465 | 192.25 | 158.2716 | 54.3311 | 20.6211 | 18.1922 | 10.6083 | 7.313 | 3.504 | 0.18368 | -9.7303 | -38.5123 | -68.0988 | -105.3242
|  | CT |  |  | 243.9672 | 243.8008 | 243.3055 | 242.2237 | 241.3097 | 223.3723 | 222.2688 | 220.3709 | 214.0294 | 211.5763 | 203.6671 | 183.6735 | 170.5637 | 170.3553 | 164.4362 | 164.2302 | 163.6093 | 162.4118 | 161.2747 | 143.1298 | 141.8171 | 139.5026 | 132.6841 | 129.7978 | 120.5895 | 97.5016 | 82.7129 | 85.9637 | 194.4224 | 194.2451 | 193.7151 | 192.6014 | 191.6258 | 173.6312 | 172.4699 | 170.4571 | 163.9839 | 161.4977 | 153.5705 | 133.5342 | 120.9519 | 128.7684
|  | LW |  |  | 241.9915 | 241.806 | 208.4107 | 109.5287 | 79.8313 | 77.6097 | 70.3437 | 67.3596 | 63.9014 | 60.9406 | 51.7264 | 19.4331 | -7.6441 | -31.8285 | 162.4598 | 162.2343 | 122.2539 | 12.6036 | -22.358 | -24.8515 | -32.5346 | -35.927 | -39.8454 | -43.2778 | -53.7428 | -85.8484 | -115.6764 | -148.7601 | 192.4465 | 192.25 | 158.2716 | 54.3311 | 20.6211 | 18.1922 | 10.6083 | 7.313 | 3.504 | 0.18368 | -9.7303 | -38.5123 | -68.0988 | -105.3242
|  | ST |  |  | 242.1635 | 242.0337 | 241.6125 | 240.9171 | 240.1919 | 239.1826 | 237.9006 | 236.5429 | 234.7917 | 231.8049 | 222.0497 | 202.5804 | 191.7447 | 193.9593 | 162.6391 | 162.4772 | 161.9476 | 161.1804 | 160.2747 | 159.0754 | 157.5321 | 155.8937 | 153.7601 | 150.3295 | 139.4949 | 117.2949 | 105.1778 | 111.2351 | 192.6205 | 192.4819 | 192.0308 | 191.3156 | 190.5405 | 189.4788 | 188.1247 | 186.6895 | 184.8328 | 181.7304 | 171.9604 | 152.4533 | 142.1506 | 152.6783
|  | SP |  |  | 244.1875 | 242.2773 | 241.9808 | 241.7094 | 241.4974 | 238.2535 | 234.8844 | 231.5335 | 225.0806 | 223.8453 | 216.5714 | 210.1207 | 205.9323 | 213.6248 | 164.6918 | 162.773 | 162.3998 | 162.1126 | 161.8498 | 158.5491 | 155.0904 | 151.6546 | 145.0926 | 143.6973 | 134.5209 | 127.2622 | 122.7851 | 135.2402 | 194.6525 | 192.7399 | 192.4222 | 192.1465 | 191.9205 | 188.6609 | 185.267 | 181.8927 | 175.4097 | 174.1303 | 164.4493 | 157.7756 | 154.0075 | 170.0259
COWLEY GSP | COWLEY LOCAL (2 X 45) | MINIMUM HEADROOM | SP5617503067 | NO | 122.6563 | 122.6584 | 122.6328 | 122.4573 | 122.3041 | 122.1059 | 121.8336 | 127.5794 | 125.9025 | 124.2197 | 117.9312 | 108.5431 | 102.9669 | 101.4439 | 78.7009 | 78.6994 | 78.6699 | 78.4873 | 78.3108 | 78.0816 | 77.766 | 82.7969 | 80.8561 | 78.8996 | 71.5849 | 60.6783 | 54.2095 | 52.4603 | 97.8763 | 97.8755 | 97.8466 | 97.6653 | 97.4929 | 97.2691 | 96.9612 | 102.118 | 100.2237 | 98.3154 | 91.1814 | 80.5423 | 74.2307 | 72.5213
|  | CT |  |  | 133.5321 | 133.4243 | 133.3203 | 132.7088 | 132.0776 | 131.374 | 130.616 | 129.6494 | 128.4329 | 127.0146 | 121.8893 | 114.4995 | 110.6242 | 107.3594 | 89.5692 | 89.4445 | 89.3243 | 88.678 | 87.9487 | 87.1353 | 86.2586 | 85.1389 | 83.7285 | 82.0784 | 76.1131 | 67.5969 | 63.1193 | 59.3378 | 108.7459 | 108.6242 | 108.5068 | 107.8667 | 107.1547 | 106.3606 | 105.5048 | 104.4121 | 103.0359 | 101.4265 | 95.6092 | 87.2914 | 82.9199 | 79.2294
|  | LW |  |  | 133.4955 | 133.3943 | 133.3002 | 132.4546 | 131.4275 | 130.2744 | 128.9671 | 127.5794 | 125.9025 | 124.2197 | 117.9312 | 108.5431 | 102.9669 | 101.4439 | 89.535 | 89.4188 | 89.3109 | 88.4356 | 87.2485 | 85.9152 | 84.4026 | 82.7969 | 80.8561 | 78.8996 | 71.5849 | 60.6783 | 54.2095 | 52.4603 | 108.7113 | 108.5977 | 108.4923 | 107.6222 | 106.4633 | 105.1617 | 103.6853 | 102.118 | 100.2237 | 98.3154 | 91.1814 | 80.5423 | 74.2307 | 72.5213
|  | ST |  |  | 122.6563 | 133.5423 | 133.4934 | 133.1373 | 132.6772 | 132.1444 | 131.4971 | 130.7193 | 129.71 | 128.5166 | 124.1536 | 118.3571 | 114.975 | 112.089 | 78.7009 | 89.5774 | 89.5211 | 89.1504 | 88.6211 | 88.0071 | 87.2598 | 86.3605 | 85.1935 | 83.806 | 78.7309 | 71.9886 | 68.0742 | 64.7254 | 97.8763 | 108.7545 | 108.6994 | 108.3314 | 107.8142 | 107.2146 | 106.4848 | 105.607 | 104.4678 | 103.1144 | 98.1648 | 91.589 | 87.7684 | 84.5011
|  | SP |  |  | 122.6972 | 122.6584 | 122.6328 | 122.4573 | 122.3041 | 122.1059 | 121.8336 | 132.4959 | 132.15 | 131.7306 | 130.0098 | 127.6324 | 126.3696 | 125.673 | 78.7443 | 78.6994 | 78.6699 | 78.4873 | 78.3108 | 78.0816 | 77.766 | 88.383 | 87.9816 | 87.4935 | 85.4898 | 82.7222 | 81.2555 | 80.4507 | 97.9192 | 97.8755 | 97.8466 | 97.6653 | 97.4929 | 97.2691 | 96.9612 | 107.5861 | 107.1945 | 106.7185 | 104.7646 | 102.0658 | 100.635 | 99.8493
COWLEY GSP | COWLEY LOCAL (2 X 90) | MINIMUM HEADROOM | SP5617503067 | NO | 142.2905 | 142.4756 | 142.4485 | 139.8426 | 139.6003 | 139.3527 | 139.0989 | 138.8466 | 136.9927 | 134.7264 | 126.7721 | 120.7088 | 111.4909 | 95.3176 | 108.1086 | 108.2272 | 108.1311 | 105.5988 | 105.1985 | 104.7868 | 104.2289 | 102.4787 | 99.7838 | 97.2054 | 88.15 | 81.3826 | 71.8072 | 50.9848 | 116.9158 | 117.0714 | 116.9954 | 114.4314 | 114.077 | 113.7129 | 111.5919 | 109.3107 | 106.6305 | 104.0672 | 95.0651 | 88.3339 | 78.8099 | 57.5356
|  | CT |  |  | 142.5025 | 142.4756 | 142.4485 | 140.8522 | 140.6278 | 140.4009 | 140.4777 | 140.2425 | 139.9484 | 138.7403 | 132.2228 | 120.7512 | 112.2376 | 110.4198 | 108.3183 | 108.2272 | 108.1311 | 106.4519 | 106.1105 | 105.7665 | 105.8638 | 105.3744 | 103.8006 | 101.5954 | 94.1738 | 81.3826 | 71.8072 | 71.9206 | 117.1278 | 117.0714 | 116.9954 | 115.3403 | 115.0328 | 114.7227 | 114.4663 | 112.7449 | 110.6313 | 108.439 | 101.0612 | 88.3339 | 78.8099 | 80.7841
|  | LW |  |  | 142.2905 | 142.5508 | 142.5045 | 139.8426 | 139.6003 | 139.3527 | 139.0989 | 138.8466 | 136.9927 | 134.7264 | 126.7721 | 120.7088 | 111.4909 | 95.3176 | 108.1086 | 108.4513 | 108.3384 | 105.5988 | 105.1985 | 104.7868 | 104.2289 | 102.4787 | 99.7838 | 97.2054 | 88.15 | 83.3866 | 72.9081 | 50.9848 | 116.9158 | 117.2421 | 117.1485 | 114.4314 | 114.077 | 113.7129 | 111.5919 | 109.3107 | 106.6305 | 104.0672 | 95.0651 | 92.1931 | 81.7757 | 57.5356
|  | ST |  |  | 142.6075 | 142.59 | 142.5726 | 141.5092 | 141.4058 | 141.3013 | 141.5021 | 141.395 | 141.2747 | 141.2275 | 139.0904 | 131.3808 | 125.5378 | 125.9854 | 108.4404 | 108.4157 | 108.3612 | 107.2768 | 107.1179 | 106.9526 | 107.2104 | 107.0097 | 106.769 | 106.5779 | 101.8226 | 93.0352 | 86.3896 | 89.0329 | 117.2328 | 117.2153 | 117.1947 | 116.1165 | 115.9736 | 115.826 | 116.057 | 115.8834 | 115.6776 | 114.7836 | 108.6722 | 99.9369 | 93.3302 | 97.8215
|  | SP |  |  | 142.6989 | 142.604 | 142.5952 | 142.0635 | 142.0196 | 141.9756 | 141.9316 | 141.8875 | 141.8431 | 141.8234 | 142.0687 | 141.9734 | 141.5073 | 148.1573 | 108.5306 | 108.3907 | 108.3458 | 107.8062 | 107.7396 | 107.6686 | 107.5884 | 107.5102 | 107.4215 | 107.3508 | 107.5445 | 106.9859 | 104.403 | 114.2996 | 117.3214 | 117.2085 | 117.1837 | 116.6464 | 116.5864 | 116.5232 | 116.4535 | 116.3852 | 116.3094 | 116.2534 | 116.4513 | 114.1532 | 111.195 | 122.9117
BRAMLEY (FLEE) | COXMOOR WOOD BSP | MINIMUM HEADROOM | SU7827550779 | YES | 142.5587 | 31.3381 | -22.7544 | -24.2037 | -33.1725 | -42.1922 | -50.5894 | -59.0552 | -65.2238 | -71.1554 | -92.9243 | -121.9793 | -144.6416 | -150.9023 | 108.8635 | -13.6826 | -74.2458 | -75.9966 | -86.8207 | -97.6986 | -107.8151 | -118.009 | -125.3955 | -132.5565 | -158.8312 | -193.8654 | -221.0828 | -228.6315 | 128.7098 | 14.8056 | -45.2276 | -46.9731 | -57.7645 | -68.6097 | -78.696 | -88.8595 | -96.2245 | -103.3639 | -129.5593 | -164.4883 | -191.6255 | -199.1515
|  | CT |  |  | 142.6556 | 37.3908 | 7.5058 | -24.1451 | -28.7945 | -32.9224 | -37.0556 | -41.2501 | -44.8378 | -49.3455 | -64.7964 | -83.1032 | -98.1861 | -113.3548 | 108.9503 | 3.6393 | -37.6577 | -75.9297 | -81.5493 | -86.5364 | -91.5282 | -96.5917 | -100.9143 | -106.3616 | -125.0303 | -147.0709 | -165.196 | -183.4844 | 128.8213 | 23.5564 | -9.1453 | -46.9064 | -52.5088 | -57.4809 | -62.4575 | -67.5057 | -71.8154 | -77.2462 | -95.8582 | -117.8332 | -135.9047 | -154.1382
|  | LW |  |  | 142.6496 | 31.3381 | -22.7544 | -24.2037 | -33.1725 | -42.1922 | -50.5894 | -59.0552 | -65.2238 | -71.1554 | -92.9243 | -121.9793 | -144.6416 | -150.9023 | 108.9437 | -13.6826 | -74.2458 | -75.9966 | -86.8207 | -97.6986 | -107.8151 | -118.009 | -125.3955 | -132.5565 | -158.8312 | -193.8654 | -221.0828 | -228.6315 | 128.8153 | 14.8056 | -45.2276 | -46.9731 | -57.7645 | -68.6097 | -78.696 | -88.8595 | -96.2245 | -103.3639 | -129.5593 | -164.4883 | -191.6255 | -199.1515
|  | ST |  |  | 142.6565 | 142.6565 | 113.3844 | 82.4245 | 78.6335 | 74.8081 | 71.5215 | 67.3766 | 64.028 | 59.7598 | 45.0035 | 28.2582 | 14.6262 | 0.93772 | 108.9645 | 108.9381 | 68.3488 | 30.9118 | 26.3312 | 21.7106 | 17.7427 | 12.7391 | 8.7051 | 3.5501 | -14.2664 | -34.4838 | -50.8619 | -67.3772 | 128.8222 | 128.8221 | 96.8395 | 59.9304 | 55.3637 | 50.757 | 46.8012 | 41.8126 | 37.7907 | 32.6513 | 14.8887 | -5.2676 | -21.5974 | -38.0629
|  | SP |  |  | 142.5587 | 142.5586 | 119.4006 | 119.4004 | 119.3946 | 119.3885 | 119.3821 | 119.3751 | 119.3636 | 119.4265 | 106.826 | 92.1566 | 80.5674 | 74.3151 | 108.8635 | 108.854 | 85.6822 | 85.6774 | 85.6028 | 85.518 | 84.9664 | 83.1518 | 80.7248 | 77.639 | 59.161 | 41.4411 | 27.5021 | 20.0115 | 128.7098 | 128.7097 | 105.5517 | 105.5515 | 105.5457 | 105.5397 | 105.5332 | 105.4509 | 105.3026 | 105.2054 | 87.4979 | 69.9953 | 56.0976 | 48.6288
IVER 132KV | DENHAM | MINIMUM HEADROOM | TQ0173587553 | NO | 132.8275 | 110.6669 | 91.7973 | 90.9525 | 89.133 | 87.3067 | 85.9206 | 84.5239 | 82.8151 | 81.1079 | 74.9263 | 66.335 | 60.4847 | 57.6414 | 102.3534 | 80.1756 | 46.5663 | 45.571 | 43.4284 | 41.2785 | 39.6479 | 38.0057 | 35.999 | 33.9891 | 26.7126 | 16.6055 | 9.7403 | 6.3927 | 120.6164 | 98.4557 | 65.9169 | 64.9247 | 62.7885 | 60.6451 | 59.0194 | 57.3822 | 55.3815 | 53.3777 | 46.1233 | 36.0468 | 29.202 | 25.8645
|  | CT |  |  | 132.8275 | 132.8275 | 132.8275 | 113.239 | 111.9933 | 110.8155 | 109.626 | 108.7432 | 107.5751 | 106.2165 | 101.5992 | 95.5896 | 90.8934 | 85.5376 | 102.3549 | 102.3389 | 102.3178 | 67.88 | 66.4207 | 65.0416 | 63.6492 | 62.6185 | 61.2577 | 59.6592 | 54.2271 | 47.1898 | 41.7049 | 35.4082 | 120.6164 | 120.6164 | 120.6164 | 87.2332 | 85.7781 | 84.4031 | 83.0148 | 81.9871 | 80.6301 | 79.0365 | 73.6208 | 66.6042 | 61.1352 | 54.8575
|  | LW |  |  | 132.8275 | 110.6669 | 91.7973 | 90.9525 | 89.133 | 87.3067 | 85.9206 | 84.5239 | 82.8151 | 81.1079 | 74.9263 | 66.335 | 60.4847 | 57.6414 | 102.3534 | 80.1756 | 46.5663 | 45.571 | 43.4284 | 41.2785 | 39.6479 | 38.0057 | 35.999 | 33.9891 | 26.7126 | 16.6055 | 9.7403 | 6.3927 | 120.6164 | 98.4557 | 65.9169 | 64.9247 | 62.7885 | 60.6451 | 59.0194 | 57.3822 | 55.3815 | 53.3777 | 46.1233 | 36.0468 | 29.202 | 25.8645
|  | ST |  |  | 132.8275 | 132.8275 | 132.8275 | 114.1332 | 113.2584 | 112.3121 | 111.5649 | 110.7021 | 109.6107 | 108.3471 | 104.0179 | 98.8202 | 94.7794 | 90.1581 | 102.3634 | 102.3539 | 102.3427 | 68.9334 | 67.9158 | 66.8143 | 65.9479 | 64.9459 | 63.6829 | 62.2023 | 57.1292 | 51.0298 | 46.3402 | 40.9179 | 120.6164 | 120.6164 | 120.6164 | 88.2833 | 87.2687 | 86.1703 | 85.3063 | 84.3071 | 83.0476 | 81.5713 | 76.5132 | 70.4319 | 65.7554 | 60.3493
|  | SP |  |  | 132.8275 | 132.8275 | 132.8275 | 132.8275 | 132.8196 | 132.8118 | 132.8039 | 132.7958 | 132.7831 | 132.7474 | 132.6305 | 132.5724 | 132.3794 | 132.2139 | 102.3732 | 102.3715 | 102.3697 | 102.368 | 102.3473 | 102.3245 | 102.3013 | 102.278 | 102.2453 | 102.1866 | 101.9773 | 101.792 | 101.4956 | 100.5526 | 120.6164 | 120.6164 | 120.6164 | 120.6164 | 120.6084 | 120.6006 | 120.5927 | 120.5846 | 120.5719 | 120.5362 | 120.3346 | 120.1257 | 119.8102 | 119.5664
COWLEY GSP | DRAYTON BSP | MINIMUM HEADROOM | SU4653592295 | YES | 208.4032 | 208.0709 | 206.6521 | 201.0405 | 202.1108 | 200.3833 | 198.5737 | 196.7603 | 193.6283 | 191.9763 | 186.1749 | 126.8403 | 108.3213 | 102.5885 | 113.3341 | 112.9356 | 111.2232 | 102.7224 | 104.1101 | 102.2896 | 100.3728 | 98.4514 | 95.1872 | 93.9931 | 88.7654 | 11.4844 | -10.0411 | -16.65 | 148.0809 | 147.7009 | 146.0729 | 136.2414 | 137.5172 | 135.7194 | 133.8288 | 131.9338 | 128.7018 | 127.5255 | 124.4491 | 42.8459 | 21.5917 | 15.0618
|  | CT |  |  | 218.5038 | 208.5175 | 209.0046 | 207.0964 | 204.9415 | 202.5699 | 200.1143 | 197.7122 | 194.8454 | 191.9763 | 186.1749 | 189.659 | 176.712 | 174.9596 | 123.897 | 113.6626 | 114.3478 | 112.1768 | 109.671 | 106.9278 | 104.0866 | 101.3093 | 97.9971 | 94.6503 | 88.7654 | 103.8998 | 88.9476 | 85.8438 | 158.4814 | 148.3076 | 148.9143 | 146.8075 | 144.3874 | 141.6854 | 138.879 | 136.1356 | 132.8635 | 129.5598 | 124.4491 | 146.9934 | 132.0369 | 128.93
|  | LW |  |  | 220.3156 | 218.9065 | 218.0935 | 216.0019 | 213.3581 | 210.3999 | 207.5216 | 204.5547 | 201.1144 | 197.8432 | 217.2215 | 126.8403 | 108.3213 | 102.5885 | 127.3278 | 125.6754 | 124.7227 | 122.3816 | 119.2905 | 115.8503 | 112.5047 | 109.0563 | 105.0562 | 101.2388 | 134.8128 | 11.4844 | -10.0411 | -16.65 | 162.3916 | 160.7986 | 159.8801 | 157.5999 | 154.6181 | 151.276 | 147.9726 | 144.5676 | 140.6179 | 136.8498 | 177.703 | 42.8459 | 21.5917 | 15.0618
|  | ST |  |  | 210.2396 | 209.7769 | 209.8118 | 208.7896 | 207.3513 | 205.5806 | 203.8724 | 201.986 | 199.737 | 196.98 | 191.1638 | 166.9437 | 153.2956 | 153.1209 | 115.6789 | 115.1363 | 115.2903 | 114.1363 | 112.4666 | 110.424 | 108.4552 | 106.2778 | 103.6838 | 100.542 | 94.8603 | 66.7479 | 50.1168 | 48.8562 | 150.252 | 149.729 | 149.8237 | 148.7019 | 147.0888 | 145.1126 | 143.1925 | 141.0414 | 138.4785 | 135.3714 | 130.4442 | 102.683 | 85.5544 | 84.3918
|  | SP |  |  | 208.4032 | 208.0709 | 206.6521 | 201.0405 | 202.1108 | 200.3833 | 198.5737 | 196.7603 | 193.6283 | 192.5726 | 191.21 | 187.1255 | 183.5813 | 181.4766 | 113.3341 | 112.9356 | 111.2232 | 102.7224 | 104.1101 | 102.2896 | 100.3728 | 98.4514 | 95.1872 | 93.9931 | 92.6977 | 88.1936 | 84.1988 | 81.7985 | 148.0809 | 147.7009 | 146.0729 | 136.2414 | 137.5172 | 135.7194 | 133.8288 | 131.9338 | 128.7018 | 127.5255 | 126.048 | 121.5231 | 117.5689 | 115.1953
EALING GSP | EALING | MINIMUM HEADROOM | TQ1844579506 | NO | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5191 | 51.4856 | 51.4507 | 51.4145 | 51.1279 | 50.5656 | 48.8821 | 45.2602 | 41.0411 | 37.1515 | 48.1919 | 47.9773 | 47.6741 | 46.8254 | 45.1536 | 43.4381 | 41.7495 | 40.9642 | 40.2735 | 39.6127 | 37.6345 | 33.3784 | 28.4206 | 23.9941 | 49.3003 | 49.2616 | 49.2069 | 49.1064 | 47.7064 | 46.1693 | 44.4601 | 43.6937 | 43.0254 | 42.386 | 40.4473 | 36.1729 | 31.1939 | 26.7581
|  | CT |  |  | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.1279 | 50.5656 | 48.8821 | 45.2602 | 41.0411 | 37.1515 | 48.1919 | 47.9773 | 47.6741 | 46.8254 | 45.1536 | 43.4381 | 41.7495 | 40.9642 | 40.2735 | 39.6127 | 37.6345 | 33.3784 | 28.4206 | 23.9941 | 49.3003 | 49.2616 | 49.2069 | 49.1064 | 47.7064 | 46.1693 | 44.4601 | 43.6937 | 43.0254 | 42.386 | 40.4473 | 36.1729 | 31.1939 | 26.7581
|  | LW |  |  | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5191 | 51.4856 | 51.4507 | 51.4145 | 51.3595 | 51.3518 | 50.2972 | 46.9265 | 42.6091 | 38.4195 | 48.2156 | 48.035 | 47.7636 | 47.2732 | 45.7944 | 44.241 | 43.4917 | 42.6981 | 41.983 | 41.3411 | 39.3368 | 35.5277 | 30.4716 | 25.5494 | 49.3063 | 49.272 | 49.2231 | 49.1346 | 48.2748 | 46.8848 | 46.2123 | 45.422 | 44.6988 | 44.0519 | 42.1118 | 38.3421 | 33.2649 | 28.3216
|  | ST |  |  | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 49.5339 | 47.1604 | 48.2982 | 48.2357 | 48.1294 | 47.9546 | 47.7442 | 47.4875 | 47.2747 | 46.6344 | 46.1873 | 45.7556 | 44.4602 | 41.655 | 38.4003 | 35.7555 | 49.3286 | 49.3118 | 49.289 | 49.2575 | 49.2196 | 49.1733 | 49.1349 | 49.028 | 48.629 | 48.2436 | 47.0876 | 44.3644 | 41.213 | 38.5698
|  | SP |  |  | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.5515 | 51.7172 | 48.3411 | 48.3171 | 48.2856 | 48.2593 | 48.1964 | 48.0863 | 48.0023 | 47.916 | 47.8227 | 47.7675 | 47.6019 | 47.1633 | 45.7855 | 44.8761 | 49.3401 | 49.3337 | 49.3252 | 49.3181 | 49.3012 | 49.2813 | 49.2661 | 49.2505 | 49.2337 | 49.2238 | 49.1939 | 49.1265 | 48.2703 | 47.5317
EALING GSP | EALING (D) | MINIMUM HEADROOM | TQ1844579505 | NO | 122.1249 | 122.1249 | 122.1249 | 122.0698 | 121.5649 | 121.0282 | 120.5332 | 120.02 | 119.2625 | 119.1261 | 118.6659 | 117.5324 | 111.9495 | 106.6001 | 105.0781 | 105.0266 | 104.9889 | 104.9161 | 104.4365 | 103.931 | 103.4476 | 102.9465 | 102.2004 | 101.6558 | 99.7117 | 96.0231 | 89.8874 | 83.4239 | 105.8792 | 105.81 | 105.7594 | 105.6616 | 105.1634 | 104.635 | 104.1373 | 103.2453 | 102.0497 | 101.4712 | 99.5825 | 95.9629 | 89.7656 | 83.1663
|  | CT |  |  | 122.1249 | 122.1249 | 122.1249 | 122.0698 | 121.934 | 121.7966 | 121.6588 | 121.5863 | 121.4972 | 121.4541 | 121.3149 | 118.9746 | 114.3879 | 110.3642 | 105.0781 | 105.0266 | 104.9889 | 104.9161 | 104.8133 | 104.7093 | 104.327 | 103.7737 | 103.2295 | 102.727 | 101.1039 | 96.9445 | 91.8051 | 87.5972 | 105.8792 | 105.81 | 105.7594 | 105.6616 | 105.5345 | 105.406 | 104.1373 | 103.6019 | 103.0747 | 102.5893 | 101.0217 | 96.8658 | 91.6647 | 87.2542
|  | LW |  |  | 122.1249 | 122.1249 | 122.1249 | 122.087 | 121.5649 | 121.0282 | 120.5332 | 120.02 | 119.2625 | 119.1261 | 118.6659 | 117.5324 | 111.9495 | 106.6001 | 105.0806 | 105.0309 | 104.9956 | 104.9278 | 104.4365 | 103.931 | 103.4476 | 102.9465 | 102.2004 | 101.6558 | 99.7117 | 96.0231 | 89.8874 | 83.4239 | 105.8826 | 105.8158 | 105.7684 | 105.6773 | 105.1634 | 104.635 | 104.143 | 103.2453 | 102.0497 | 101.4712 | 99.5825 | 95.9629 | 89.7656 | 83.1663
|  | ST |  |  | 122.1249 | 122.1249 | 122.1249 | 122.1249 | 121.9276 | 121.7271 | 121.4987 | 121.2474 | 120.8959 | 120.7601 | 120.3251 | 119.8317 | 118.6988 | 116.9203 | 105.0987 | 105.0855 | 105.0477 | 105.0249 | 104.8002 | 104.5663 | 104.335 | 104.0963 | 103.7526 | 103.6247 | 103.2154 | 102.0952 | 97.8799 | 95.2827 | 105.9069 | 105.8892 | 105.8384 | 105.8078 | 105.5736 | 105.3284 | 105.0879 | 104.8399 | 104.4905 | 104.3567 | 103.9285 | 101.9205 | 97.8203 | 95.2081
|  | SP |  |  | 122.1249 | 122.1249 | 122.1249 | 122.1249 | 122.1249 | 122.1249 | 122.1249 | 122.1249 | 122.1249 | 122.1249 | 122.1249 | 122.09 | 121.9771 | 122.1924 | 105.1085 | 105.1038 | 105.0768 | 105.073 | 105.0618 | 105.0486 | 105.0385 | 105.0282 | 105.016 | 105.0094 | 104.988 | 104.9298 | 104.8528 | 105.1163 | 105.92 | 105.9138 | 105.8775 | 105.8724 | 105.8574 | 105.8396 | 105.826 | 105.8122 | 105.7958 | 105.787 | 105.7582 | 105.6801 | 105.5766 | 105.9704
LALEHAM | EAST BEDFONT 11 | MINIMUM HEADROOM | TQ0840573836 | NO | 34.3356 | 34.3356 | 34.3356 | 34.3356 | 34.0813 | 33.8153 | 33.545 | 33.2627 | 32.8274 | 32.7723 | 32.5951 | 30.0416 | 26.23 | 23.0975 | 26.2639 | 26.2616 | 26.2537 | 26.2416 | 25.9666 | 25.6811 | 25.3879 | 25.0576 | 24.5821 | 24.2522 | 22.7081 | 18.9802 | 14.6817 | 11.0336 | 29.1008 | 29.1008 | 29.1008 | 29.1008 | 28.848 | 28.582 | 28.3117 | 28.0294 | 27.5941 | 27.539 | 26.063 | 22.3309 | 17.9919 | 14.337
|  | CT |  |  | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 34.0813 | 33.8153 | 33.545 | 33.2627 | 32.8274 | 32.7723 | 32.5951 | 30.0416 | 26.23 | 23.0975 | 26.2726 | 26.2616 | 26.2537 | 26.2416 | 25.9666 | 25.6811 | 25.3879 | 25.0576 | 24.5821 | 24.2522 | 22.7081 | 18.9802 | 14.6817 | 11.0336 | 29.1095 | 29.1095 | 29.1095 | 29.1095 | 28.848 | 28.582 | 28.3117 | 28.0294 | 27.5941 | 27.539 | 26.063 | 22.3309 | 17.9919 | 14.337
|  | LW |  |  | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 32.3824 | 29.4549 | 26.5539 | 26.2726 | 26.2616 | 26.2537 | 26.2416 | 26.2281 | 26.2086 | 26.1646 | 26.1165 | 26.0228 | 25.5593 | 24.1922 | 21.2834 | 17.8691 | 14.4493 | 29.1095 | 29.1095 | 29.1095 | 29.1095 | 29.1095 | 29.1095 | 29.1095 | 29.1095 | 29.1095 | 28.898 | 27.551 | 24.6309 | 21.1761 | 17.7526
|  | ST |  |  | 34.3428 | 34.3428 | 34.3428 | 34.3428 | 34.3249 | 34.3068 | 34.2883 | 34.2691 | 34.2395 | 34.2295 | 34.1975 | 34.1707 | 32.3189 | 30.4411 | 26.2735 | 26.2715 | 26.2581 | 26.2509 | 26.2244 | 26.1961 | 26.1567 | 26.1104 | 26.0535 | 26.018 | 25.6227 | 23.5902 | 21.2533 | 19.0677 | 29.1095 | 29.1095 | 29.1095 | 29.1095 | 29.0916 | 29.0735 | 29.055 | 29.0358 | 29.0062 | 28.9962 | 28.9584 | 26.9553 | 24.6036 | 22.3924
|  | SP |  |  | 34.3356 | 34.3356 | 34.3356 | 34.3356 | 34.3284 | 34.298 | 34.2676 | 34.2366 | 34.1882 | 34.0536 | 33.6268 | 33.4235 | 32.7833 | 32.2479 | 26.2639 | 26.263 | 26.2601 | 26.2567 | 26.2456 | 26.2108 | 26.1743 | 26.1367 | 26.0827 | 25.9411 | 25.488 | 25.2192 | 24.2857 | 22.7289 | 29.1008 | 29.1008 | 29.1008 | 29.1008 | 29.0936 | 29.0632 | 29.0327 | 29.0017 | 28.9534 | 28.8188 | 28.392 | 28.1886 | 27.5485 | 26.0758
LALEHAM | EAST BEDFONT A | MINIMUM HEADROOM | TQ0840573835 | NO | 105.8091 | 105.8091 | 105.8091 | 105.8091 | 117.6924 | 117.572 | 117.4461 | 117.3157 | 117.1177 | 117.0902 | 116.9962 | 116.8406 | 115.896 | 111.4452 | 83.6646 | 83.6506 | 83.6391 | 83.6174 | 113.4775 | 113.3345 | 113.1735 | 113.0042 | 112.7711 | 112.7101 | 112.51 | 108.8068 | 103.1147 | 97.7552 | 102.7924 | 102.7924 | 102.7924 | 102.7924 | 114.6756 | 114.5552 | 114.4294 | 114.299 | 114.1009 | 114.0735 | 113.9352 | 111.2018 | 105.5629 | 100.2016
|  | CT |  |  | 105.8091 | 105.8091 | 105.8091 | 105.8091 | 117.7983 | 117.7872 | 117.776 | 117.7643 | 117.7462 | 117.7439 | 117.7366 | 117.7026 | 117.2991 | 112.8591 | 83.6649 | 83.6512 | 83.64 | 83.6191 | 113.5856 | 113.5527 | 113.5186 | 113.468 | 113.4149 | 113.379 | 113.2656 | 109.9383 | 104.5639 | 99.2152 | 102.7924 | 102.7924 | 102.7924 | 102.7924 | 114.7815 | 114.7705 | 114.7592 | 114.7475 | 114.7294 | 114.7272 | 114.6909 | 112.2696 | 107.0122 | 101.6618
|  | LW |  |  | 105.8091 | 105.8091 | 105.8091 | 105.8091 | 117.6924 | 117.572 | 117.4461 | 117.3157 | 117.1177 | 117.0902 | 116.9962 | 116.8406 | 115.896 | 111.4452 | 83.6646 | 83.6506 | 83.6391 | 83.6174 | 113.4775 | 113.3345 | 113.1735 | 113.0042 | 112.7711 | 112.7101 | 112.51 | 108.8068 | 103.1147 | 97.7552 | 102.7924 | 102.7924 | 102.7924 | 102.7924 | 114.6756 | 114.5552 | 114.4294 | 114.299 | 114.1009 | 114.0735 | 113.9352 | 111.2018 | 105.5629 | 100.2016
|  | ST |  |  | 105.8091 | 105.8091 | 105.8091 | 105.8091 | 117.7213 | 117.632 | 117.5409 | 117.4468 | 117.3012 | 117.2519 | 117.0942 | 116.9675 | 116.554 | 116.1916 | 83.667 | 83.6631 | 83.6481 | 83.6363 | 113.5344 | 113.4304 | 113.3173 | 113.1987 | 113.0294 | 112.957 | 112.726 | 111.9521 | 108.4188 | 104.9048 | 102.7924 | 102.7924 | 102.7924 | 102.7924 | 114.7045 | 114.6153 | 114.5242 | 114.4301 | 114.2845 | 114.2351 | 114.0774 | 113.8536 | 110.8395 | 107.3537
|  | SP |  |  | 105.8091 | 105.8091 | 105.8091 | 105.8091 | 117.8091 | 117.8091 | 117.8091 | 117.8091 | 117.8091 | 117.8091 | 117.8091 | 117.8091 | 117.8091 | 117.8091 | 83.6695 | 83.6679 | 83.6646 | 83.6599 | 113.6536 | 113.6477 | 113.6396 | 113.6308 | 113.6219 | 113.6129 | 113.5843 | 113.5138 | 113.4217 | 113.3247 | 102.7924 | 102.7924 | 102.7924 | 102.7924 | 114.7924 | 114.7924 | 114.7924 | 114.7924 | 114.7924 | 114.7924 | 114.7924 | 114.7924 | 114.7924 | 114.7499
LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | MINIMUM HEADROOM | SU5644404017 | NO | 124.7251 | 71.6122 | 69.4982 | 52.84 | 52.2402 | 51.4072 | 50.5504 | 49.4018 | 48.1653 | 46.9365 | 42.7099 | 24.4434 | 16.5573 | 10.2767 | 79.0942 | 25.7801 | 21.627 | 4.7808 | 3.9638 | 2.9065 | 1.816 | 0.31515 | -1.3005 | -2.953 | -8.3428 | -32.028 | -42.1507 | -50.3035 | 87.5472 | 34.1586 | 30.0453 | 13.1296 | 12.2321 | 11.0918 | 9.9148 | 8.2835 | 6.5275 | 4.7181 | -1.2022 | -29.6768 | -41.2531 | -50.6954
|  | CT |  |  | 124.7914 | 71.6919 | 69.4982 | 52.84 | 52.2402 | 51.4072 | 50.5504 | 49.4018 | 48.1653 | 46.9365 | 42.9427 | 30.1412 | 22.7895 | 16.2736 | 79.1656 | 25.8687 | 21.627 | 4.7808 | 3.9638 | 2.9065 | 1.816 | 0.31515 | -1.3005 | -2.953 | -8.3428 | -25.4667 | -34.8929 | -43.5924 | 87.6204 | 34.2505 | 30.0453 | 13.1296 | 12.2321 | 11.0918 | 9.9148 | 8.2835 | 6.5275 | 4.7181 | -1.2022 | -21.1352 | -31.9512 | -42.0699
|  | LW |  |  | 124.7251 | 71.6122 | 71.3164 | 54.3599 | 53.5899 | 52.5347 | 51.2051 | 49.8721 | 48.4334 | 47.0919 | 42.7099 | 24.4434 | 16.5573 | 10.2767 | 79.0942 | 25.7801 | 25.3679 | 8.2131 | 7.1699 | 5.8287 | 4.1021 | 2.3721 | 0.506 | -1.288 | -7.1363 | -32.028 | -42.1507 | -50.3035 | 87.5472 | 34.1586 | 33.7033 | 16.4751 | 15.3308 | 13.8837 | 12.0101 | 10.1331 | 8.1088 | 6.1472 | -0.47908 | -29.6768 | -41.2531 | -50.6954
|  | ST |  |  | 124.9861 | 124.5938 | 122.2131 | 69.1299 | 68.6678 | 67.9163 | 67.0288 | 66.1191 | 65.1318 | 63.2245 | 57.2363 | 44.2844 | 38.3982 | 33.6594 | 79.429 | 78.9124 | 74.4062 | 21.2069 | 20.5812 | 19.6389 | 18.5055 | 17.3416 | 16.0783 | 13.8568 | 6.82 | -9.847 | -17.1313 | -23.3604 | 87.9093 | 87.3468 | 82.8484 | 29.6061 | 28.9197 | 27.9069 | 26.6825 | 25.4245 | 24.059 | 21.7211 | 14.2961 | -4.556 | -12.7904 | -19.9881
|  | SP |  |  | 124.985 | 124.8295 | 122.5048 | 122.2999 | 122.165 | 119.297 | 116.357 | 113.421 | 107.7212 | 106.866 | 104.1526 | 99.4709 | 95.9389 | 93.7255 | 79.3297 | 79.146 | 74.7179 | 74.485 | 74.3004 | 71.3748 | 68.3478 | 65.3264 | 59.5213 | 58.5486 | 55.4234 | 50.0651 | 45.9473 | 43.138 | 87.8334 | 87.6393 | 83.2272 | 82.984 | 82.7809 | 79.834 | 76.7748 | 73.7218 | 67.8777 | 66.8616 | 63.5839 | 57.975 | 53.6165 | 50.5866
LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | MINIMUM HEADROOM | SU5644404017 | NO | 93.2229 | 93.2081 | 93.1933 | 92.2928 | 92.219 | 92.1451 | 92.0713 | 91.9975 | 91.9237 | 91.8942 | 91.8056 | 90.6111 | 86.4137 | 82.163 | 69.8422 | 69.8275 | 69.8127 | 68.9121 | 68.8383 | 68.7645 | 68.6907 | 68.6169 | 68.543 | 68.5135 | 68.4249 | 66.6261 | 61.6901 | 56.7046 | 86.5052 | 86.4849 | 86.4629 | 85.5458 | 85.4533 | 85.359 | 85.2475 | 85.1357 | 85.0208 | 84.9477 | 84.7347 | 80.7387 | 75.8676 | 70.9466
|  | CT |  |  | 93.2937 | 93.2849 | 93.276 | 92.7357 | 92.6914 | 92.6471 | 92.6028 | 92.5585 | 92.5142 | 92.4965 | 92.4434 | 90.9096 | 86.5732 | 82.3236 | 69.9131 | 69.9042 | 69.8954 | 69.355 | 69.3107 | 69.2665 | 69.2222 | 69.1779 | 69.1336 | 69.1159 | 69.0627 | 66.9531 | 61.8783 | 56.8941 | 86.5753 | 86.5604 | 86.5436 | 85.9851 | 85.9207 | 85.8544 | 85.7896 | 85.7073 | 85.622 | 85.5607 | 85.3831 | 81.0632 | 76.0532 | 71.1335
|  | LW |  |  | 93.2229 | 93.2081 | 93.1933 | 92.2928 | 92.219 | 92.1451 | 92.0713 | 91.9975 | 91.9237 | 91.8942 | 91.8056 | 90.6111 | 86.4137 | 82.163 | 69.8422 | 69.8275 | 69.8127 | 68.9121 | 68.8383 | 68.7645 | 68.6907 | 68.6169 | 68.543 | 68.5135 | 68.4249 | 66.6261 | 61.6901 | 56.7046 | 86.5052 | 86.4849 | 86.4629 | 85.5458 | 85.4533 | 85.359 | 85.2475 | 85.1357 | 85.0208 | 84.9477 | 84.7347 | 80.7387 | 75.8676 | 70.9466
|  | ST |  |  | 93.3292 | 93.3233 | 93.3174 | 92.9571 | 92.9276 | 92.8981 | 92.8686 | 92.839 | 92.8095 | 92.7977 | 92.7623 | 92.7032 | 92.0298 | 89.3505 | 69.9485 | 69.9426 | 69.9367 | 69.5765 | 69.547 | 69.5174 | 69.4879 | 69.4584 | 69.4289 | 69.417 | 69.3816 | 69.3226 | 68.1182 | 64.9691 | 86.6149 | 86.6061 | 86.5968 | 86.2296 | 86.1906 | 86.1494 | 86.0965 | 86.0433 | 85.986 | 85.9443 | 85.8235 | 85.3951 | 82.2244 | 79.1165
|  | SP |  |  | 93.3646 | 93.3617 | 93.3587 | 93.1786 | 93.1614 | 93.1443 | 93.1272 | 93.1101 | 93.0916 | 93.0753 | 93.0248 | 92.9796 | 92.9127 | 92.839 | 69.984 | 69.981 | 69.9781 | 69.7979 | 69.7808 | 69.7637 | 69.7466 | 69.7294 | 69.711 | 69.6947 | 69.6441 | 69.599 | 69.532 | 69.4584 | 86.6521 | 86.6479 | 86.6438 | 86.4613 | 86.4397 | 86.4174 | 86.3925 | 86.3676 | 86.3391 | 86.3112 | 86.2273 | 86.1166 | 85.9719 | 85.8186
BRAMLEY (FLEE) | FERNHURST | MINIMUM HEADROOM | SU7268539765 | YES | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 108.7826 | 108.7826 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 84.8905 | 84.8905 | 108 | 108 | 108 | 108 | 107.9114 | 107.8136 | 107.7025 | 107.5785 | 107.3728 | 107.3419 | 107.2155 | 106.9044 | 106.4219 | 106.2944
|  | CT |  |  | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 117 | 118.0946 | 118.0946 | 118.0946 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 90 | 90.9941 | 90.9941 | 90.9941 | 108 | 108 | 108 | 108 | 107.9114 | 107.8194 | 107.724 | 107.6207 | 107.4539 | 107.4317 | 107.3517 | 106.9044 | 106.4219 | 106.2944
|  | LW |  |  | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 118.0946 | 118.0946 | 118.0946 | 118.4096 | 108.7826 | 108.7826 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90.9941 | 90.9941 | 90.9941 | 91.2802 | 84.8905 | 84.8905 | 108 | 108 | 108 | 108 | 107.9119 | 107.8136 | 107.7025 | 107.5785 | 107.3728 | 107.3419 | 107.2155 | 106.9695 | 106.4316 | 106.3972
|  | ST |  |  | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 117 | 118.0946 | 117.7345 | 117.7345 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 90 | 90.9941 | 90.6671 | 90.6671 | 108 | 108 | 108 | 108 | 107.9152 | 107.8277 | 107.7366 | 107.6403 | 107.4862 | 107.4317 | 107.2415 | 107.0672 | 106.518 | 106.3423
|  | SP |  |  | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 115.047 | 117.7345 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 88.7856 | 90.6671 | 108 | 108 | 108 | 108 | 107.9904 | 107.9809 | 107.9713 | 107.9614 | 107.9458 | 107.9017 | 107.755 | 107.6806 | 107.4278 | 107.209
LOVEDEAN GSP | FORT WIDLEY | MINIMUM HEADROOM | SU6497405375 | NO | 38.0137 | 37.8743 | 37.6903 | 36.615 | 35.5999 | 34.4288 | 32.9653 | 31.4286 | 29.6734 | 27.9883 | 22.1489 | 14.2298 | -8.8277 | -13.6587 | 36.5715 | 36.413 | 36.2032 | 35.0793 | 33.923 | 32.602 | 30.9697 | 29.2546 | 27.2954 | 25.4014 | 18.8573 | 9.9659 | -16.3417 | -21.6504 | 37.5204 | 37.3631 | 37.1551 | 36.0346 | 34.888 | 33.5773 | 31.9566 | 30.2538 | 28.3086 | 26.4289 | 19.9333 | 11.1087 | -14.9755 | -20.2514
|  | CT |  |  | 38.0878 | 37.9633 | 37.7972 | 37.0492 | 36.4305 | 35.7144 | 34.9851 | 33.6561 | 32.2455 | 30.7852 | 26.1078 | 18.8769 | 4.457 | -1.7115 | 36.6472 | 36.5049 | 36.3145 | 35.5215 | 34.8139 | 34.0066 | 33.1843 | 31.7246 | 30.1615 | 28.5231 | 23.2783 | 15.3143 | -0.98591 | -7.8461 | 37.596 | 37.4549 | 37.2661 | 36.4762 | 35.7747 | 34.9737 | 34.1578 | 32.7071 | 31.1544 | 29.5283 | 24.3225 | 16.409 | 0.23794 | -6.5747
|  | LW |  |  | 38.0137 | 37.8743 | 37.6903 | 36.615 | 35.5999 | 34.4288 | 32.9653 | 31.4286 | 29.6734 | 27.9883 | 22.1489 | 14.2298 | -8.8277 | -13.6587 | 36.5715 | 36.413 | 36.2032 | 35.0793 | 33.923 | 32.602 | 30.9697 | 29.2546 | 27.2954 | 25.4014 | 18.8573 | 9.9659 | -16.3417 | -21.6504 | 37.5204 | 37.3631 | 37.1551 | 36.0346 | 34.888 | 33.5773 | 31.9566 | 30.2538 | 28.3086 | 26.4289 | 19.9333 | 11.1087 | -14.9755 | -20.2514
|  | ST |  |  | 38.1499 | 38.0607 | 37.9515 | 37.4854 | 36.9956 | 36.3666 | 35.5912 | 34.7005 | 33.6105 | 32.1314 | 27.4204 | 21.6602 | 9.1578 | 4.9104 | 36.7142 | 36.6121 | 36.4868 | 35.9955 | 35.4385 | 34.7341 | 33.8733 | 32.8814 | 31.6683 | 30.0413 | 24.8475 | 18.4852 | 4.2511 | -0.53583 | 37.6627 | 37.5614 | 37.4372 | 36.9476 | 36.3953 | 35.696 | 34.8412 | 33.8562 | 32.6515 | 31.0347 | 25.8741 | 19.5531 | 5.4381 | 0.68826
|  | SP |  |  | 38.2449 | 38.2131 | 38.177 | 37.9867 | 37.8418 | 36.6353 | 35.3674 | 34.0379 | 31.6167 | 31.0295 | 29.0031 | 26.0246 | 23.711 | 22.231 | 36.8193 | 36.783 | 36.7417 | 36.5454 | 36.3803 | 35.1493 | 33.8474 | 32.482 | 30.0176 | 29.3781 | 27.1609 | 23.9188 | 21.3748 | 19.7211 | 37.767 | 37.731 | 37.6901 | 37.4942 | 37.3305 | 36.1012 | 34.8016 | 33.4387 | 30.9773 | 30.3414 | 28.1372 | 24.9132 | 22.3851 | 20.7434
MELKSHAM GSP | FROME BSP | MINIMUM HEADROOM | ST7885048051 | NO | 68.9277 | 68.2106 | 66.0114 | 63.1245 | 53.4093 | 43.22 | 32.7498 | 23.0108 | 13.0402 | 3.9098 | -29.5238 | -83.4906 | -128.1349 | -142.8921 | 4.4618 | 3.6256 | 0.65051 | -3.1553 | -13.6827 | -25.4779 | -37.5932 | -48.4432 | -59.9054 | -70.5389 | -109.5212 | -170.6079 | -222.1106 | -242.0865 | 15.3387 | 14.5101 | 11.4781 | 7.73 | -2.7451 | -14.4381 | -26.4489 | -37.1219 | -48.4893 | -59.0272 | -98.102 | -159.3354 | -211.0352 | -231.285
|  | CT |  |  | 108.8099 | 98.3482 | 66.3372 | 64.3963 | 59.9713 | 55.7803 | 51.6024 | 46.3045 | 40.6787 | 33.8047 | 11.0288 | -25.2245 | -53.0908 | -67.8416 | 45.974 | 33.7774 | 0.99825 | -1.056 | -6.2315 | -11.0701 | -15.8914 | -22.0262 | -28.5393 | -36.5537 | -62.7272 | -104.3219 | -136.3291 | -151.372 | 56.7472 | 44.6609 | 11.8244 | 9.7773 | 4.6496 | -0.14779 | -4.9282 | -11.0098 | -17.4665 | -25.4084 | -51.2595 | -92.8768 | -125.003 | -139.9716
|  | LW |  |  | 68.9277 | 68.2106 | 66.0114 | 63.1245 | 53.4093 | 43.22 | 32.7498 | 23.0108 | 13.0402 | 3.9098 | -29.5238 | -83.4906 | -128.1349 | -142.8921 | 4.4618 | 3.6256 | 0.65051 | -2.3665 | -13.6827 | -25.4779 | -37.5932 | -48.4432 | -59.9054 | -70.5389 | -109.5212 | -170.6079 | -222.1106 | -242.0865 | 15.3387 | 14.5101 | 11.4781 | 8.4693 | -2.7451 | -14.4381 | -26.4489 | -37.1219 | -48.4893 | -59.0272 | -98.102 | -159.3354 | -211.0352 | -231.285
|  | ST |  |  | 79.2031 | 68.9521 | 67.4523 | 66.117 | 62.2277 | 58.0502 | 53.9861 | 48.9628 | 43.6852 | 35.6576 | 9.4204 | -26.346 | -53.3876 | -66.8704 | 16.3989 | 4.4487 | 2.2913 | 0.87279 | -3.6812 | -8.5107 | -13.2057 | -19.026 | -25.1391 | -34.2523 | -63.7193 | -104.5602 | -136.0173 | -149.5388 | 27.1701 | 15.3279 | 13.1061 | 11.6929 | 7.1812 | 2.3931 | -2.2617 | -8.0313 | -14.0913 | -23.1355 | -52.2908 | -93.0898 | -124.6903 | -138.1302
|  | SP |  |  | 89.1588 | 78.7333 | 73.7699 | 63.9978 | 62.8541 | 57.2607 | 51.0784 | 38.8452 | 27.7977 | 23.5883 | 8.2389 | -14.6953 | -31.8757 | -36.4012 | 28.0833 | 15.7067 | 8.253 | -3.1553 | -4.4915 | -10.3035 | -16.8073 | -33.3997 | -44.867 | -49.6505 | -66.9393 | -93.0283 | -112.598 | -115.6609 | 38.7446 | 26.6232 | 19.0343 | 7.73 | 6.4061 | 0.60796 | -5.8754 | -22.9869 | -34.4275 | -39.1744 | -56.6023 | -82.4907 | -101.9084 | -104.5337
MINETY GSP | GALILEO | MINIMUM HEADROOM | SU 10596 83733 | YES | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.505 | 57.4425 | 57.379 | 57.3126 | 57.2104 | 57.1974 | 57.1558 | 56.4095 | 54.6987 | 53.1348 | 50.7899 | 50.7711 | 50.7465 | 50.6982 | 50.607 | 50.5008 | 50.3935 | 50.2482 | 50.0667 | 49.9697 | 49.5409 | 48.0625 | 46.1101 | 44.3037 | 51.4735 | 51.4636 | 51.4505 | 51.4249 | 51.3476 | 51.2619 | 51.1752 | 50.992 | 50.7519 | 50.5925 | 50.0835 | 48.5183 | 46.6097 | 44.8473
|  | CT |  |  | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.505 | 57.4425 | 57.379 | 57.3126 | 57.2104 | 57.1974 | 57.1558 | 56.4095 | 54.6987 | 53.1348 | 50.7926 | 50.7758 | 50.7539 | 50.7111 | 50.607 | 50.5008 | 50.3935 | 50.2482 | 50.0667 | 49.9697 | 49.5409 | 48.0625 | 46.1101 | 44.3037 | 51.4749 | 51.466 | 51.4544 | 51.4317 | 51.3476 | 51.2619 | 51.1752 | 50.992 | 50.7519 | 50.5925 | 50.0835 | 48.5183 | 46.6097 | 44.8473
|  | LW |  |  | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 56.8958 | 55.3921 | 53.8816 | 50.7899 | 50.7711 | 50.7465 | 50.6982 | 50.6502 | 50.6012 | 50.5227 | 50.4437 | 50.3645 | 50.2804 | 49.838 | 48.5302 | 46.7848 | 45.0317 | 51.4735 | 51.4636 | 51.4505 | 51.4249 | 51.3994 | 51.3734 | 51.2818 | 51.1443 | 51.0065 | 50.8601 | 50.3927 | 48.9894 | 47.2878 | 45.5787
|  | ST |  |  | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 56.9827 | 56.0198 | 50.9597 | 50.8 | 50.7925 | 50.7814 | 50.7678 | 50.7513 | 50.7014 | 50.6514 | 50.5975 | 50.54 | 50.3566 | 49.6765 | 48.631 | 47.5134 | 51.5636 | 51.4789 | 51.4749 | 51.469 | 51.4618 | 51.453 | 51.4266 | 51.4 | 51.3714 | 51.3119 | 50.9926 | 50.2066 | 49.0876 | 47.9982
|  | SP |  |  | 57.5664 | 57.5664 | 57.5664 | 57.5664 | 57.5604 | 57.5545 | 57.5486 | 57.5426 | 57.5333 | 57.5072 | 57.4244 | 57.385 | 57.2609 | 57.1571 | 50.9606 | 50.9566 | 50.7989 | 50.7948 | 50.7768 | 50.7568 | 50.7343 | 50.7116 | 50.6812 | 50.6327 | 50.4787 | 50.2657 | 49.9216 | 49.3989 | 51.5641 | 51.562 | 51.4783 | 51.4761 | 51.4637 | 51.4504 | 51.4356 | 51.4208 | 51.4002 | 51.3623 | 51.2417 | 50.9688 | 50.4617 | 49.9502
WILLESDEN GSP | GREENFORD | MINIMUM HEADROOM | TQ 14695 83785 | NO | 77.1121 | 77.1121 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 75.2023 | 71.4917 | 67.3536 | 63.2829 | 76.0003 | 75.9806 | 69.3258 | 69.3213 | 69.3159 | 69.3099 | 69.2999 | 69.2886 | 69.2753 | 69.2605 | 72.7939 | 68.2772 | 63.4146 | 58.6311 | 68.7399 | 68.509 | 61.777 | 61.7247 | 61.6618 | 61.5914 | 61.4737 | 61.341 | 61.1847 | 61.0121 | 62.7062 | 59.7111 | 56.4865 | 53.3145
|  | CT |  |  | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 75.6109 | 71.9287 | 67.791 | 63.7198 | 76.0003 | 75.9806 | 75.9203 | 75.9029 | 75.8841 | 75.8628 | 75.8399 | 75.7825 | 75.7224 | 75.6675 | 73.2822 | 68.7907 | 63.9285 | 59.1445 | 68.7399 | 68.509 | 67.8021 | 67.598 | 67.3773 | 67.1271 | 66.859 | 66.1856 | 65.4807 | 64.8367 | 63.0468 | 60.0516 | 56.8274 | 53.655
|  | LW |  |  | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 75.2023 | 71.4917 | 67.3536 | 63.2829 | 76.0003 | 75.9806 | 75.9203 | 75.9029 | 75.8841 | 75.8628 | 75.8109 | 75.7535 | 75.6933 | 75.2643 | 72.7939 | 68.2772 | 63.4146 | 58.6311 | 68.7399 | 68.509 | 67.8021 | 67.598 | 67.3773 | 67.1271 | 66.5185 | 65.8453 | 65.1401 | 64.4962 | 62.7062 | 59.7111 | 56.4865 | 53.3145
|  | ST |  |  | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 77.0639 | 77.015 | 76.965 | 76.9133 | 76.8334 | 76.8063 | 76.7198 | 75.2919 | 72.5427 | 69.8624 | 76.0022 | 75.9955 | 75.9772 | 75.9671 | 75.907 | 75.8437 | 75.7662 | 75.6835 | 75.5629 | 75.4982 | 75.3069 | 72.9832 | 69.6319 | 66.4942 | 68.7629 | 68.6837 | 68.4698 | 68.351 | 68.1634 | 67.9459 | 67.574 | 67.1573 | 66.6005 | 66.1324 | 64.8171 | 62.704 | 60.3792 | 58.2756
|  | SP |  |  | 77.1121 | 77.1121 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 72.1367 | 77.1121 | 77.1121 | 77.1121 | 77.1121 | 76.0045 | 76.0004 | 69.3258 | 69.3213 | 69.3159 | 69.3099 | 69.2999 | 69.2886 | 69.2753 | 69.2605 | 75.8797 | 75.8105 | 75.7361 | 75.644 | 68.7892 | 68.7412 | 61.777 | 61.7247 | 61.6618 | 61.5914 | 61.4737 | 61.341 | 61.1847 | 61.0121 | 67.3258 | 66.5146 | 65.6416 | 64.7738
LOVEDEAN GSP | HAVANT | MINIMUM HEADROOM | SU7055105721 | NO | 143.2309 | 143.2296 | 140.9905 | 140.9816 | 140.8493 | 140.8129 | 140.7651 | 140.6584 | 141.9543 | 152.3309 | 151.0271 | 149.9205 | 129.4684 | 123.173 | 110.486 | 110.4537 | 109.2937 | 109.2875 | 109.19 | 109.1588 | 109.1198 | 109.0216 | 110.3281 | 123.0692 | 121.2385 | 108.9461 | 82.4029 | 72.1356 | 127.854 | 127.8105 | 125.3929 | 125.3928 | 125.373 | 125.3536 | 125.3342 | 125.2554 | 126.5854 | 139.1828 | 136.5148 | 124.3964 | 96.6472 | 86.5171
|  | CT |  |  | 143.2309 | 143.2296 | 143.2282 | 143.2259 | 154.522 | 154.4823 | 154.4416 | 153.9681 | 153.5539 | 153.2629 | 152.3242 | 150.6378 | 144.9837 | 129.4353 | 110.486 | 110.4537 | 110.38 | 110.3469 | 125.2771 | 125.2374 | 125.1967 | 124.7233 | 124.3091 | 124.0181 | 122.887 | 112.7724 | 101.8516 | 80.805 | 127.854 | 127.8105 | 127.7108 | 127.6666 | 141.3813 | 141.3416 | 141.3009 | 140.8275 | 140.4133 | 140.1223 | 138.9524 | 128.1744 | 117.3967 | 95.5924
|  | LW |  |  | 154.5611 | 154.5571 | 154.5527 | 154.5467 | 154.3372 | 154.1187 | 153.6914 | 153.2485 | 152.6479 | 152.3309 | 151.0271 | 149.9205 | 129.4684 | 123.173 | 125.3163 | 125.3123 | 125.3078 | 125.3019 | 125.0923 | 124.8738 | 124.4466 | 124.0037 | 123.4031 | 123.0692 | 121.2385 | 108.9461 | 82.4029 | 72.1356 | 141.4205 | 141.4165 | 141.412 | 141.4061 | 141.1965 | 140.978 | 140.5508 | 140.1079 | 139.5073 | 139.1828 | 136.5148 | 124.3964 | 96.6472 | 86.5171
|  | ST |  |  | 143.2316 | 143.2315 | 143.2314 | 143.2313 | 154.4587 | 154.3494 | 154.1399 | 153.9146 | 153.5801 | 153.4352 | 152.9733 | 152.4282 | 144.3513 | 143.3735 | 110.4908 | 110.4825 | 110.3983 | 110.3821 | 125.2139 | 125.1046 | 124.8951 | 124.6697 | 124.3353 | 124.1904 | 123.714 | 121.149 | 105.3025 | 98.6737 | 127.8603 | 127.849 | 127.7345 | 127.7125 | 141.3181 | 141.2088 | 140.9993 | 140.7739 | 140.4394 | 140.2946 | 139.8282 | 136.4485 | 119.7958 | 113.2627
|  | SP |  |  | 143.2315 | 143.2314 | 140.9905 | 140.9816 | 140.8493 | 140.8129 | 140.7651 | 140.6584 | 141.9543 | 154.639 | 154.2211 | 153.978 | 153.5389 | 153.1578 | 110.4961 | 110.4925 | 109.2937 | 109.2875 | 109.19 | 109.1588 | 109.1198 | 109.0216 | 110.3281 | 125.4897 | 125.0717 | 124.8287 | 124.2771 | 123.7839 | 127.8675 | 127.8628 | 125.3929 | 125.3928 | 125.373 | 125.3536 | 125.3342 | 125.2554 | 126.5854 | 141.3315 | 140.9135 | 140.6135 | 140.0257 | 139.5016
NORTH HYDE GSP | HAYES | MINIMUM HEADROOM | TQ0953579555 | NO | 76.1042 | 75.9726 | 75.8906 | 72.6528 | 72.3509 | 72.0445 | 71.6688 | 71.2945 | 70.9225 | 70.7013 | 68.9279 | 64.6849 | 60.325 | 55.7285 | 73.5714 | 73.4917 | 73.4302 | 70.2189 | 69.9445 | 69.6688 | 69.3718 | 68.921 | 68.4307 | 67.844 | 65.6483 | 60.7976 | 55.7523 | 50.4748 | 73.5628 | 73.4782 | 73.415 | 70.2015 | 69.9249 | 69.6467 | 69.3433 | 69.0405 | 68.7384 | 68.2935 | 65.822 | 61.0556 | 56.0551 | 50.8222
|  | CT |  |  | 76.356 | 76.2453 | 76.1843 | 74.2264 | 74.0294 | 73.8279 | 73.6273 | 73.3579 | 73.0907 | 72.9115 | 71.5725 | 65.5631 | 60.7078 | 56.1126 | 73.8231 | 73.7645 | 73.724 | 71.7925 | 71.623 | 71.4522 | 71.2816 | 71.0551 | 70.6771 | 70.2748 | 68.351 | 61.7406 | 56.2 | 50.924 | 73.8146 | 73.7509 | 73.7087 | 71.7751 | 71.6034 | 71.4301 | 71.257 | 71.0591 | 70.862 | 70.7569 | 68.522 | 61.9944 | 56.4986 | 51.2671
|  | LW |  |  | 76.1042 | 75.9726 | 75.8906 | 72.6528 | 72.3509 | 72.0445 | 71.6688 | 71.2945 | 70.9225 | 70.7013 | 68.9279 | 64.6849 | 60.325 | 55.7285 | 73.5714 | 73.4917 | 73.4302 | 70.2189 | 69.9445 | 69.6688 | 69.3718 | 68.921 | 68.4307 | 67.844 | 65.6483 | 60.7976 | 55.7523 | 50.4748 | 73.5628 | 73.4782 | 73.415 | 70.2015 | 69.9249 | 69.6467 | 69.3433 | 69.0405 | 68.7384 | 68.2935 | 65.822 | 61.0556 | 56.0551 | 50.8222
|  | ST |  |  | 76.4819 | 76.4492 | 76.3678 | 75.0693 | 74.941 | 74.806 | 74.6572 | 74.5093 | 74.3296 | 74.2082 | 73.8419 | 71.8346 | 69.074 | 66.2597 | 73.9763 | 73.9215 | 73.882 | 72.5965 | 72.4844 | 72.3703 | 72.252 | 72.1339 | 72.0061 | 71.9061 | 71.1618 | 68.5159 | 65.3224 | 62.0703 | 73.9728 | 73.9117 | 73.8689 | 72.5823 | 72.4689 | 72.3531 | 72.2323 | 72.1118 | 71.9798 | 71.909 | 71.696 | 68.6916 | 65.5716 | 62.3481
|  | SP |  |  | 76.6078 | 76.5973 | 76.5513 | 75.9076 | 75.8472 | 75.7846 | 75.7187 | 75.6533 | 75.5857 | 75.534 | 75.3781 | 75.0912 | 74.8312 | 74.4008 | 74.1061 | 74.0658 | 74.0401 | 73.399 | 73.3441 | 73.2886 | 73.232 | 73.1756 | 73.1185 | 73.0882 | 72.9968 | 72.7695 | 72.2271 | 71.2912 | 74.1034 | 74.0575 | 74.029 | 73.3877 | 73.3324 | 73.2763 | 73.219 | 73.1618 | 73.1039 | 73.0718 | 72.9751 | 72.8043 | 72.6699 | 71.5331
COWLEY GSP | HEADINGTON BSP | MINIMUM HEADROOM | SP5444008085 | YES | 107.1961 | 106.9168 | 104.9459 | 104.8493 | 102.0763 | 97.3041 | 92.4108 | 87.4573 | 82.7136 | 78.1048 | 61.8566 | 35.076 | 16.9294 | 9.4445 | 53.697 | 53.3558 | 50.5456 | 50.4274 | 47.7107 | 42.1052 | 36.4417 | 30.7139 | 25.2681 | 19.9479 | 1.4688 | -29.3024 | -50.827 | -59.0673 | 61.8101 | 61.471 | 58.0393 | 57.9218 | 56.3489 | 50.9937 | 45.5133 | 39.9696 | 34.6907 | 29.5396 | 11.8214 | -17.5083 | -39.051 | -47.1117
|  | CT |  |  | 107.1961 | 106.9168 | 106.2123 | 105.0024 | 102.6249 | 100.4878 | 98.3743 | 95.0928 | 91.8166 | 88.1022 | 77.3424 | 58.0683 | 46.0769 | 35.48 | 53.697 | 53.3558 | 52.4945 | 51.1095 | 48.1228 | 45.4329 | 42.8666 | 39.1767 | 35.4667 | 31.2019 | 19.3541 | -2.7004 | -15.9509 | -27.4293 | 61.8101 | 61.471 | 60.6149 | 59.2357 | 56.3489 | 53.7555 | 51.281 | 47.6882 | 44.0814 | 39.9474 | 28.9057 | 7.5122 | -5.2084 | -15.9844
|  | LW |  |  | 108.7712 | 108.4785 | 107.7578 | 106.5198 | 102.0763 | 97.3041 | 92.4108 | 87.4573 | 82.7136 | 78.1048 | 61.8566 | 35.076 | 16.9294 | 9.4445 | 55.892 | 55.5359 | 54.6563 | 53.2386 | 47.7107 | 42.1052 | 36.4417 | 30.7139 | 25.2681 | 19.9479 | 1.4688 | -29.3024 | -50.827 | -59.0673 | 64.4177 | 64.0637 | 63.1894 | 61.7777 | 56.4011 | 50.9937 | 45.5133 | 39.9696 | 34.6907 | 29.5396 | 11.8214 | -17.5083 | -39.051 | -47.1117
|  | ST |  |  | 107.3217 | 107.1507 | 106.9375 | 106.5605 | 104.6458 | 102.733 | 100.7719 | 98.3291 | 95.5883 | 92.4851 | 83.5613 | 67.9243 | 58.0328 | 50.9577 | 53.8503 | 53.6412 | 53.3803 | 52.919 | 50.5779 | 48.1897 | 45.7999 | 42.8781 | 39.7397 | 36.1243 | 26.2096 | 7.957 | -3.7339 | -11.4904 | 61.9625 | 61.7546 | 61.4953 | 61.0368 | 58.7283 | 56.423 | 54.1081 | 51.2791 | 48.2352 | 44.7416 | 35.6099 | 17.9792 | 6.3991 | -0.70269
|  | SP |  |  | 107.648 | 107.402 | 104.9459 | 104.8493 | 104.2548 | 103.5968 | 102.7557 | 101.7925 | 100.5364 | 98.9966 | 92.4714 | 83.9152 | 77.6658 | 75.052 | 54.2496 | 53.9487 | 50.5456 | 50.4274 | 49.6966 | 48.8694 | 47.8114 | 46.6344 | 45.0966 | 43.1879 | 35.2983 | 25.2693 | 18.1714 | 15.5809 | 62.3593 | 62.0603 | 58.0393 | 57.9218 | 57.2014 | 56.4038 | 55.3837 | 54.244 | 52.7554 | 50.911 | 43.2881 | 33.6093 | 26.9436 | 24.8402
COWLEY GSP | HIGH WYCOMBE BSP | MINIMUM HEADROOM | SU8473392200 | YES | 125.7092 | 125.2478 | 124.7842 | 121.1925 | 119.3157 | 117.2186 | 115.1181 | 113.012 | 110.632 | 108.526 | 101.467 | 89.8758 | 71.6755 | 64.6748 | 69.96 | 69.4464 | 68.9159 | 65.1882 | 63.0644 | 60.7214 | 58.3757 | 56.0247 | 53.3668 | 50.9736 | 42.8933 | 29.6591 | 8.6499 | 0.68038 | 91.314 | 90.8848 | 90.4624 | 86.9543 | 85.2295 | 83.2838 | 81.3342 | 79.3789 | 77.1699 | 75.2406 | 68.7835 | 57.8325 | 37.3016 | 29.497
|  | CT |  |  | 125.8718 | 125.3901 | 124.8945 | 122.2902 | 120.7636 | 119.104 | 117.449 | 115.8211 | 113.9322 | 112.1399 | 106.4008 | 95.187 | 81.6418 | 72.9545 | 70.1143 | 69.5743 | 69.0037 | 66.2467 | 64.5219 | 62.6738 | 60.8317 | 59.0222 | 56.9238 | 54.8851 | 48.35 | 35.8557 | 20.3972 | 10.4331 | 91.4818 | 91.036 | 90.5864 | 88.0762 | 86.6716 | 85.128 | 83.5882 | 82.0719 | 80.3121 | 78.6714 | 73.4221 | 62.918 | 48.7398 | 38.9989
|  | LW |  |  | 125.7092 | 125.2478 | 124.7842 | 121.1925 | 119.3157 | 117.2186 | 115.1181 | 113.012 | 110.632 | 108.526 | 101.467 | 89.8758 | 71.6755 | 64.6748 | 69.96 | 69.4464 | 68.9159 | 65.1882 | 63.0644 | 60.7214 | 58.3757 | 56.0247 | 53.3668 | 50.9736 | 42.8933 | 29.6591 | 8.6499 | 0.68038 | 91.314 | 90.8848 | 90.4624 | 86.9543 | 85.2295 | 83.2838 | 81.3342 | 79.3789 | 77.1699 | 75.2406 | 68.7835 | 57.8325 | 37.3016 | 29.497
|  | ST |  |  | 126.2291 | 125.9713 | 125.7225 | 124.2459 | 123.3527 | 122.1871 | 120.9753 | 119.6852 | 118.2305 | 115.9095 | 108.602 | 99.2798 | 88.0735 | 81.5107 | 70.5116 | 70.2154 | 69.9297 | 68.3927 | 67.3817 | 66.0863 | 64.7378 | 63.2987 | 61.675 | 59.1512 | 51.1811 | 40.9297 | 28.1258 | 20.6003 | 91.8145 | 91.5803 | 91.3541 | 89.9148 | 89.0941 | 88.0083 | 86.8808 | 85.6822 | 84.3316 | 82.1354 | 75.2357 | 66.474 | 56.1417 | 48.8918
|  | SP |  |  | 126.5349 | 126.4425 | 126.3929 | 125.8084 | 125.5621 | 122.9016 | 120.1461 | 117.3941 | 112.1627 | 111.2091 | 108.0611 | 102.9067 | 98.9339 | 96.546 | 70.8491 | 70.7433 | 70.6872 | 70.0969 | 69.8187 | 67.1214 | 64.314 | 61.5107 | 56.2125 | 55.1876 | 51.7794 | 46.2373 | 41.9157 | 39.2742 | 92.1008 | 92.0166 | 91.971 | 91.3901 | 91.1634 | 88.5255 | 85.802 | 83.0816 | 77.8912 | 76.9815 | 73.9937 | 69.0779 | 65.3197 | 63.111
IVER 66KV | HILLINGDON | MINIMUM HEADROOM | TQ0744082847 | NO | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 58.034 | 58.034 | 57.1551 | 52.8318 | 48.551 | 49.887 | 49.8716 | 49.8626 | 49.8507 | 49.877 | 49.8752 | 49.8684 | 49.8617 | 49.8532 | 56.9712 | 56.8569 | 52.696 | 47.5956 | 42.5454 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 56.7687 | 56.7063 | 52.1192 | 47.1511 | 42.1043
|  | CT |  |  | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 57.5549 | 53.2317 | 48.9517 | 49.887 | 49.8716 | 49.8626 | 49.8507 | 57.1245 | 57.1133 | 57.1019 | 57.0658 | 57.0302 | 56.9921 | 56.8778 | 53.1676 | 48.0673 | 43.0181 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 52.5785 | 47.6106 | 42.5772
|  | LW |  |  | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 57.1551 | 52.8318 | 48.551 | 57.1719 | 57.1568 | 57.1483 | 57.1373 | 57.1275 | 57.1171 | 57.081 | 57.0449 | 57.0093 | 56.9712 | 56.8569 | 52.696 | 47.5956 | 42.5454 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7063 | 52.1192 | 47.1511 | 42.1043
|  | ST |  |  | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 57.8955 | 55.1335 | 49.8907 | 49.887 | 49.8741 | 49.8704 | 57.1512 | 57.1465 | 57.1243 | 57.1021 | 57.0778 | 57.0518 | 56.9744 | 56.8229 | 53.5695 | 50.311 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.1951 | 52.97 | 49.7961
|  | SP |  |  | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 52.1263 | 58.034 | 58.034 | 58.034 | 58.034 | 58.034 | 49.8922 | 49.8901 | 49.8794 | 49.8785 | 49.877 | 49.8752 | 49.8684 | 49.8617 | 49.8532 | 57.1275 | 57.0975 | 57.0427 | 56.9848 | 56.9276 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 50.2809 | 56.7687 | 56.7687 | 56.7687 | 56.7687 | 56.7687
EALING GSP | IRONBRIDGE | MINIMUM HEADROOM | TQ1426580175 | NO | 50.9526 | 50.94 | 50.9195 | 50.8792 | 50.949 | 50.9394 | 50.9286 | 50.9173 | 50.9054 | 55.116 | 55.0625 | 54.5062 | 50.9714 | 47.5664 | 49.386 | 49.3716 | 49.3483 | 49.3024 | 49.3818 | 49.3709 | 49.3586 | 49.3457 | 49.3322 | 55.0682 | 54.8695 | 51.2766 | 47.1321 | 43.1221 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 54.5622 | 53.5727 | 50.1015 | 46.102 | 42.2359
|  | CT |  |  | 50.9526 | 50.94 | 50.9195 | 50.8792 | 55.3269 | 55.2841 | 55.2405 | 55.195 | 55.1248 | 55.116 | 55.0625 | 54.5062 | 50.9714 | 47.5664 | 49.386 | 49.3716 | 49.3483 | 49.3024 | 55.4137 | 55.3441 | 55.2734 | 55.1987 | 55.1026 | 55.0682 | 54.8858 | 51.2766 | 47.1321 | 43.1221 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 54.7732 | 54.7303 | 54.6867 | 54.6412 | 54.5711 | 54.5622 | 53.5848 | 50.1015 | 46.102 | 42.2359
|  | LW |  |  | 55.3691 | 55.3691 | 55.3691 | 55.3691 | 55.3432 | 55.3164 | 55.2884 | 55.2595 | 55.2154 | 55.2093 | 55.1553 | 54.6055 | 51.1344 | 47.7645 | 55.5277 | 55.5193 | 55.5058 | 55.4791 | 55.4263 | 55.3717 | 55.3162 | 55.258 | 55.188 | 55.1564 | 54.8695 | 51.3581 | 47.2773 | 43.3024 | 54.8153 | 54.8153 | 54.8153 | 54.8153 | 54.7894 | 54.7626 | 54.7347 | 54.7057 | 54.6617 | 54.6556 | 53.5727 | 50.1873 | 46.2515 | 42.4204
|  | ST |  |  | 50.9609 | 50.9546 | 50.9444 | 50.9278 | 55.3691 | 55.3691 | 55.3691 | 55.3691 | 55.3691 | 55.3691 | 55.3691 | 55.359 | 55.1759 | 53.6724 | 49.3954 | 49.3882 | 49.3766 | 49.3578 | 55.4998 | 55.4845 | 55.4662 | 55.447 | 55.4293 | 55.4119 | 55.36 | 55.2546 | 52.76 | 50.2186 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 54.8153 | 54.8153 | 54.8153 | 54.8153 | 54.8153 | 54.8153 | 54.8153 | 54.0713 | 51.5462 | 49.0969
|  | SP |  |  | 50.9666 | 50.9649 | 50.9614 | 50.9573 | 50.949 | 50.9394 | 50.9286 | 50.9173 | 50.9054 | 55.3691 | 55.3691 | 55.3691 | 55.3691 | 55.3691 | 49.4018 | 49.3999 | 49.396 | 49.3913 | 49.3818 | 49.3709 | 49.3586 | 49.3457 | 49.3322 | 55.4915 | 55.4714 | 55.4293 | 55.3797 | 55.3293 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 49.4057 | 54.8153 | 54.8153 | 54.8153 | 54.8153 | 54.8153
FAWLEY GSP | LANGLEY BSP | MINIMUM HEADROOM | SU4515801418 | YES | 65.9662 | 65.9328 | 65.2646 | 65.2612 | 65.2255 | 65.1772 | 64.7508 | 64.234 | 63.6476 | 63.0189 | 60.8646 | 54.8041 | 52.5761 | 50.8182 | 46.1934 | 46.1542 | 45.308 | 45.304 | 45.2621 | 45.2054 | 44.7672 | 44.1609 | 43.4733 | 42.7354 | 40.2069 | 33.0935 | 30.4816 | 28.4179 | 48.1032 | 48.0654 | 47.2793 | 47.2754 | 47.235 | 47.1804 | 46.7285 | 46.1441 | 45.4812 | 44.77 | 42.3329 | 35.4768 | 32.9316 | 30.8955
|  | CT |  |  | 65.9802 | 65.9569 | 65.9262 | 65.8619 | 65.7164 | 65.5548 | 65.39 | 64.9551 | 64.4583 | 63.8816 | 61.9596 | 57.8276 | 55.793 | 53.6757 | 46.2098 | 46.1825 | 46.1465 | 46.071 | 45.9001 | 45.7105 | 45.5171 | 45.0066 | 44.4236 | 43.7466 | 41.4904 | 36.6414 | 34.2551 | 31.77 | 48.119 | 48.0927 | 48.058 | 47.9852 | 47.8205 | 47.6378 | 47.4513 | 46.9593 | 46.3974 | 45.7449 | 43.5704 | 38.8965 | 36.5962 | 34.2009
|  | LW |  |  | 65.9662 | 65.9328 | 65.8889 | 65.7965 | 65.5413 | 65.2594 | 64.7508 | 64.234 | 63.6476 | 63.0189 | 60.8646 | 54.8041 | 52.5761 | 50.8182 | 46.1934 | 46.1542 | 46.1027 | 45.9942 | 45.6947 | 45.3639 | 44.7672 | 44.1609 | 43.4733 | 42.7354 | 40.2069 | 33.0935 | 30.4816 | 28.4179 | 48.1032 | 48.0654 | 48.0157 | 47.9112 | 47.6225 | 47.3037 | 46.7285 | 46.1441 | 45.4812 | 44.77 | 42.3329 | 35.4768 | 32.9316 | 30.8955
|  | ST |  |  | 66.0461 | 65.9513 | 65.9217 | 65.8713 | 65.7404 | 65.5822 | 65.3151 | 65.0274 | 64.6563 | 64.2182 | 62.7397 | 59.2736 | 57.8426 | 56.3071 | 46.2873 | 46.1759 | 46.1412 | 46.082 | 45.9284 | 45.7426 | 45.4291 | 45.0914 | 44.656 | 44.1417 | 42.4064 | 38.3378 | 36.6603 | 34.8585 | 48.1937 | 48.0863 | 48.0529 | 47.9959 | 47.8478 | 47.6687 | 47.3665 | 47.0411 | 46.6214 | 46.1257 | 44.4531 | 40.5318 | 38.9145 | 37.1777
|  | SP |  |  | 66.0742 | 66.0705 | 65.2646 | 65.2612 | 65.2255 | 65.1772 | 65.089 | 64.9999 | 64.8819 | 64.7201 | 64.8714 | 64.0772 | 63.4839 | 63.0095 | 46.3202 | 46.3159 | 45.308 | 45.304 | 45.2621 | 45.2054 | 45.1018 | 44.9972 | 44.8587 | 44.6688 | 44.9084 | 43.9761 | 43.2803 | 42.724 | 48.2254 | 48.2212 | 47.2793 | 47.2754 | 47.235 | 47.1804 | 47.0805 | 46.9798 | 46.8462 | 46.6632 | 46.8646 | 45.9661 | 45.2953 | 44.7591
IVER 132KV | LONGFORD | MINIMUM HEADROOM | TQ0383076784 | NO | 76.641 | 76.641 | 76.641 | 76.641 | 76.6398 | 76.6386 | 76.6374 | 76.6362 | 76.6344 | 76.6292 | 76.6128 | 78.0909 | 78.0663 | 78.0457 | 54.3928 | 54.389 | 54.3056 | 54.3019 | 54.2866 | 54.2688 | 54.2404 | 54.2122 | 54.1751 | 54.1302 | 53.9685 | 55.1112 | 54.8525 | 54.6002 | 61.3752 | 61.3744 | 61.3588 | 61.3581 | 61.3543 | 61.35 | 61.3437 | 61.3375 | 61.329 | 61.3164 | 61.2728 | 62.6499 | 62.5815 | 62.5175
|  | CT |  |  | 103.1088 | 103.1088 | 103.1088 | 103.0884 | 103.068 | 103.0272 | 103.0272 | 102.9863 | 103.8304 | 103.81 | 103.7692 | 103.6671 | 103.6263 | 103.5446 | 72.1144 | 72.1081 | 72.1058 | 72.0805 | 72.0554 | 72.0099 | 72.0052 | 71.9562 | 73.0487 | 73.0196 | 72.9473 | 72.7965 | 72.2199 | 71.0599 | 85.2867 | 85.2567 | 85.2457 | 85.2024 | 85.1597 | 85.0965 | 85.0743 | 84.9948 | 86.1545 | 86.0929 | 85.9028 | 85.5698 | 85.2792 | 84.9497
|  | LW |  |  | 103.1088 | 103.1088 | 103.1088 | 103.9325 | 103.8803 | 103.8068 | 103.7726 | 103.6964 | 103.6426 | 103.6147 | 103.5483 | 103.4062 | 103.286 | 103.1988 | 72.1143 | 72.1079 | 72.1055 | 73.1807 | 73.1237 | 73.0452 | 73.0029 | 72.9185 | 72.8566 | 72.82 | 72.7221 | 72.5313 | 71.7903 | 70.6244 | 85.2862 | 85.2558 | 85.2444 | 86.3983 | 86.3229 | 86.2261 | 86.1532 | 86.0383 | 85.9461 | 85.877 | 85.6614 | 85.2884 | 84.9184 | 84.5833
|  | ST |  |  | 103.1088 | 103.1088 | 103.1088 | 103.0884 | 103.068 | 103.068 | 103.0272 | 103.0272 | 103.8712 | 103.8508 | 103.8508 | 103.81 | 103.7896 | 103.7692 | 72.1155 | 72.1145 | 72.1088 | 72.0864 | 72.0637 | 72.0608 | 72.0146 | 72.0093 | 73.1044 | 73.078 | 73.0565 | 72.9828 | 72.9282 | 72.8658 | 85.2916 | 85.287 | 85.2599 | 85.2304 | 85.1988 | 85.1853 | 85.1189 | 85.0937 | 86.2656 | 86.2171 | 86.1148 | 85.9185 | 85.7361 | 85.5558
|  | SP |  |  | 76.641 | 76.641 | 76.641 | 76.641 | 76.6398 | 76.6386 | 76.6374 | 76.6362 | 76.6344 | 76.6292 | 76.6128 | 78.0909 | 78.0663 | 78.0457 | 54.3928 | 54.389 | 54.3056 | 54.3019 | 54.2866 | 54.2688 | 54.2404 | 54.2122 | 54.1751 | 54.1302 | 53.9685 | 55.1112 | 54.8525 | 54.6002 | 61.3752 | 61.3744 | 61.3588 | 61.3581 | 61.3543 | 61.35 | 61.3437 | 61.3375 | 61.329 | 61.3164 | 61.2728 | 62.6499 | 62.5815 | 62.5175
AMERSHAM | LOUDWATER BSP | MINIMUM HEADROOM | SU9064791105 | NO | 93.8941 | 93.8867 | 51.0494 | 113.9682 | 113.7015 | 113.4318 | 113.1591 | 112.8983 | 112.5284 | 112.4318 | 112.1317 | 111.2438 | 108.4809 | 104.7822 | 59.5777 | 59.5645 | 17.2975 | 107.1476 | 106.8155 | 106.4806 | 106.1428 | 105.8344 | 105.4183 | 105.1487 | 104.2805 | 101.3414 | 96.4784 | 92.1812 | 87.9636 | 87.9577 | 45.5624 | 108.495 | 108.2414 | 107.9847 | 107.7251 | 107.4739 | 107.1133 | 107.0264 | 106.761 | 102.8928 | 98.0118 | 93.697
|  | CT |  |  | 95.4494 | 95.415 | 51.0494 | 113.9682 | 113.7015 | 113.4318 | 113.1591 | 112.8983 | 112.5284 | 112.4318 | 112.1317 | 111.2438 | 108.4809 | 104.7822 | 61.764 | 61.7004 | 17.2975 | 107.1476 | 106.8155 | 106.4806 | 106.1428 | 105.8344 | 105.4183 | 105.1487 | 104.2805 | 101.3414 | 96.4784 | 92.1812 | 89.949 | 89.9204 | 45.5624 | 108.495 | 108.2414 | 107.9847 | 107.7251 | 107.4739 | 107.1133 | 107.0264 | 106.761 | 102.8928 | 98.0118 | 93.697
|  | LW |  |  | 95.4509 | 95.4176 | 51.0535 | 113.9754 | 113.8848 | 113.7939 | 113.7196 | 113.6451 | 113.563 | 113.5026 | 113.319 | 113.0039 | 111.2225 | 107.6853 | 61.7667 | 61.7052 | 17.305 | 107.1608 | 107.0073 | 106.8537 | 106.7314 | 106.6092 | 106.4809 | 106.3349 | 105.5817 | 103.5393 | 99.2884 | 95.1523 | 89.9502 | 89.9226 | 45.5658 | 108.5009 | 108.4229 | 108.3446 | 108.28 | 108.2151 | 108.1422 | 108.0915 | 107.9413 | 105.0927 | 100.8238 | 96.6701
|  | ST |  |  | 95.4594 | 95.4342 | 95.405 | 158.3611 | 113.9494 | 113.8485 | 113.7639 | 113.6784 | 113.577 | 113.5167 | 113.3354 | 113.0843 | 112.6943 | 112.4408 | 61.7823 | 61.7359 | 61.6819 | 151.6009 | 107.1456 | 106.9926 | 106.8702 | 106.7475 | 106.6146 | 106.5216 | 106.2457 | 105.4226 | 104.3739 | 102.0082 | 89.9573 | 89.9364 | 89.9121 | 152.8757 | 108.4728 | 108.3823 | 108.3053 | 108.2273 | 108.1322 | 108.0784 | 107.9161 | 107.7019 | 106.3034 | 103.5573
|  | SP |  |  | 93.8941 | 93.8867 | 93.8793 | 156.8734 | 156.8588 | 156.842 | 156.8258 | 156.8099 | 156.7905 | 156.7749 | 156.7297 | 156.6531 | 156.5772 | 156.5041 | 59.5777 | 59.5645 | 59.5515 | 149.5409 | 149.5151 | 149.4853 | 149.4566 | 149.4283 | 149.3939 | 149.3445 | 149.1502 | 148.8203 | 148.493 | 148.1786 | 87.9636 | 87.9577 | 87.9518 | 150.9471 | 150.9355 | 150.9221 | 150.9091 | 150.8964 | 150.881 | 150.8685 | 150.8325 | 150.7714 | 150.7107 | 150.6525
MANNINGTON GSP | LYTCHETT | MINIMUM HEADROOM | SY9783994358 | YES | 89.715 | 50.3045 | 41.5627 | 40.1768 | 31.3878 | 22.0724 | 11.3767 | 0.56927 | -8.6129 | -17.2908 | -49.8358 | -99.0889 | -137.6349 | -149.8127 | 37.3532 | -3.8547 | -12.9312 | -14.3667 | -23.9376 | -34.579 | -46.6519 | -58.8424 | -69.1189 | -78.8986 | -115.5169 | -171.2704 | -214.5039 | -227.6048 | 51.373 | 9.9292 | 0.84476 | -0.59723 | -10.4702 | -21.2857 | -33.5393 | -45.9114 | -56.3316 | -66.256 | -103.409 | -160.0159 | -203.8649 | -217.0869
|  | CT |  |  | 89.8672 | 60.7 | 41.5627 | 40.1768 | 35.8688 | 31.8911 | 27.8798 | 21.5398 | 15.1389 | 8.3537 | -14.7449 | -49.9647 | -77.7515 | -99.5789 | 37.5033 | 7.8715 | -12.9312 | -14.3667 | -19.2799 | -23.7743 | -28.3054 | -35.1008 | -42.1437 | -49.7595 | -75.725 | -114.792 | -145.4784 | -169.6842 | 51.5229 | 21.8661 | 0.84476 | -0.59723 | -5.5899 | -10.1522 | -14.7515 | -21.77 | -28.8972 | -36.622 | -62.9639 | -102.536 | -133.603 | -158.1211
|  | LW |  |  | 89.715 | 50.3045 | 41.7756 | 40.3547 | 31.3878 | 22.0724 | 11.3767 | 0.56927 | -8.6129 | -17.2908 | -49.8358 | -99.0889 | -137.6349 | -149.8127 | 37.3532 | -3.8547 | -12.4087 | -13.6493 | -23.9376 | -34.579 | -46.6519 | -58.8424 | -69.1189 | -78.8986 | -115.5169 | -171.2704 | -214.5039 | -227.6048 | 51.373 | 9.9292 | 1.3718 | -0.0083869 | -10.4702 | -21.2857 | -33.5393 | -45.9114 | -56.3316 | -66.256 | -103.409 | -160.0159 | -203.8649 | -217.0869
|  | ST |  |  | 90.0718 | 61.7851 | 41.8333 | 40.9741 | 37.347 | 33.6044 | 29.1482 | 24.343 | 19.0341 | 12.1677 | -11.0046 | -41.2281 | -62.4957 | -79.37 | 37.7282 | 9.1106 | -12.6343 | -13.5179 | -17.6662 | -21.91 | -26.8997 | -32.1569 | -38.076 | -45.7391 | -71.6781 | -105.572 | -129.5412 | -148.5953 | 51.7504 | 23.1255 | 1.1451 | 0.25834 | -3.9584 | -8.268 | -13.3278 | -18.8076 | -24.8069 | -32.5745 | -58.8767 | -93.2525 | -117.5763 | -136.9167
|  | SP |  |  | 90.0393 | 62.2421 | 52.9204 | 52.1418 | 51.1229 | 47.0965 | 48.7672 | 40.9187 | 33.6779 | 29.7803 | 13.9346 | -6.265 | -22.1152 | -30.4145 | 37.5384 | 9.7273 | 0.25075 | -0.83608 | -2.0046 | -6.2016 | -4.7967 | -15.1299 | -22.7187 | -27.0856 | -44.9333 | -67.5108 | -85.3568 | -94.6937 | 51.561 | 23.7481 | 14.2512 | 13.16 | 11.9718 | 7.7524 | 9.1224 | -1.2735 | -8.9081 | -13.3366 | -31.4472 | -54.5001 | -72.6082 | -82.0813
BRAMLEY (FLEE) | MAIDENHEAD BSP | MINIMUM HEADROOM | SU8648579800 | YES | 144.7162 | 144.7162 | 39.8829 | 39.8829 | 39.8825 | 39.8822 | 39.8818 | 39.8813 | 39.8806 | 39.8782 | 39.868 | 39.8613 | 39.8325 | 39.8053 | 111.8346 | 111.8049 | 42.1441 | 42.0762 | 41.8549 | 41.5931 | 41.3336 | 41.0616 | 40.7126 | 40.3456 | 39.0167 | 37.328 | 35.9248 | 22.1892 | 125.8686 | 125.8333 | 28.8602 | 28.8439 | 28.7904 | 28.7271 | 28.6644 | 28.5986 | 28.5141 | 28.424 | 28.0966 | 27.6852 | 27.3257 | 23.5959
|  | CT |  |  | 144.7162 | 144.7162 | 144.7162 | 144.7162 | 144.5259 | 144.3314 | 144.133 | 143.9248 | 143.6013 | 143.5599 | 142.6884 | 135.8652 | 130.2466 | 124.5607 | 111.8354 | 111.8062 | 111.7723 | 111.7048 | 111.4295 | 111.1507 | 110.8303 | 109.3445 | 107.4448 | 105.5034 | 99.2965 | 91.448 | 85.011 | 78.4101 | 125.8695 | 125.835 | 125.7947 | 125.7147 | 125.4238 | 125.1294 | 124.8314 | 124.5487 | 124.1334 | 123.9827 | 122.6253 | 114.9574 | 108.6645 | 102.0593
|  | LW |  |  | 144.7162 | 144.7162 | 144.7162 | 144.7162 | 144.4839 | 144.241 | 143.984 | 143.7143 | 143.2981 | 143.2396 | 139.0065 | 130.4348 | 123.9399 | 120.2459 | 111.8346 | 111.8049 | 111.7701 | 111.701 | 111.3583 | 111.0026 | 109.5591 | 107.5393 | 105.0091 | 102.7289 | 95.0677 | 85.1274 | 77.6549 | 73.3529 | 125.8686 | 125.8333 | 125.7922 | 125.7103 | 125.3472 | 124.9706 | 124.617 | 124.2453 | 123.7077 | 123.5222 | 118.4928 | 108.7935 | 101.293 | 96.9405
|  | ST |  |  | 144.7162 | 144.7162 | 144.7162 | 144.7162 | 144.6169 | 144.5153 | 144.411 | 144.3024 | 144.1325 | 144.074 | 143.8805 | 142.6412 | 138.2993 | 40.4511 | 111.853 | 111.8359 | 111.814 | 111.7861 | 111.6368 | 111.4783 | 111.3264 | 111.1626 | 110.9306 | 110.5097 | 105.2709 | 99.1934 | 94.2236 | 22.1892 | 125.8904 | 125.8701 | 125.8442 | 125.8111 | 125.6525 | 125.4836 | 125.3228 | 125.1488 | 124.9053 | 124.7571 | 124.2717 | 122.5321 | 117.6728 | 23.5959
|  | SP |  |  | 144.7162 | 144.7162 | 39.8829 | 39.8829 | 39.8825 | 39.8822 | 39.8818 | 39.8813 | 39.8806 | 39.8782 | 39.868 | 39.8613 | 39.8325 | 39.8053 | 111.8672 | 111.8575 | 42.1441 | 42.0762 | 41.8549 | 41.5931 | 41.3336 | 41.0616 | 40.7126 | 40.3456 | 39.0167 | 37.328 | 35.9248 | 34.9213 | 125.9072 | 125.8958 | 28.8602 | 28.8439 | 28.7904 | 28.7271 | 28.6644 | 28.5986 | 28.5141 | 28.424 | 28.0966 | 27.6852 | 27.3257 | 27.0637
MANNINGTON GSP | MANNINGTON BSP | MINIMUM HEADROOM | SU0759205256 | YES | 161.5444 | 144.3518 | 143.9816 | 141.135 | 136.7522 | 131.7115 | 126.1366 | 120.4522 | 108.8948 | 103.1921 | 85.9331 | 54.8395 | 10.9303 | 1.3409 | 125.7002 | 107.1899 | 106.7621 | 103.8153 | 98.7818 | 93.0784 | 86.7539 | 80.3052 | 70.0951 | 62.1437 | 40.5021 | 4.9082 | -45.5179 | -56.2284 | 137.5182 | 116.5393 | 116.1152 | 113.1747 | 108.1826 | 102.5213 | 96.2445 | 89.8445 | 79.3401 | 71.1336 | 50.3773 | 15.0696 | -34.942 | -45.5812
|  | CT |  |  | 161.714 | 144.5248 | 144.1572 | 142.1905 | 139.9849 | 137.4598 | 134.8294 | 131.4551 | 127.1442 | 122.4376 | 106.5945 | 83.6978 | 55.7073 | 38.4452 | 125.8675 | 107.3582 | 106.9303 | 104.858 | 102.3142 | 99.4797 | 96.5226 | 92.6936 | 87.7833 | 82.3348 | 63.9684 | 38.1179 | 6.2124 | -13.5544 | 137.6827 | 116.7079 | 116.2839 | 114.2182 | 111.6959 | 108.8811 | 105.9448 | 102.1447 | 97.2725 | 91.8712 | 73.6653 | 48.0027 | 16.3461 | -3.2615
|  | LW |  |  | 161.5444 | 144.3518 | 143.9816 | 141.135 | 136.7522 | 131.7115 | 126.1366 | 120.4522 | 113.4834 | 107.4553 | 85.9331 | 54.8395 | 10.9303 | 1.3409 | 125.7002 | 107.1899 | 106.7621 | 103.8153 | 98.7818 | 93.0784 | 86.7539 | 80.3052 | 72.4043 | 65.4348 | 40.5021 | 4.9082 | -45.5179 | -56.2284 | 137.5182 | 116.5393 | 116.1152 | 113.1747 | 108.1826 | 102.5213 | 96.2445 | 89.8445 | 82.0028 | 75.0932 | 50.3773 | 15.0696 | -34.942 | -45.5812
|  | ST |  |  | 161.954 | 144.7541 | 144.509 | 143.2644 | 141.4559 | 139.1073 | 136.4293 | 133.3358 | 129.457 | 123.0179 | 101.9695 | 78.0035 | 51.4187 | 36.0005 | 126.1348 | 107.6105 | 107.3251 | 106.0215 | 103.9338 | 101.299 | 98.278 | 94.7704 | 90.3566 | 83.2419 | 59.8718 | 33.2515 | 3.0335 | -14.618 | 137.9835 | 116.9588 | 116.6759 | 115.3761 | 113.3061 | 110.6895 | 107.6903 | 104.2091 | 99.8292 | 92.7576 | 69.5351 | 43.0836 | 13.0966 | -4.4128
|  | SP |  |  | 162.1647 | 162.0659 | 144.9973 | 144.4777 | 142.4697 | 135.8985 | 128.9967 | 122.0876 | 108.8948 | 103.1921 | 93.815 | 80.0378 | 69.8329 | 64.6748 | 126.3307 | 126.2152 | 107.8555 | 107.3245 | 104.221 | 97.5664 | 90.5233 | 83.4718 | 70.0951 | 62.1437 | 51.8474 | 36.8686 | 25.7561 | 20.0732 | 138.2199 | 138.084 | 117.1969 | 116.6666 | 113.431 | 106.7817 | 99.7476 | 92.7051 | 79.3401 | 71.1336 | 60.8957 | 45.9933 | 34.9385 | 29.289
BOTLEY WOOD GSP | NETLEY COMMON BSP | MINIMUM HEADROOM | SU4761512025 | NO | 172.4234 | 172.42 | 172.4166 | 232.5122 | 226.9433 | 224.7531 | 221.949 | 219.1338 | 215.7683 | 213.2341 | 204.5029 | 187.9864 | 159.0028 | 146.6952 | 124.2298 | 124.2199 | 124.1976 | 184.0714 | 183.9025 | 183.1227 | 182.1313 | 179.4132 | 175.6956 | 172.797 | 162.8364 | 143.7891 | 110.2943 | 96.1317 | 153.0314 | 153.0279 | 151.9917 | 211.0054 | 202.6676 | 200.3153 | 197.3414 | 194.3582 | 190.8089 | 188.0845 | 178.7117 | 160.8743 | 127.9203 | 113.8791
|  | CT |  |  | 173.3528 | 173.3417 | 173.3304 | 233.7132 | 233.4803 | 232.3438 | 231.0181 | 228.9096 | 226.617 | 224.4579 | 217.2932 | 202.4873 | 181.4572 | 167.4984 | 125.1394 | 125.0904 | 125.0249 | 185.3591 | 185.0625 | 184.7635 | 184.4605 | 183.7774 | 183.0503 | 182.6686 | 177.1875 | 160.3083 | 136.0789 | 120.0028 | 153.9249 | 153.1774 | 152.1097 | 211.5488 | 210.0784 | 208.6328 | 207.1799 | 204.8941 | 202.4067 | 200.035 | 192.3166 | 176.4285 | 153.4871 | 137.5495
|  | LW |  |  | 173.2684 | 173.2485 | 173.2281 | 233.1977 | 226.9433 | 224.7531 | 221.949 | 219.1338 | 215.7683 | 213.2341 | 204.5029 | 187.9864 | 159.0028 | 146.6952 | 125.0548 | 124.9967 | 124.9217 | 184.8422 | 183.9025 | 183.1227 | 182.1313 | 179.4132 | 175.6956 | 172.797 | 162.8364 | 143.7891 | 110.2943 | 96.1317 | 153.8347 | 153.0739 | 151.9917 | 211.0054 | 202.6676 | 200.3153 | 197.3414 | 194.3582 | 190.8089 | 188.0845 | 178.7117 | 160.8743 | 127.9203 | 113.8791
|  | ST |  |  | 173.3937 | 173.3869 | 173.3801 | 233.9698 | 233.91 | 233.8492 | 233.4402 | 232.2134 | 230.7363 | 229.1717 | 223.991 | 214.1616 | 198.4382 | 189.3674 | 125.1861 | 125.1613 | 125.1216 | 185.6841 | 185.5777 | 185.4644 | 185.2651 | 185.0516 | 184.7727 | 184.5908 | 184.0014 | 173.2001 | 154.8931 | 144.35 | 154.0016 | 153.7207 | 153.0741 | 213.1372 | 212.1708 | 211.0864 | 209.8032 | 208.4503 | 206.8242 | 205.0876 | 199.3995 | 188.7383 | 171.6664 | 161.7346
|  | SP |  |  | 172.4234 | 172.42 | 172.4166 | 232.5122 | 232.4847 | 233.4639 | 233.4325 | 233.3535 | 233.2565 | 233.1595 | 232.219 | 229.3702 | 225.2678 | 221.4333 | 124.2298 | 124.2199 | 124.1976 | 184.0714 | 184.0314 | 184.9961 | 184.9442 | 184.8452 | 184.7228 | 184.5952 | 184.1424 | 184.6362 | 184.0589 | 181.6918 | 153.0314 | 153.0279 | 152.8794 | 212.6705 | 212.3995 | 213.0976 | 212.6666 | 212.1996 | 211.6094 | 210.9182 | 208.4644 | 205.3051 | 200.7906 | 196.6468
MELKSHAM GSP | NORRINGTON | MINIMUM HEADROOM | ST8833564965 | NO | 250.2401 | 249.0877 | 90.1596 | 92.7937 | 83.6743 | 74.2777 | 64.4443 | 54.563 | 44.0111 | 33.8363 | -4.5094 | -67.1236 | -158.7469 | -173.9608 | 129.9635 | 128.4978 | -30.5892 | -26.2706 | -37.9041 | -49.8162 | -62.277 | -74.7918 | -88.125 | -101.1057 | -148.4862 | -220.8411 | -328.0223 | -346.7958 | 179.4186 | 178.6755 | 19.9547 | 24.2723 | 18.4355 | 12.3229 | 4.5369 | -4.8901 | -15.8145 | -26.8745 | -72.9971 | -143.9972 | -249.5652 | -268.487
|  | CT |  |  | 250.5225 | 249.4216 | 248.4486 | 245.67 | 241.114 | 236.9157 | 232.7092 | 227.306 | 227.4952 | 219.7128 | 193.1799 | 153.3024 | 99.0528 | 72.4702 | 130.2569 | 128.8504 | 127.7288 | 124.6763 | 118.8984 | 113.641 | 108.3765 | 101.5789 | 102.0677 | 92.1397 | 58.2706 | 9.7171 | -53.4659 | -83.618 | 179.6868 | 178.9848 | 178.2059 | 175.7849 | 172.8243 | 170.0087 | 167.1835 | 163.6011 | 167.2817 | 159.9523 | 132.4794 | 85.1656 | 22.9089 | -6.5283
|  | LW |  |  | 250.2401 | 249.0877 | 90.1596 | 92.7937 | 83.6743 | 74.2777 | 64.4443 | 54.563 | 44.0111 | 33.8363 | -4.5094 | -67.1236 | -158.7469 | -173.9608 | 129.9635 | 128.4978 | -30.5892 | -26.2706 | -37.9041 | -49.8162 | -62.277 | -74.7918 | -88.125 | -101.1057 | -148.4862 | -220.8411 | -328.0223 | -346.7958 | 179.4186 | 178.6755 | 19.9547 | 24.2723 | 18.4355 | 12.3229 | 4.5369 | -4.8901 | -15.8145 | -26.8745 | -72.9971 | -143.9972 | -249.5652 | -268.487
|  | ST |  |  | 250.9173 | 250.3393 | 249.2611 | 247.4418 | 242.9478 | 238.6938 | 234.4323 | 229.2718 | 229.684 | 221.3545 | 193.1326 | 156.4882 | 104.5603 | 80.6586 | 130.7304 | 129.9928 | 128.6121 | 126.6191 | 121.067 | 115.7654 | 110.4578 | 103.9998 | 104.8255 | 94.4725 | 59.2811 | 14.0396 | -46.3605 | -73.3866 | 179.979 | 179.6092 | 178.9258 | 177.3335 | 174.221 | 171.3348 | 168.439 | 164.9725 | 168.7274 | 161.4747 | 132.7658 | 89.3702 | 29.8486 | 3.4913
|  | SP |  |  | 251.3431 | 250.8488 | 248.5216 | 245.566 | 244.5171 | 243.9656 | 236.8141 | 232.1385 | 224.8175 | 221.2285 | 213.6097 | 194.2813 | 182.4743 | 175.9666 | 131.1352 | 130.5025 | 126.8762 | 122.2936 | 120.9609 | 120.0862 | 110.4181 | 105.2639 | 97.3088 | 92.8676 | 83.6692 | 59.6822 | 44.2747 | 36.9274 | 179.9406 | 179.6269 | 176.1181 | 170.9705 | 170.292 | 170.1625 | 160.8292 | 156.7784 | 150.2855 | 147.8089 | 146.1353 | 128.3939 | 116.1032 | 110.3801
NORTH HYDE GSP | NORTH HYDE (D) | MINIMUM HEADROOM | TQ1035578925 | NO | 104.1033 | 104.0107 | 104.0107 | 104.0107 | 103.9828 | 103.9813 | 103.9798 | 103.9764 | 103.9627 | 103.9608 | 103.9472 | 103.9369 | 103.0311 | 99.1536 | 89.654 | 89.5463 | 89.5373 | 89.5227 | 89.4989 | 89.473 | 89.4274 | 89.3822 | 89.3336 | 89.296 | 88.7554 | 85.6063 | 81.2267 | 76.7515 | 89.6856 | 89.5808 | 89.5736 | 89.5618 | 89.5222 | 89.517 | 89.4802 | 89.442 | 89.4002 | 89.3696 | 89.2701 | 86.1393 | 81.7113 | 77.2072
|  | CT |  |  | 104.1033 | 104.0107 | 104.0107 | 104.0107 | 104.0043 | 103.9978 | 103.9912 | 103.9844 | 103.9738 | 103.9724 | 103.9681 | 103.9469 | 103.2253 | 99.3433 | 89.654 | 89.5463 | 89.5373 | 89.5227 | 89.5006 | 89.4767 | 89.452 | 89.4089 | 89.3635 | 89.3264 | 88.9478 | 85.8219 | 81.4519 | 76.9723 | 89.6856 | 89.5808 | 89.5736 | 89.5618 | 89.5428 | 89.5222 | 89.5011 | 89.4651 | 89.4264 | 89.3964 | 89.2991 | 86.3692 | 81.9373 | 77.4321
|  | LW |  |  | 104.1033 | 104.0107 | 104.0107 | 104.0107 | 104.0026 | 103.9942 | 103.9855 | 103.9764 | 103.9627 | 103.9608 | 103.9542 | 103.9445 | 103.0311 | 99.1536 | 89.654 | 89.5463 | 89.5373 | 89.5227 | 89.4989 | 89.473 | 89.4274 | 89.3822 | 89.3336 | 89.296 | 88.7554 | 85.6063 | 81.2267 | 76.7515 | 89.6856 | 89.5808 | 89.5736 | 89.5618 | 89.5411 | 89.5186 | 89.4802 | 89.442 | 89.4002 | 89.3696 | 89.2701 | 86.1393 | 81.7113 | 77.2072
|  | ST |  |  | 104.1033 | 104.0107 | 104.0107 | 104.0107 | 104.0035 | 103.9963 | 103.9889 | 103.9812 | 103.9694 | 103.9654 | 103.9526 | 103.9423 | 103.9083 | 103.8976 | 89.6563 | 89.5585 | 89.5452 | 89.5373 | 89.5205 | 89.5014 | 89.48 | 89.4588 | 89.4233 | 89.3949 | 89.3028 | 88.0007 | 85.3569 | 82.5731 | 89.6874 | 89.5906 | 89.5798 | 89.5735 | 89.5586 | 89.5418 | 89.5232 | 89.5046 | 89.4738 | 89.4501 | 89.3735 | 88.7707 | 85.8757 | 83.0627
|  | SP |  |  | 104.1033 | 104.0107 | 104.0107 | 104.0107 | 103.9828 | 103.9813 | 103.9798 | 103.9782 | 103.9757 | 103.9689 | 103.9472 | 103.9369 | 103.9044 | 103.8772 | 89.6589 | 89.5636 | 89.5534 | 89.5508 | 89.5049 | 89.4988 | 89.4922 | 89.4858 | 89.4785 | 89.4622 | 89.4096 | 89.3163 | 89.0216 | 88.0844 | 89.6895 | 89.5947 | 89.5865 | 89.5844 | 89.5222 | 89.517 | 89.5114 | 89.506 | 89.4996 | 89.4851 | 89.4386 | 89.3615 | 89.2409 | 88.8315
NORTH HYDE GSP | NORTH HYDE 11 | MINIMUM HEADROOM | TQ1035578926 | NO | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.504 | 100.0867 | 99.6509 | 99.1991 | 97.972 | 97.2632 | 94.8536 | 89.363 | 81.1496 | 75.1432 | 98.5711 | 98.479 | 98.4601 | 98.4429 | 98.0207 | 97.5865 | 96.9671 | 96.1586 | 94.7631 | 93.919 | 91.1701 | 84.8831 | 75.5028 | 68.5451 | 98.5647 | 98.4698 | 98.4502 | 98.4326 | 98.0099 | 97.5751 | 96.9978 | 96.1649 | 94.9266 | 94.2577 | 92.032 | 85.6836 | 76.1548 | 69.076
|  | CT |  |  | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.8528 | 100.7963 | 100.7389 | 100.679 | 100.3947 | 99.7692 | 97.6724 | 92.5137 | 85.6698 | 79.6655 | 98.5711 | 98.479 | 98.4601 | 98.4429 | 98.3696 | 98.2961 | 98.2213 | 97.8633 | 97.2561 | 96.5069 | 94.0486 | 88.0935 | 80.1918 | 73.2363 | 98.5647 | 98.4698 | 98.4502 | 98.4326 | 98.3587 | 98.2847 | 98.2093 | 97.8745 | 97.3267 | 96.741 | 94.8771 | 88.9016 | 80.8653 | 73.7887
|  | LW |  |  | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.504 | 100.0867 | 99.6509 | 99.1991 | 97.972 | 97.2632 | 94.8536 | 89.363 | 81.1496 | 75.1432 | 98.5711 | 98.479 | 98.4601 | 98.4429 | 98.0207 | 97.5865 | 96.9671 | 96.1586 | 94.7631 | 93.919 | 91.1701 | 84.8831 | 75.5028 | 68.5451 | 98.5647 | 98.4698 | 98.4502 | 98.4326 | 98.0099 | 97.5751 | 96.9978 | 96.1649 | 94.9266 | 94.2577 | 92.032 | 85.6836 | 76.1548 | 69.076
|  | ST |  |  | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.0205 | 96.5899 | 91.9946 | 88.2075 | 98.5798 | 98.5555 | 98.4765 | 98.467 | 98.456 | 98.4445 | 98.4276 | 98.4106 | 98.3469 | 98.1215 | 96.7406 | 92.7339 | 87.4043 | 83.0121 | 98.5737 | 98.5486 | 98.4672 | 98.4574 | 98.446 | 98.4342 | 98.4168 | 98.3993 | 98.3699 | 98.1369 | 96.9977 | 93.5913 | 88.1908 | 83.7216
|  | SP |  |  | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.9083 | 100.8926 | 99.2044 | 97.3424 | 98.5833 | 98.5651 | 98.4917 | 98.4881 | 98.4835 | 98.4792 | 98.4735 | 98.4679 | 98.4616 | 98.45 | 98.4129 | 97.7895 | 95.7661 | 93.6066 | 98.5773 | 98.5585 | 98.4829 | 98.4792 | 98.4744 | 98.47 | 98.4641 | 98.4584 | 98.4518 | 98.4399 | 98.4017 | 97.8132 | 96.2631 | 94.4671
IVER 66KV | NORTHOLT | MINIMUM HEADROOM | TQ1155583245 | NO | 62.357 | 62.357 | 62.357 | 62.357 | 61.9683 | 61.5729 | 61.1711 | 60.7514 | 60.1044 | 60.0225 | 59.7591 | 57.7713 | 50.8528 | 44.8628 | 47.6676 | 47.6621 | 47.655 | 47.6417 | 47.243 | 46.8345 | 46.4195 | 45.9605 | 45.2741 | 45.1502 | 43.9902 | 37.6367 | 29.7052 | 22.6979 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 53.7634 | 53.368 | 52.9662 | 52.5465 | 51.8995 | 51.8175 | 51.5542 | 45.9747 | 38.1197 | 31.1102
|  | CT |  |  | 62.357 | 62.357 | 62.357 | 62.357 | 61.9683 | 61.5729 | 61.1711 | 60.7514 | 60.1044 | 60.0225 | 59.7591 | 57.7713 | 50.8528 | 44.8628 | 47.6681 | 47.663 | 47.6564 | 47.6442 | 47.243 | 46.8345 | 46.4195 | 45.9605 | 45.2741 | 45.1502 | 43.9902 | 37.6367 | 29.7052 | 22.6979 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 53.7634 | 53.368 | 52.9662 | 52.5465 | 51.8995 | 51.8175 | 51.5542 | 45.9747 | 38.1197 | 31.1102
|  | LW |  |  | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 61.1273 | 55.4917 | 49.8311 | 47.6676 | 47.6621 | 47.655 | 47.6417 | 47.6282 | 47.6142 | 47.5751 | 47.5357 | 47.4963 | 47.408 | 46.2979 | 40.9104 | 34.2618 | 27.5838 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 49.2624 | 42.6761 | 35.9959
|  | ST |  |  | 62.357 | 62.357 | 62.357 | 62.357 | 62.2903 | 62.2224 | 62.1532 | 62.0816 | 61.971 | 61.9334 | 61.8136 | 61.7173 | 59.8141 | 56.1065 | 47.6691 | 47.6652 | 47.6604 | 47.6532 | 47.5775 | 47.4988 | 47.411 | 47.3206 | 47.1831 | 47.1169 | 46.825 | 44.2554 | 39.5381 | 35.1821 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.0854 | 54.0175 | 53.9483 | 53.8767 | 53.7661 | 53.7285 | 53.6087 | 52.5041 | 47.9002 | 43.5971
|  | SP |  |  | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 62.357 | 47.6724 | 47.6712 | 47.6698 | 47.6685 | 47.6657 | 47.6625 | 47.6572 | 47.6519 | 47.6454 | 47.6342 | 47.5987 | 47.5122 | 47.0151 | 45.786 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.1521 | 54.0352
COWLEY GSP | OXFORD (OSNEY) BSP | MINIMUM HEADROOM | SP 50148 05901 | YES | 115.6378 | 114.6723 | 113.8901 | 99.409 | 96.9604 | 94.4466 | 92.6491 | 90.7555 | 88.6348 | 86.8358 | 80.9535 | 72.0404 | 64.2756 | 58.8615 | 112.9698 | 112.5815 | 112.2606 | 98.8887 | 97.7908 | 96.6567 | 95.8028 | 94.8909 | 92.7042 | 90.6482 | 83.9194 | 73.7823 | 64.6212 | 58.4728 | 102.01 | 100.8852 | 99.9757 | 85.3409 | 82.5195 | 79.6251 | 77.5672 | 75.4026 | 72.9713 | 70.8815 | 64.0416 | 53.7374 | 44.4347 | 38.19
|  | CT |  |  | 115.8382 | 114.8566 | 114.0468 | 100.0403 | 97.9661 | 95.8797 | 93.8083 | 93.0879 | 91.4636 | 89.9485 | 85.2755 | 76.2786 | 69.3122 | 61.9354 | 113.2027 | 112.8217 | 112.5039 | 99.4739 | 98.5696 | 97.6499 | 96.7544 | 96.9759 | 95.6556 | 93.9208 | 88.5675 | 78.5824 | 70.7063 | 62.1551 | 102.2014 | 101.054 | 100.1085 | 85.8325 | 83.4356 | 81.0272 | 78.6312 | 77.8033 | 75.9388 | 74.1752 | 68.7325 | 58.6176 | 50.6221 | 41.9382
|  | LW |  |  | 115.6378 | 114.6723 | 113.8901 | 99.409 | 96.9604 | 94.4466 | 92.6491 | 90.7555 | 88.6348 | 86.8358 | 80.9535 | 72.0404 | 64.2756 | 58.8615 | 112.9698 | 112.5815 | 112.2606 | 98.8887 | 97.7908 | 96.6567 | 95.8028 | 94.8909 | 92.7042 | 90.6482 | 83.9194 | 73.7823 | 64.6212 | 58.4728 | 102.01 | 100.8852 | 99.9757 | 85.3409 | 82.5195 | 79.6251 | 77.5672 | 75.4026 | 72.9713 | 70.8815 | 64.0416 | 53.7374 | 44.4347 | 38.19
|  | ST |  |  | 116.3708 | 116.0879 | 115.3602 | 113.5453 | 112.3977 | 100.6047 | 99.467 | 98.946 | 97.5644 | 96.2638 | 92.1892 | 86.6174 | 81.2579 | 76.0369 | 113.4782 | 113.3609 | 113.0799 | 111.5934 | 111.0249 | 99.8946 | 99.3166 | 99.6239 | 98.9301 | 98.3742 | 96.4511 | 90.085 | 83.8161 | 77.8955 | 102.805 | 102.4764 | 101.6254 | 99.7199 | 98.4125 | 86.4366 | 85.1445 | 84.5472 | 82.9759 | 81.4697 | 76.7434 | 70.2731 | 63.9126 | 57.8938
|  | SP |  |  | 116.7127 | 116.6217 | 116.1824 | 115.4488 | 115.0439 | 114.5814 | 114.1378 | 113.6852 | 102.6017 | 102.0553 | 100.1695 | 98.3666 | 95.6857 | 93.5543 | 113.6836 | 113.6435 | 113.4752 | 112.8009 | 112.6028 | 112.3838 | 112.1717 | 111.9561 | 101.1666 | 100.8826 | 99.9262 | 99.7312 | 98.3632 | 97.304 | 103.1845 | 103.0795 | 102.5654 | 101.8155 | 101.3535 | 100.8238 | 100.3162 | 99.7983 | 88.6337 | 88.0149 | 85.8726 | 83.7784 | 80.7351 | 78.3736
WILLESDEN GSP | PERIVALE | MINIMUM HEADROOM | TQ1755582965 | NO | 61.0647 | 86.6647 | 86.6647 | 86.6647 | 86.561 | 86.4539 | 86.3421 | 86.2262 | 86.0501 | 86.0257 | 85.9422 | 84.564 | 81.8325 | 79.2324 | 47.9299 | 81.5212 | 81.5099 | 81.4866 | 81.36 | 81.1466 | 80.8873 | 80.4427 | 79.9249 | 79.5364 | 78.3066 | 75.6661 | 72.4558 | 69.4431 | 60.4551 | 86.0551 | 86.055 | 86.0316 | 85.905 | 85.775 | 85.6436 | 85.3367 | 84.8176 | 84.4278 | 83.1938 | 80.5443 | 77.3233 | 74.2998
|  | CT |  |  | 61.0647 | 86.6647 | 86.6647 | 86.6647 | 86.6571 | 86.6493 | 86.6414 | 86.6332 | 86.6204 | 86.6188 | 86.6136 | 85.3907 | 82.8591 | 80.2698 | 47.9305 | 81.5224 | 81.5117 | 81.4897 | 81.4606 | 81.3858 | 81.2156 | 80.9165 | 80.5619 | 80.1963 | 79.0448 | 76.5057 | 73.4916 | 70.4898 | 60.4551 | 86.0551 | 86.0551 | 86.0348 | 86.0056 | 85.9762 | 85.9467 | 85.8106 | 85.4549 | 85.0879 | 83.9323 | 81.3842 | 78.3593 | 75.3467
|  | LW |  |  | 61.0647 | 86.6647 | 86.6647 | 86.6647 | 86.561 | 86.4539 | 86.3421 | 86.2262 | 86.0501 | 86.0257 | 85.9422 | 84.564 | 81.8325 | 79.2324 | 47.9299 | 81.5212 | 81.5099 | 81.4866 | 81.36 | 81.1466 | 80.8873 | 80.4427 | 79.9249 | 79.5364 | 78.3066 | 75.6661 | 72.4558 | 69.4431 | 60.4551 | 86.0551 | 86.055 | 86.0316 | 85.905 | 85.775 | 85.6436 | 85.3367 | 84.8176 | 84.4278 | 83.1938 | 80.5443 | 77.3233 | 74.2998
|  | ST |  |  | 61.0647 | 86.6647 | 86.6647 | 86.6647 | 86.6647 | 86.6647 | 86.6647 | 86.6647 | 86.6647 | 86.6647 | 86.6647 | 86.6647 | 85.9636 | 84.4204 | 47.9358 | 81.5317 | 81.5269 | 81.5189 | 81.5091 | 81.4972 | 81.4857 | 81.4742 | 81.4609 | 81.4008 | 80.883 | 79.1576 | 77.1985 | 75.2862 | 60.4551 | 86.0551 | 86.0551 | 86.0551 | 86.0542 | 86.0423 | 86.0308 | 86.0192 | 86.0058 | 85.9916 | 85.7769 | 84.0454 | 82.0791 | 80.16
|  | SP |  |  | 61.0647 | 86.6647 | 86.6647 | 86.6647 | 86.6543 | 86.6441 | 86.6338 | 86.6234 | 86.6072 | 86.5619 | 86.4185 | 86.3501 | 86.1349 | 85.9549 | 47.9393 | 81.5381 | 81.537 | 81.5358 | 81.5214 | 81.5064 | 81.4923 | 81.478 | 81.4569 | 81.4061 | 81.2453 | 81.1255 | 80.3699 | 79.3042 | 60.4551 | 86.0551 | 86.0551 | 86.0551 | 86.0446 | 86.0344 | 86.0242 | 86.0138 | 85.9975 | 85.9512 | 85.7903 | 85.6821 | 85.264 | 84.195
MANNINGTON GSP | POOLE PS (HAMWORTHY) | MINIMUM HEADROOM | SZ0021890892 | YES | 89.6612 | 81.2291 | 81.218 | 83.4489 | 83.3913 | 83.2039 | 83.0141 | 82.8218 | 82.6201 | 82.3929 | 81.5318 | 66.6198 | 62.4027 | 60.1871 | 65.297 | 56.8648 | 56.8537 | 59.7309 | 59.6734 | 59.4859 | 59.2961 | 59.1038 | 58.315 | 58.0286 | 57.1675 | 41.4275 | 36.7116 | 34.2457 | 69.2092 | 60.777 | 60.7659 | 63.4294 | 63.3718 | 63.1844 | 62.9946 | 62.8022 | 62.2273 | 61.2289 | 56.8119 | 38.8433 | 34.1118 | 31.6381
|  | CT |  |  | 89.7146 | 89.7079 | 89.7012 | 89.2947 | 89.2608 | 89.1169 | 88.9725 | 88.8273 | 91.5874 | 91.4856 | 91.1778 | 84.37 | 80.8746 | 77.5019 | 65.3503 | 65.3436 | 65.3369 | 64.9305 | 64.8965 | 64.7526 | 64.6082 | 64.463 | 67.8694 | 67.7676 | 67.4598 | 60.6813 | 56.7949 | 52.9638 | 69.2625 | 69.2559 | 69.2492 | 68.8427 | 68.8088 | 68.6622 | 68.4901 | 68.3062 | 71.5679 | 71.461 | 68.9008 | 58.1441 | 54.2454 | 50.4
|  | LW |  |  | 89.6612 | 81.2291 | 81.218 | 83.4489 | 83.3913 | 83.2039 | 83.0141 | 82.8218 | 82.6201 | 82.4926 | 82.0914 | 66.6198 | 62.4027 | 60.1871 | 65.297 | 56.8648 | 56.8537 | 59.7309 | 59.6734 | 59.4859 | 59.2961 | 59.1038 | 58.9022 | 58.7746 | 58.3854 | 41.4275 | 36.7116 | 34.2457 | 69.2092 | 60.777 | 60.7659 | 63.4294 | 63.3718 | 63.1844 | 62.9946 | 62.8022 | 62.5454 | 61.2289 | 56.8119 | 38.8433 | 34.1118 | 31.6381
|  | ST |  |  | 89.7412 | 89.7368 | 89.7323 | 89.4613 | 89.4387 | 89.3025 | 89.1659 | 89.0287 | 91.7975 | 91.224 | 89.4987 | 83.3285 | 80.2731 | 77.4111 | 65.3769 | 65.3725 | 65.368 | 65.097 | 65.0744 | 64.9382 | 64.8016 | 64.6644 | 68.0795 | 67.506 | 65.7807 | 59.8517 | 56.4764 | 53.227 | 69.2892 | 69.2847 | 69.2803 | 69.0093 | 68.9867 | 68.8505 | 68.6993 | 68.5303 | 71.7779 | 71.2044 | 68.2433 | 57.321 | 53.9357 | 50.6743
|  | SP |  |  | 89.7679 | 89.7656 | 89.7634 | 89.6279 | 89.6168 | 88.2271 | 86.8374 | 85.4477 | 82.6793 | 82.3929 | 81.5318 | 82.896 | 81.8775 | 81.4894 | 65.4036 | 65.4014 | 65.3991 | 65.2636 | 65.2525 | 63.8628 | 62.4731 | 61.0834 | 58.315 | 58.0286 | 57.1675 | 59.1781 | 58.1595 | 57.7714 | 69.3158 | 69.3136 | 69.3114 | 69.1759 | 69.1648 | 67.7751 | 66.3854 | 64.9957 | 62.2273 | 61.9394 | 61.0151 | 62.8765 | 61.8174 | 60.9557
LOVEDEAN GSP | PORTSMOUTH BSP | MINIMUM HEADROOM | SZ6341099735 | NO | 156.5373 | 156.522 | 153.6268 | 152.9686 | 152.9529 | 152.9372 | 152.9216 | 152.9059 | 152.8881 | 152.867 | 152.8009 | 150.3549 | 143.1468 | 136.4254 | 120.3124 | 120.252 | 115.9461 | 115.0389 | 115.013 | 114.9855 | 114.9532 | 114.9205 | 114.8809 | 114.8391 | 114.3457 | 105.6512 | 97.4929 | 89.8471 | 134.7042 | 134.6889 | 130.8427 | 129.507 | 129.4768 | 129.4444 | 129.4051 | 129.3654 | 129.3167 | 129.2663 | 129.0992 | 128.8507 | 124.3761 | 116.6573
|  | CT |  |  | 156.5981 | 156.5899 | 156.5815 | 156.1471 | 156.0035 | 155.8579 | 155.7104 | 155.5579 | 155.343 | 155.3033 | 155.1769 | 150.3549 | 143.1468 | 136.4254 | 120.3742 | 120.3216 | 120.2946 | 119.8273 | 119.6456 | 119.4576 | 119.2713 | 119.0541 | 118.7674 | 118.6505 | 114.9701 | 105.6512 | 97.4929 | 89.8471 | 134.7649 | 134.7567 | 134.7483 | 134.3139 | 134.1703 | 134.0248 | 133.8773 | 133.7247 | 133.5098 | 133.4701 | 133.3437 | 132.229 | 124.3761 | 116.6573
|  | LW |  |  | 156.5373 | 156.522 | 156.5063 | 155.7801 | 155.6796 | 155.5764 | 155.4698 | 155.3707 | 155.2513 | 155.2178 | 155.1122 | 150.5143 | 143.7263 | 137.1379 | 120.3124 | 120.252 | 120.2167 | 119.4555 | 119.3149 | 119.1672 | 118.9981 | 118.8344 | 118.6431 | 118.5325 | 114.3457 | 105.7402 | 98.0018 | 90.4889 | 134.7042 | 134.6889 | 134.6731 | 133.9469 | 133.8465 | 133.7432 | 133.6366 | 133.5375 | 133.4181 | 133.3846 | 133.2791 | 132.5808 | 124.8885 | 117.2813
|  | ST |  |  | 156.627 | 156.6222 | 156.6175 | 156.329 | 156.2763 | 156.2232 | 156.1694 | 156.1147 | 156.0429 | 156.017 | 155.9361 | 155.8455 | 152.1954 | 147.9982 | 120.4068 | 120.3851 | 120.3386 | 120.028 | 119.9462 | 119.8574 | 119.7573 | 119.6549 | 119.5345 | 119.4559 | 118.6622 | 112.6882 | 107.5554 | 102.7681 | 134.7939 | 134.7891 | 134.7843 | 134.4958 | 134.4432 | 134.39 | 134.3363 | 134.2815 | 134.2097 | 134.1838 | 134.103 | 134.0123 | 133.6573 | 129.6308
|  | SP |  |  | 156.6553 | 156.6529 | 153.6268 | 152.9686 | 152.9529 | 152.9372 | 152.9216 | 152.9059 | 152.8881 | 152.867 | 152.8009 | 152.7512 | 152.6454 | 152.3942 | 120.4569 | 120.4348 | 115.9461 | 115.0389 | 115.013 | 114.9855 | 114.9532 | 114.9205 | 114.8809 | 114.8391 | 114.7017 | 112.902 | 110.6204 | 108.3306 | 134.8222 | 134.8197 | 130.8427 | 129.507 | 129.4768 | 129.4444 | 129.4051 | 129.3654 | 129.3167 | 129.2663 | 129.0992 | 128.8507 | 128.5774 | 128.3039
BRAMLEY (FLEE) | PYESTOCK BSP | MINIMUM HEADROOM | SU8298354548 | YES | 111.707 | 111.707 | 111.707 | 111.707 | 111.6694 | 111.631 | 111.5918 | 111.551 | 111.4877 | 111.466 | 111.3954 | 111.3371 | 111.1442 | 110.42 | 108.6371 | 108.6287 | 108.6176 | 108.5943 | 108.5535 | 108.5107 | 108.4595 | 108.4058 | 108.2887 | 107.8812 | 106.4768 | 104.3715 | 102.6679 | 101.4977 | 108.8352 | 108.8352 | 108.8352 | 108.8352 | 108.7976 | 108.7592 | 108.72 | 108.6722 | 108.595 | 108.5566 | 108.1188 | 106.0127 | 104.3087 | 103.1381
|  | CT |  |  | 111.707 | 111.707 | 111.707 | 111.707 | 111.6932 | 111.6789 | 111.6643 | 111.6488 | 111.6245 | 111.6213 | 111.6105 | 111.555 | 111.4941 | 110.8595 | 108.6371 | 108.6287 | 108.6176 | 108.5943 | 108.5535 | 108.5132 | 108.4728 | 108.4434 | 108.3295 | 107.9821 | 106.8496 | 105.1842 | 103.6667 | 102.0481 | 108.8352 | 108.8352 | 108.8352 | 108.8352 | 108.8201 | 108.779 | 108.7377 | 108.7079 | 108.6667 | 108.6436 | 108.4917 | 106.8258 | 105.3079 | 103.6886
|  | LW |  |  | 111.707 | 111.707 | 111.707 | 111.707 | 111.7064 | 111.7052 | 111.7032 | 111.7006 | 111.6952 | 111.6943 | 111.6895 | 111.678 | 111.4122 | 110.42 | 108.6383 | 108.6308 | 108.6209 | 108.6 | 108.5693 | 108.5381 | 108.5167 | 108.4947 | 108.2887 | 107.8812 | 106.4768 | 104.3715 | 102.6679 | 101.4977 | 108.8352 | 108.8352 | 108.8352 | 108.8352 | 108.8346 | 108.8038 | 108.7818 | 108.7592 | 108.7309 | 108.7064 | 108.1188 | 106.0127 | 104.3087 | 103.1381
|  | ST |  |  | 111.707 | 111.707 | 111.707 | 111.707 | 111.6694 | 111.631 | 111.5918 | 111.551 | 111.4877 | 111.466 | 111.3954 | 111.3371 | 111.1442 | 111.0827 | 108.6417 | 108.6368 | 108.6309 | 108.621 | 108.5674 | 108.5107 | 108.4595 | 108.4058 | 108.329 | 108.2911 | 107.9847 | 106.6354 | 105.3609 | 104.0735 | 108.8352 | 108.8352 | 108.8352 | 108.8352 | 108.7976 | 108.7592 | 108.72 | 108.6722 | 108.595 | 108.5566 | 108.4309 | 108.2775 | 107.0027 | 105.7149
|  | SP |  |  | 111.707 | 111.707 | 111.707 | 111.707 | 111.707 | 111.707 | 111.707 | 111.7069 | 111.7069 | 111.7067 | 111.7055 | 111.7046 | 111.7002 | 111.6958 | 108.6472 | 108.6465 | 108.6457 | 108.645 | 108.641 | 108.6363 | 108.6317 | 108.6271 | 108.6212 | 108.6153 | 108.5931 | 108.5609 | 108.5283 | 108.5026 | 108.8352 | 108.8352 | 108.8352 | 108.8352 | 108.8352 | 108.8352 | 108.8352 | 108.8351 | 108.8351 | 108.8349 | 108.8337 | 108.8273 | 108.7939 | 108.7675
BRAMLEY (FLEE) | READING BSP | MINIMUM HEADROOM | SU7459173788 | YES | 291.0392 | 291.0136 | 290.9869 | 290.0491 | 289.9121 | 289.6571 | 288.5581 | 287.3523 | 284.9587 | 284.6862 | 281.7685 | 269.7074 | 257.9293 | 248.2093 | 223.7619 | 223.6617 | 223.5671 | 222.4871 | 221.8362 | 220.7133 | 219.2037 | 217.1924 | 214.9832 | 212.4163 | 203.5006 | 189.9782 | 176.4562 | 165.1212 | 252.6993 | 252.5989 | 252.5041 | 251.4236 | 251.1086 | 250.6726 | 247.9512 | 245.9512 | 243.7543 | 241.1966 | 232.3327 | 218.576 | 204.9011 | 193.5626
|  | CT |  |  | 291.1236 | 291.1112 | 291.0984 | 290.5396 | 290.473 | 290.311 | 290.1196 | 289.8212 | 289.4992 | 289.2252 | 282.9495 | 271.4934 | 260.3822 | 249.7503 | 223.8362 | 223.7419 | 223.6517 | 222.9304 | 222.2203 | 221.1175 | 219.2037 | 217.1924 | 214.9832 | 212.5812 | 204.6995 | 191.817 | 179.1267 | 166.8308 | 252.7736 | 252.679 | 252.5886 | 251.8667 | 251.6219 | 251.146 | 247.9512 | 245.9512 | 243.7543 | 241.3663 | 233.5307 | 220.3797 | 207.4911 | 195.2725
|  | LW |  |  | 291.0392 | 291.0136 | 290.9869 | 290.0491 | 289.9121 | 289.6571 | 289.3922 | 289.0867 | 288.6407 | 288.324 | 281.7685 | 269.7074 | 257.9293 | 248.2093 | 223.7619 | 223.6617 | 223.5671 | 222.4871 | 221.8362 | 220.7133 | 219.7574 | 217.7171 | 215.0581 | 212.4163 | 203.5006 | 189.9782 | 176.4562 | 165.1212 | 252.6993 | 252.5989 | 252.5041 | 251.4236 | 251.1086 | 250.6726 | 248.8697 | 246.4676 | 243.8231 | 241.1966 | 232.3327 | 218.576 | 204.9011 | 193.5626
|  | ST |  |  | 291.1617 | 291.1555 | 291.1493 | 290.7801 | 290.6742 | 290.4694 | 290.2625 | 290.0523 | 289.7957 | 289.2554 | 287.4154 | 281.8638 | 273.6954 | 266.2934 | 223.9485 | 223.8773 | 223.8136 | 223.3849 | 223.1899 | 222.8798 | 222.4413 | 221.9093 | 221.2645 | 220.1592 | 214.2101 | 203.9745 | 194.822 | 186.5588 | 252.8508 | 252.8148 | 252.7508 | 252.3219 | 252.1267 | 251.8162 | 251.5275 | 251.2307 | 250.8857 | 250.2435 | 242.9727 | 232.7883 | 223.5863 | 215.1553
|  | SP |  |  | 291.1978 | 291.1945 | 291.1912 | 291.0065 | 290.9693 | 289.7637 | 288.5581 | 287.3523 | 284.9587 | 284.6862 | 283.8628 | 282.4839 | 281.4835 | 281.2088 | 224.0148 | 223.9764 | 223.9385 | 223.7476 | 223.6751 | 222.4366 | 221.1997 | 219.9625 | 217.529 | 217.2192 | 216.2631 | 214.1861 | 212.0914 | 210.0452 | 252.887 | 252.8837 | 252.876 | 252.6851 | 252.6119 | 251.3733 | 250.1363 | 248.899 | 246.4654 | 246.1555 | 245.1989 | 243.6167 | 241.7586 | 238.889
BRAMLEY (FLEE) | READING TOWN BSP | MINIMUM HEADROOM | SU7154074122 | YES | 137.7747 | 137.7629 | 137.751 | 137.0273 | 136.968 | 136.9086 | 136.8493 | 136.79 | 136.7307 | 136.7069 | 136.2062 | 132.2103 | 128.4042 | 124.7014 | 105.4011 | 105.3432 | 105.2839 | 104.4709 | 104.3207 | 104.1637 | 103.5387 | 102.7658 | 101.9521 | 101.1395 | 98.43 | 93.8091 | 89.3519 | 85.007 | 124.0343 | 123.9762 | 123.9168 | 123.1035 | 122.953 | 122.8009 | 122.0545 | 121.3001 | 120.506 | 119.7148 | 117.1019 | 112.6296 | 108.3272 | 104.1349
|  | CT |  |  | 137.8317 | 137.8246 | 137.8174 | 137.3832 | 137.3476 | 137.312 | 137.2764 | 137.2408 | 137.2052 | 137.191 | 136.2062 | 132.2103 | 128.4042 | 124.7014 | 105.4579 | 105.4045 | 105.3498 | 104.8258 | 104.699 | 104.5645 | 103.5387 | 102.7658 | 101.9521 | 101.1395 | 98.43 | 93.8091 | 89.3519 | 85.007 | 124.0911 | 124.0376 | 123.9826 | 123.4584 | 123.3313 | 123.2025 | 122.0545 | 121.3001 | 120.506 | 119.7148 | 117.1019 | 112.6296 | 108.3272 | 104.1349
|  | LW |  |  | 137.7747 | 137.7629 | 137.751 | 137.0273 | 136.968 | 136.9086 | 136.8493 | 136.79 | 136.7307 | 136.7069 | 136.4868 | 132.8919 | 129.1973 | 125.4941 | 105.4011 | 105.3432 | 105.2839 | 104.4709 | 104.3207 | 104.1637 | 103.9883 | 103.2341 | 102.4027 | 101.5822 | 98.8532 | 94.6334 | 90.2876 | 85.9422 | 124.0343 | 123.9762 | 123.9168 | 123.1035 | 122.953 | 122.8009 | 122.4977 | 121.7513 | 120.9334 | 120.1328 | 117.4911 | 113.4199 | 109.229 | 105.0362
|  | ST |  |  | 137.8602 | 137.8554 | 137.8507 | 137.5612 | 137.5374 | 137.5137 | 137.49 | 137.4663 | 137.4425 | 137.433 | 137.4046 | 137.3571 | 137.0682 | 134.736 | 105.5097 | 105.489 | 105.4514 | 105.1312 | 105.069 | 104.9995 | 104.9409 | 104.8815 | 104.8279 | 104.7873 | 104.644 | 102.2439 | 99.4145 | 96.6725 | 124.143 | 124.1223 | 124.0845 | 123.7642 | 123.7019 | 123.6322 | 123.5735 | 123.514 | 123.4603 | 123.4196 | 123.2858 | 120.7943 | 118.0572 | 115.4127
|  | SP |  |  | 137.8886 | 137.8863 | 137.8839 | 137.7391 | 137.7273 | 137.7154 | 137.7036 | 137.6917 | 137.6798 | 137.6751 | 137.6608 | 137.6371 | 137.6229 | 137.5968 | 105.5491 | 105.5406 | 105.5187 | 105.3667 | 105.3375 | 105.3059 | 105.2803 | 105.2546 | 105.2261 | 105.2092 | 105.1536 | 105.0647 | 104.9803 | 104.8826 | 124.1824 | 124.1739 | 124.1519 | 123.9999 | 123.9707 | 123.939 | 123.9133 | 123.8876 | 123.8591 | 123.8421 | 123.7864 | 123.6972 | 123.6126 | 123.5147
MANNINGTON GSP | REDHILL BSP | MINIMUM HEADROOM | SZ0851296149 | YES | 104.9525 | 104.027 | 103.8963 | 103.6653 | 104.0344 | 103.9625 | 103.8223 | 103.3913 | 102.6754 | 101.9801 | 99.9247 | 67.1489 | 60.2675 | 55.4279 | 56.7924 | 55.7048 | 55.5512 | 55.2797 | 55.7137 | 55.6293 | 55.4647 | 55.223 | 54.4549 | 53.6404 | 51.2337 | 12.5658 | 4.4475 | -1.262 | 76.8705 | 75.7933 | 75.6411 | 75.3722 | 75.802 | 75.7184 | 75.5554 | 75.0275 | 74.2627 | 73.4559 | 71.0714 | 32.8429 | 24.8332 | 19.2
|  | CT |  |  | 104.9525 | 104.027 | 103.8963 | 103.6653 | 104.806 | 104.4638 | 104.1596 | 103.4449 | 102.6754 | 101.9801 | 99.9247 | 81.1535 | 75.0269 | 70.1219 | 56.7924 | 55.7048 | 55.5512 | 55.2797 | 56.8981 | 56.5088 | 56.1643 | 55.3381 | 54.4549 | 53.6404 | 51.2337 | 29.2146 | 22.033 | 16.2584 | 76.8705 | 75.7933 | 75.6411 | 75.3722 | 76.686 | 76.2997 | 75.9578 | 75.1387 | 74.2627 | 73.4559 | 71.0714 | 49.2596 | 42.1706 | 36.4723
|  | LW |  |  | 106.4164 | 105.4948 | 105.3691 | 105.1488 | 104.9134 | 104.6548 | 104.0286 | 103.3913 | 102.7418 | 102.0618 | 100.055 | 67.1489 | 60.2675 | 55.4279 | 58.7778 | 57.6948 | 57.5471 | 57.2882 | 57.0116 | 56.7077 | 55.9719 | 55.223 | 54.4597 | 53.6608 | 51.3026 | 12.5658 | 4.4475 | -1.262 | 78.5486 | 77.4759 | 77.3296 | 77.0732 | 76.7992 | 76.4981 | 75.7693 | 75.0275 | 74.2715 | 73.4801 | 71.1442 | 32.8429 | 24.8332 | 19.2
|  | ST |  |  | 105.606 | 104.9107 | 104.0245 | 103.9083 | 105.2249 | 105.052 | 104.5963 | 104.1351 | 103.6933 | 103.2286 | 101.8594 | 84.6324 | 80.4374 | 77.3413 | 57.5602 | 56.7432 | 55.7018 | 55.5653 | 57.3776 | 57.1744 | 56.639 | 56.097 | 55.5779 | 55.0318 | 53.4228 | 33.1795 | 28.2426 | 24.5901 | 77.6311 | 76.8218 | 75.7903 | 75.6551 | 77.1617 | 76.9605 | 76.4301 | 75.8933 | 75.379 | 74.8381 | 73.2444 | 53.1929 | 48.3101 | 44.7064
|  | SP |  |  | 105.8423 | 105.5975 | 104.1373 | 104.0973 | 104.0344 | 103.9625 | 103.8223 | 103.681 | 103.5024 | 104.7765 | 104.2338 | 103.0791 | 101.6894 | 100.2665 | 57.8379 | 57.5503 | 55.8344 | 55.7874 | 55.7137 | 55.6293 | 55.4647 | 55.2988 | 55.0891 | 56.8521 | 56.2162 | 54.8601 | 53.2299 | 51.5602 | 77.9062 | 77.6212 | 75.9216 | 75.875 | 75.802 | 75.7184 | 75.5554 | 75.391 | 75.1833 | 76.6411 | 76.0111 | 74.6679 | 73.0529 | 71.3989
NURSLING GSP | ROWNHAMS | MINIMUM HEADROOM | SU3723416928 | NO | 48.9125 | 47.7075 | -14.9204 | -17.2511 | -20.3982 | -23.3689 | -27.2238 | -34.1355 | -39.7604 | -43.7269 | -58.9787 | -81.9308 | -105.9534 | -115.2483 | 14.8071 | 13.4149 | -54.4976 | -57.0467 | -60.9255 | -64.2141 | -68.8855 | -78.7554 | -85.9954 | -90.9656 | -110.5962 | -139.7568 | -169.6934 | -181.0531 | -1.8899 | -3.2805 | -72.0067 | -74.554 | -78.4265 | -81.65 | -86.3145 | -96.471 | -103.7908 | -108.7524 | -128.4509 | -157.7273 | -187.7071 | -199.0491
|  | CT |  |  | 60.1488 | 59.093 | -0.25293 | -6.4949 | -8.2866 | -9.7051 | -11.7659 | -12.8666 | -16.578 | -19.7915 | -24.7659 | -41.8519 | -59.0148 | -73.1606 | 26.0519 | 24.8152 | -38.9107 | -46.6682 | -48.8918 | -50.2921 | -52.7714 | -53.999 | -58.8153 | -62.8549 | -66.4212 | -87.1804 | -108.1062 | -125.9767 | 9.3548 | 8.1197 | -56.1925 | -63.9371 | -66.157 | -67.4951 | -69.9708 | -71.4325 | -76.3017 | -80.3343 | -83.2889 | -104.0168 | -124.9105 | -142.8117
|  | LW |  |  | 48.9125 | 47.7075 | -14.9204 | -17.2511 | -20.3982 | -23.3689 | -27.2238 | -34.1355 | -39.7604 | -43.7269 | -58.9787 | -81.9308 | -105.9534 | -115.2483 | 14.8071 | 13.4149 | -54.4976 | -57.0467 | -60.9255 | -64.2141 | -68.8855 | -78.7554 | -85.9954 | -90.9656 | -110.5962 | -139.7568 | -169.6934 | -181.0531 | -1.8899 | -3.2805 | -72.0067 | -74.554 | -78.4265 | -81.65 | -86.3145 | -96.471 | -103.7908 | -108.7524 | -128.4509 | -157.7273 | -187.7071 | -199.0491
|  | ST |  |  | 60.3382 | 59.4232 | 52.588 | 46.9718 | 45.5077 | 44.2376 | 42.3461 | 41.6571 | 38.2991 | 34.0798 | 20.1473 | 3.5652 | -12.3047 | -23.5435 | 26.2776 | 25.2846 | 14.0066 | 6.9641 | 5.1589 | 3.9493 | 1.6878 | 0.98912 | -3.3709 | -8.305 | -24.7341 | -44.397 | -63.8314 | -77.7438 | 9.5803 | 8.5879 | -3.2758 | -10.3062 | -12.1085 | -13.2562 | -15.5146 | -16.4483 | -20.8622 | -25.7902 | -42.198 | -61.8346 | -81.301 | -95.1906
|  | SP |  |  | 90.2883 | 60.1665 | 53.6712 | 53.32 | 52.9707 | 48.7221 | 38.5881 | 34.2034 | 25.8244 | 24.1469 | 19.653 | 10.584 | 4.38 | 2.579 | 44.4643 | 26.1352 | 15.2548 | 14.8925 | 14.452 | 10.0956 | -4.5653 | -9.084 | -17.6363 | -19.5392 | -24.4739 | -34.7823 | -41.6436 | -42.7692 | 48.0572 | 9.4376 | -2.0291 | -2.3913 | -2.831 | -7.1865 | -22.0868 | -26.6169 | -35.1839 | -37.1059 | -42.3989 | -52.8123 | -59.6278 | -60.5489
MANNINGTON GSP | SALISBURY | MINIMUM HEADROOM | SU1106531365 | YES | 163.1571 | 163.1454 | 163.1337 | 162.131 | 161.7553 | 157.9562 | 153.6095 | 149.1914 | 143.7035 | 138.3477 | 119.089 | 89.8614 | 69.6094 | 63.1454 | 122.0834 | 121.7559 | 121.395 | 119.8625 | 115.127 | 110.3548 | 105.2614 | 100.0869 | 93.6631 | 87.3668 | 64.726 | 30.5091 | 6.7672 | -0.79808 | 145.3847 | 145.0664 | 144.7158 | 143.1311 | 138.5304 | 133.8937 | 128.9448 | 123.9165 | 117.6737 | 111.5593 | 89.5726 | 55.9363 | 32.2647 | 24.7217
|  | CT |  |  | 163.1571 | 163.1454 | 163.1337 | 162.4096 | 162.2167 | 162.1203 | 160.5561 | 158.2649 | 154.8667 | 150.7282 | 136.8664 | 117.4855 | 103.3712 | 88.612 | 122.0834 | 121.7559 | 121.395 | 119.9666 | 117.5005 | 115.5039 | 113.2845 | 110.6313 | 106.6499 | 101.7824 | 85.4787 | 62.9876 | 46.4791 | 29.1524 | 145.3847 | 145.0664 | 144.7158 | 143.308 | 140.9116 | 138.9456 | 136.7884 | 134.1765 | 130.3078 | 125.5813 | 109.7499 | 87.8603 | 71.8148 | 54.5818
|  | LW |  |  | 163.1956 | 163.176 | 163.1565 | 162.131 | 161.7553 | 157.9562 | 153.6095 | 149.1914 | 143.7035 | 138.3477 | 119.089 | 89.8614 | 69.6094 | 63.1454 | 122.1975 | 121.8616 | 121.4922 | 119.8625 | 115.127 | 110.3548 | 105.2614 | 100.0869 | 93.6631 | 87.3668 | 64.726 | 30.5091 | 6.7672 | -0.79808 | 145.4676 | 145.1409 | 144.7818 | 143.1311 | 138.5304 | 133.8937 | 128.9448 | 123.9165 | 117.6737 | 111.5593 | 89.5726 | 55.9363 | 32.2647 | 24.7217
|  | ST |  |  | 163.204 | 163.1962 | 163.1884 | 162.7061 | 162.4614 | 162.2395 | 161.7996 | 159.6413 | 156.2886 | 152.3539 | 139.0177 | 122.1325 | 109.0169 | 95.585 | 122.5676 | 122.0986 | 121.8423 | 121.0468 | 118.9401 | 117.0359 | 114.7728 | 112.3025 | 108.4176 | 103.8063 | 88.175 | 68.4226 | 53.1787 | 37.4361 | 145.8561 | 145.4006 | 145.1515 | 144.3652 | 142.3136 | 140.4333 | 138.2294 | 135.7906 | 132.0087 | 127.5282 | 112.3408 | 93.1429 | 78.3106 | 62.8391
|  | SP |  |  | 163.2509 | 163.247 | 163.2431 | 162.9439 | 162.9209 | 162.8977 | 162.8744 | 162.8118 | 162.7076 | 162.5821 | 158.2904 | 151.7729 | 146.3434 | 143.1695 | 122.763 | 122.7221 | 122.3125 | 121.9372 | 121.4172 | 120.821 | 119.936 | 119.049 | 117.8819 | 116.3699 | 110.4926 | 102.8663 | 96.499 | 92.7906 | 146.0472 | 146.0074 | 145.6096 | 145.2493 | 144.7438 | 144.1643 | 143.3046 | 142.4427 | 141.3091 | 139.8406 | 134.1077 | 126.6576 | 120.4717 | 116.8667
MANNINGTON GSP | SHAFTESBURY BSP | MINIMUM HEADROOM | ST8560523325 | YES | 116.6468 | 115.7522 | 115.6276 | 115.3376 | 112.5528 | 109.708 | 106.0465 | 102.3566 | 97.779 | 93.7082 | 78.816 | 46.4691 | 22.5627 | 16.64 | 60.4272 | 59.3692 | 59.2226 | 58.8869 | 55.6634 | 52.3732 | 48.1726 | 43.9454 | 38.7109 | 33.9758 | 16.6785 | -21.25 | -49.1248 | -55.9078 | 81.8282 | 80.8503 | 80.7144 | 80.4012 | 77.3926 | 74.3206 | 70.3842 | 66.4203 | 61.5076 | 57.098 | 40.5826 | 2.8294 | -24.9676 | -31.7337
|  | CT |  |  | 116.6542 | 115.7645 | 115.6456 | 115.3686 | 113.9734 | 112.6873 | 111.3551 | 108.8336 | 105.789 | 102.5649 | 91.651 | 70.9558 | 55.4161 | 44.1345 | 60.4351 | 59.3821 | 59.2417 | 58.9199 | 57.3086 | 55.8283 | 54.2947 | 51.452 | 47.9827 | 44.2336 | 31.5341 | 7.4949 | -10.5279 | -23.6357 | 81.8359 | 80.8629 | 80.733 | 80.4332 | 78.9278 | 77.5426 | 76.1077 | 73.4223 | 70.1612 | 66.6693 | 54.8447 | 31.4907 | 13.5166 | 0.44468
|  | LW |  |  | 116.6468 | 115.7522 | 115.6276 | 115.3376 | 112.5528 | 109.708 | 106.0465 | 102.3566 | 97.779 | 93.7082 | 78.816 | 46.4691 | 22.5627 | 16.64 | 60.4272 | 59.3692 | 59.2226 | 58.8869 | 55.6634 | 52.3732 | 48.1726 | 43.9454 | 38.7109 | 33.9758 | 16.6785 | -21.25 | -49.1248 | -55.9078 | 81.8282 | 80.8503 | 80.7144 | 80.4012 | 77.3926 | 74.3206 | 70.3842 | 66.4203 | 61.5076 | 57.098 | 40.5826 | 2.8294 | -24.9676 | -31.7337
|  | ST |  |  | 116.786 | 116.6203 | 115.743 | 115.5885 | 114.5042 | 113.4176 | 111.9491 | 110.2297 | 107.8076 | 105.0362 | 95.5752 | 77.9652 | 64.7103 | 55.4583 | 60.591 | 60.3948 | 59.3564 | 59.177 | 57.9123 | 56.6457 | 54.9532 | 52.9677 | 50.1676 | 46.9199 | 35.8227 | 15.1169 | -0.39553 | -11.2572 | 81.98 | 81.7987 | 80.8392 | 80.672 | 79.4957 | 78.3173 | 76.7346 | 74.8794 | 72.2646 | 69.2502 | 58.9548 | 39.1007 | 23.6325 | 12.8024
|  | SP |  |  | 116.8868 | 116.2936 | 115.6915 | 115.6478 | 115.3721 | 115.0552 | 114.5361 | 113.9471 | 113.1846 | 112.2329 | 108.7877 | 103.8101 | 100.0352 | 97.7354 | 60.7102 | 59.9473 | 59.2346 | 59.1839 | 58.8597 | 58.4867 | 57.8744 | 57.1947 | 56.313 | 55.2009 | 51.2282 | 45.3775 | 40.9503 | 38.2675 | 82.0901 | 81.4141 | 80.7556 | 80.7083 | 80.4079 | 80.0624 | 79.4958 | 78.8605 | 78.0372 | 77.0037 | 73.2754 | 67.8525 | 63.745 | 61.2497
IVER 132KV | SLOUGH | MINIMUM HEADROOM | SU95578175 | NO | 150.2922 | 106.1305 | 106.1218 | 70.0457 | 70.0218 | 68.6339 | 67.2459 | 65.8578 | 63.1007 | 62.7795 | 61.8078 | 60.2164 | 59.0331 | 58.4971 | 116.136 | 71.961 | 71.9579 | 48.2782 | 48.1754 | 46.6962 | 45.1987 | 43.7033 | 40.8056 | 40.3164 | 38.7145 | 36.0943 | 33.9209 | 32.5678 | 131.041 | 86.8782 | 86.8699 | 56.5375 | 56.4909 | 55.0765 | 53.6569 | 52.2378 | 49.4401 | 49.0703 | 47.9165 | 45.9403 | 44.316 | 43.4162
|  | CT |  |  | 150.3686 | 150.338 | 150.3124 | 149.6833 | 149.5161 | 149.2168 | 148.9675 | 148.6597 | 148.3622 | 148.1472 | 147.4995 | 145.3084 | 141.1083 | 135.6859 | 116.2108 | 116.2014 | 116.1921 | 115.5977 | 115.4813 | 115.2307 | 115.0281 | 114.7736 | 114.5396 | 114.3994 | 113.9995 | 107.5115 | 100.8249 | 94.2993 | 131.1172 | 131.0884 | 131.0642 | 130.4381 | 130.2751 | 129.9799 | 129.7345 | 129.4312 | 129.139 | 128.9304 | 128.3034 | 125.5844 | 121.6826 | 115.1365
|  | LW |  |  | 150.2922 | 150.2541 | 150.2207 | 149.2085 | 149.0238 | 148.6856 | 148.3957 | 148.0545 | 147.7396 | 147.4908 | 146.7203 | 143.3182 | 137.2297 | 132.7985 | 116.136 | 116.1205 | 116.1049 | 115.1307 | 115.021 | 114.7582 | 114.5423 | 114.2747 | 114.045 | 113.8841 | 111.4422 | 103.2327 | 95.9983 | 90.711 | 131.041 | 131.0048 | 130.9729 | 129.9639 | 129.7855 | 129.4536 | 129.1699 | 128.8349 | 128.5272 | 128.2858 | 127.4266 | 124.094 | 116.8384 | 111.5352
|  | ST |  |  | 150.4147 | 150.4028 | 150.381 | 149.9645 | 149.8389 | 149.6226 | 149.3495 | 149.1201 | 148.8548 | 148.1745 | 146.1769 | 143.7916 | 142.1504 | 139.3628 | 116.2481 | 116.2419 | 116.2357 | 115.8312 | 115.7348 | 115.55 | 115.3147 | 115.1267 | 114.913 | 114.2948 | 112.5054 | 109.3057 | 104.1084 | 99.228 | 131.1627 | 131.1512 | 131.1307 | 130.7153 | 130.5921 | 130.3784 | 130.1085 | 129.8826 | 129.6217 | 128.9465 | 126.9664 | 124.6071 | 122.3846 | 120.0884
|  | SP |  |  | 150.4567 | 106.1305 | 106.1218 | 70.0457 | 70.0218 | 68.6339 | 67.2459 | 65.8578 | 63.1007 | 62.7795 | 61.8078 | 60.2164 | 59.0331 | 58.4971 | 116.2855 | 71.961 | 71.9579 | 48.2782 | 48.1754 | 46.6962 | 45.1987 | 43.7033 | 40.8056 | 40.3164 | 38.7145 | 36.0943 | 33.9209 | 32.5678 | 131.2042 | 86.8782 | 86.8699 | 56.5375 | 56.4909 | 55.0765 | 53.6569 | 52.2378 | 49.4401 | 49.0703 | 47.9165 | 45.9403 | 44.316 | 43.4162
NURSLING GSP | SOUTHAMPTON (2 X 60) | MINIMUM HEADROOM | SU4143512045 | NO | 93.8479 | 93.6525 | 93.4085 | 93.7066 | 93.623 | 93.5433 | 93.2824 | 92.9026 | 89.0064 | 88.7041 | 87.6698 | 85.182 | 82.174 | 79.0699 | 56.3728 | 56.0689 | 55.6871 | 56.1756 | 56.0514 | 55.9333 | 55.7222 | 55.1923 | 49.9357 | 49.4766 | 48.117 | 45.0438 | 41.3972 | 37.769 | 66.4321 | 66.2001 | 65.9098 | 66.2719 | 66.1747 | 66.0821 | 65.9875 | 65.8895 | 60.2359 | 59.8351 | 58.652 | 56.0372 | 52.4228 | 48.7935
|  | CT |  |  | 93.9411 | 93.7626 | 93.5388 | 95.0053 | 94.6557 | 94.3238 | 93.9954 | 93.6493 | 90.9469 | 90.6586 | 89.66 | 86.4707 | 83.1894 | 80.1072 | 56.4746 | 56.194 | 55.8406 | 57.9569 | 57.4529 | 56.9778 | 56.5089 | 56.0127 | 52.3516 | 51.9065 | 50.5967 | 46.8129 | 42.9319 | 39.3529 | 66.5281 | 66.3153 | 66.0479 | 68.4757 | 68.3569 | 68.1074 | 67.6908 | 67.2505 | 62.9653 | 62.5786 | 61.4401 | 58.0604 | 54.1783 | 50.6104
|  | LW |  |  | 93.8479 | 93.6525 | 93.4085 | 94.4457 | 94.0359 | 93.6436 | 93.2824 | 92.9026 | 89.0064 | 88.7041 | 87.6698 | 85.182 | 82.174 | 79.0699 | 56.3728 | 56.0689 | 55.6871 | 57.3565 | 56.7754 | 56.2231 | 55.7222 | 55.1923 | 49.9357 | 49.4766 | 48.117 | 45.0438 | 41.3972 | 37.769 | 66.4321 | 66.2001 | 65.9098 | 67.9769 | 67.8234 | 67.3805 | 66.9316 | 66.4576 | 60.2359 | 59.8351 | 58.652 | 56.0372 | 52.4228 | 48.7935
|  | ST |  |  | 94.0138 | 93.8833 | 93.7321 | 95.507 | 95.3074 | 95.1002 | 94.9 | 94.6891 | 92.1622 | 91.9722 | 91.4063 | 89.8319 | 87.9873 | 86.205 | 56.5675 | 56.362 | 56.1231 | 58.6132 | 58.3126 | 57.9999 | 57.6983 | 57.3795 | 53.9445 | 53.6473 | 52.7626 | 50.6644 | 48.3563 | 46.187 | 66.6076 | 66.4519 | 66.2712 | 68.7459 | 68.6974 | 68.6481 | 68.5995 | 68.4956 | 64.4176 | 64.1603 | 63.3943 | 61.5816 | 59.6039 | 57.4461
|  | SP |  |  | 94.1033 | 94.0302 | 93.9547 | 93.7066 | 93.623 | 93.5433 | 93.462 | 93.3777 | 93.2815 | 93.2061 | 92.9812 | 94.7459 | 94.0715 | 93.2491 | 56.6874 | 56.572 | 56.4528 | 56.1756 | 56.0514 | 55.9333 | 55.8127 | 55.6873 | 55.5429 | 55.4258 | 55.0766 | 57.3275 | 56.2566 | 55.1929 | 66.7073 | 66.62 | 66.5298 | 66.2719 | 66.1747 | 66.0821 | 65.9875 | 65.8895 | 65.7771 | 65.6876 | 65.421 | 68.4841 | 67.5608 | 66.6709
NURSLING GSP | SOUTHAMPTON (2 X 90) | MINIMUM HEADROOM | SU4143512045 | NO | 139.2628 | 139.1741 | 139.1443 | 137.3268 | 137.1495 | 134.7159 | 130.3482 | 125.9806 | 103.2621 | 101.4687 | 96.0884 | 89.9526 | 87.4097 | 83.5772 | 101.7319 | 101.5907 | 101.5106 | 99.5957 | 99.3351 | 97.1266 | 92.735 | 88.3436 | 65.3098 | 63.4225 | 57.2544 | 49.2656 | 43.0302 | 37.8727 | 108.8067 | 108.695 | 108.6432 | 106.7831 | 106.5693 | 104.2342 | 99.8561 | 95.4781 | 72.6216 | 70.7976 | 65.3216 | 56.5534 | 50.4376 | 45.4
|  | CT |  |  | 139.4058 | 139.329 | 139.3111 | 138.2206 | 138.1312 | 137.6977 | 137.2643 | 136.8308 | 136.3973 | 136.0862 | 135.1531 | 131.2616 | 123.561 | 116.9072 | 101.8788 | 101.7524 | 101.6879 | 100.5078 | 100.3427 | 99.8214 | 99.3041 | 98.6799 | 97.9251 | 97.1995 | 94.9444 | 86.5389 | 77.4578 | 70.0126 | 108.9515 | 108.8529 | 108.8146 | 107.6849 | 107.5624 | 107.0904 | 106.6203 | 106.1458 | 105.6696 | 105.3139 | 102.5046 | 93.9575 | 85.0583 | 77.7988
|  | LW |  |  | 139.2628 | 139.1741 | 139.1443 | 137.3268 | 137.1495 | 136.5697 | 135.9885 | 135.4063 | 134.8077 | 134.4201 | 133.2547 | 129.9387 | 121.6801 | 114.6849 | 101.7319 | 101.5907 | 101.5106 | 99.5957 | 99.3351 | 98.6599 | 97.986 | 97.1153 | 96.1692 | 95.3564 | 92.8688 | 84.9592 | 75.5707 | 67.7413 | 108.8067 | 108.695 | 108.6432 | 106.7831 | 106.5693 | 105.9477 | 105.326 | 104.7027 | 104.0614 | 103.6292 | 100.2888 | 92.3926 | 83.186 | 75.5381
|  | ST |  |  | 139.4773 | 139.4065 | 139.3945 | 138.6675 | 138.608 | 138.1926 | 137.7772 | 137.3618 | 103.2621 | 101.4687 | 96.0884 | 89.9526 | 87.4097 | 83.5772 | 101.9589 | 101.8617 | 101.8053 | 101.0276 | 100.9181 | 100.4363 | 99.956 | 99.4754 | 65.3098 | 63.4225 | 57.2544 | 49.2656 | 43.0302 | 37.8727 | 109.0267 | 108.9443 | 108.9129 | 108.1637 | 108.0823 | 107.6378 | 107.194 | 106.7501 | 72.6216 | 70.7976 | 65.3216 | 56.5534 | 50.4376 | 45.4
|  | SP |  |  | 139.5488 | 139.4839 | 139.478 | 139.1145 | 139.0835 | 134.7159 | 130.3482 | 125.9806 | 118.2019 | 117.3 | 114.5935 | 109.7481 | 107.0165 | 105.869 | 102.0477 | 101.9725 | 101.9423 | 101.5652 | 101.5171 | 97.1266 | 92.735 | 88.3436 | 80.5355 | 79.6065 | 76.8147 | 71.7948 | 68.4921 | 66.5016 | 109.1058 | 109.0364 | 109.0198 | 108.6504 | 108.6119 | 104.2342 | 99.8561 | 95.4781 | 87.6865 | 86.7728 | 84.0289 | 79.1071 | 76.2822 | 74.6627
EALING GSP | SOUTHFIELD ROAD | MINIMUM HEADROOM | TQ2054579745 | NO | 48.7941 | 66.9941 | 66.9941 | 66.9941 | 66.9894 | 66.9847 | 66.98 | 66.9752 | 66.9678 | 66.9471 | 66.8814 | 66.8501 | 66.7517 | 66.6693 | 47.8867 | 63.083 | 63.0781 | 63.0682 | 63.0585 | 63.0487 | 63.0393 | 63.0365 | 63.0336 | 63.0306 | 62.965 | 62.9212 | 62.804 | 62.7011 | 48.2075 | 66.4038 | 66.3989 | 66.389 | 66.3793 | 66.3694 | 66.3601 | 66.3572 | 66.3543 | 66.3512 | 66.2859 | 66.242 | 66.1247 | 66.0218
|  | CT |  |  | 48.7941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 47.8867 | 63.083 | 63.0782 | 63.0684 | 63.0588 | 63.049 | 63.0393 | 63.0365 | 63.0336 | 63.0306 | 63.0192 | 62.9779 | 62.9215 | 62.8641 | 48.2076 | 66.4039 | 66.399 | 66.3892 | 66.3796 | 66.3698 | 66.3601 | 66.3572 | 66.3543 | 66.3512 | 66.3398 | 66.2984 | 66.2419 | 66.1842
|  | LW |  |  | 48.7941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 47.8867 | 63.083 | 63.0781 | 63.0682 | 63.0585 | 63.0487 | 63.046 | 63.0431 | 63.0402 | 63.0372 | 63.0258 | 62.9845 | 62.9282 | 62.8707 | 48.2075 | 66.4038 | 66.3989 | 66.389 | 66.3793 | 66.3694 | 66.3667 | 66.3638 | 66.3609 | 66.3579 | 66.3464 | 66.3051 | 66.2485 | 66.1909
|  | ST |  |  | 48.7941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 66.9941 | 47.8879 | 63.0851 | 63.0819 | 63.0765 | 63.07 | 63.062 | 63.059 | 63.056 | 63.054 | 63.0519 | 63.044 | 63.0147 | 62.9771 | 62.941 | 48.2087 | 66.406 | 66.4027 | 66.3974 | 66.3908 | 66.3828 | 66.3798 | 66.3767 | 66.3747 | 66.3727 | 66.3647 | 66.3353 | 66.2976 | 66.2614
|  | SP |  |  | 48.7941 | 66.9941 | 66.9941 | 66.9941 | 66.9894 | 66.9847 | 66.98 | 66.9752 | 66.9678 | 66.9471 | 66.8814 | 66.8501 | 66.7517 | 66.6693 | 47.8908 | 63.0902 | 63.0897 | 63.0891 | 63.0826 | 63.0759 | 63.0701 | 63.0642 | 63.0553 | 63.0338 | 62.965 | 62.9212 | 62.804 | 62.7011 | 48.2116 | 66.4111 | 66.4105 | 66.41 | 66.4035 | 66.3968 | 66.391 | 66.385 | 66.3762 | 66.3547 | 66.2859 | 66.242 | 66.1247 | 66.0218
LALEHAM | STAINES | MINIMUM HEADROOM | TQ0454572135 | NO | 405.9065 | 405.8952 | 405.884 | 405.1984 | 405.0698 | 404.938 | 404.8018 | 404.6618 | 404.4763 | 404.4356 | 404.3035 | 404.0878 | 398.984 | 392.3758 | 335.3526 | 335.3413 | 335.3301 | 334.6444 | 334.5159 | 333.245 | 331.326 | 329.3999 | 327.4809 | 325.7237 | 319.5901 | 310.5343 | 300.4937 | 292.7227 | 375.3225 | 375.3112 | 375.3 | 374.6144 | 374.4858 | 374.354 | 374.2178 | 374.0778 | 373.8923 | 373.8516 | 373.7195 | 373.5038 | 364.0579 | 356.5633
|  | CT |  |  | 405.9604 | 405.9537 | 405.9469 | 405.5356 | 405.5016 | 405.4673 | 405.4329 | 405.3981 | 405.3619 | 405.348 | 405.3052 | 404.7943 | 402.7145 | 395.5687 | 335.4065 | 335.3998 | 335.393 | 334.9816 | 334.9476 | 334.2539 | 332.9216 | 331.2409 | 329.622 | 327.9815 | 322.3937 | 313.7633 | 304.7546 | 296.3479 | 375.3764 | 375.3697 | 375.3629 | 374.9516 | 374.9176 | 374.8834 | 374.8489 | 374.8141 | 374.7779 | 374.764 | 374.7212 | 374.2103 | 368.1927 | 360.0858
|  | LW |  |  | 405.9065 | 405.8952 | 405.884 | 405.1984 | 405.0698 | 404.938 | 404.8018 | 404.6618 | 404.4763 | 404.4356 | 404.3035 | 404.0878 | 398.984 | 392.3758 | 335.3526 | 335.3413 | 335.3301 | 334.6444 | 334.5159 | 333.245 | 331.326 | 329.3999 | 327.4809 | 325.7237 | 319.5901 | 310.5343 | 300.4937 | 292.7227 | 375.3225 | 375.3112 | 375.3 | 374.6144 | 374.4858 | 374.354 | 374.2178 | 374.0778 | 373.8923 | 373.8516 | 373.7195 | 373.5038 | 364.0579 | 356.5633
|  | ST |  |  | 405.9874 | 405.9829 | 405.9784 | 405.7042 | 405.6676 | 405.6306 | 405.5931 | 405.5548 | 405.5074 | 405.4897 | 405.4329 | 405.3613 | 405.2402 | 405.1618 | 335.4335 | 335.429 | 335.4245 | 335.1502 | 335.1136 | 335.0766 | 334.7643 | 333.5296 | 332.3523 | 331.1458 | 327.0121 | 321.1605 | 314.8566 | 309.1833 | 375.4034 | 375.3989 | 375.3944 | 375.1202 | 375.0836 | 375.0466 | 375.0091 | 374.9708 | 374.9234 | 374.9057 | 374.8489 | 374.7773 | 374.6562 | 372.4813
|  | SP |  |  | 406.0144 | 406.0121 | 406.0099 | 405.8728 | 405.8476 | 405.8227 | 405.7977 | 405.7726 | 405.7395 | 405.6743 | 405.4675 | 405.3524 | 405.045 | 404.7735 | 335.4605 | 335.4582 | 335.456 | 335.3188 | 335.2936 | 335.2688 | 335.2438 | 335.2186 | 335.1856 | 335.1204 | 334.3608 | 331.8996 | 329.2154 | 326.7335 | 375.4304 | 375.4281 | 375.4259 | 375.2888 | 375.2636 | 375.2387 | 375.2138 | 375.1886 | 375.1555 | 375.0903 | 374.8835 | 374.7684 | 374.461 | 374.1895
MINETY GSP | STRATTON (2 X 60) | MINIMUM HEADROOM | SU1699888837 | NO | 70.0715 | 69.0555 | 56.3873 | 55.021 | 50.7053 | 46.2418 | 41.7106 | 37.1315 | 31.3973 | 25.859 | 3.3825 | -56.1476 | -90.7513 | -96.7684 | 21.6289 | 20.4135 | 7.6587 | 6.1534 | 0.99285 | -4.3184 | -9.7055 | -15.1544 | -22.1579 | -29.0311 | -56.1425 | -126.2563 | -166.8976 | -173.8783 | 29.1927 | 28.0185 | 15.2815 | 13.8049 | 8.8186 | 3.6822 | -1.5283 | -6.7977 | -13.3937 | -19.9803 | -46.7323 | -116.3818 | -156.9046 | -163.8664
|  | CT |  |  | 70.1308 | 69.1227 | 56.4612 | 55.3518 | 53.0313 | 50.8518 | 48.6701 | 46.0836 | 42.5281 | 38.257 | 21.0635 | -12.0393 | -33.4159 | -48.7893 | 21.6863 | 20.4774 | 7.7274 | 6.475 | 3.7019 | 1.1181 | -1.4672 | -4.5374 | -8.7637 | -13.8725 | -34.4519 | -74.0441 | -99.0348 | -117.0554 | 29.2505 | 28.083 | 15.3513 | 14.1284 | 11.4486 | 8.9483 | 6.4462 | 3.4758 | -0.61214 | -5.5481 | -25.3548 | -64.326 | -89.2484 | -107.2171
|  | LW |  |  | 70.0715 | 69.0555 | 56.3873 | 55.021 | 50.7053 | 46.2418 | 41.7106 | 37.1315 | 31.3973 | 25.859 | 3.3825 | -56.1476 | -90.7513 | -96.7684 | 21.6289 | 20.4135 | 7.6587 | 6.1534 | 0.99285 | -4.3184 | -9.7055 | -15.1544 | -22.1579 | -29.0311 | -56.1425 | -126.2563 | -166.8976 | -173.8783 | 29.1927 | 28.0185 | 15.2815 | 13.8049 | 8.8186 | 3.6822 | -1.5283 | -6.7977 | -13.3937 | -19.9803 | -46.7323 | -116.3818 | -156.9046 | -163.8664
|  | ST |  |  | 92.4658 | 92.205 | 56.885 | 56.2588 | 54.3497 | 52.3476 | 50.3532 | 47.9227 | 44.5484 | 40.0969 | 23.6559 | -8.3516 | -28.7813 | -42.9193 | 44.0506 | 43.7383 | 8.228 | 7.5284 | 5.2605 | 2.9016 | 0.55292 | -2.3181 | -6.3073 | -11.5416 | -31.0677 | -69.5493 | -93.3757 | -109.9702 | 51.6088 | 51.3071 | 15.8361 | 15.1516 | 12.9577 | 10.6724 | 8.3968 | 5.6167 | 1.7543 | -3.3185 | -22.0294 | -59.8967 | -83.6094 | -100.1557
|  | SP |  |  | 93.009 | 80.3186 | 79.4983 | 79.1621 | 78.6374 | 76.8729 | 74.8914 | 72.908 | 66.3066 | 64.7009 | 58.452 | 49.0138 | 42.5791 | 39.0896 | 44.6981 | 31.9116 | 30.9266 | 30.5343 | 29.9092 | 28.0329 | 25.8962 | 23.7572 | 14.895 | 13.0291 | 5.7158 | -5.0412 | -12.5131 | -16.5658 | 52.2348 | 39.4681 | 38.5171 | 38.1472 | 37.5428 | 35.6896 | 33.5849 | 31.478 | 22.5163 | 20.7041 | 13.6104 | 3.1146 | -4.1433 | -8.0799
MINETY GSP | STRATTON (2 X 90) | MINIMUM HEADROOM | SU1699888838 | YES | 107.5601 | 107.4625 | 107.3542 | 106.092 | 105.8258 | 105.1122 | 102.7193 | 100.3262 | 95.6064 | 94.9905 | 93.1255 | 89.5789 | 86.7246 | 83.2905 | 68.8049 | 68.693 | 68.5686 | 67.2754 | 66.9777 | 66.3486 | 63.9444 | 61.54 | 56.8064 | 56.1661 | 54.2248 | 50.5067 | 47.4436 | 41.6796 | 84.727 | 84.6155 | 84.4914 | 83.1988 | 82.9017 | 82.271 | 79.867 | 77.4628 | 72.7294 | 72.0897 | 70.1499 | 66.4352 | 63.3763 | 57.6593
|  | CT |  |  | 107.6538 | 107.5691 | 107.4754 | 106.6646 | 106.4497 | 106.0405 | 105.6333 | 104.911 | 104.1904 | 103.507 | 101.3862 | 95.7253 | 89.7273 | 84.5388 | 68.9 | 68.802 | 68.6936 | 67.8547 | 67.6111 | 67.1712 | 66.7337 | 65.925 | 65.1183 | 64.3432 | 61.9347 | 55.6506 | 48.9191 | 42.9964 | 84.8221 | 84.7244 | 84.6163 | 83.778 | 83.5349 | 83.0956 | 82.6588 | 81.8519 | 81.0469 | 80.2735 | 77.8709 | 71.5994 | 64.8827 | 58.9747
|  | LW |  |  | 107.5601 | 107.4625 | 107.3542 | 106.092 | 105.8258 | 105.3348 | 104.5465 | 103.7577 | 102.9707 | 102.2486 | 100.0112 | 94.7228 | 88.625 | 83.2905 | 68.8049 | 68.693 | 68.5686 | 67.2754 | 66.9777 | 66.4533 | 65.5786 | 64.7035 | 63.8303 | 63.0166 | 60.4914 | 54.5799 | 47.7486 | 41.6796 | 84.727 | 84.6155 | 84.4914 | 83.1988 | 82.9017 | 82.378 | 81.5051 | 80.6317 | 79.7602 | 78.9484 | 76.4289 | 70.53 | 63.7135 | 57.6593
|  | ST |  |  | 107.7206 | 107.658 | 107.5947 | 107.0705 | 106.9245 | 106.5623 | 106.119 | 105.6751 | 105.1195 | 103.8098 | 99.8353 | 94.1567 | 89.6006 | 86.0497 | 68.971 | 68.8985 | 68.8252 | 68.2853 | 68.1196 | 67.7331 | 67.251 | 66.7681 | 66.1538 | 64.7814 | 60.6108 | 54.505 | 49.468 | 45.4474 | 84.8931 | 84.8208 | 84.7477 | 84.208 | 84.0427 | 83.6567 | 83.1754 | 82.6933 | 82.0802 | 80.7091 | 76.5424 | 70.4453 | 65.4179 | 61.4068
|  | SP |  |  | 107.8103 | 107.787 | 107.7691 | 107.5368 | 107.4841 | 105.1122 | 102.7193 | 100.3262 | 95.6064 | 94.9905 | 93.1255 | 89.5789 | 86.7246 | 84.8872 | 69.0691 | 69.0422 | 69.0218 | 68.7869 | 68.728 | 66.3486 | 63.9444 | 61.54 | 56.8064 | 56.1661 | 54.2248 | 50.5067 | 47.4436 | 45.3902 | 84.9909 | 84.9641 | 84.9438 | 84.709 | 84.6502 | 82.271 | 79.867 | 77.4628 | 72.7294 | 72.0897 | 70.1499 | 66.4352 | 63.3763 | 61.3273
MINETY GSP | SWINDON BSP | MINIMUM HEADROOM | SP1245387050 | NO | 137.4014 | 137.9683 | 107.0872 | 103.852 | 102.3544 | 100.4655 | 98.2299 | 100.5393 | 98.0943 | 95.7161 | 87.744 | 66.8672 | 33.6078 | 25.6507 | 89.9259 | 90.5474 | 56.991 | 53.6009 | 51.7297 | 49.5773 | 47.0105 | 49.4511 | 47.3759 | 45.0811 | 36.9661 | 9.2387 | -29.3148 | -38.3418 | 102.8189 | 103.427 | 69.814 | 66.4013 | 64.4755 | 62.2683 | 59.6444 | 62.0989 | 60.019 | 57.7435 | 50.2649 | 21.8481 | -16.3687 | -25.3277
|  | CT |  |  | 137.6235 | 138.5926 | 107.3535 | 105.2285 | 104.3408 | 103.2482 | 102.0956 | 100.5393 | 98.7912 | 96.9138 | 95.2735 | 83.2679 | 61.4992 | 51.6612 | 90.1491 | 91.4642 | 57.2599 | 54.9818 | 53.8512 | 52.5509 | 51.2432 | 49.4511 | 47.3759 | 45.0811 | 45.3046 | 31.8103 | 6.3518 | -4.9788 | 103.0419 | 104.0902 | 70.0832 | 67.7827 | 66.6167 | 65.2831 | 63.942 | 62.0989 | 60.019 | 57.7435 | 58.5164 | 45.1822 | 19.9798 | 8.8098
|  | LW |  |  | 137.4014 | 138.3488 | 107.0872 | 103.852 | 102.3544 | 100.4655 | 98.2299 | 100.7693 | 98.0943 | 95.7161 | 87.744 | 66.8672 | 33.6078 | 25.6507 | 89.9259 | 91.2185 | 56.991 | 53.6009 | 51.7297 | 49.5773 | 47.0105 | 51.9874 | 48.9572 | 46.2063 | 36.9661 | 9.2387 | -29.3148 | -38.3418 | 102.8189 | 103.845 | 69.814 | 66.4013 | 64.4755 | 62.2683 | 59.6444 | 65.0714 | 62.0795 | 59.3686 | 50.2649 | 21.8481 | -16.3687 | -25.3277
|  | ST |  |  | 138.2437 | 138.8703 | 133.603 | 132.2459 | 105.6676 | 104.7374 | 103.7087 | 102.5382 | 101.1039 | 98.5528 | 95.0756 | 83.8796 | 60.4948 | 53.0979 | 90.9682 | 91.8041 | 83.5731 | 82.1333 | 55.372 | 54.2441 | 53.0121 | 51.673 | 50.0178 | 47.144 | 45.6006 | 32.8993 | 3.6508 | -4.8193 | 103.8131 | 104.4148 | 96.4057 | 94.9539 | 68.1659 | 67.0091 | 65.7445 | 64.369 | 62.6661 | 59.7867 | 58.7592 | 46.0789 | 16.5488 | 8.147
|  | SP |  |  | 138.4737 | 137.9683 | 132.8339 | 132.2456 | 132.0519 | 128.9783 | 127.0604 | 111.2711 | 105.1835 | 104.1448 | 100.6517 | 94.8112 | 90.2729 | 87.4837 | 91.2384 | 90.5474 | 82.4984 | 81.8982 | 81.6566 | 78.5277 | 76.9463 | 61.074 | 54.8798 | 53.7003 | 49.7917 | 43.373 | 38.2278 | 35.0174 | 104.079 | 103.427 | 95.5871 | 94.9851 | 94.7366 | 91.5996 | 89.7667 | 73.8822 | 67.6725 | 66.4725 | 62.4889 | 56.0171 | 50.9 | 47.7117
BRAMLEY (ANDO-THAT) | THATCHAM BSP | MINIMUM HEADROOM | SU5281066430 | YES | 271.4853 | 264.8442 | 264.5414 | 251.9587 | 249.0558 | 246.0412 | 243.0388 | 240.5506 | 237.4976 | 234.3312 | 220.3856 | 190.296 | 175.4107 | 166.9759 | 191.5446 | 181.3355 | 180.1926 | 166.3946 | 162.8497 | 159.2013 | 155.5697 | 152.5829 | 148.9245 | 145.0268 | 130.3652 | 92.7643 | 75.7234 | 66.0763 | 217.5393 | 205.6291 | 204.6444 | 191.1672 | 188.0768 | 184.8772 | 181.691 | 179.0571 | 175.8274 | 172.4474 | 158.9941 | 118.9359 | 101.7158 | 91.9679
|  | CT |  |  | 271.624 | 264.8442 | 264.5414 | 251.9587 | 249.0558 | 246.0412 | 243.0388 | 240.5506 | 237.4976 | 234.3312 | 229.6175 | 212.8064 | 199.7319 | 186.4897 | 191.7167 | 181.3355 | 180.1926 | 166.3946 | 162.8497 | 159.2013 | 155.5697 | 152.5829 | 148.9245 | 145.0268 | 141.1181 | 122.0432 | 107.2261 | 92.0029 | 217.7054 | 205.6291 | 204.6444 | 191.1672 | 188.0768 | 184.8772 | 181.691 | 179.0571 | 175.8274 | 172.4474 | 169.8734 | 150.6103 | 135.6484 | 120.2721
|  | LW |  |  | 271.4853 | 271.1445 | 270.8203 | 257.5414 | 253.6881 | 249.5678 | 246.233 | 242.8681 | 238.8513 | 234.7826 | 220.3856 | 190.296 | 175.4107 | 166.9759 | 191.5446 | 190.2837 | 189.0879 | 174.5499 | 169.7827 | 164.7241 | 160.6475 | 156.536 | 151.7541 | 147.0449 | 130.3652 | 92.7643 | 75.7234 | 66.0763 | 217.5393 | 216.443 | 215.4031 | 201.1817 | 197.0289 | 192.601 | 189.0231 | 185.4135 | 180.626 | 175.8636 | 158.9941 | 118.9359 | 101.7158 | 91.9679
|  | ST |  |  | 271.7305 | 265.1057 | 264.817 | 263.8306 | 262.0848 | 259.4129 | 257.424 | 255.2174 | 252.605 | 249.1943 | 244.1745 | 229.8396 | 212.8424 | 201.8812 | 192.023 | 182.1607 | 181.0576 | 179.11 | 176.3844 | 173.1502 | 170.7696 | 168.1194 | 164.9928 | 160.9475 | 156.6538 | 140.411 | 119.1126 | 106.5262 | 217.9793 | 206.3481 | 205.3984 | 203.6319 | 201.2535 | 198.4174 | 196.3141 | 193.9779 | 191.2154 | 187.6194 | 185.4905 | 169.0891 | 146.2035 | 133.4936
|  | SP |  |  | 271.7941 | 265.5011 | 265.388 | 265.0364 | 264.8326 | 262.8771 | 260.9128 | 258.9494 | 255.2062 | 253.9372 | 249.145 | 242.3503 | 236.915 | 233.6366 | 192.8128 | 183.5117 | 183.0831 | 182.6595 | 181.9988 | 179.4808 | 176.9289 | 174.3821 | 169.8959 | 168.3522 | 162.7075 | 154.7476 | 148.3877 | 144.5215 | 218.6723 | 207.519 | 207.1499 | 206.7398 | 206.1652 | 203.7532 | 201.312 | 198.8751 | 194.5289 | 193.1396 | 188.0985 | 180.9635 | 175.2582 | 171.8446
MINETY GSP | TOOTHILL BSP | MINIMUM HEADROOM | SU1321583986 | YES | 89.8712 | 89.0014 | 88.5996 | 87.2125 | 85.8304 | 84.3485 | 82.779 | 81.1082 | 79.1366 | 77.4163 | 69.9267 | 58.3793 | 47.3316 | 43.352 | 46.6165 | 45.6095 | 45.1454 | 43.6533 | 42.0799 | 40.3917 | 38.6032 | 36.6983 | 34.4574 | 32.4711 | 22.9923 | 9.6486 | -3.1014 | -7.6928 | 63.88 | 63.0009 | 62.5949 | 61.185 | 59.6908 | 58.0879 | 56.3899 | 54.5818 | 52.4523 | 50.576 | 40.986 | 27.4136 | 14.4468 | 9.7776
|  | CT |  |  | 89.9489 | 89.0984 | 88.7206 | 87.666 | 86.7181 | 85.7101 | 84.6537 | 83.3883 | 81.9041 | 80.3898 | 75.3173 | 66.7811 | 62.1522 | 56.9694 | 46.6974 | 45.7122 | 45.2752 | 44.1219 | 43.0325 | 41.8735 | 40.6586 | 39.2015 | 37.4935 | 35.7406 | 29.868 | 20.0717 | 16.4011 | 10.4173 | 63.9579 | 63.0984 | 62.7166 | 61.6474 | 60.6165 | 59.52 | 58.3706 | 56.9928 | 55.3774 | 53.7231 | 47.9292 | 37.9724 | 34.1807 | 28.0948
|  | LW |  |  | 89.8712 | 89.0014 | 88.5996 | 87.2125 | 85.8304 | 84.3485 | 82.779 | 81.1082 | 79.1366 | 77.4163 | 69.9267 | 58.3793 | 47.3316 | 43.352 | 46.6165 | 45.6095 | 45.1454 | 43.6533 | 42.0799 | 40.3917 | 38.6032 | 36.6983 | 34.4574 | 32.4711 | 22.9923 | 9.6486 | -3.1014 | -7.6928 | 63.88 | 63.0009 | 62.5949 | 61.185 | 59.6908 | 58.0879 | 56.3899 | 54.5818 | 52.4523 | 50.576 | 40.986 | 27.4136 | 14.4468 | 9.7776
|  | ST |  |  | 90.5085 | 89.8997 | 89.0451 | 88.4243 | 87.6689 | 86.8167 | 85.8805 | 84.8243 | 83.5196 | 82.2655 | 77.9847 | 71.0933 | 64.3124 | 60.3272 | 47.3418 | 46.6365 | 45.6461 | 44.9727 | 44.1219 | 43.1593 | 42.0997 | 40.9018 | 39.4287 | 37.9881 | 33.068 | 25.1162 | 17.3586 | 12.7751 | 64.5232 | 63.9079 | 63.0441 | 62.4198 | 61.6486 | 60.7317 | 59.7231 | 58.5838 | 57.1803 | 55.8168 | 51.1611 | 43.1101 | 35.2282 | 30.5685
|  | SP |  |  | 90.5603 | 89.7742 | 88.9899 | 88.7276 | 88.4883 | 88.2095 | 87.8811 | 87.5362 | 87.1242 | 86.6912 | 85.0893 | 83.0832 | 84.492 | 83.1455 | 47.3629 | 46.2802 | 45.371 | 45.0902 | 44.8145 | 44.493 | 44.1141 | 43.716 | 43.2401 | 42.7388 | 40.8838 | 38.5615 | 41.8445 | 40.2893 | 64.5368 | 63.5506 | 62.758 | 62.4945 | 62.2526 | 61.971 | 61.6392 | 61.268 | 60.8185 | 60.3455 | 58.5952 | 56.4037 | 59.6121 | 58.1433
IVER 132KV | UPTON BSP | MINIMUM HEADROOM | TQ0080079434 | NO | 90.6444 | 90.6444 | 90.6444 | 90.6444 | 90.5736 | 90.5017 | 90.4281 | 90.5649 | 90.2004 | 90.1337 | 89.7795 | 89.2056 | 88.2739 | 87.263 | 71.8904 | 71.8904 | 71.8904 | 71.8904 | 71.8196 | 71.7477 | 71.6741 | 71.8109 | 71.4464 | 71.3884 | 70.5779 | 66.4793 | 62.0729 | 58.6862 | 81.8992 | 81.8757 | 81.8581 | 81.8313 | 81.7514 | 81.6462 | 81.5515 | 81.6443 | 81.1894 | 81.0925 | 80.7678 | 79.7671 | 75.3961 | 72.0411
|  | CT |  |  | 90.6444 | 90.6444 | 90.6444 | 90.6444 | 90.6225 | 90.6002 | 91.5879 | 91.5639 | 91.5265 | 91.5217 | 91.4018 | 91.0841 | 90.7354 | 90.4537 | 71.8904 | 71.8904 | 71.8904 | 71.8904 | 71.8685 | 71.8462 | 72.8339 | 72.8098 | 72.7724 | 72.7676 | 72.7517 | 69.4836 | 65.8218 | 62.1203 | 81.901 | 81.8793 | 81.8636 | 81.8313 | 81.7745 | 81.7173 | 82.6697 | 82.6175 | 82.5479 | 82.507 | 82.3789 | 82.1072 | 79.1319 | 75.4653
|  | LW |  |  | 90.6444 | 90.6444 | 90.6444 | 91.6549 | 91.4104 | 91.1577 | 90.8932 | 90.6186 | 90.2004 | 90.1337 | 89.7795 | 89.2056 | 88.2739 | 87.263 | 71.8904 | 71.8904 | 71.8904 | 72.9009 | 72.6564 | 72.4037 | 72.1392 | 71.8646 | 71.4464 | 71.3884 | 70.5779 | 66.4793 | 62.0729 | 58.6862 | 81.8992 | 81.8757 | 81.8581 | 82.8322 | 82.5443 | 82.2479 | 81.9514 | 81.6443 | 81.1894 | 81.0925 | 80.7678 | 79.7671 | 75.3961 | 72.0411
|  | ST |  |  | 90.6444 | 90.6444 | 90.6444 | 90.6444 | 90.5736 | 90.5017 | 90.4281 | 91.3625 | 91.2445 | 91.2043 | 91.075 | 90.8048 | 90.3146 | 90.0417 | 71.8904 | 71.8904 | 71.8904 | 71.8904 | 71.8196 | 71.7477 | 71.6741 | 72.6085 | 72.4905 | 72.4503 | 72.321 | 71.5724 | 68.8161 | 66.2141 | 81.901 | 81.8923 | 81.8707 | 81.8502 | 81.7514 | 81.6462 | 81.5515 | 82.4638 | 82.3221 | 82.2549 | 82.0405 | 81.7936 | 81.3362 | 79.5131
|  | SP |  |  | 90.6444 | 90.6444 | 90.6444 | 90.6444 | 90.6243 | 90.6047 | 90.585 | 90.5649 | 90.5336 | 90.4465 | 90.1699 | 91.0483 | 90.6313 | 90.282 | 71.8904 | 71.8904 | 71.8904 | 71.8904 | 71.8703 | 71.8507 | 71.831 | 71.8109 | 71.7796 | 71.6925 | 71.4159 | 72.2943 | 71.8773 | 71.528 | 81.901 | 81.901 | 81.9009 | 81.899 | 81.8718 | 81.8438 | 81.8164 | 81.7886 | 81.747 | 81.6499 | 81.3398 | 82.1595 | 81.6805 | 81.273
IVER 66KV | UXBRIDGE | MINIMUM HEADROOM | TQ0496983466 | NO | 87.1267 | 87.0906 | 87.0545 | 84.8507 | 84.6686 | 83.5572 | 80.1321 | 76.707 | 69.8929 | 69.1865 | 67.0661 | 63.2579 | 60.77 | 59.9218 | 67.7078 | 67.6497 | 67.5979 | 65.3656 | 65.1209 | 64.1141 | 60.676 | 57.2379 | 50.4072 | 49.6843 | 47.4863 | 43.0752 | 38.0745 | 32.5425 | 68.4175 | 68.3814 | 68.3453 | 66.1414 | 65.9594 | 64.848 | 61.4229 | 57.9978 | 51.1837 | 50.4773 | 48.3569 | 44.5487 | 41.7227 | 36.2475
|  | CT |  |  | 87.3002 | 87.2785 | 87.2568 | 85.9345 | 85.8257 | 85.4476 | 85.0691 | 84.69 | 84.3088 | 84.0497 | 83.2705 | 79.1198 | 72.5126 | 67.0426 | 67.8796 | 67.8346 | 67.7957 | 66.4415 | 66.2812 | 65.8381 | 65.1914 | 64.4813 | 63.5387 | 62.2566 | 58.2312 | 49.8299 | 42.5342 | 36.4487 | 68.591 | 68.5693 | 68.5476 | 67.2253 | 67.1165 | 66.7384 | 66.3599 | 65.9808 | 65.5996 | 65.3405 | 61.7078 | 53.3516 | 46.1009 | 40.1132
|  | LW |  |  | 87.1267 | 87.0906 | 87.0545 | 84.8507 | 84.6686 | 84.1712 | 83.672 | 83.1711 | 82.6638 | 82.3382 | 81.3569 | 75.6796 | 68.507 | 63.5376 | 67.7078 | 67.6497 | 67.5979 | 65.3656 | 65.1209 | 64.4545 | 63.5264 | 62.4226 | 60.7844 | 59.2865 | 54.3934 | 46.0057 | 38.0745 | 32.5425 | 68.4175 | 68.3814 | 68.3453 | 66.1414 | 65.9594 | 65.4619 | 64.9628 | 64.4619 | 63.9545 | 62.7442 | 57.8882 | 49.5773 | 41.7227 | 36.2475
|  | ST |  |  | 87.3869 | 87.3724 | 87.358 | 86.4764 | 86.4039 | 86.053 | 85.7017 | 85.3501 | 84.9968 | 83.5836 | 79.3405 | 74.4841 | 71.315 | 67.1864 | 67.9727 | 67.9492 | 67.9166 | 67.0208 | 66.9215 | 66.5442 | 66.1463 | 65.6799 | 65.0292 | 63.2426 | 56.5401 | 47.9805 | 42.0574 | 37.4766 | 68.6777 | 68.6632 | 68.6488 | 67.7672 | 67.6947 | 67.3438 | 66.9925 | 66.6409 | 66.2876 | 64.8744 | 59.9955 | 51.4709 | 45.5776 | 41.0519
|  | SP |  |  | 87.4736 | 87.4664 | 87.4591 | 87.0184 | 86.9822 | 83.5572 | 80.1321 | 76.707 | 69.8929 | 69.1865 | 67.0661 | 63.2579 | 60.77 | 59.9218 | 68.0657 | 68.0547 | 68.0357 | 67.5918 | 67.5472 | 64.1141 | 60.676 | 57.2379 | 50.4072 | 49.6843 | 47.4863 | 43.0752 | 39.5458 | 37.7991 | 68.7644 | 68.7571 | 68.7499 | 68.3091 | 68.273 | 64.848 | 61.4229 | 57.9978 | 51.1837 | 50.4773 | 48.3569 | 44.5487 | 42.0608 | 41.2332
NURSLING GSP | VELMORE BSP | MINIMUM HEADROOM | SU4293519205 | NO | 138.0815 | 137.9973 | 137.9973 | 136.7659 | 136.7605 | 136.7551 | 136.7498 | 136.7443 | 136.3519 | 136.2917 | 136.0972 | 134.0013 | 124.7418 | 126.2508 | 105.0856 | 105.0014 | 105.0014 | 103.8024 | 103.797 | 103.7916 | 103.7862 | 103.7177 | 103.1822 | 103.0554 | 101.9633 | 91.6774 | 80.9485 | 80.4687 | 125.7018 | 125.6175 | 125.6175 | 124.0792 | 124.053 | 124.0241 | 123.9952 | 123.5878 | 121.8244 | 120.3683 | 115.9422 | 106.1414 | 95.4094 | 94.9253
|  | CT |  |  | 138.0815 | 137.9973 | 137.9973 | 137.9973 | 137.7141 | 137.4258 | 137.1325 | 136.8257 | 136.3519 | 136.2917 | 136.0972 | 134.0013 | 124.7418 | 127.5439 | 105.0856 | 105.0014 | 105.0014 | 105.0014 | 104.7182 | 104.4298 | 104.086 | 103.7177 | 103.1822 | 103.0554 | 101.9633 | 91.6774 | 80.9485 | 82.4841 | 125.7018 | 125.6175 | 125.6175 | 125.6175 | 125.3344 | 125.046 | 124.7527 | 123.5878 | 121.8244 | 120.3683 | 115.9422 | 106.1414 | 95.4094 | 96.9422
|  | LW |  |  | 148.1868 | 148.1026 | 148.1026 | 148.1026 | 147.9792 | 147.8508 | 147.7154 | 147.5739 | 147.3565 | 147.326 | 147.2187 | 142.7998 | 132.6369 | 126.2508 | 115.1908 | 115.1066 | 115.1066 | 115.1066 | 114.9833 | 114.8548 | 114.6605 | 114.4494 | 114.1616 | 114.0593 | 111.8801 | 99.9247 | 87.9983 | 80.4687 | 135.807 | 135.7228 | 135.7228 | 135.7228 | 135.5995 | 135.471 | 135.3357 | 133.9898 | 132.3021 | 130.7675 | 125.9469 | 114.3876 | 102.4574 | 94.9253
|  | ST |  |  | 138.0815 | 137.9973 | 137.9973 | 137.9973 | 137.9971 | 137.9966 | 137.9959 | 137.9949 | 137.9925 | 137.9914 | 137.9854 | 137.9775 | 136.9291 | 142.1908 | 105.0856 | 105.0014 | 105.0014 | 105.0014 | 105.0011 | 105.0006 | 104.9999 | 104.9989 | 104.9846 | 104.9335 | 104.7741 | 101.7344 | 94.6338 | 99.0267 | 125.7018 | 125.6175 | 125.6175 | 125.6175 | 125.6173 | 125.6168 | 125.6161 | 125.6151 | 125.6127 | 125.6116 | 122.5868 | 115.8672 | 109.0979 | 113.489
|  | SP |  |  | 138.0815 | 137.9973 | 137.9973 | 136.7659 | 136.7605 | 136.7551 | 136.7498 | 136.7443 | 136.7357 | 136.7117 | 136.6347 | 136.5973 | 136.4767 | 136.3748 | 105.0856 | 105.0014 | 105.0014 | 103.8024 | 103.797 | 103.7916 | 103.7862 | 103.7808 | 103.7722 | 103.7482 | 103.6574 | 103.5153 | 103.2867 | 103.0863 | 125.7018 | 125.6175 | 125.6175 | 124.0792 | 124.053 | 124.0241 | 123.9952 | 123.9676 | 123.9333 | 123.884 | 123.7253 | 123.5453 | 122.0894 | 119.9283
NORTH HYDE GSP | VICARAGE FARM ROAD | MINIMUM HEADROOM | TQ1236576425 | NO | 61.1191 | 60.6644 | 60.6644 | 60.6644 | 60.6391 | 60.6391 | 60.6391 | 60.6391 | 60.6391 | 60.6391 | 58.8643 | 55.2222 | 51.0845 | 46.9746 | 46.943 | 46.4539 | 46.4442 | 46.4295 | 46.4147 | 46.3985 | 46.3657 | 46.3317 | 45.941 | 45.2437 | 43.1432 | 38.9192 | 34.1203 | 29.3537 | 55.2186 | 54.7188 | 54.7061 | 54.687 | 54.6675 | 54.6463 | 54.6033 | 54.5542 | 54.2642 | 53.6122 | 51.6482 | 47.3734 | 42.4903 | 37.6401
|  | CT |  |  | 61.1191 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 59.225 | 55.5825 | 51.4455 | 47.3357 | 46.9432 | 46.4543 | 46.4449 | 46.4308 | 46.4165 | 46.4008 | 46.3845 | 46.3505 | 46.3193 | 45.6615 | 43.5615 | 39.337 | 34.539 | 29.7726 | 55.2189 | 54.7194 | 54.7071 | 54.6886 | 54.6698 | 54.6493 | 54.628 | 54.5814 | 54.5362 | 54.0029 | 52.0393 | 47.7986 | 42.9164 | 38.0664
|  | LW |  |  | 61.1191 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 58.8643 | 55.2222 | 51.0845 | 46.9746 | 46.943 | 46.4539 | 46.4442 | 46.4295 | 46.4147 | 46.3985 | 46.3657 | 46.3317 | 45.941 | 45.2437 | 43.1432 | 38.9192 | 34.1203 | 29.3537 | 55.2186 | 54.7188 | 54.7061 | 54.687 | 54.6675 | 54.6463 | 54.6033 | 54.5542 | 54.2642 | 53.6122 | 51.6482 | 47.3734 | 42.4903 | 37.6401
|  | ST |  |  | 61.1191 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 60.6644 | 58.4891 | 55.783 | 53.1494 | 46.9925 | 46.4868 | 46.4545 | 46.4482 | 46.4407 | 46.4314 | 46.4121 | 46.392 | 46.3707 | 46.3492 | 45.5934 | 42.708 | 39.5696 | 36.5152 | 55.2835 | 54.7619 | 54.7197 | 54.7114 | 54.7015 | 54.6894 | 54.6641 | 54.6377 | 54.6099 | 54.5795 | 53.9391 | 51.2287 | 48.0352 | 44.9272
|  | SP |  |  | 61.1191 | 60.6644 | 60.6644 | 60.6644 | 60.6391 | 60.6391 | 60.6391 | 60.6391 | 60.6391 | 60.6391 | 60.6391 | 60.6391 | 60.6391 | 59.7992 | 46.9946 | 46.533 | 46.4617 | 46.4596 | 46.4286 | 46.4251 | 46.4182 | 46.4111 | 46.4034 | 46.395 | 46.37 | 46.3183 | 45.5544 | 44.2035 | 55.2863 | 54.8225 | 54.7291 | 54.7264 | 54.6773 | 54.6723 | 54.6623 | 54.652 | 54.6408 | 54.6288 | 54.5926 | 54.5179 | 53.8943 | 52.6312
MANNINGTON GSP | WAREHAM | MINIMUM HEADROOM | SY9150188410 | YES | 31.7724 | 25.3379 | 25.322 | 29.5584 | 29.3639 | 26.5865 | 23.7076 | 20.8291 | 15.3071 | 14.2584 | 10.56 | -6.9765 | -17.9624 | -21.7894 | 7.5568 | -0.34874 | -0.36711 | 10.6156 | 10.3792 | 7.5527 | 4.5978 | 1.6435 | -3.977 | -5.1577 | -9.3964 | -29.4296 | -41.9782 | -46.2299 | 19.853 | 12.0323 | 12.0206 | 14.013 | 13.8644 | 11.0555 | 8.1279 | 5.2008 | -0.38447 | -1.5178 | -5.563 | -23.8553 | -36.3849 | -40.6314
|  | CT |  |  | 31.9298 | 31.8721 | 31.7892 | 35.1065 | 34.2314 | 33.226 | 32.2049 | 30.869 | 29.1583 | 27.2599 | 20.8744 | 7.9795 | -0.025191 | -7.1081 | 10.1861 | 10.1206 | 10.0245 | 20.0642 | 19.0332 | 17.8872 | 16.7227 | 15.1787 | 13.1868 | 10.9375 | 3.357 | -11.5613 | -20.7114 | -28.9794 | 22.8108 | 22.7487 | 22.6584 | 23.7101 | 22.7471 | 21.6623 | 20.5603 | 19.107 | 17.2377 | 15.1413 | 8.0816 | -6.0191 | -15.1566 | -23.4115
|  | LW |  |  | 31.7724 | 31.7017 | 31.6056 | 34.123 | 32.3844 | 30.3748 | 28.1738 | 25.944 | 23.2599 | 20.8057 | 12.0253 | -6.9765 | -17.9624 | -21.7894 | 10.0288 | 9.9501 | 9.8409 | 19.0807 | 17.0228 | 14.6884 | 12.1245 | 9.5274 | 6.3911 | 3.4833 | -6.9481 | -29.4296 | -41.9782 | -46.2299 | 22.6535 | 22.5783 | 22.4748 | 22.7266 | 20.8079 | 18.615 | 16.2093 | 13.7722 | 10.833 | 8.1229 | -1.589 | -23.8553 | -36.3849 | -40.6314
|  | ST |  |  | 32.0272 | 31.9905 | 31.9403 | 35.7248 | 34.9975 | 34.059 | 33.0269 | 31.8254 | 30.2395 | 27.5721 | 18.866 | 5.867 | -1.5287 | -7.9033 | 10.2874 | 10.2459 | 10.188 | 20.7088 | 19.8521 | 18.7843 | 17.604 | 16.2197 | 14.377 | 11.3831 | 1.555 | -13.3614 | -21.7944 | -29.2506 | 22.9104 | 22.871 | 22.8165 | 24.3432 | 23.5429 | 22.5315 | 21.4158 | 20.1111 | 18.3803 | 15.5287 | 6.1896 | -7.8912 | -16.2442 | -23.6885
|  | SP |  |  | 33.2118 | 25.3379 | 25.322 | 29.5584 | 29.3639 | 26.5865 | 23.7076 | 20.8291 | 15.3071 | 14.2584 | 10.56 | 5.0115 | 1.0075 | -0.92914 | 7.5568 | -0.34874 | -0.36711 | 10.6156 | 10.3792 | 7.5527 | 4.5978 | 1.6435 | -3.977 | -5.1577 | -9.3964 | -15.6433 | -20.1829 | -22.4171 | 19.853 | 12.0323 | 12.0206 | 14.013 | 13.8644 | 11.0555 | 8.1279 | 5.2008 | -0.38447 | -1.5178 | -5.563 | -11.5596 | -15.9073 | -18.035
MELKSHAM GSP | WEST GRAFTON | MINIMUM HEADROOM | SU2432759109 | YES | 73.8917 | 73.7589 | 73.5942 | 73.2668 | 72.2247 | 71.1829 | 70.0915 | 68.9992 | 67.6741 | 66.3697 | 61.7361 | 51.2548 | 46.8614 | 44.7089 | 48.0461 | 47.9095 | 47.7401 | 47.4033 | 46.3315 | 45.2601 | 44.1378 | 43.0145 | 41.6523 | 40.3102 | 35.5424 | 24.7582 | 20.2416 | 18.0278 | 62.8184 | 62.7021 | 62.5579 | 62.2703 | 61.3499 | 60.2025 | 58.9542 | 57.7047 | 56.1913 | 54.6808 | 49.2245 | 36.8861 | 31.7375 | 29.2093
|  | CT |  |  | 73.8936 | 73.7622 | 73.5991 | 73.2744 | 72.6365 | 72.0542 | 71.4702 | 70.7739 | 69.8782 | 68.8323 | 65.3528 | 58.8174 | 55.3185 | 51.3204 | 48.0481 | 47.9129 | 47.745 | 47.411 | 46.7553 | 46.1571 | 45.5571 | 44.8416 | 43.9214 | 42.8453 | 39.2653 | 32.5454 | 28.9505 | 24.8386 | 62.8204 | 62.7055 | 62.5628 | 62.2779 | 61.7157 | 61.1681 | 60.5382 | 59.7452 | 58.7252 | 57.5261 | 53.4924 | 45.8256 | 41.7383 | 37.0426
|  | LW |  |  | 73.8917 | 73.7589 | 73.5942 | 73.2668 | 72.2247 | 71.1829 | 70.0915 | 68.9992 | 67.6741 | 66.3697 | 61.7361 | 51.2548 | 46.8614 | 44.7089 | 48.0461 | 47.9095 | 47.7401 | 47.4033 | 46.3315 | 45.2601 | 44.1378 | 43.0145 | 41.6523 | 40.3102 | 35.5424 | 24.7582 | 20.2416 | 18.0278 | 62.8184 | 62.7021 | 62.5579 | 62.2703 | 61.3499 | 60.2025 | 58.9542 | 57.7047 | 56.1913 | 54.6808 | 49.2245 | 36.8861 | 31.7375 | 29.2093
|  | ST |  |  | 74.0196 | 73.8527 | 73.7526 | 73.5887 | 73.1151 | 72.6235 | 72.1486 | 71.5918 | 70.8272 | 69.8929 | 66.7499 | 60.9575 | 58.1439 | 54.7919 | 48.1777 | 48.0059 | 47.9029 | 47.7343 | 47.2473 | 46.7419 | 46.2536 | 45.681 | 44.8949 | 43.9336 | 40.6996 | 34.7388 | 31.8467 | 28.3977 | 62.9305 | 62.7846 | 62.6971 | 62.5533 | 62.137 | 61.7049 | 61.2685 | 60.6665 | 59.7985 | 58.7271 | 55.1177 | 48.2927 | 44.9977 | 41.0512
|  | SP |  |  | 74.0981 | 74.0718 | 73.9715 | 73.9474 | 73.8252 | 73.6866 | 73.4977 | 73.3108 | 73.0662 | 72.7476 | 71.5022 | 69.8359 | 68.4687 | 67.6097 | 48.2586 | 48.2315 | 48.1282 | 48.1035 | 47.9778 | 47.8352 | 47.6408 | 47.4485 | 47.1968 | 46.8691 | 45.5878 | 43.873 | 42.4671 | 41.5841 | 62.9992 | 62.9762 | 62.8885 | 62.8673 | 62.7601 | 62.6386 | 62.4731 | 62.3094 | 62.0952 | 61.8157 | 60.5641 | 58.652 | 57.0883 | 56.1078
NURSLING GSP | WINCHESTER | MINIMUM HEADROOM | SU4498126740 | NO | 124.7286 | 112.3234 | 82.7601 | 81.3385 | 69.7162 | 57.9884 | 46.5878 | 35.0831 | 25.1603 | 15.5441 | -20.3661 | -66.7051 | -109.0951 | -117.0582 | 71.9891 | 59.4866 | 25.7545 | 24.0787 | 10.4613 | -3.2802 | -16.5868 | -30.0058 | -41.5273 | -52.7481 | -94.6143 | -148.7258 | -198.1876 | -207.2392 | 88.4947 | 75.9921 | 42.2508 | 40.5743 | 26.9526 | 13.2067 | -0.10419 | -13.5275 | -25.0524 | -36.2768 | -78.1561 | -132.2848 | -181.6114 | -190.6412
|  | CT |  |  | 124.7286 | 112.3878 | 106.118 | 81.36 | 75.4647 | 70.24 | 64.9793 | 58.9612 | 53.0502 | 45.7593 | 20.5165 | -8.9532 | -35.336 | -54.8 | 71.9891 | 59.5399 | 53.145 | 24.0787 | 17.1621 | 11.0348 | 4.8671 | -2.0957 | -8.9403 | -17.4368 | -46.8622 | -81.0127 | -111.5187 | -134.02 | 88.4947 | 76.0454 | 69.6502 | 40.5743 | 33.6555 | 27.5262 | 21.3565 | 14.3915 | 7.5449 | -0.95427 | -30.3889 | -64.5497 | -95.0648 | -117.5728
|  | LW |  |  | 124.7578 | 112.3234 | 82.7601 | 81.3385 | 69.7162 | 57.9884 | 46.5878 | 35.0831 | 25.1603 | 15.5441 | -20.3661 | -66.7051 | -109.0951 | -117.0582 | 72.0246 | 59.4866 | 25.7545 | 24.0873 | 10.4613 | -3.2802 | -16.5868 | -30.0058 | -41.5273 | -52.7481 | -94.6143 | -148.7258 | -198.1876 | -207.2392 | 88.5303 | 75.9921 | 42.2508 | 40.583 | 26.9526 | 13.2067 | -0.10419 | -13.5275 | -25.0524 | -36.2768 | -78.1561 | -132.2848 | -181.6114 | -190.6412
|  | ST |  |  | 125.2844 | 124.2458 | 123.6327 | 88.7098 | 78.797 | 74.1824 | 69.7348 | 64.1142 | 58.6822 | 51.8594 | 28.0694 | 1.659 | -22.0425 | -39.023 | 72.6413 | 71.5148 | 70.8286 | 31.756 | 21.0411 | 15.6321 | 10.4412 | 3.8783 | -2.4438 | -10.4274 | -38.2634 | -69.1452 | -96.7619 | -116.58 | 89.1472 | 88.0205 | 87.3341 | 48.2523 | 37.5356 | 32.1249 | 26.9324 | 20.3674 | 14.0433 | 6.0572 | -21.7878 | -52.6794 | -80.3047 | -100.1291
|  | SP |  |  | 140.6217 | 122.1448 | 121.9566 | 121.888 | 120.4992 | 118.9005 | 105.6085 | 98.0935 | 95.1246 | 91.2286 | 77.5203 | 56.2388 | 39.8495 | 31.3446 | 104.6116 | 68.7458 | 68.5351 | 68.4546 | 66.8251 | 64.9491 | 51.2734 | 43.3802 | 39.9116 | 35.3509 | 19.5659 | -5.3769 | -24.5333 | -34.4358 | 122.1642 | 85.6051 | 85.3944 | 85.3139 | 83.6839 | 81.8073 | 68.1307 | 60.2367 | 56.767 | 52.2049 | 36.0601 | 11.1091 | -8.0534 | -17.9589
MANNINGTON GSP | WINFRITH HEATH | MINIMUM HEADROOM | SY8070586455 | YES | 23.9531 | 23.8974 | -20.7221 | -20.8469 | -22.4579 | -24.1172 | -25.8599 | -27.6408 | -29.8538 | -32.0118 | -39.9238 | -54.0645 | -70.7626 | -72.2869 | 15.0326 | 14.9634 | -38.4759 | -38.6203 | -40.5011 | -42.4369 | -44.4686 | -46.5464 | -49.125 | -51.6467 | -60.8894 | -77.4021 | -96.8857 | -98.6584 | 18.9828 | 18.9156 | -32.7918 | -32.9319 | -34.7523 | -36.6263 | -38.5933 | -40.6047 | -43.1015 | -45.5418 | -54.4868 | -70.4688 | -89.3293 | -91.0464
|  | CT |  |  | 23.9651 | 23.9173 | 23.8415 | -20.7997 | -21.5644 | -22.2639 | -23.0016 | -23.9634 | -25.2794 | -26.9161 | -32.5049 | -40.7471 | -50.1798 | -55.3963 | 15.046 | 14.9855 | 14.8893 | -38.5689 | -39.4624 | -40.2791 | -41.1403 | -42.2631 | -43.7986 | -45.7112 | -52.2411 | -61.8475 | -72.8379 | -78.9108 | 18.9959 | 18.9373 | 18.8442 | -32.8815 | -33.7461 | -34.5366 | -35.3702 | -36.4569 | -37.9433 | -39.7942 | -46.1136 | -55.4147 | -66.0567 | -71.9379
|  | LW |  |  | 23.9531 | 23.8974 | -20.7221 | -20.8469 | -22.4579 | -24.1172 | -25.8599 | -27.6408 | -29.8538 | -32.0118 | -39.9238 | -54.0645 | -70.7626 | -72.2869 | 15.0326 | 14.9634 | -38.4759 | -38.6203 | -40.5011 | -42.4369 | -44.4686 | -46.5464 | -49.125 | -51.6467 | -60.8894 | -77.4021 | -96.8857 | -98.6584 | 18.9828 | 18.9156 | -32.7918 | -32.9319 | -34.7523 | -36.6263 | -38.5933 | -40.6047 | -43.1015 | -45.5418 | -54.4868 | -70.4688 | -89.3293 | -91.0464
|  | ST |  |  | 23.968 | 23.9291 | 23.873 | -20.7295 | -21.3942 | -22.0659 | -22.7605 | -23.6489 | -24.88 | -26.4392 | -31.8265 | -39.6573 | -48.8095 | -53.7286 | 15.0494 | 14.9997 | 14.9281 | -38.4883 | -39.2645 | -40.0488 | -40.8594 | -41.8966 | -43.3328 | -45.1547 | -51.4477 | -60.5965 | -71.2704 | -77.012 | 18.9993 | 18.9512 | 18.8819 | -32.8031 | -33.5544 | -34.3135 | -35.0982 | -36.1021 | -37.4923 | -39.2555 | -45.3459 | -54.1998 | -64.5333 | -70.0909
|  | SP |  |  | 23.9933 | 23.9774 | 23.9541 | 23.9374 | 23.7766 | -20.9702 | -21.2732 | -21.5818 | -21.9681 | -22.4815 | -24.6154 | -27.3416 | -29.3946 | -30.4679 | 15.0818 | 15.0614 | 15.0317 | 15.0104 | 14.8051 | -38.7696 | -39.1238 | -39.4846 | -39.9362 | -40.5362 | -43.0295 | -46.2156 | -48.6084 | -49.8557 | 19.0306 | 19.0109 | 18.9822 | 18.9616 | 18.7629 | -33.0753 | -33.4181 | -33.7673 | -34.2042 | -34.7848 | -37.1977 | -40.2809 | -42.5977 | -43.8061
COWLEY GSP | WITNEY BSP | MINIMUM HEADROOM | SP3560808335 | YES | 131.7121 | 106.9062 | 72.5384 | 70.8035 | 67.2118 | 63.3486 | 59.4148 | 55.4362 | 50.5001 | 46.2071 | 31.1219 | 10.0972 | -10.1017 | -16.3494 | 71.5711 | 40.8119 | 0.27133 | -1.5932 | -5.7483 | -10.1846 | -14.6985 | -19.2638 | -24.9148 | -29.9261 | -47.5507 | -71.9648 | -95.2314 | -102.3788 | 84.4725 | 54.6726 | 15.183 | 13.3405 | 9.2814 | 4.9426 | 0.52751 | -3.9378 | -9.4671 | -14.3561 | -31.9489 | -56.3703 | -79.6434 | -86.7928
|  | CT |  |  | 131.7905 | 130.969 | 106.5872 | 71.2799 | 69.3781 | 67.428 | 65.5243 | 63.293 | 60.4058 | 57.0827 | 46.1951 | 31.506 | 18.0313 | 5.9151 | 71.6483 | 70.6982 | 40.4204 | -1.1237 | -3.3473 | -5.5972 | -7.7916 | -10.3713 | -13.7173 | -17.6049 | -30.3491 | -47.2371 | -62.7713 | -76.8524 | 84.5495 | 83.5746 | 54.2934 | 13.8112 | 11.6424 | 9.4436 | 7.2986 | 4.7783 | 1.5104 | -2.2811 | -14.7427 | -31.6354 | -47.1741 | -61.2594
|  | LW |  |  | 131.7121 | 106.9062 | 72.5384 | 70.8035 | 67.2118 | 63.3486 | 59.4148 | 55.4362 | 50.5001 | 46.2071 | 31.1219 | 10.0972 | -10.1017 | -16.3494 | 71.5711 | 40.8119 | 0.27133 | -1.5932 | -5.7483 | -10.1846 | -14.6985 | -19.2638 | -24.9148 | -29.9261 | -47.5507 | -71.9648 | -95.2314 | -102.3788 | 84.4725 | 54.6726 | 15.183 | 13.3405 | 9.2814 | 4.9426 | 0.52751 | -3.9378 | -9.4671 | -14.3561 | -31.9489 | -56.3703 | -79.6434 | -86.7928
|  | ST |  |  | 132.1967 | 131.7932 | 107.0695 | 72.3719 | 70.7029 | 68.8123 | 66.8896 | 64.6653 | 61.653 | 57.7335 | 44.9362 | 30.3892 | 17.1558 | 6.1575 | 72.1126 | 71.6461 | 40.9802 | 0.11857 | -1.789 | -3.9259 | -6.099 | -8.6257 | -12.0482 | -16.4832 | -31.0052 | -47.5393 | -62.6017 | -75.3422 | 85.0249 | 84.5463 | 54.84 | 15.0279 | 13.1609 | 11.066 | 8.9355 | 6.4603 | 3.1077 | -1.2396 | -15.4679 | -31.9359 | -47.0023 | -59.7464
|  | SP |  |  | 132.358 | 132.1701 | 131.4484 | 131.1751 | 106.8247 | 104.279 | 95.4969 | 92.7974 | 87.8339 | 86.4029 | 81.1914 | 73.773 | 68.0727 | 65.1745 | 72.2934 | 72.0761 | 71.2403 | 70.9556 | 40.7238 | 38.1005 | 26.2613 | 23.4566 | 18.3573 | 16.7531 | 10.8591 | 2.5393 | -3.8728 | -7.1872 | 85.2094 | 84.9865 | 84.1288 | 83.8418 | 54.5855 | 51.9755 | 39.1026 | 36.3157 | 31.2396 | 29.6649 | 23.8871 | 15.7208 | 9.4299 | 6.1863
BRAMLEY (FLEE) | WOKINGHAM BSP | MINIMUM HEADROOM | SU7959967739 | YES | 126.3803 | 94.7882 | 94.7751 | 93.9752 | 93.8682 | 93.6634 | 93.456 | 93.2463 | 92.9617 | 92.7862 | 90.3883 | 86.1463 | 82.3668 | 79.5319 | 97.0873 | 65.4603 | 65.3933 | 64.5164 | 64.292 | 62.5361 | 61.5743 | 60.5839 | 59.4715 | 58.4971 | 55.3079 | 50.565 | 46.3486 | 43.1576 | 115.4193 | 83.8272 | 83.8141 | 83.0142 | 82.9072 | 82.6221 | 81.6365 | 80.6215 | 79.4814 | 78.4798 | 75.2007 | 70.3595 | 66.0875 | 62.8512
|  | CT |  |  | 126.4432 | 94.8564 | 94.8485 | 94.3686 | 94.289 | 94.1265 | 93.9632 | 93.7867 | 93.5414 | 93.3938 | 91.1624 | 86.9341 | 83.3251 | 80.1387 | 97.1503 | 65.5285 | 65.4668 | 64.91 | 64.7468 | 63.217 | 61.6229 | 60.7753 | 59.8151 | 58.9272 | 56.0935 | 51.4339 | 47.42 | 43.8161 | 115.4822 | 83.8954 | 83.8875 | 83.4076 | 83.328 | 83.1655 | 81.6706 | 80.8014 | 79.8169 | 78.9038 | 75.9892 | 71.2388 | 67.1733 | 63.5162
|  | LW |  |  | 126.3803 | 94.7882 | 94.7751 | 93.9752 | 93.8682 | 93.6634 | 93.456 | 93.2463 | 92.9617 | 92.7862 | 90.3883 | 86.1463 | 82.3668 | 79.5319 | 97.0873 | 65.4603 | 65.3933 | 64.5164 | 64.292 | 62.5361 | 61.5743 | 60.5839 | 59.4715 | 58.4971 | 55.3079 | 50.565 | 46.3486 | 43.1576 | 115.4193 | 83.8272 | 83.8141 | 83.0142 | 82.9072 | 82.6221 | 81.6365 | 80.6215 | 79.4814 | 78.4798 | 75.2007 | 70.3595 | 66.0875 | 62.8512
|  | ST |  |  | 126.4747 | 126.4695 | 126.4642 | 94.5653 | 94.5389 | 94.4276 | 94.3162 | 94.2045 | 94.0922 | 93.6592 | 92.3586 | 90.6351 | 88.1253 | 85.8335 | 97.195 | 97.1732 | 97.1391 | 65.2048 | 65.1289 | 64.9595 | 64.8167 | 64.6716 | 64.2182 | 63.1858 | 59.9262 | 55.9636 | 53.0848 | 50.5259 | 115.5137 | 115.5085 | 115.5032 | 83.6043 | 83.5779 | 83.4666 | 83.3552 | 83.2435 | 83.1312 | 82.6982 | 79.971 | 75.9304 | 72.9877 | 70.3616
|  | SP |  |  | 126.5062 | 126.5035 | 126.5009 | 126.3409 | 126.3278 | 125.2808 | 124.2338 | 123.1867 | 121.1057 | 120.8893 | 120.2395 | 119.0732 | 118.3103 | 118.0153 | 97.2434 | 97.2375 | 97.2227 | 97.0579 | 97.0288 | 95.9635 | 94.9041 | 93.8446 | 91.7481 | 91.5187 | 90.8242 | 89.5984 | 88.7845 | 88.0878 | 115.5452 | 115.5426 | 115.5399 | 115.3799 | 115.3668 | 114.3198 | 113.2728 | 112.2257 | 110.1447 | 109.9283 | 109.2786 | 108.1123 | 107.3494 | 107.0544
LOVEDEAN GSP | WYMERING BSP | MINIMUM HEADROOM | SU6497405375 | NO | 199.7481 | 199.5183 | 199.4222 | 198.8636 | 198.5808 | 198.1788 | 196.9134 | 195.542 | 209.794 | 209.2996 | 207.6656 | 203.9355 | 186.6399 | 178.5318 | 160.453 | 159.5963 | 159.2725 | 158.3748 | 157.4988 | 156.4305 | 156.5806 | 154.9538 | 168.9007 | 168.0028 | 164.9425 | 150.9201 | 126.1955 | 115.4379 | 173.1376 | 172.4068 | 172.1287 | 171.299 | 170.5421 | 169.6077 | 169.4735 | 167.898 | 181.9062 | 181.0893 | 178.3154 | 166.9567 | 141.4541 | 132.032
|  | CT |  |  | 199.8324 | 199.6179 | 199.5396 | 198.8636 | 198.5808 | 198.1788 | 208.8641 | 207.775 | 223.6147 | 222.7444 | 219.9112 | 209.8734 | 200.5146 | 187.0718 | 160.5642 | 159.7424 | 159.4619 | 158.3748 | 157.4988 | 156.4305 | 169.4011 | 167.0949 | 181.6268 | 179.3089 | 171.6939 | 158.0809 | 145.7985 | 126.5059 | 173.2433 | 172.5435 | 172.3036 | 171.299 | 170.5421 | 169.6077 | 181.4525 | 179.3907 | 194.1852 | 192.1579 | 185.503 | 173.501 | 162.6924 | 143.3334
|  | LW |  |  | 199.7481 | 199.5183 | 199.4222 | 209.4563 | 208.7173 | 207.8218 | 206.5019 | 205.1414 | 220.3577 | 219.3251 | 214.6536 | 203.9355 | 186.6399 | 178.5318 | 160.453 | 159.5963 | 159.2725 | 171.7956 | 170.2374 | 168.4276 | 165.7588 | 163.012 | 176.7385 | 174.1493 | 165.1703 | 150.9201 | 126.1955 | 115.4379 | 173.1376 | 172.4068 | 172.1287 | 183.4851 | 182.0914 | 180.4652 | 178.0673 | 175.5988 | 189.6244 | 187.3478 | 179.4263 | 166.9567 | 141.4541 | 132.032
|  | ST |  |  | 200.0926 | 199.8356 | 199.6413 | 199.2072 | 199.0082 | 198.681 | 209.2461 | 208.6851 | 224.8463 | 223.8744 | 220.8075 | 215.2612 | 204.3808 | 198.7804 | 161.4917 | 160.4881 | 159.7334 | 159.0705 | 158.4566 | 157.6226 | 170.4317 | 169.1023 | 184.3065 | 182.2522 | 175.5577 | 165.497 | 149.7077 | 142.0829 | 174.0368 | 173.1832 | 172.541 | 171.924 | 171.3934 | 170.6612 | 182.3529 | 181.1778 | 196.5741 | 194.7371 | 188.771 | 179.8946 | 163.5646 | 156.9603
|  | SP |  |  | 200.1535 | 199.9346 | 199.7601 | 199.5587 | 199.4774 | 198.206 | 196.9134 | 195.542 | 209.794 | 209.2996 | 207.6656 | 216.344 | 214.3371 | 212.982 | 161.6292 | 160.7686 | 160.0845 | 159.815 | 159.5838 | 158.1242 | 156.5806 | 154.9538 | 168.9007 | 168.0028 | 164.9425 | 174.1109 | 169.8319 | 166.426 | 174.159 | 173.4272 | 172.8455 | 172.5896 | 172.3885 | 170.9667 | 169.4735 | 167.898 | 181.9062 | 181.0893 | 178.3154 | 186.7185 | 182.8957 | 179.9015
COWLEY GSP | YARNTON BSP | MINIMUM HEADROOM | SP3560808335 | YES | 116.1909 | 79.8433 | 74.4268 | 72.8316 | 70.4729 | 67.8754 | 65.0826 | 62.2174 | 58.8389 | 55.9686 | 47.2852 | 31.2498 | 5.8581 | 0.67127 | 75.7262 | 33.7848 | 27.5349 | 25.7666 | 23.1403 | 20.2205 | 17.0783 | 13.8551 | 10.0705 | 6.7876 | -3.1379 | -21.0526 | -50.0577 | -55.933 | 85.4505 | 42.7747 | 36.4154 | 34.6225 | 31.9629 | 29.0009 | 25.8128 | 22.5425 | 18.7046 | 15.3676 | 5.279 | -12.9379 | -42.4174 | -48.383
|  | CT |  |  | 116.1909 | 115.3804 | 79.1981 | 72.8461 | 71.1447 | 69.3037 | 67.4757 | 65.4503 | 63.0951 | 60.6474 | 53.7607 | 41.9878 | 26.3401 | 19.4384 | 75.7262 | 74.7919 | 33.0319 | 25.7666 | 23.8221 | 21.7316 | 19.6567 | 17.3547 | 14.6808 | 11.873 | 3.9775 | -9.3636 | -27.2009 | -34.6865 | 85.4505 | 84.4999 | 42.0076 | 34.6225 | 32.646 | 30.5228 | 28.4154 | 26.0771 | 23.3614 | 20.5063 | 12.4784 | -1.0685 | -19.1933 | -26.8111
|  | LW |  |  | 116.2068 | 79.8433 | 74.4268 | 72.8316 | 70.4729 | 67.8754 | 65.0826 | 62.2174 | 58.8389 | 55.9686 | 47.2852 | 31.2498 | 5.8581 | 0.67127 | 75.7533 | 33.7848 | 27.5349 | 25.8041 | 23.1403 | 20.2205 | 17.0783 | 13.8551 | 10.0705 | 6.7876 | -3.1379 | -21.0526 | -50.0577 | -55.933 | 85.479 | 42.7747 | 36.4154 | 34.6668 | 31.9629 | 29.0009 | 25.8128 | 22.5425 | 18.7046 | 15.3676 | 5.279 | -12.9379 | -42.4174 | -48.383
|  | ST |  |  | 116.4726 | 116.2098 | 79.9274 | 74.323 | 73.3654 | 72.2061 | 70.8364 | 69.3252 | 67.5777 | 65.1807 | 58.1313 | 47.5867 | 33.7452 | 28.3739 | 76.047 | 75.7445 | 33.8686 | 27.4441 | 26.3426 | 25.0239 | 23.4624 | 21.7379 | 19.7412 | 17.0534 | 9.155 | -2.743 | -18.5522 | -24.2977 | 85.7765 | 85.4687 | 42.8584 | 36.3263 | 35.2059 | 33.8662 | 32.2796 | 30.527 | 28.4977 | 25.7717 | 17.7618 | 5.6862 | -10.3813 | -16.2315
|  | SP |  |  | 141.0042 | 116.3983 | 116.0548 | 115.7505 | 79.1422 | 77.5097 | 75.7627 | 74.0163 | 70.9471 | 70.0034 | 64.0939 | 60.5803 | 57.3745 | 56.0738 | 101.8335 | 75.93 | 75.5338 | 75.2047 | 32.8341 | 31.1402 | 29.3143 | 27.4891 | 24.3256 | 23.2775 | 14.8102 | 11.0893 | 7.5394 | 6.4739 | 113.2351 | 85.6579 | 85.2548 | 84.9224 | 41.9537 | 40.2518 | 38.4155 | 36.58 | 33.404 | 32.3423 | 23.8025 | 19.8961 | 16.301 | 15.2108
AXMINSTER | YEOVIL BSP | MINIMUM HEADROOM | ST5769016833 | YES | 136.8391 | 136.3173 | 83.3921 | 82.9874 | 70.6969 | 58.2494 | 44.1739 | 29.9311 | 19.7288 | 10.1147 | -25.6088 | -73.5879 | -113.288 | -124.9188 | 75.0644 | 74.4381 | 10.659 | 10.1805 | -4.5549 | -19.4592 | -35.7959 | -52.3138 | -64.0218 | -75.1555 | -116.4631 | -172.2055 | -218.0084 | -231.0575 | 92.1806 | 91.5991 | 31.4407 | 30.9735 | 16.6107 | 2.0817 | -13.8593 | -29.9791 | -41.4236 | -52.2914 | -92.6218 | -147.0057 | -191.7407 | -204.5416
|  | CT |  |  | 136.8518 | 136.3374 | 135.7949 | 83.0264 | 77.1737 | 72.0532 | 66.8786 | 58.7989 | 51.9016 | 44.3563 | 18.537 | -14.8866 | -43.0362 | -65.4328 | 75.0767 | 74.4575 | 73.8047 | 10.2178 | 3.2556 | -2.8195 | -8.9553 | -18.3452 | -26.2263 | -34.9374 | -64.7676 | -103.003 | -135.0351 | -160.6555 | 92.1931 | 91.6188 | 91.0133 | 31.0111 | 24.2179 | 18.2883 | 12.299 | 3.1088 | -4.612 | -13.1192 | -42.2475 | -79.6409 | -110.9936 | -136.0498
|  | LW |  |  | 136.8391 | 136.3173 | 83.3921 | 82.9874 | 70.6969 | 58.2494 | 44.1739 | 29.9311 | 19.7288 | 10.1147 | -25.6088 | -73.5879 | -113.288 | -124.9188 | 75.0644 | 74.4381 | 10.659 | 10.1805 | -4.5549 | -19.4592 | -35.7959 | -52.3138 | -64.0218 | -75.1555 | -116.4631 | -172.2055 | -218.0084 | -231.0575 | 92.1806 | 91.5991 | 31.4407 | 30.9735 | 16.6107 | 2.0817 | -13.8593 | -29.9791 | -41.4236 | -52.2914 | -92.6218 | -147.0057 | -191.7407 | -204.5416
|  | ST |  |  | 137.58 | 136.7462 | 136.2044 | 83.5683 | 78.7934 | 74.1662 | 69.0702 | 62.602 | 57.3039 | 50.7277 | 27.9814 | 0.9206 | -20.8664 | -38.4312 | 75.9538 | 74.9489 | 74.2961 | 10.8655 | 5.1168 | -0.45165 | -6.5247 | -14.2413 | -20.4951 | -28.1668 | -54.7121 | -86.2597 | -111.5845 | -132.0306 | 93.0065 | 92.0748 | 91.4696 | 31.6427 | 26.0423 | 20.6173 | 14.6932 | 7.1668 | 1.0616 | -6.4184 | -32.2989 | -63.0614 | -87.7671 | -107.7089
|  | SP |  |  | 137.6804 | 137.165 | 136.7104 | 136.4112 | 135.019 | 133.2174 | 130.7963 | 128.2324 | 124.8489 | 120.3169 | 101.0854 | 76.9506 | 57.8648 | 47.3313 | 76.0748 | 75.4537 | 74.906 | 74.5364 | 72.8637 | 70.7413 | 67.8288 | 64.7796 | 60.7523 | 55.3321 | 32.3209 | 3.3589 | -19.4581 | -31.7307 | 93.1186 | 92.5428 | 92.035 | 91.702 | 90.1495 | 88.1645 | 85.4626 | 82.6213 | 78.8698 | 73.8301 | 52.4382 | 24.2715 | 2.0231 | -9.953
IVER 66KV | YIEWSLEY | MINIMUM HEADROOM | TQ0565680987 | NO | 70.9811 | 70.9529 | 70.9247 | 69.2052 | 68.8702 | 68.529 | 68.179 | 67.8043 | 67.2933 | 67.1477 | 66.6886 | 64.7719 | 60.4548 | 56.4618 | 67.9779 | 67.8921 | 67.8504 | 66.1044 | 65.7421 | 65.3752 | 64.9786 | 64.5742 | 64.056 | 63.7584 | 61.8958 | 58.16 | 53.2328 | 48.5883 | 68.6411 | 68.5693 | 68.5308 | 66.7913 | 66.4356 | 66.075 | 65.6896 | 65.2965 | 64.7911 | 64.6515 | 62.8535 | 59.3133 | 54.4936 | 49.9023
|  | CT |  |  | 71.1164 | 71.0995 | 71.0826 | 70.0508 | 69.9663 | 69.8817 | 69.7971 | 69.7126 | 69.6056 | 69.5281 | 69.2931 | 66.6681 | 62.5641 | 58.9875 | 68.1147 | 68.0416 | 68.0128 | 66.9581 | 66.8496 | 66.7425 | 66.637 | 66.5058 | 66.3747 | 66.2622 | 64.966 | 59.9478 | 55.2224 | 51.193 | 68.7777 | 68.7181 | 68.6922 | 67.643 | 67.5403 | 67.4387 | 67.3383 | 67.2184 | 67.0986 | 67.0271 | 65.9112 | 60.988 | 56.3813 | 52.5055
|  | LW |  |  | 70.9811 | 70.9529 | 70.9247 | 69.2052 | 68.8702 | 68.529 | 68.179 | 67.8043 | 67.2933 | 67.1477 | 66.6886 | 64.7719 | 60.4548 | 56.4618 | 67.9779 | 67.8921 | 67.8504 | 66.1044 | 65.7421 | 65.3752 | 64.9786 | 64.5742 | 64.056 | 63.7584 | 61.8958 | 58.16 | 53.2328 | 48.5883 | 68.6411 | 68.5693 | 68.5308 | 66.7913 | 66.4356 | 66.075 | 65.6896 | 65.2965 | 64.7911 | 64.6515 | 62.8535 | 59.3133 | 54.4936 | 49.9023
|  | ST |  |  | 71.184 | 71.1728 | 71.1615 | 70.4737 | 70.4173 | 70.3609 | 70.3045 | 70.2482 | 70.1918 | 70.1617 | 70.0033 | 69.7083 | 68.1988 | 66.1168 | 68.1988 | 68.1642 | 68.0982 | 67.3953 | 67.3201 | 67.2429 | 67.1602 | 67.0775 | 66.9894 | 66.9329 | 66.625 | 64.3181 | 61.4566 | 59.165 | 68.8661 | 68.8287 | 68.776 | 68.0767 | 68.0061 | 67.934 | 67.8576 | 67.7813 | 67.7009 | 67.6526 | 67.5067 | 65.292 | 62.5007 | 60.3782
|  | SP |  |  | 71.2517 | 71.2461 | 71.2404 | 70.8965 | 70.8525 | 70.8089 | 70.7652 | 70.7212 | 70.6685 | 70.5887 | 70.3378 | 70.178 | 69.742 | 69.575 | 68.2711 | 68.2484 | 68.1978 | 67.8511 | 67.8014 | 67.7521 | 67.6996 | 67.6469 | 67.5831 | 67.4902 | 67.1992 | 66.9572 | 66.439 | 66.073 | 68.9397 | 68.9124 | 68.8705 | 68.5246 | 68.4763 | 68.4283 | 68.3779 | 68.3273 | 68.2662 | 68.1765 | 67.8953 | 67.6732 | 67.2424 | 67.1048

## LEP Reference
LEP | Local Authority | Grid Supply Point | Bulk Supply Point | Primary Substation
Buckinghamshire Thames Valley | Chiltern | AMERSHAM | LOUDWATER BSP | BOWERDEAN
Buckinghamshire Thames Valley | Chiltern | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | DENHAM | COKES LANE
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | DENHAM | GERRARDS CROSS
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Buckinghamshire Thames Valley | Chiltern | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Buckinghamshire Thames Valley | South Bucks | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Buckinghamshire Thames Valley | South Bucks | AMERSHAM | LOUDWATER BSP | WELL END
Buckinghamshire Thames Valley | South Bucks | BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD
Buckinghamshire Thames Valley | South Bucks | BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | CHALVEY BSP | CHALVEY
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | DENHAM | DENHAM AVENUE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | DENHAM | GERRARDS CROSS
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | LONGFORD | POYLE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | SLOUGH | FARNHAM ROYAL
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | SLOUGH | TAPLOW
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | UPTON BSP | SUTTON LANE
Buckinghamshire Thames Valley | South Bucks | IVER 132KV | UPTON BSP | UPTON
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | BOWERDEAN
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | FLACKWELL HEATH
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | WELL END
Buckinghamshire Thames Valley | Wycombe | AMERSHAM | LOUDWATER BSP | WYCOMBE MARSH
Buckinghamshire Thames Valley | Wycombe | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Buckinghamshire Thames Valley | Wycombe | BRAMLEY (FLEE) | READING BSP | HENLEY
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | FRYERS LANE
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | HIGH WYCOMBE TOWN
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH
Buckinghamshire Thames Valley | Wycombe | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON
Buckinghamshire Thames Valley | Wycombe | IVER 132KV | SLOUGH | TAPLOW
Buckinghamshire Thames Valley | Wycombe | IVER 132KV | UPTON BSP | BEACONSFIELD (END BB)
Coast to Capital | Arun | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ARGYLE ROAD
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILSHAM
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN
Coast to Capital | Arun | LOVEDEAN GSP | CHICHESTER & HUNSTON | SOUTH BERSTEAD
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | MIDHURST
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Coast to Capital | Chichester | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | BIRDHAM
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | CHICHESTER
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | HUNSTON
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | MARKET
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | ROSE GREEN
Coast to Capital | Chichester | LOVEDEAN GSP | CHICHESTER & HUNSTON | SELSEY
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | EMSWORTH
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | GABLE HEAD
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | HORNDEAN
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | LEIGH PARK
Coast to Capital | Chichester | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Coast to Capital | Horsham | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Coast to Capital | Horsham | BRAMLEY (FLEE) | FERNHURST | HASLINGBOURNE
Coast to Capital | Horsham | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Coast to Capital | Horsham | LOVEDEAN GSP | CHICHESTER & HUNSTON | BILLINGSHURST
Coast to Capital | Mole Valley | BRAMLEY (FLEE) | FERNHURST | FIVE OAKS
Coventry and Warwickshire | Stratford-on-Avon | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Coventry and Warwickshire | Stratford-on-Avon | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | ALDERNEY
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | CENTRAL
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | ELECTRIC HOUSE
Dorset | Bournemouth | MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | BOSCOMBE EAST
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Dorset | Bournemouth | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE
Dorset | Bournemouth | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | Bournemouth | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Dorset | Bournemouth | MANNINGTON GSP | REDHILL BSP | REDHILL
Dorset | Bournemouth | MANNINGTON GSP | REDHILL BSP | WINTON
Dorset | Christchurch | MANNINGTON GSP | ARNEWOOD | NEW MILTON
Dorset | Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Dorset | Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Dorset | Christchurch | MANNINGTON GSP | CHRISTCHURCH BSP | SOUTHBOURNE
Dorset | Christchurch | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | Christchurch | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
Dorset | Christchurch | MANNINGTON GSP | REDHILL BSP | REDHILL
Dorset | Christchurch | MANNINGTON GSP | REDHILL BSP | WINTON
Dorset | East Dorset | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | BLANDFORD
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Dorset | East Dorset | MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | HINTON MARTELL
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | VERWOOD
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Dorset | East Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES
Dorset | East Dorset | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Dorset | East Dorset | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Dorset | East Dorset | MANNINGTON GSP | REDHILL BSP | REDHILL
Dorset | East Dorset | MANNINGTON GSP | SALISBURY | HOMINGTON
Dorset | East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL
Dorset | East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Dorset | East Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | PULHAM
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | SHERBORNE
Dorset | North Dorset | AXMINSTER | YEOVIL BSP | YETMINSTER
Dorset | North Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE
Dorset | North Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Dorset | North Dorset | MANNINGTON GSP | LYTCHETT | BLANDFORD
Dorset | North Dorset | MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON
Dorset | North Dorset | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GILLINGHAM
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | GUSSAGE ST MICHAEL
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | TARRANT RUSHTON
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR
Dorset | North Dorset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | ALDERNEY
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | BOURNE VALLEY
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE NORTH
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH
Dorset | Poole | MANNINGTON GSP | BOURNEMOUTH | WESTBOURNE
Dorset | Poole | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Dorset | Poole | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Dorset | Poole | MANNINGTON GSP | LYTCHETT | HOLES BAY
Dorset | Poole | MANNINGTON GSP | MANNINGTON BSP | FERNDOWN
Dorset | Poole | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE
Dorset | Poole | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Dorset | Poole | MANNINGTON GSP | REDHILL BSP | EAST HOWE
Dorset | Poole | MANNINGTON GSP | REDHILL BSP | WINTON
Dorset | Purbeck | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Dorset | Purbeck | MANNINGTON GSP | BOURNEMOUTH | PARKSTONE SOUTH
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | BLANDFORD
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | CORFE MULLEN
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | CREEKMOOR
Dorset | Purbeck | MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON
Dorset | Purbeck | MANNINGTON GSP | POOLE PS (HAMWORTHY) | HAMWORTHY
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | BOVINGTON
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | BUSHEY
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | SWANAGE
Dorset | Purbeck | MANNINGTON GSP | WAREHAM | WAREHAM TOWN
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | CHILTON CANTELLO
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | MILBORNE PORT
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | PULHAM
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | SHERBORNE
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | WEST HENDFORD
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | YEOVIL
Dorset | West Dorset | AXMINSTER | YEOVIL BSP | YETMINSTER
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | CERNE ABBAS
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | CHARMINSTER
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER TOWN
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | MAIDEN NEWTON
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | PIDDLETRENTHIDE
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | PUDDLETOWN
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | REDLANDS
Dorset | West Dorset | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH
Dorset | West Dorset | MANNINGTON GSP | LYTCHETT | WINTERBOURNE KINGSTON
Dorset | West Dorset | MANNINGTON GSP | WAREHAM | BOVINGTON
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | CHICKERELL
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | DORCHESTER TOWN
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | PORTLAND
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | REDLANDS
Dorset | Weymouth and Portland | CHICKERELL GSP | CHICKERELL BSP | WEYMOUTH
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY
Enterprise M3 | Basingstoke and Deane | BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | BASINGSTOKE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1A & T2A | JAYS CLOSE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | DOWN GRANGE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | BROOK STREET
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | HOUNDMILLS
Enterprise M3 | Basingstoke and Deane | BRAMLEY (BASI) | BASINGSTOKE T3 & T4 | OAKRIDGE
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | ALRESFORD
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | ALTON | HERRIARD
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Enterprise M3 | Basingstoke and Deane | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Enterprise M3 | Elmbridge | LALEHAM | STAINES | SUNBURY CROSS
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | NORMANDY
Enterprise M3 | Guildford | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Enterprise M3 | Guildford | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Enterprise M3 | Guildford | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Enterprise M3 | Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Enterprise M3 | Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | BRAMLEY GREEN
Enterprise M3 | Hart | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | CHINEHAM
Enterprise M3 | Hart | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Enterprise M3 | Hart | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Enterprise M3 | Hart | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Enterprise M3 | Hart | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Enterprise M3 | Hart | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Enterprise M3 | Hart | BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Enterprise M3 | Hart | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Enterprise M3 | Hart | BRAMLEY (FLEE) | PYESTOCK BSP | Crookham (Church)
Enterprise M3 | Runnymede | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Enterprise M3 | Runnymede | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Enterprise M3 | Runnymede | IVER 132KV | CHALVEY BSP | CHALVEY
Enterprise M3 | Runnymede | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Enterprise M3 | Runnymede | LALEHAM | STAINES | CAUSEWAY
Enterprise M3 | Runnymede | LALEHAM | STAINES | EGHAM
Enterprise M3 | Runnymede | LALEHAM | STAINES | SIDNEY ROAD
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | COVE
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Enterprise M3 | Rushmoor | BRAMLEY (FLEE) | PYESTOCK BSP | Crookham (Church)
Enterprise M3 | Spelthorne | IVER 132KV | CHALVEY BSP | CHALVEY
Enterprise M3 | Spelthorne | IVER 132KV | LONGFORD | POYLE
Enterprise M3 | Spelthorne | LALEHAM | EAST BEDFONT A | CHURCH ROAD
Enterprise M3 | Spelthorne | LALEHAM | STAINES | CAUSEWAY
Enterprise M3 | Spelthorne | LALEHAM | STAINES | SIDNEY ROAD
Enterprise M3 | Spelthorne | LALEHAM | STAINES | STANWELL
Enterprise M3 | Spelthorne | LALEHAM | STAINES | SUNBURY CROSS
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FARNBOROUGH
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | FRIMLEY
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | CAMBERLEY RESERVE | QUEENSMEAD
Enterprise M3 | Surrey Heath | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HAWLEY
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | ALDERSHOT
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | GODALMING
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | LABURNAM ROAD
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | MILFORD
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALDERSHOT BSP | TONGHAM
Enterprise M3 | Waverley | BRAMLEY (FLEE) | ALTON | BORDON
Enterprise M3 | Waverley | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Enterprise M3 | Waverley | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Enterprise M3 | Waverley | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Enterprise M3 | Waverley | BRAMLEY (FLEE) | FERNHURST | PLAISTOW
Enterprise M3 | Woking | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Gloucestershire | Cheltenham | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Gloucestershire | Cotswold | BRAMLEY (FLEE) | BURGHFIELD MAIN | WHITELEY WOOD
Gloucestershire | Cotswold | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Gloucestershire | Cotswold | COWLEY GSP | WITNEY BSP | RISSINGTON
Gloucestershire | Cotswold | MELKSHAM GSP | CHIPPENHAM | ALDERTON
Gloucestershire | Cotswold | MELKSHAM GSP | CHIPPENHAM | MALMESBURY
Gloucestershire | Cotswold | MELKSHAM GSP | CHIPPENHAM | TETBURY
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Gloucestershire | Cotswold | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Gloucestershire | Cotswold | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Gloucestershire | Cotswold | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Gloucestershire | Tewkesbury | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Gloucestershire | Tewkesbury | MINETY GSP | CIRENCESTER BSP | SHIPTON OLIFFE
Heart of the South West | Mendip | AXMINSTER | YEOVIL BSP | SPARKFORD
Heart of the South West | Mendip | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | BRUTON
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | CROCKERTON
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | FROME
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | HAWKERIDGE
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | HOLWELL
Heart of the South West | Mendip | MELKSHAM GSP | FROME BSP | WESTBURY
Heart of the South West | Mendip | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
Heart of the South West | Mendip | MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | CASTLE CARY
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | CHILTON CANTELLO
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | HENSTRIDGE
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | LARKHILL
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | MILBORNE PORT
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | SHERBORNE
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | SPARKFORD
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | WEST HENDFORD
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | YEOVIL
Heart of the South West | South Somerset | AXMINSTER | YEOVIL BSP | YETMINSTER
Heart of the South West | South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Heart of the South West | South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WEST STOUR
Heart of the South West | South Somerset | MANNINGTON GSP | SHAFTESBURY BSP | WINCANTON
Heart of the South West | South Somerset | MELKSHAM GSP | FROME BSP | BRUTON
Heart of the South West | South Somerset | MELKSHAM GSP | FROME BSP | HOLWELL
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | COKES LANE
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | DENHAM AVENUE
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | GRASSINGHAM ROAD
Hertfordshire | Three Rivers | IVER 132KV | DENHAM | HAREFIELD
London | Brent | WILLESDEN GSP | ACTON LANE | PARK ROYAL
London | Brent | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
London | Ealing | EALING GSP | EALING (D) | BRENTFORD
London | Ealing | EALING GSP | EALING (D) | DEAN GARDENS
London | Ealing | EALING GSP | EALING (D) | HARVARD LANE
London | Ealing | NORTH HYDE GSP | NORTH HYDE (D) | SPRINGFIELD ROAD
London | Ealing | NORTH HYDE GSP | NORTH HYDE (D) | THE GREEN
London | Ealing | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
London | Ealing | WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK
London | Ealing | WILLESDEN GSP | ACTON LANE | PARK ROYAL
London | Ealing | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
London | Hammersmith and Fulham | EALING GSP | EALING (D) | HARVARD LANE
London | Hammersmith and Fulham | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
London | Hammersmith and Fulham | WILLESDEN GSP | ACTON LANE | LEAMINGTON PARK
London | Hammersmith and Fulham | WILLESDEN GSP | CANAL BANK | CANAL BANK 11kV
London | Hillingdon | IVER 132KV | DENHAM | DENHAM AVENUE
London | Hillingdon | IVER 132KV | DENHAM | HAREFIELD
London | Hillingdon | IVER 132KV | LONGFORD | BATH ROAD WEST
London | Hillingdon | IVER 132KV | LONGFORD | POYLE
London | Hillingdon | IVER 132KV | UPTON BSP | UPTON
London | Hillingdon | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
London | Hillingdon | NORTH HYDE GSP | NORTH HYDE (D) | BATH ROAD EAST
London | Hillingdon | NORTH HYDE GSP | NORTH HYDE (D) | SPRINGFIELD ROAD
London | Hounslow | EALING GSP | EALING (D) | BRENTFORD
London | Hounslow | EALING GSP | EALING (D) | HARVARD LANE
London | Hounslow | LALEHAM | EAST BEDFONT A | CHURCH ROAD
London | Hounslow | LALEHAM | EAST BEDFONT A | FELTHAM
London | Hounslow | LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR
London | Hounslow | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
London | Hounslow | LALEHAM | STAINES | STANWELL
London | Hounslow | LALEHAM | STAINES | SUNBURY CROSS
London | Hounslow | NORTH HYDE GSP | NORTH HYDE (D) | BATH ROAD EAST
London | Hounslow | NORTH HYDE GSP | NORTH HYDE (D) | THE GREEN
London | Hounslow | WILLESDEN GSP | ACTON LANE | GOLDSMITHS
London | Richmond upon Thames | EALING GSP | EALING (D) | BRENTFORD
London | Richmond upon Thames | EALING GSP | EALING (D) | HARVARD LANE
London | Richmond upon Thames | LALEHAM | EAST BEDFONT A | FELTHAM
London | Richmond upon Thames | LALEHAM | EAST BEDFONT A | HOPE AND ANCHOR
London | Richmond upon Thames | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
London | Richmond upon Thames | LALEHAM | STAINES | SUNBURY CROSS
Oxfordshire LEP | Cherwell | COWLEY GSP | HEADINGTON BSP | ARNCOTT
Oxfordshire LEP | Cherwell | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | Cherwell | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | DEDDINGTON
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | KIDDINGTON
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | WOODSTOCK
Oxfordshire LEP | Cherwell | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH | BICESTER
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD
Oxfordshire LEP | Cherwell | EAST CLAYDON GSP | BICESTER NORTH | UPPER HEYFORD
Oxfordshire LEP | Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxfordshire LEP | Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | Oxford | COWLEY GSP | COWLEY LOCAL (2 X 90) | UNION STREET
Oxfordshire LEP | Oxford | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | Oxford | COWLEY GSP | HEADINGTON BSP | OLD ROAD
Oxfordshire LEP | Oxford | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | FRENCHAY ROAD
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | OSNEY
Oxfordshire LEP | Oxford | COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES
Oxfordshire LEP | Oxford | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxfordshire LEP | Oxford | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | South Oxfordshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | HENLEY
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | KIDMORE END
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | READING
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING BSP | TWYFORD
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM
Oxfordshire LEP | South Oxfordshire | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | CHOLSEY
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | FULSCOT
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | MILTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | DRAYTON BSP | WINSMORE LANE
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | ARNCOTT
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | OLD ROAD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HEADINGTON BSP | WHEATLEY
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | NUFFIELD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | STOKENCHURCH
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | HIGH WYCOMBE BSP | WATLINGTON
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | YARNTON BSP | LOVELACE ROAD
Oxfordshire LEP | South Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | Vale of White Horse | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Oxfordshire LEP | Vale of White Horse | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 45) | BERINSFIELD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 45) | KENNINGTON
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | COWLEY LOCAL
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | COWLEY LOCAL (2 X 90) | WALLINGFORD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | CHOLSEY
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | FULSCOT
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | GROVE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | MILTON
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | WANTAGE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | DRAYTON BSP | WINSMORE LANE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | NORTH HINKSEY
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | OSNEY
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | ST EBBES
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | OXFORD (OSNEY) BSP | WOOTTON ROAD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | WITNEY BSP | FYFIELD
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | WITNEY BSP | STANDLAKE
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | YARNTON BSP | EYNSHAM
Oxfordshire LEP | Vale of White Horse | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Oxfordshire LEP | Vale of White Horse | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Oxfordshire LEP | Vale of White Horse | MINETY GSP | TOOTHILL BSP | CHISLEDON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | BLEDDINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | BURFORD
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | CARTERTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | FYFIELD
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | LEAFIELD
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | RISSINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | STANDLAKE
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | WINDRUSH PARK
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | WITNEY BSP | WITNEY TOWN
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | CHARLBURY
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | CHIPPING NORTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | DEDDINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | EYNSHAM
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | KIDDINGTON
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | WOODSTOCK
Oxfordshire LEP | West Oxfordshire | COWLEY GSP | YARNTON BSP | YARNTON
Oxfordshire LEP | West Oxfordshire | EAST CLAYDON GSP | BICESTER NORTH | UPPER HEYFORD
Oxfordshire LEP | West Oxfordshire | MINETY GSP | CIRENCESTER BSP | NORTHLEACH
Oxfordshire LEP | West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | BLACK BOURTON
Oxfordshire LEP | West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Oxfordshire LEP | West Oxfordshire | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Solent | East Hampshire | BRAMLEY (FLEE) | ALDERSHOT BSP | FARNHAM
Solent | East Hampshire | BRAMLEY (FLEE) | ALDERSHOT BSP | HINDHEAD
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | ALRESFORD
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | ALTON LOCAL
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | BORDON
Solent | East Hampshire | BRAMLEY (FLEE) | ALTON | HERRIARD
Solent | East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | COXMOOR WOOD
Solent | East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HOOK
Solent | East Hampshire | BRAMLEY (FLEE) | COXMOOR WOOD BSP | WRECCLESHAM
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | HASLEMERE
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | LANGLEY COURT
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Solent | East Hampshire | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Solent | East Hampshire | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Solent | East Hampshire | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Solent | East Hampshire | LOVEDEAN GSP | HAVANT | EMSWORTH
Solent | East Hampshire | LOVEDEAN GSP | HAVANT | HORNDEAN
Solent | East Hampshire | LOVEDEAN GSP | HAVANT | LEIGH PARK
Solent | Eastleigh | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK
Solent | Eastleigh | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON
Solent | Eastleigh | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Eastleigh | NURSLING GSP | ROWNHAMS | SILKSTEAD
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | BASSETT
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | BISHOPSTOKE
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | CHANDLERSFORD
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | HEDGE END
Solent | Eastleigh | NURSLING GSP | VELMORE BSP | VELMORE
Solent | Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE
Solent | Fareham | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY
Solent | Fareham | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSY TITCHFIELD
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT
Solent | Fareham | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK
Solent | Fareham | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Solent | Fareham | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | LEE-ON-SOLENT
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ROWNER PARK
Solent | Gosport | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD
Solent | Havant | LOVEDEAN GSP | CHICHESTER & HUNSTON | ASHLING ROAD
Solent | Havant | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Solent | Havant | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Solent | Havant | LOVEDEAN GSP | HAVANT | BROCKHAMPTON
Solent | Havant | LOVEDEAN GSP | HAVANT | EMSWORTH
Solent | Havant | LOVEDEAN GSP | HAVANT | GABLE HEAD
Solent | Havant | LOVEDEAN GSP | HAVANT | HORNDEAN
Solent | Havant | LOVEDEAN GSP | HAVANT | LEIGH PARK
Solent | Havant | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Solent | Havant | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK
Solent | Havant | LOVEDEAN GSP | WYMERING BSP | FARLINGTON
Solent | Havant | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | BINSTEAD
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | NEWPORT
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | RYDE
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SANDOWN
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHALFLEET
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | SHANKLIN
Solent | Isle of Wight | FAWLEY GSP | COWES & WOOTTON COMMON BSP | VENTNOR
Solent | Isle of Wight | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET
Solent | New Forest | BOTLEY WOOD GSP | NETLEY COMMON BSP | HAMBLE
Solent | New Forest | FAWLEY GSP | COWES & WOOTTON COMMON BSP | FRESHWATER
Solent | New Forest | FAWLEY GSP | LANGLEY BSP | BUTTS ASH
Solent | New Forest | FAWLEY GSP | LANGLEY BSP | LANGLEY
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | HINCHELSEA
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | LYMINGTON
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | MILFORD-ON-SEA
Solent | New Forest | MANNINGTON GSP | ARNEWOOD | NEW MILTON
Solent | New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | CHRISTCHURCH
Solent | New Forest | MANNINGTON GSP | CHRISTCHURCH BSP | SOMERFORD
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | FORDINGBRIDGE
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | MANNINGTON
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | Mill Lane, Ringwood
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | VERWOOD
Solent | New Forest | MANNINGTON GSP | MANNINGTON BSP | WIMBORNE ST GILES
Solent | New Forest | MANNINGTON GSP | SALISBURY | HOMINGTON
Solent | New Forest | MANNINGTON GSP | SALISBURY | REDLYNCH
Solent | New Forest | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Solent | New Forest | NURSLING GSP | ROWNHAMS | FLETCHWOOD
Solent | New Forest | NURSLING GSP | ROWNHAMS | LORDSHILL
Solent | New Forest | NURSLING GSP | ROWNHAMS | ROMSEY
Solent | New Forest | NURSLING GSP | ROWNHAMS | TOTTON
Solent | New Forest | NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE
Solent | New Forest | NURSLING GSP | WINCHESTER | DUNBRIDGE
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | HOEFORD
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | WEST END
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1B T2B (1X90, 1X60MVA) | ZETLAND ROAD
Solent | Portsmouth | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Solent | Portsmouth | LOVEDEAN GSP | HAVANT | MEYRICK ROAD
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | BRANDON ROAD
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | EASTNEY
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | FRATTON PARK
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | GREETHAM STREET
Solent | Portsmouth | LOVEDEAN GSP | PORTSMOUTH BSP | PORTSMOUTH
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | COLLEGE PARK
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | FARLINGTON
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | GAMBLE ROAD
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | HILSEA
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Solent | Portsmouth | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | BITTERNE
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | TOWNHILL PARK
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WESTON
Solent | Southampton | BOTLEY WOOD GSP | NETLEY COMMON BSP | WOOLSTON
Solent | Southampton | NURSLING GSP | ROWNHAMS | LORDSHILL
Solent | Southampton | NURSLING GSP | ROWNHAMS | MAYBUSH
Solent | Southampton | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | BEVOIS VALLEY
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | CENTRAL BRIDGE
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 60) | CHAPEL
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | SHIRLEY
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | WESTERN ESPLANADE
Solent | Southampton | NURSLING GSP | SOUTHAMPTON (2 X 90) | WOODMILL LANE
Solent | Southampton | NURSLING GSP | VELMORE BSP | BASSETT
Solent | Southampton | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Solent | Southampton | NURSLING GSP | VELMORE BSP | VELMORE
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER EAST
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | ANDOVER TOWN
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | PORTWAY
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON
Solent | Test Valley | BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH
Solent | Test Valley | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Solent | Test Valley | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Solent | Test Valley | MANNINGTON GSP | SALISBURY | PETERSFINGER
Solent | Test Valley | MELKSHAM GSP | AMESBURY | PARK HOUSE
Solent | Test Valley | MELKSHAM GSP | WEST GRAFTON | TIDWORTH
Solent | Test Valley | MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE
Solent | Test Valley | NURSLING GSP | ROWNHAMS | FLETCHWOOD
Solent | Test Valley | NURSLING GSP | ROWNHAMS | LORDSHILL
Solent | Test Valley | NURSLING GSP | ROWNHAMS | MAYBUSH
Solent | Test Valley | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Test Valley | NURSLING GSP | ROWNHAMS | ROMSEY
Solent | Test Valley | NURSLING GSP | ROWNHAMS | SILKSTEAD
Solent | Test Valley | NURSLING GSP | ROWNHAMS | TOTTON
Solent | Test Valley | NURSLING GSP | SOUTHAMPTON (2 X 90) | REGENTS PARK
Solent | Test Valley | NURSLING GSP | VELMORE BSP | BASSETT
Solent | Test Valley | NURSLING GSP | VELMORE BSP | CHANDLERSFORD
Solent | Test Valley | NURSLING GSP | VELMORE BSP | VELMORE
Solent | Test Valley | NURSLING GSP | WINCHESTER | DUNBRIDGE
Solent | Test Valley | NURSLING GSP | WINCHESTER | HARESTOCK
Solent | Test Valley | NURSLING GSP | WINCHESTER | HOUGHTON
Solent | Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | PARK GATE
Solent | Winchester | BOTLEY WOOD GSP | BOTLEY WOOD BSP | WHITELEY
Solent | Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | BISHOPS WALTHAM
Solent | Winchester | BOTLEY WOOD GSP | NETLEY COMMON BSP | NETLEY COMMON 11kV
Solent | Winchester | BRAMLEY (ANDO-THAT) | ANDOVER BSP | BARTON STACEY
Solent | Winchester | BRAMLEY (ANDO-THAT) | ANDOVER BSP | WHITCHURCH
Solent | Winchester | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | OVERTON
Solent | Winchester | BRAMLEY (FLEE) | ALTON | ALRESFORD
Solent | Winchester | BRAMLEY (FLEE) | FERNHURST | PETERSFIELD
Solent | Winchester | BRAMLEY (FLEE) | FERNHURST | PRESTON CANDOVER
Solent | Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | NORTH FAREHAM
Solent | Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | PLESSY TITCHFIELD
Solent | Winchester | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | TITCHFIELD
Solent | Winchester | LOVEDEAN GSP | FORT WIDLEY | PURBROOK
Solent | Winchester | LOVEDEAN GSP | FORT WIDLEY | WATERLOOVILLE
Solent | Winchester | LOVEDEAN GSP | HAVANT | HORNDEAN
Solent | Winchester | LOVEDEAN GSP | WYMERING BSP | PORTCHESTER
Solent | Winchester | LOVEDEAN GSP | WYMERING BSP | WYMERING
Solent | Winchester | NURSLING GSP | ROWNHAMS | NORTH BADDESLEY
Solent | Winchester | NURSLING GSP | ROWNHAMS | SILKSTEAD
Solent | Winchester | NURSLING GSP | VELMORE BSP | CHANDLERSFORD
Solent | Winchester | NURSLING GSP | VELMORE BSP | EASTLEIGH NORTH
Solent | Winchester | NURSLING GSP | VELMORE BSP | HEDGE END
Solent | Winchester | NURSLING GSP | WINCHESTER | DUNBRIDGE
Solent | Winchester | NURSLING GSP | WINCHESTER | GORDON ROAD
Solent | Winchester | NURSLING GSP | WINCHESTER | HARESTOCK
Solent | Winchester | NURSLING GSP | WINCHESTER | HOUGHTON
Solent | Winchester | NURSLING GSP | WINCHESTER | ST CROSS
South East Midlands | Aylesbury Vale | COWLEY GSP | HEADINGTON BSP | ARNCOTT
South East Midlands | Aylesbury Vale | COWLEY GSP | HEADINGTON BSP | WHEATLEY
South East Midlands | Aylesbury Vale | EAST CLAYDON GSP | BICESTER NORTH | BICESTER
South East Midlands | Aylesbury Vale | EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD
South East Midlands | South Northamptonshire | COWLEY GSP | YARNTON BSP | DEDDINGTON
South East Midlands | South Northamptonshire | EAST CLAYDON GSP | BICESTER NORTH | COTTISFORD
Swindon and Wiltshire | Swindon | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Swindon and Wiltshire | Swindon | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Swindon and Wiltshire | Swindon | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Swindon and Wiltshire | Swindon | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | FARINGDON
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | LECHLADE
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 60) | STRATTON
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | DRAKES WAY
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | PARK NORTH
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | PLESSEY Swindon
Swindon and Wiltshire | Swindon | MINETY GSP | STRATTON (2 X 90) | PRESSED STEEL SWINDON SE
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | MANCHESTER ROAD
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | SWINDON
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | TRADING ESTATE
Swindon and Wiltshire | Swindon | MINETY GSP | SWINDON BSP | WOOTTON BASSETT
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | CHISLEDON
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | DORCAN SOUTH
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | QUARRY ROAD
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | TOOTHILL
Swindon and Wiltshire | Swindon | MINETY GSP | TOOTHILL BSP | WROUGHTON
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | MIDDLE WALLOP
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | THRUXTON
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Swindon and Wiltshire | Wiltshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | MANNINGTON BSP | ROCKBOURNE
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | BEMERTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | HOMINGTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | NETHERHAMPTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | PETERSFINGER
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | REDLYNCH
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | SALISBURY CENTRAL
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | STAPLEFORD
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SALISBURY | TEFFONT
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | BOURTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | MINCHINGTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHAFTESBURY
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | SHROTON
Swindon and Wiltshire | Wiltshire | MANNINGTON GSP | SHAFTESBURY BSP | TISBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | ENFORD
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | PARK HOUSE
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | AMESBURY | PEWSEY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | ALDERTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | CALNE
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | COCKLEBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | LYNEHAM
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | MALMESBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | ROWDEN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | SUTTON BENGER
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | TETBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | CHIPPENHAM | YATTON KEYNALL
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | BRUTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | CODFORD
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | CROCKERTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | FROME
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | HAWKERIDGE
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | HOLWELL
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | WARMINSTER
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | FROME BSP | WESTBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | ASHTON PARK
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | BROMHAM
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | CORSHAM
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | DEVIZES
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | EASTERTON
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | MELKSHAM TOWN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | NORRINGTON | TROWBRIDGE TOWN
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | MARLBOROUGH SOUTH
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | TIDWORTH
Swindon and Wiltshire | Wiltshire | MELKSHAM GSP | WEST GRAFTON | WEST GRAFTON VILLAGE
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | CIRENCESTER TOWN
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | CRICKLADE
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | FAIRFORD
Swindon and Wiltshire | Wiltshire | MINETY GSP | CIRENCESTER BSP | MINETY VILLAGE
Swindon and Wiltshire | Wiltshire | MINETY GSP | STRATTON (2 X 60) | SHRIVENHAM
Swindon and Wiltshire | Wiltshire | MINETY GSP | STRATTON (2 X 60) | STANTON FITZWARREN
Swindon and Wiltshire | Wiltshire | MINETY GSP | SWINDON BSP | SWINDON
Swindon and Wiltshire | Wiltshire | MINETY GSP | SWINDON BSP | WOOTTON BASSETT
Swindon and Wiltshire | Wiltshire | MINETY GSP | TOOTHILL BSP | CHISLEDON
Swindon and Wiltshire | Wiltshire | MINETY GSP | TOOTHILL BSP | TOOTHILL
Swindon and Wiltshire | Wiltshire | MINETY GSP | TOOTHILL BSP | WROUGHTON
Swindon and Wiltshire | Wiltshire | NURSLING GSP | ROWNHAMS | ROMSEY
Swindon and Wiltshire | Wiltshire | NURSLING GSP | WINCHESTER | DUNBRIDGE
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | EASTHAMPSTEAD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | CAMBERLEY
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | KINGS RIDE
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD
Thames Valley Berkshire | Bracknell Forest | BRAMLEY (FLEE) | WOKINGHAM BSP | PEACOCK FARM
Thames Valley Berkshire | Bracknell Forest | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Thames Valley Berkshire | Bracknell Forest | LALEHAM | STAINES | EGHAM
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | KIDMORE END
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | READING
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING BSP | SILVER STREET
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING TOWN BSP | CAVERSHAM
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Thames Valley Berkshire | Reading | BRAMLEY (FLEE) | READING TOWN BSP | THE MALL
Thames Valley Berkshire | Reading | MELKSHAM GSP | AMESBURY | BOSCOMBE DOWN
Thames Valley Berkshire | Reading | MINETY GSP | CIRENCESTER BSP | WHITEWAY
Thames Valley Berkshire | Slough | IVER 132KV | CHALVEY BSP | CHALVEY
Thames Valley Berkshire | Slough | IVER 132KV | CHALVEY BSP | PETERSFIELD AVENUE
Thames Valley Berkshire | Slough | IVER 132KV | LONGFORD | POYLE
Thames Valley Berkshire | Slough | IVER 132KV | SLOUGH | FARNHAM ROYAL
Thames Valley Berkshire | Slough | IVER 132KV | SLOUGH | TAPLOW
Thames Valley Berkshire | Slough | IVER 132KV | UPTON BSP | SUTTON LANE
Thames Valley Berkshire | Slough | IVER 132KV | UPTON BSP | UPTON
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | ANDOVER BSP | HURSTBOURNE TARRANT
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BALL HILL
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | BEENHAM
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | HUNGERFORD
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINGSCLERE
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | KINTBURY
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LAMBOURN
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LECKHAMPSTEAD
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | LOVE LANE
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | RIVERSIDE
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | ST JOHNS
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | TADLEY
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | THATCHAM
Thames Valley Berkshire | West Berkshire | BRAMLEY (ANDO-THAT) | THATCHAM BSP | YATTENDON
Thames Valley Berkshire | West Berkshire | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | KENTWOOD HILL
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD MAIN | WILSON ROAD
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | GORING
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | MORTIMER
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PADWORTH
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | PANGBOURNE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | SOUTHCOTE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | THEALE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | BURGHFIELD RESERVE | WOODCOTE
Thames Valley Berkshire | West Berkshire | BRAMLEY (FLEE) | READING TOWN BSP | READING TOWN
Thames Valley Berkshire | West Berkshire | COWLEY GSP | DRAYTON BSP | CHOLSEY
Thames Valley Berkshire | West Berkshire | COWLEY GSP | DRAYTON BSP | WANTAGE
Thames Valley Berkshire | West Berkshire | MELKSHAM GSP | WEST GRAFTON | RAMSBURY
Thames Valley Berkshire | West Berkshire | MINETY GSP | CIRENCESTER BSP | WHITEWAY
Thames Valley Berkshire | Windsor and Maidenhead | AMERSHAM | LOUDWATER BSP | WELL END
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | ASCOT
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL MAIN | WARFIELD
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | BAGSHOT
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | CHOBHAM
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | M V E E
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | BRACKNELL RESERVE | SUNNINGHILL
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | BRAYWICK ROAD
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | CORDWALLIS
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | MAIDENHEAD
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | READING BSP | HENLEY
Thames Valley Berkshire | Windsor and Maidenhead | BRAMLEY (FLEE) | READING BSP | TWYFORD
Thames Valley Berkshire | Windsor and Maidenhead | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Thames Valley Berkshire | Windsor and Maidenhead | COWLEY GSP | HIGH WYCOMBE BSP | LITTLE MARLOW
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | CHALVEY BSP | CHALVEY
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | CIPPENHAM | CLARENCE ROAD
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | LONGFORD | POYLE
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | SLOUGH | TAPLOW
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | UPTON BSP | SUTTON LANE
Thames Valley Berkshire | Windsor and Maidenhead | IVER 132KV | UPTON BSP | UPTON
Thames Valley Berkshire | Windsor and Maidenhead | LALEHAM | STAINES | CAUSEWAY
Thames Valley Berkshire | Windsor and Maidenhead | LALEHAM | STAINES | EGHAM
Thames Valley Berkshire | Wokingham | BRAMLEY (BASI) | BASINGSTOKE T1B & T2B | ARBORFIELD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | BRACKNELL MAIN | BRACKNELL
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | BURGHFIELD MAIN | COURAGES
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | BURGHFIELD RESERVE | TRASH GREEN
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | CAMBERLEY MAIN | CROWTHORNE
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | CAMBERLEY MAIN | SANDHURST
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | COXMOOR WOOD BSP | HITCHES LANE
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | MAIDENHEAD BSP | KNOWL HILL
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | MAIDENHEAD BSP | TEMPLE FARM
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | HENLEY
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | LITTLE HUNGERFORD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | NORTHUMBERLAND AVENUE
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | READING
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | SILVER STREET
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | READING BSP | TWYFORD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | WOKINGHAM BSP | ELMS ROAD
Thames Valley Berkshire | Wokingham | BRAMLEY (FLEE) | WOKINGHAM BSP | WOKINGHAM
Thames Valley Berkshire | Wokingham | COWLEY GSP | HIGH WYCOMBE BSP | CHISBRIDGE
Thames Valley Berkshire | Wokingham | MINETY GSP | CIRENCESTER BSP | WHITEWAY
West of England | Bath and North East Somerset | MELKSHAM GSP | NORRINGTON | BRADFORD-ON-AVON
West of England | Bath and North East Somerset | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
West of England | South Gloucestershire | MELKSHAM GSP | CHIPPENHAM | ALDERTON
West of England | South Gloucestershire | MELKSHAM GSP | NORRINGTON | SPRING QUARRY WEST
| Data Centre ESA | BRAMLEY (FLEE) | READING BSP | HENLEY
Solent | Portsmouth | LOVEDEAN GSP | FAREHAM T1A T2A (90MVAS) | BROCKHURST
Solent | Southampton | FAWLEY GSP | LANGLEY BSP | BUTTS ASH
| BSP ESA | MELKSHAM GSP | FROME BSP | FROME
| BSP ESA | COWLEY GSP | HEADINGTON BSP | HEADINGTON
Oxfordshire LEP | Cherwell | LALEHAM | EAST BEDFONT A | NORTH FELTHAM
Oxfordshire LEP | Cherwell | COWLEY GSP | COWLEY LOCAL (2 X 90) | ROSE HILL
Oxfordshire LEP | Cherwell | COWLEY GSP | WITNEY BSP | WINDRUSH PARK